## PUBLIC_CIP Violations
Region | Registered Entity | NCR_ID | NERC Violation ID # | Notice of Confirmed Violation or Settlement Agreement | Description of the Violation | Reliability Standard | Req. | Violation Risk Factor | Violation Severity Level | Risk Assessment | Violation Start Date | Violation End Date | Total Penalty or Sanction ($) | Method of Discovery | Description of Mitigation Activity | Mitigation Completion Date | Date Regional Entity Verified Completion of Mitigation | "Admits" "Neither Admits nor Denies" "Agrees and Stipulates to the Facts" or "Does Not Contest" | Factors Affecting the Penalty and Other Considerations
Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2012009757 | Notice of Confirmed Violation | MRO_URE1 submitted a Self-Report to MRO stating that, it was in violation of CIP-006-1 R1 because it discovered that its Physical Security Plan was not approved by a senior manager as required by its corporate CIP cyber security policy. To mitigate this issue, a full review of the MRO_URE1 Physical Security Plan was performed. While conducting the review, MRO_URE1 discovered that a required six-wall Physical Security Perimeter (PSP) was not established at a control center. MRO_URE1 also identified two other non-continuous six-wall barriers at two different facilities. Each PSP opening was greater than 96 square inches. One facility had motion detectors, which are monitored by security personnel; however, the motion detectors were not documented as "alternative measures," as required by CIP-006-1 R1.1. MRO_URE1's other facility also did not have continuous six-wall barriers, and there were no alternative measures in place. Two rooms had walls that did not extend above the dropped ceiling. Additionally, one room had large openings in a concrete block wall above the ceiling tiles. All openings were remediated through installation of wire mesh fencing material. | CIP-006-1 | R1 | Medium | Severe | This violation posed a moderate risk and not a serious or substantial risk to the reliability of the bulk power system. Approximately 150 individuals had physical access to the PSP for one facility while an additional 676 individuals only had access to the building containing the PSP. The facility was manned continuously and thus, provided monitoring and detection of unauthorized access. At the other facility, one room was continuously manned, but the other room was not. The alternative measures (motion detectors) were a mitigating control for a non-continuous six-wall barrier. The fact that the measures were not previously documented resulted in a documentation deficiency issue. Additionally, although the Physical Security Plan was not initially approved by the senior manager, it was reviewed and updated at least annually. | When the Standard became mandatory and enforceable on MRO_URE1 | Mitigation Plan completion | 15000 | Self-Certification | To mitigate this violation, MRO_URE1: 1) performed a full PSP inspection on all MRO_URE1 NERC CIP Cyber Assets; 2) updated its physical security policy on findings from the physical security inspections; and 3) closed any gaps discovered to ensure a continuous six-wall border. | 2012-09-25 | 2012-10-30 | Admits | MRO reviewed MRO_URE1's internal compliance program and considered it to be a mitigating factor in the penalty determination.
Midwest Reliability Organization (MRO) | Unidentified Registered Entity 2 (MRO_URE2) | NCRXXXXX | MRO201100439 | Settlement Agreement | During a Spot Check, MRO discovered that MRO_URE2 failed to require that each password has a combination of alpha, numeric, and "special" characters as required by CIP-007-1 R5.3.2. MRO_URE2's policy states that passwords must contain three of the following categories: upper case letters, lower case letters, and special characters (any nonletter or number, such as ! @ # * <), and/or numbers. However, upon reviewing password settings on several devices, MRO discovered that the operating system's default setting was used and the setting did not meet the CIP-007 R5.3.2 requirements on complexity settings. More specifically, MRO discovered that one device was not enabled for password complexity settings and another device had system limitations which did not allow it to systematically enforce password requirements. MRO_URE2 had not submitted a Technical Feasibility Exception (TFE) for the device with system limitations. Additionally, MRO discovered that passwords were not changed annually as required by R5.3.3. Specifically, MRO_URE2 failed to change passwords annually on multiple separate accounts. Of those multiple accounts, some were domain administrative accounts, administrative accounts on Front End Processors (FEPs), administrative accounts on Inter-Control Center Communications Protocol (ICCP) servers, and administrative accounts on Supervisory Control and Data Acquisition (SCADA) servers. The FEPs and SCADA servers are the devices used to monitor and control the bulk power system (BPS) and serve as the interface between field devices and the Energy Management System (EMS). The remaining accounts were non-administrative accounts on EMS servers, as well as accounts on MRO_URE2's system used for testing, but no BPS control and system used to retrieve historical operating data. These administrative accounts were also shared accounts, with access being granted to different individuals at the entity. Some of the devices had accounts with passwords that had not been changed since 2009. | CIP-007-1 | R5.3; R5.3.2; R5.3.3 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the BPS. MRO determined that this violation posed a moderate risk because it affected a substantial number of separate accounts. The lack of secure passwords could have resulted in unauthorized access to the devices on which these shared administrative accounts resided. The risk to the reliability of the BPS was mitigated because all the affected devices, including the domain controllers, are within the protected Electronic Security Perimeter (ESP). In addition, all of the individuals with shared access to the administrative accounts had proper cybersecurity training and personnel risk assessments. Furthermore, MRO_URE2 did not experience any cyber incidents during this period. | When the Standard became mandatory and enforceable on MRO_URE2 | Mitigation Plan completion | $10,000 (for MRO201100439, MRO2012009156, and MRO2012010180) | Spot Check | To mitigate this violation, MRO_URE2: 1) set password complexity to meet the complexity requirements of CIP-007-3 R5.3.2; 2) revised its cybersecurity policy to reflect specific password complexity requirements of CIP-007-3 R5.3.2; 3) disabled defunct accounts that were overlooked in the access reviews; 4) researched use of operating system custom password filters to supplement the directory service default password complexity; 5) documented and submitted TFE requests for devices with technical limitations that do not support enforcement of the password control requirements of R5.3; 6) revised the cybersecurity training program to emphasize specific password complexity requirements of CIP-007-3 R5.3.2; and 7) reset local account passwords to ensure they meet the requirements of CIP-007-3 R5.3. | 2012-03-26 | 2012-07-31 | Admits | MRO did not consider MRO_URE2's internal compliance program in the penalty determination. Also, MRO determined that the concurrently filed violation of CIP-007-1 R5 (MRO2012010180) should not serve as an aggravating factor in penalty determination because it occurred concurrently with the instant violation. Additionally, MRO_URE2 completed or will complete the following above and beyond measures, which MRO considered as a mitigating factor in the penalty determination: 1) MRO_URE2 will hire an external consultant to provide a professional and knowledgeable perspective on the configuration of MRO_URE2’s security appliances that define and protect the Electronic Security Perimeter. This expertise will include reviewing the following configurations: a) intrusion detection system management; b) system information and event management; c) adaptive security appliance; and d) firewall services module. In reviewing these configurations, the consultant: will identify any ports or services that are not essential for providing effective security configuration for the environment; assess virtual local area network, firewall services, and security event management configurations for optimal protection of the ESP; provide additional insight and scrutiny in identifying any potential vulnerabilities; and assist with the complex configuration of the existing intrusion detection module which will enhance detection of intrusion attempts and provide defense in depth for the ESP environment. The services are anticipated to be conducted over a 40 hour consulting period; and 2) MRO_URE2 will purchase vulnerability port scan software including physical servers. MRO_URE2 currently uses another type of scan software and manual assessment of results. The new scanning tool will reduce the potential for human error by automating performance. Currently, MRO_URE2 manually performs an annual review of the ports and services assessment. The vulnerability port scan software will be automated to periodically perform this assessment and the tool can be customized to conduct analytic comparisons to identify changes that a subject matter expert can further investigate to enhance and improve the security and reliability of the CIP environment.
Midwest Reliability Organization (MRO) | Unidentified Registered Entity 2 (MRO_URE2) | NCRXXXXX | MRO2012010180 | Settlement Agreement | This violation was discovered by MRO during verification of MRO_URE2's certification of Mitigation Plan completion for another violation of CIP-007-1 R5 (NERC Violation ID MRO201100439). MRO discovered that technical controls for the automatic expiration of passwords were not enabled for one device. MRO_URE2 submitted its access policy platform appliances' configuration in an effort to show completion of mitigation for MRO201100439. Upon MRO's recommendation, MRO_URE2 submitted a Self-Report to MRO stating that it had a violation of CIP-007-1 R5 for failing to implement technical controls that ensure annual password changes. While updating technical password complexity requirements on its access policy platform appliance, MRO_URE2 discovered that an option to enable restricted password duration was inadvertently left unchecked. Consequently, no technical control was implemented to enforce annual password changes for this appliance as required by R5.3.3. | CIP-007-1 | R5.3; R5.3.3 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The access policy platform appliance only has a few individuals with access to it. Both of those individuals have appropriate personnel risk assessments and are current with cybersecurity training as required by the Standards. Additionally, although MRO_URE2 did not implement technical control, it did have procedural controls such as internal processes with annual reminders to change passwords, which meet the requirements of CIP-007 R5.3.3. | When the Standard became mandatory and enforceable on MRO_URE2 | Mitigation Plan completion | $10,000 (for MRO201100439, MRO2012009156, and MRO2012010180) | Self-Report | To mitigate this violation, MRO_URE2, upon discovering the violation, enabled the password lifetime option on the access policy platform appliance to enforce systematically the password change requirements of CIP-007-3 R5.3.3. | 2012-03-26 | 2012-07-31 | Admits | MRO did not consider MRO_URE2's internal compliance program in the penalty determination. Also, MRO determined that the concurrently filed violation of CIP-007-1 R5 (MRO2012010180) should not serve as an aggravating factor in penalty determination because it occurred concurrently with the instant violation. Additionally, MRO_URE2 completed or will complete the following above and beyond measures, which MRO considered as a mitigating factor in the penalty determination: 1) MRO_URE2 will hire an external consultant to provide a professional and knowledgeable perspective on the configuration of MRO_URE2’s security appliances that define and protect the Electronic Security Perimeter. This expertise will include reviewing the following configurations: a) intrusion detection system management; b) system information and event management; c) adaptive security appliance; and d) firewall services module. In reviewing these configurations, the consultant: will identify any ports or services that are not essential for providing effective security configuration for the environment; assess virtual local area network, firewall services, and security event management configurations for optimal protection of the ESP; provide additional insight and scrutiny in identifying any potential vulnerabilities; and assist with the complex configuration of the existing intrusion detection module which will enhance detection of intrusion attempts and provide defense in depth for the ESP environment. The services are anticipated to be conducted over a 40 hour consulting period; and 2) MRO_URE2 will purchase vulnerability port scan software including physical servers. MRO_URE2 currently uses another type of scan software and manual assessment of results. The new scanning tool will reduce the potential for human error by automating performance. Currently, MRO_URE2 manually performs an annual review of the ports and services assessment. The vulnerability port scan software will be automated to periodically perform this assessment and the tool can be customized to conduct analytic comparisons to identify changes that a subject matter expert can further investigate to enhance and improve the security and reliability of the CIP environment.
Midwest Reliability Organization (MRO) | Unidentified Registered Entity 2 (MRO_URE2) | NCRXXXXX | MRO2012009156 | Settlement Agreement | MRO_URE2 submitted a Self-Report to MRO stating that it had a violation of CIP-006-1 R1.1 because its Physical Security Perimeter (PSP) was not completely enclosed within a "six-wall" border and no documented alternative measures were deployed. MRO_URE2 identified areas of the PSP above ceiling tiles that were not fully enclosed to the solid ceiling. MRO_URE2 personnel subsequently completed a review of the PSP and identified openings in the PSP large enough to constitute a deficiency in the complete six-wall border of the PSP. When MRO_URE2 originally constructed additional barriers from the top of solid walls to the solid ceiling in the area above dropped ceilings to create a complete six-wall security perimeter, the barrier was not extended fully from the existing solid wall to the solid ceiling in the areas identified. Therefore, openings existed above the dropped ceiling where the solid surface wall did not extend completely to the solid surface ceiling. Because the dropped ceiling kept this area from view, it was not identified until HVAC work required access to the area. | CIP-006-1 | R1; R1.1 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). MRO determined that the violation posed a moderate risk because although the PSP is located within a secured building, there were large gaps and the violation duration was almost two and a half years. While most of the individuals with approved access to the PSP are MRO_URE2 employees, some individuals were contractors such as janitorial staff. Additionally, not all of the individuals with access to the secured building had approved access to the PSP. The risk to the BPS was mitigated because, for the duration of the violation, the secured building was staffed 24 hours per day, seven days per week. | When the Standard became mandatory and enforceable on MRO_URE2 | Mitigation Plan completion | $10,000 (for MRO201100439, MRO2012009156, and MRO2012010180) | Self-Report | To mitigate this violation, MRO_URE2: 1) implemented additional security measures to reinforce security awareness and physical access controls; 2) heightened awareness messages sent to affected personnel; 3) configured main external entrances to building for continuous authentication; 4) conducted a comprehensive review of the PSPs to assess compliance with the requirements of CIP-006-3 R1.1, and acceptable opening dimensions; and 5) closed identified gaps in the PSP and installed restrictions in ductwork that traverse the perimeter boundaries. | 2011-12-22 | 2012-06-13 | Admits | MRO did not consider MRO_URE2's internal compliance program in the penalty determination.
Northeast Power Coordinating Council, Inc. (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2011008334 | Notice of Confirmed Violation | NPCC_URE1 submitted a Self-Report to NPCC stating that it had a violation of CIP-005-1 R2.2 because NPCC_URE1 did not complete all of the activities required by CIP-005-3 R2.2 for one firewall and one switch. Specifically, NPCC_URE1 failed to complete assessment and documentation for the review of ports and services for the firewall and the switch. | CIP-005-1 | R2.2 | Medium | Moderate | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. All of the devices were protected by Electronic Security Perimeter (ESP) and Physical Security Perimeter (PSP) systems. The devices resided within a PSP and all individuals were required to have an authorized access card per CIP-004 for entry or be escorted per CIP-006. The switch resided within an ESP protected by a firewall that is monitored per CIP-005-1 R4 and only authorized personnel per CIP-004 requirements had access to the ESP. In addition, risk was also mitigated because of network isolation, which prevented exposure of the device to untrusted networks, including the internet and business network. Finally, all personnel authorized for unescorted physical and electronic access were trained on the requirements of CIP-007 R5. | When the Standard became mandatory and enforceable on NPCC_URE1 | Mitigation Plan completion | $50,000 (for NPCC2011008340, NPCC2011008340, NPCC2012009745, NPCC2012009937, and NPCC2012010466) | Self-Report | To mitigate this violation, NPCC_URE1: 1) established the baseline of ports and services of the firewall and switch in question to verify that only ports and services required for operation are enabled; 2) created unique device identifiers for each device for ease of tracking data collection; 3) revised procedure for configuring firewalls and switches to provide improved guidance to network engineering personnel responsible for the processing of ports and services; and 4) trained engineering personnel on the revised procedure. | 2011-11-02 | 2013-02-04 | Does Not Contest | NPCC reviewed NPCC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
Northeast Power Coordinating Council, Inc. (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2011008340 | Notice of Confirmed Violation | NPCC_URE1 submitted a Self-Report to NPCC stating that it had a violation of CIP-007-1 R2.1 and R2.2 because NPCC_URE1 failed to meet the requirements of the Standard for one firewall and one switch. Although NPCC_URE1 established, documented, and implemented a process to ensure that only ports and services required for normal and emergency operations were enabled, the process failed to have complete assessment and documentation for the review of ports and services for the firewall and the switch. | CIP-007-1 | R2.2 | Medium | Moderate | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. All of these devices were protected by Electronic Security Perimeter (ESP) and Physical Security Perimeter (PSP) systems. The devices resided within a PSP. All individuals were required to have an authorized access card per CIP-004-1 requirements for entry into the PSP or were required be escorted per CIP-006-1. The switch resided within an ESP which was protected by a firewall. The ESP was monitored per CIP-005-1 R4 and only authorized personnel per CIP requirements have access to the ESP. Network isolation prevented exposure of the devices to untrusted networks, including the internet and business network. In addition, all personnel authorized for unescorted physical and electronic access were trained annually on the requirements of CIP-007 R5. | When the Standard became mandatory and enforceable on NPCC_URE1 | Mitigation Plan completion | $50,000 (for NPCC2011008340, NPCC2011008340, NPCC2012009745, NPCC2012009937, and NPCC2012010466) | Self-Report | To mitigate this violation, NPCC_URE1: 1) established the baseline of ports and services of the firewall and switch in question to verify that only ports and services required for operation are enabled; 2) created unique device identifiers for each device for ease of tracking data collection; 3) revised the procedure for configuring firewalls and switches to provide improved guidance to network engineering personnel responsible for the processing of ports and services; and 4) trained engineering personnel on the revised procedure. | 2011-11-02 | 2013-02-04 | Does Not Contest | NPCC reviewed NPCC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
Northeast Power Coordinating Council, Inc. (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2012009745 | Notice of Confirmed Violation | NPCC_URE1 submitted a Self-Report to NPCC stating that it had a violation of CIP-004-3 R4.1 because an employee that retired from the company did not have his access to Critical Cyber Assets (CCAs) revoked within seven days of his last day of employment. The revocation of the employee's access was not completed until nine days after his retirement date. | CIP-004-3 | R4; R4.1 | Lower | Moderate | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The employee's access and identification (ID) card was turned in to the plant on the employee's last day on-site. The employee cannot access the Physical Security Perimeter containing all CCAs without the access and ID card. Also, the revocation of the employee's access was completed in nine days, two days after the required date. | When NPCC_URE1 was required to revoke access to the CCAs | When NPCC_URE1 revoked access to the CCAs | $50,000 (for NPCC2011008340, NPCC2011008340, NPCC2012009745, NPCC2012009937, and NPCC2012010466) | Self-Report | To mitigate this violation, NPCC_URE1: 1) identified and trained a designated backup gate keeper to assure authorized availability to revoke access; 2) revised the site process document to include responsibility for taking possession of physical access card from employee on last day of employment; 3) modified the termination notification process from human resources to generate a work order to the site gate keeper and designated backup to revoke access; and 4) modified termination procedure to initiate a reminder on open termination tickets after 48 hours. | 2012-04-02 | 2013-01-11 | Does Not Contest | NPCC reviewed NPCC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
Northeast Power Coordinating Council, Inc. (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2012009937 | Notice of Confirmed Violation | On March 17, 2012, NPCC_URE1 submitted a Self-Report to NPCC stating that, as a Generator Owner and as a Generator Operator, it had a violation of CIP-007-3 R5.3.3. Two administrative passwords were not changed within the annual period as defined by its parent company for certain devices as required by the Standard. | CIP-007-3 | R5; R5.3.3 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. NPCC_URE1 had a designated site gatekeeper, who is the only employee that administers authorized access to the devices. The gatekeeper is responsible for issuing passwords to authorized personnel. Also, these devices resided within a Physical Security Perimeter (PSP). All individuals were required to have authorized access cards per CIP-004-3 requirements for entry into the PSP or were required to be escorted per CIP-006-3. All devices resided within an Electronic Secure Perimeter (ESP) protected by a firewall that is monitored per CIP-005-3 R4. Only authorized personnel per CIP-004-3 had access to the ESP. Network isolation prevented exposure of device to untrusted networks, including the Internet and business network. | When the passwords should have been changed | When the passwords were changed | $50,000 (for NPCC2011008340, NPCC2011008340, NPCC2012009745, NPCC2012009937, and NPCC2012010466) | Self-Report | To mitigate this violation, NPCC_URE1: 1) changed the administrator password for certain devices; 2) cataloged the accounts with passwords for use with future annual password changes and created vulnerability script to run twice a year to verify password age; 3) changed the current compliance activity frequency for password changes to semi-annually; and 4) added language to check password age. | 2012-03-19 | 2013-01-11 | Does Not Contest | NPCC reviewed NPCC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
Northeast Power Coordinating Council, Inc. (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2012010466 | Notice of Confirmed Violation | During an on-site Compliance Audit, NPCC discovered that NPCC_URE1 was in violation of CIP-007-3 R3.1. NPCC_URE1 did not document the assessment of security patches and security upgrades for applicability for three personal computers and one switch within 30 calendar days as required by CIP-007-3 R3.1. | CIP-007-3 | R3; R3.1 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. All of these devices were protected by the Electronic Security Perimeter (ESP) and Physical Security Perimeter (PSP) systems. The devices resided within a PSP. All individuals were required to have an authorized access card per CIP-004-3 requirements for entry into the PSP or were required to be escorted per CIP-006-3. The switch resided within an ESP protected by a firewall that is monitored per CIP-005-3 R4. Only authorized personnel per CIP-004-3 requirements had access to the ESP. Network isolation prevented exposure of the device to untrusted networks, including the internet and business network. In addition, all personnel that were authorized for unescorted physical and electronic access were trained annually on the requirements of CIP-007-3. | When NPCC_URE1 was required to document the assessment of security patches and security upgrades | Mitigation Plan completion | $50,000 (for NPCC2011008340, NPCC2011008340, NPCC2012009745, NPCC2012009937, and NPCC2012010466) | Compliance Audit | To mitigate this violation NPCC_URE1: 1) created unique device identifiers for each device for ease of tracking data collection; 2) created a master spreadsheet of all third-party applications; 3) created a guidance document to maintain ongoing compliance assessment and implementation using the master spreadsheet; 4) trained personnel on the use of the guidance document; 5) tested applicable patches from assessment stage using the established process; and 6) documented and deployed the applicable patches to production. | 2012-07-02 | 2013-02-04 | Does Not Contest | NPCC reviewed NPCC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
Northeast Power Coordinating Council, Inc. (NPCC) | Unidentified Registered Entity 2 (NPCC_URE2) | NCRXXXXX | NPCC2011008438 | Notice of Confirmed Violation | NPCC_URE2 submitted a Self-Report to NPCC stating that it was in violation of CIP-005-1 R2.2 because it failed to document, individually or by specified grouping, the configuration of ports and services required for operation and for monitoring Cyber Assets within the Electronic Security Perimeter (ESP) for one firewall. A CIP management program had been established, documented, and implemented per CIP-005-1 R2, however, not all of the activities to meet requirements of CIP-005-1 R2.2 were completed for one firewall. These deficiencies were incomplete assessment and documentation for review of ports and services for the firewall. | CIP-005-1 | R2.2 | Medium | Moderate | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. All of the devices were protected by ESP and Physical Security Perimeter (PSP) systems. The devices resided within a PSP and all individuals were required to have an authorized access card per CIP-004 for entry or be escorted per CIP-006. In addition, risk was also mitigated because of network isolation, which prevented exposure of the device to untrusted networks, including the internet and business network. Finally, all personnel authorized for unescorted physical and electronic access were trained on the requirements of CIP-007 R5. | When the Standard became mandatory and enforceable on NPCC_URE2 | Mitigation Plan completion | $10,000 (for NPCC2011008438, NPCC2011008439, and NPCC2011008440) | Self-Report | To mitigate this violation, NPCC_URE2: 1) established the baseline of ports and services of the firewall and switch in question to verify that only ports and services required for operation are enabled; 2) created unique device identifiers for each device for ease of tracking data collection; 3) revised the procedure for configuring firewalls and switches to provide improved guidance to network engineering personnel responsible for the processing of ports and services; and 4) trained engineering personnel on the revised procedure. | 2011-12-22 | 2013-02-05 | Does Not Contest | NPCC reviewed NPCC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
Northeast Power Coordinating Council, Inc. (NPCC) | Unidentified Registered Entity 2 (NPCC_URE2) | NCRXXXXX | NPCC2011008439 | Notice of Confirmed Violation | NPCC_URE2 submitted a Self-Report to NPCC stating that it was in violation of CIP-007-1 R2.2 because it failed to disable ports and services not required for normal and emergency operations, including those used for testing purposes, prior to production use of all Cyber Assets inside the Electronic Security Perimeter (ESP). A CIP management program had been established, documented, and implemented per CIP-007-1 R2, however, not all of the activities to meet CIP-007-1 R2.2 were completed. The deficiencies included incomplete assessment and documentation for review of ports and services for the switches, programmable logic controllers (PLCs), and media converters. More than 15% of total Cyber Assets within the ESP were affected by this violation. | CIP-007-1 | R2.2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. All of the devices were protected by the ESP and Physical Security Perimeter (PSP) systems. The devices resided within a PSP and all individuals were required to have an authorized access card per CIP-004 for entry or be escorted per CIP-006. In addition, the risk was also mitigated because of network isolation, which prevented exposure of the devices to untrusted networks, including the internet and business network. Finally, all personnel authorized for unescorted physical and electronic access were trained on the requirements of CIP-007 R5. | When the Standard became mandatory and enforceable on NPCC_URE2 | Mitigation Plan completion | $10,000 (for NPCC2011008438, NPCC2011008439, and NPCC2011008440) | Self-Report | To mitigate this violation, NPCC_URE2: 1) established the baseline of ports and services of the firewall and switch in question to verify that only ports and services required for operation are enabled; 2) created unique device identifiers for each device for ease of tracking data collection; 3) revised procedure for configuring firewalls and switches to provide improved guidance to network engineering personnel responsible for the processing of ports and services; and 4) trained engineering personnel on the revised procedure. | 2011-12-22 | 2013-02-06 | Does Not Contest | NPCC reviewed NPCC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
Northeast Power Coordinating Council, Inc. (NPCC) | Unidentified Registered Entity 2 (NPCC_URE2) | NCRXXXXX | NPCC2011008440 | Notice of Confirmed Violation | NPCC_URE2 submitted a Self-Report to NPCC stating that it was in violation of CIP-007-1 R3.1 because it did not document the assessment of security patches and security upgrades for applicability for personal computers (PCs), network switches, programmable logic controllers (PLCs), and media converters within 30 calendar days. In addition, it was in violation of CIP-007-1 R3.2 because of incomplete documentation for the implementation of security patches for the operating system of the network switches. | CIP-007-1 | R3.1; R3.2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The devices were protected by the Electronic Security Perimeter (ESP) protected by a firewall and were monitored per CIP-005 requirements. The devices resided in a Physical Security Perimeter (PSP) which is secured with a card access system as per CIP-006 requirements. Additionally, network isolation prevented exposure of devices to untrusted networks. Finally, review determined that there were no intrusions during the violation period. | When the Standard became mandatory and enforceable on NPCC_URE2 | Mitigation Plan completion | $10,000 (for NPCC2011008438, NPCC2011008439, and NPCC2011008440) | Self-Report | To mitigate this violation, NPCC_URE2: 1) created unique device identifiers for each device for ease of tracking data collection; 2) established a master spreadsheet of all third party applications, including patch levels for all PC assets, PLC patches for all assets, media converter patches for all assets; 3) formed a guidance document to maintain ongoing compliance assessment and implementation using the master spreadsheet; 4) trained personnel on the use of the guidance document; and 5) tested applicable patches from assessment stage using established process and documented and deployed to production. | 2012-07-08 | 2013-02-06 | Does Not Contest | NPCC reviewed NPCC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
Northeast Power Coordinating Council, Inc. (NPCC) | Unidentified Registered Entity 3 (NPCC_URE3) | NCRXXXXX | NPCC2012009111 | Notice of Confirmed Violation | NPCC_URE3 submitted a Self-Report to NPCC stating that it was in violation of CIP-005-3 R2.2 because it failed to document, individually or by specified grouping, the configuration of ports and services required for operations and for monitoring of Cyber Assets within the Electronic Security Perimeter (ESP). Not all the activities required by the Standard were completed for seven firewalls and one personal computer (PC). NPCC_URE3 failed to complete the assessment and documentation for review of ports and services for the firewalls and the PC. | CIP-005-1 | R2.2 | Medium | Moderate | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. All of the devices were protected by ESP and Physical Security Perimeter (PSP) systems. The devices resided within a PSP secured with a card access system per CIP-006-3 requirements. Network isolation prevented exposure of the devices to untrusted networks, including the internet and business network. Finally, a review determined that there were no intrusions during the violation period. | When the Standard became mandatory and enforceable on NPCC_URE3 | Mitigation Plan completion | $30,000 (for NPCC2012009111, NPCC2012009112, NPCC2012009119, NPCC2012009120, NPCC2012009121, NPCC2012009122, NPCC2011008476, and NPCC2011008477) | Self-Report | To mitigate this violation, NPCC_URE3: 1) reviewed the ports and services of the seven firewalls and PC in question to verify that only ports and services required for operation were enabled; 2) created unique device identifiers for each device for ease of tracking data collection; 3) revised the procedure for configuring firewalls and switches to provide improved guidance to network engineering personnel responsible for the processing of ports and services; and 4) trained the engineering personnel on the revised procedure. | 2011-12-08 | 2013-03-05 | Does Not Contest | NPCC reviewed NPCC_URE3's internal compliance program (ICP) and considered it to be a mitigating factor in assessing the penalty.
Northeast Power Coordinating Council, Inc. (NPCC) | Unidentified Registered Entity 3 (NPCC_URE3) | NCRXXXXX | NPCC2012009112 | Notice of Confirmed Violation | NPCC_URE3 submitted a Self-Report to NPCC stating that it was in violation of NERC CIP-007-1 R2.2 because it failed to disable ports and services not required for normal and emergency operations, including those used for testing purposes, prior to production use of all Cyber Assets inside the Electronic Security Perimeter (ESP). NPCC_URE3 failed to complete the activities required for 12 switches, 20 programmable logic controllers (PLCs), 2 personal computers (PCs), 2 remote terminal units (RTUs), 10 demand meters, 9 card-reader interfaces, 1 network attached storage drive, and 2 media converters. The deficiencies included incomplete assessment and documentation for review of ports and services for the switches, PLCs, PCs, RTUs, demand meters, card-reader interfaces, network attached storage drive, and media converters. | CIP-007-1 | R2.2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. All of the devices were protected by ESP and Physical Security Perimeter (PSP) systems. The devices resided within a PSP secured with a card access system per CIP-006-3 requirements. Network isolation prevented exposure of the devices to untrusted networks, including the internet and business network. Finally, a review determined that there were no intrusions during the violation period. | When the Standard became mandatory and enforceable on NPCC_URE3 | Mitigation Plan completion | $30,000 for NPCC2012009111, NPCC2012009112, NPCC2012009119, NPCC2012009120, NPCC2012009121, NPCC2012009122, NPCC2011008476, and NPCC2011008477) | Self-Report | To mitigate this violation, NPCC_URE3: 1) established the baseline of ports and services of the firewall and switch in question to verify that only ports and services required for operation were enabled; 2) created unique device identifiers for tracking data collection; 3) revised the procedure for configuring firewalls and switches to provide improved guidance to network engineering personnel responsible for the processing of ports and services; and 4) trained the engineering personnel on the revised procedure. | 2012-10-01 | 2013-02-07 | Does Not Contest | NPCC reviewed NPCC_URE3's internal compliance program (ICP) and considered it to be a mitigating factor in assessing the penalty.
Northeast Power Coordinating Council, Inc. (NPCC) | Unidentified Registered Entity 3 (NPCC_URE3) | NCRXXXXX | NPCC2012009119 | Notice of Confirmed Violation | NPCC_URE3 submitted a Self-Report to NPCC stating that it was in violation of CIP-007-1 R3.1 because it failed to document the assessment of security patches and security upgrades according to the Standard. NPCC_URE3 did not complete the assessment of security patches and security upgrades for 8 programmable logic controllers (PLCs), 12 switches, 10 demand meters, 9 card-reader interfaces, 1 network hard drive, and 2 remote terminal units within the 30 calendar day requirement. Also, there was insufficient documentation to determine whether ports and services were originally disabled. NPCC_URE3 also failed to provide complete documentation for the implementation of security patches on the operating systems of the network switches, as required by CIP-007-1 R3.2. | CIP-007-1 | R3.1; R3.2 | Medium | Moderate | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. All of the devices were protected by Electronic Security Perimeter (ESP) and Physical Security Perimeter (PSP) systems. The devices within the ESP were protected by a firewall and were monitored per CIP-005 requirements. Network isolation prevented exposure of these devices to untrusted networks, including internet and business networks. Finally, review determined that there were no intrusions during the violation period. | When the Standard became mandatory and enforceable on NPCC_URE3 | Mitigation Plan completion | $30,000 (for NPCC2012009111, NPCC2012009112, NPCC2012009119, NPCC2012009120, NPCC2012009121, NPCC2012009122, NPCC2011008476, and NPCC2011008477) | Self-Report | To mitigate this violation, NPCC_URE3: 1) created unique device identifiers for tracking data collection; 2) established a master spreadsheet of all third party applications; 3) formed a guidance document to maintain ongoing compliance assessment and implementation using the master spreadsheet; 4) trained personnel on the using the guidance document; and 5) tested applicable patches from the assessment stage using an established process of documenting and deploying to production. | 2012-08-06 | 2013-03-04 | Does Not Contest | NPCC reviewed NPCC_URE3's internal compliance program (ICP) and considered it to be a mitigating factor in assessing the penalty.
Northeast Power Coordinating Council, Inc. (NPCC) | Unidentified Registered Entity 3 (NPCC_URE3) | NCRXXXXX | NPCC2012009120 | Notice of Confirmed Violation | NPCC_URE3 submitted a Self-Report to NPCC stating that it was in violation of CIP-007-1 R4 because anti-virus and anti-malware software was not tested and applied for one personal computer (PC) that performs monitoring, alerting, and logging functions. | CIP-007-1 | R4.1; R4.2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Network isolation prevented exposure to untrusted networks, including the internet and business network. This device was protected by the Electronic Security Perimeter (ESP) protected by a firewall and was monitored per CIP-005 requirements. The device was configured with trend micro office scan. The device resides in a Physical Security Perimeter (PSP), and the PSP is secured with a card access system as per CIP-006 requirements. Finally, review determined that there were no intrusions during the violation period. | When the Standard became mandatory and enforceable on NPCC_URE3 | Mitigation Plan completion | $30,000 (for NPCC2012009111, NPCC2012009112, NPCC2012009119, NPCC2012009120, NPCC2012009121, NPCC2012009122, NPCC2011008476, and NPCC2011008477) | Self-Report | To mitigate this violation, NPCC_URE3: 1) created unique device identifiers for tracking data collection; 2) applied and updated anti-virus and anti-malware for the PC; and 3) provided evidence that anti-virus and anti-malware are being properly maintained and tested. | 2012-11-15 | 2013-03-05 | Does Not Contest | NPCC reviewed NPCC_URE3's internal compliance program (ICP) and considered it to be a mitigating factor in assessing the penalty.
Northeast Power Coordinating Council, Inc. (NPCC) | Unidentified Registered Entity 3 (NPCC_URE3) | NCRXXXXX | NPCC2012009121 | Notice of Confirmed Violation | NPCC_URE3 submitted a Self-Report to NPCC stating that it was in violation of CIP-007-1 R5.1.1 and R5.1.3 because there was no documentation to show that monitoring, alerting and logging devices were managed as required by the Standard. One personal computer (PC), 2 remote terminal units (RTU), nine DSX land cards, 11 ION demand meters (IED) and 20 programmable logic controllers (PLC) devices did not have factory default passwords changed in accordance with CIP-007 R5.2.1; and one PC, 20 PLC, 2 RTU, and 11 IED devices did not have documentation to show that the passwords were updated in the intervals as required by CIP-007-1 R5.3.3. | CIP-007-1 | R5.1; R5.1.1; R5.1.3; R5.2; R5.2.1; R5.3; R5.3.3 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. All of the devices were protected by Electronic Security Perimeter (ESP) and Physical Security Perimeter (PSP) systems. All devices within the ESP were protected by a firewall and were monitored per CIP-005 requirements. The devices resided within a PSP and all individuals were required to have an authorized access card per CIP-006. A Site Keeper, must verify that proper credentials are in place before granting electronic local or remote interactive access to Critical Cyber Assets (CCAs) or unescorted physical access to CCAs. Finally, all personnel authorized for unescorted physical and electronic access were trained on the requirements of CIP-007 Requirement 5. | When the Standard became mandatory and enforceable on NPCC_URE3 | Mitigation Plan completion | $30,000 (for NPCC2012009111, NPCC2012009112, NPCC2012009119, NPCC2012009120, NPCC2012009121, NPCC2012009122, NPCC2011008476, and NPCC2011008477) | Self-Report | To mitigate this violation, NPCC_URE3: 1) created unique device identifiers for tracking data collection; 2) changed all existing administrator passwords; 3) created a process to run vulnerability script twice per year to verify password age; and 4) changed the frequency for password changes to biannually to assure compliance with CIP-007. | 2012-09-04 | 2013-03-07 | Does Not Contest | NPCC reviewed NPCC_URE3's internal compliance program (ICP) and considered it to be a mitigating factor in assessing the penalty.
Northeast Power Coordinating Council, Inc. (NPCC) | Unidentified Registered Entity 3 (NPCC_URE3) | NCRXXXXX | NPCC2012009122 | Notice of Confirmed Violation | NPCC_URE3 submitted a Self-Report to NPCC stating that, as a Generator Owner and as a Generator Operator, it was in violation of CIP-007-1 R6.5 because a monitoring, alerting and logging device was not managed according to the Standard. Logs were generated but not reviewed on a regular basis for one personal computer. | CIP-007-1 | R6.5 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to reliability of the bulk power system (BPS). The risk posed to the reliability of the BPS was mitigated by the fact that this issue was a documentation issue. This device did not control any other devices. The device resided within an Electronic Security Perimeter protected by firewall and network isolation prevented exposure of this device to untrusted networks. The device was previously configured with symantec endpoint protection that provided additional cybersecurity. Finally, review of the logs showed normal activity for the violation period. | When the Standard became mandatory and enforceable on NPCC_URE3 | Mitigation Plan completion | $30,000 (for NPCC2012009111, NPCC2012009112, NPCC2012009119, NPCC2012009120, NPCC2012009121, NPCC2012009122, NPCC2011008476, and NPCC2011008477) | Self-Report | To mitigate this violation, NPCC_URE3: 1) reviewed logs and set an initial baseline date for review; and 2) established a procedure for reviewing logs from the alerting and logging devices to ensure compliance with CIP-007. | 2011-12-19 | 2013-03-08 | Does Not Contest | NPCC reviewed NPCC_URE3's internal compliance program (ICP) and considered it to be a mitigating factor in assessing the penalty.
Northeast Power Coordinating Council, Inc. (NPCC) | Unidentified Registered Entity 3 (NPCC_URE3) | NCRXXXXX | NPCC2011008476 | Notice of Confirmed Violation | NPCC_URE3 submitted a Self-Report to NPCC stating that it was in violation of CIP-006-3c R5 because the telephone line failed at an unmanned blackstart unit. The line was from the unit to the remote control room. The loss of the communication line affected two functions: real-time alarm monitoring capabilities were lost from the unit to the remote control room, and the ability to quick-start the unit remotely was lost. The loss of monitoring lasted until an operator manned the station. | CIP-006-3c | R5 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). While the alarm capability was lost for the time period, the unit still had functional physical access controls because the access control systems were still activated. In addition, logging capabilities were still functional and showed no intrusions during the period. The loss of monitoring was for approximately seven hours. | When NPCC_URE3's unit lost real-time alarm capability at the unit | Mitigation Plan completion | $30,000 for NPCC2012009111, NPCC2012009112, NPCC2012009119, NPCC2012009120, NPCC2012009121, NPCC2012009122, NPCC2011008476, and NPCC2011008477) | Self-Report | To mitigate this violation, NPCC_URE3: 1) reviewed and updated the procedure for operator response when there is a loss of communication to the remote site; 2) trained control room operators on their responsibility to notify the appropriate entities when communication to a remote site is lost; and 3) added a backup line to the remote sites to reduce the chance of remote communication malfunction. | 2011-11-29 | 2013-03-06 | Does Not Contest | NPCC reviewed NPCC_URE3's internal compliance program (ICP) and considered it to be a mitigating factor in assessing the penalty.
Northeast Power Coordinating Council, Inc. (NPCC) | Unidentified Registered Entity 3 (NPCC_URE3) | NCRXXXXX | NPCC2011008477 | Notice of Confirmed Violation | NPCC_URE3 submitted a Self-Report to NPCC stating that it was in violation of TOP-002-2a R14.1 because NPCC_URE3 failed to notify the appropriate entities of a change in real and reactive capabilities as required by the Standard. A telephone line failed at an unmanned blackstart unit. Since the line failed, NPCC_URE3 was unable to remote start the unit. The blackstart unit was later manned for local dispatch. The result was no real-time alarm monitoring capability for the unit. The loss of communication may have also affected the availability of the unit, but the control room operator did not notify Operations that the unit's availability had been affected by the loss. Therefore the appropriate entities were not promptly notified that the unit could not be quick-started remotely. Operations was notified by the on-call person upon arrival at the unit to change availability to "available for dispatch." The appropriate entities were later notified that the unit was available for verbal dispatch. | TOP-002-2a | R14.1 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The loss of communication made the unit unavailable for quick-start and the appropriate entity was unaware of the condition. The condition was for a short period at which time the station was manned and the appropriate entity was notified of the loss of communication and could order the unit dispatched manually through Operations. | When NPCC_URE3 failed to notify appropriate entity of changes in real output capability | Mitigation Plan completion | $30,000 (for NPCC2012009111, NPCC2012009112, NPCC2012009119, NPCC2012009120, NPCC2012009121, NPCC2012009122, NPCC2011008476, and NPCC2011008477) | Self-Report | To mitigate this violation, NPCC_URE3: 1) reviewed and updated the procedure for operator response when there is a loss of communication to the remote site; 2) trained control room operators on their responsibility to notify the appropriate entities when communication to a remote site is lost; and 3) added a backup line to the remote sites to reduce the chance of remote communication malfunction. | 2011-11-29 | 2013-03-06 | Does Not Contest | NPCC reviewed NPCC_URE3's internal compliance program (ICP) and considered it to be a mitigating factor in assessing the penalty.
Northeast Power Coordinating Council, Inc. (NPCC) | Unidentified Registered Entity 4 (NPCC_URE4) | NCRXXXXX | NPCC2012009113 | Notice of Confirmed Violation | NPCC_URE4 submitted a Self-Report to NPCC stating that it was in violation of CIP-005 R2.2 because it failed to complete assessments and provide documentation for a review of ports and services for one firewall and one personal computer (PC). | CIP-005-1 | R2.2 | Medium | Moderate | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. All of the devices were protected by Electronic Security Perimeter (ESP) and Physical Security Perimeter (PSP) systems. The devices resided within a PSP secured with a card access system per CIP-006-3 requirements. Network isolation prevented exposure of the devices to untrusted networks, including the internet and business network. Finally, a review determined that there were no intrusions during the violation period. | When the Standard became mandatory and enforceable on NPCC_URE4 | Mitigation Plan completion | $25,000 for NPCC2012009113, NPCC2012009114, NPCC2012009115, NPCC2012009116, NPCC2012009117, and NPCC2012009118) | Self-Report | To mitigate this violation, NPCC_URE4: 1) reviewed the ports and services of the firewall and PC in question to verify that only ports and services required for operation were enabled; 2) created unique device identifiers for each device for ease of tracking data collection; 3) revised the procedure for configuring firewalls and switches to provide improved guidance to network engineering personnel responsible for the processing of ports and services; and 4) trained engineering personnel on the revised procedure. | 2012-04-26 | 2013-03-04 | Does Not Contest | NPCC reviewed NPCC_URE4's internal compliance program (ICP) and considered it to be a mitigating factor in assessing the penalty.
Northeast Power Coordinating Council, Inc. (NPCC) | Unidentified Registered Entity 4 (NPCC_URE4) | NCRXXXXX | NPCC2012009114 | Notice of Confirmed Violation | NPCC_URE4 submitted a Self-Report to NPCC stating that it was in violation of CIP-007-1 R2.2 because it failed to complete assessments and provide documentation for a review of ports and services for fifteen percent several of it's Cyber Assets, including two switches, one programmable logic controller (PLC), seven personal computers (PCs), and one media converter. | CIP-007-1 | R2.2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. All of the devices were protected by Electronic Security Perimeter (ESP) and Physical Security Perimeter (PSP) systems. The devices resided within a PSP secured with a card access system per CIP-006-3 requirements. Network isolation prevented exposure of the devices to untrusted networks, including the internet and business network. Finally, a review determined that there were no intrusions during the violation period. | When the Standard became mandatory and enforceable on NPCC_URE4 | Mitigation Plan completion | $25,000 for NPCC2012009113, NPCC2012009114, NPCC2012009115, NPCC2012009116, NPCC2012009117, and NPCC2012009118) | Self-Report | To mitigate this violation, NPCC_URE4: 1) established the baseline of ports and services of the firewall and switch in question to verify that only ports and services required for operation were enabled 2) created unique device identifiers for each device for ease of tracking data collection; 3) revised the procedure for configuring firewalls and switches to provide improved guidance to network engineering personnel responsible for the processing of ports and services; and 4) trained engineering personnel on the revised procedure. | 2012-05-31 | 2013-02-07 | Does Not Contest | NPCC reviewed NPCC_URE4's internal compliance program (ICP) and considered it to be a mitigating factor in assessing the penalty.
Northeast Power Coordinating Council, Inc. (NPCC) | Unidentified Registered Entity 4 (NPCC_URE4) | NCRXXXXX | NPCC2012009115 | Notice of Confirmed Violation | NPCC_URE4 submitted a Self-Report to NPCC stating that it was in violation of CIP-007-1 R3.1 and R3.2 because it did not perform the assessment of security patches and upgrades for one equipment including a programmable logic controller (PLC), 2 switches, and seven personal computers (PCs) within 30 calendar days of availability, as required by CIP-007-1 R3.1. NPCC_URE4 also failed to provide complete documentation for the assessment of security patches on the operating systems of the network switches, as required by CIP-007-1 R3.2. | CIP-007-1 | R3.1; R3.2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. All of the devices were protected by Electronic Security Perimeter (ESP) and Physical Security Perimeter (PSP) systems. The devices within the ESP were protected by a firewall and were monitored per CIP-005 requirements. Network isolation prevented exposure of these devices to untrusted networks, including internet and business networks. Finally, review determined that there were no intrusions during the violation period. | When the Standard became mandatory and enforceable on NPCC_URE4 | Mitigation Plan completion | $25,000 for NPCC2012009113, NPCC2012009114, NPCC2012009115, NPCC2012009116, NPCC2012009117, and NPCC2012009118) | Self-Report | To mitigate this violation, NPCC_URE4: 1) created unique device identifiers for each device for ease of tracking data collection; 2) created a master spreadsheet of all third party applications; 3) formed a guidance document to maintain ongoing compliance assessment and implementation using the master spreadsheet; 4) trained personnel on the use of the guidance document; and 5) tested applicable patches from assessment stage using established processes documented all results and deployed to production in a manner that minimized risk to the BPS. | 2012-08-06 | 2013-03-04 | Does Not Contest | NPCC reviewed NPCC_URE4's internal compliance program (ICP) and considered it to be a mitigating factor in assessing the penalty.
Northeast Power Coordinating Council, Inc. (NPCC) | Unidentified Registered Entity 4 (NPCC_URE4) | NCRXXXXX | NPCC2012009116 | Notice of Confirmed Violation | NPCC_URE4 submitted a Self-Report to NPCC stating that it was in violation of CIP-007-1 R4.1 and R4.2 because it failed to test and apply anti-virus and anti-malware software to one personal computer (PC) that performs monitoring, alerting, and logging functions. | CIP-007-1 | R4.1; R4.2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. This device was protected by the Electronic Security Perimeter (ESP) protected by a firewall and was monitored per CIP-005 requirements. The device resides in a Physical Security Perimeter (PSP) and the PSP is secured with a card access system as per CIP-006 requirements. The device was previously configured with third-party software. Finally, review determined that there were no intrusions during the violation period. | When the Standard became mandatory and enforceable on NPCC_URE4 | Mitigation Plan completion | $25,000 for NPCC2012009113, NPCC2012009114, NPCC2012009115, NPCC2012009116, NPCC2012009117, and NPCC2012009118) | Self-Report | To mitigate this violation, NPCC_URE4: 1) created unique device identifiers for each device for ease of tracking data collection; 2) applied and updated anti-virus and anti-malware for the PC; and 3) provided evidence that anti-virus and anti-malware were being properly maintained and tested. | 2012-11-15 | 2013-03-05 | Does Not Contest | NPCC reviewed NPCC_URE4's internal compliance program (ICP) and considered it to be a mitigating factor in assessing the penalty.
Northeast Power Coordinating Council, Inc. (NPCC) | Unidentified Registered Entity 4 (NPCC_URE4) | NCRXXXXX | NPCC2012009117 | Notice of Confirmed Violation | NPCC_URE4 submitted a Self-Report to NPCC stating it was in violation of CIP-007-1 R5 because it failed to produced documentation showing that the monitoring, alerting and logging device was properly managed as required by CIP-007-1 R5.1.1 and R5.1.3. Additionally, the monitoring, alerting, and logging device, one PLC, and one media converter did not have factory default passwords changed in accordance with CIP-007 R5.2.1 and passwords changed in the intervals as required by R5.3.3. | CIP-007-1 | R5.1; R5.1.1; R5.1.3; R5.2; R5.2.1; R5.3; R5.3.3 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. All of the devices were protected by Electronic Security Perimeter (ESP) and Physical Security Perimeter (PSP) systems. All devices within the ESP were protected by a firewall and were monitored per CIP-005 requirements. The devices resided within a PSP and all individuals were required to have an authorized access card per CIP-006. A Site Keeper must verify that proper credentials are in place before granting electronic local or remote interactive access to CCAs or unescorted physical access to CCAs. Finally, all personnel authorized for unescorted physical and electronic access were trained on the requirements of CIP-007 Requirement 5. | When the Standard became mandatory and enforceable on NPCC_URE4 | Mitigation Plan completion | $25,000 for NPCC2012009113, NPCC2012009114, NPCC2012009115, NPCC2012009116, NPCC2012009117, and NPCC2012009118) | Self-Report | To mitigate this violation, NPCC_URE4: 1) created unique device identifiers for each device for ease of tracking data collection; 2) changed all existing administrator passwords; 3) created a process to run a vulnerability script twice a year to verify password age; 4) changed passwords for all affected devices; and 5) changed frequency for password change to bi-annual to assure compliance with CIP-007. | 2012-09-17 | 2013-03-07 | Does Not Contest | NPCC reviewed NPCC_URE4's internal compliance program (ICP) and considered it to be a mitigating factor in assessing the penalty.
Northeast Power Coordinating Council, Inc. (NPCC) | Unidentified Registered Entity 4 (NPCC_URE4) | NCRXXXXX | NPCC2012009118 | Notice of Confirmed Violation | NPCC_URE4 submitted a Self-Report to NPCC stating it was in violation of CIP-007-1 R6.5 because its monitoring, alerting and logging device had not been managed by site personnel from the onset of its installation. Additionally, logs were being generated but were not being reviewed on a regular basis. | CIP-007-1 | R6.5 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to reliability of the bulk power system (BPS). The risk posed to the reliability of the BPS was mitigated by the fact that this issue was a documentation issue. This device did not control any other devices. The device resided within an ESP protected by firewall and Network isolation that prevented exposure of this device to untrusted networks. The device was previously configured with third-party software that provided additional cyber security. Finally, review of the logs showed normal activity for the violation period. | When the Standard became mandatory and enforceable on NPCC_URE4 | Mitigation Plan completion | $25,000 for NPCC2012009113, NPCC2012009114, NPCC2012009115, NPCC2012009116, NPCC2012009117, and NPCC2012009118) | Self-Report | To mitigate this violation, NPCC_URE4: 1) reviewed logs and set an initial date for a baseline review; and 2) established a procedure for review of logs from the alerting and logging device to assure compliance with CIP-007. | 2012-02-29 | 2013-03-08 | Does Not Contest | NPCC reviewed NPCC_URE4's internal compliance program (ICP) and considered it to be a mitigating factor in assessing the penalty.
ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2012010322 | Settlement Agreement | RFC_URE1 submitted a Self-Report to ReliabilityFirst stating that it was in violation of CIP-006-1 R1. During the 2011 cyber vulnerability assessment, RFC_URE1 discovered that it had only applied operating system patches to its Cyber Assets that authorize and/or log access to the Physical Security Perimeter (PSP) and had not applied application-based patches, as required by CIP-007-3 R3. Although RFC_URE1 had not installed such patches, once RFC_URE1 discovered the issue it quickly remediated the issue. | CIP-006-1 | R1 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). ReliabilityFirst determined that the violation posed a moderate risk because a violation of CIP-006-3c R2.2 that implicates CIP-007 R3 has the potential to affect the reliable operation of the BPS by providing the opportunity for known vulnerabilities to allow infiltration of unauthorized network traffic into the Electronic Security Perimeter that required security patches and upgrades could have prevented. The risk posed by the foregoing facts and circumstances was mitigated by the following factors. The Cyber Assets that authorize and/or log access to the PSP are located on an isolated, firewall-protected network monitored by an intrusion detection system. In addition, RFC_URE1 monitors these systems through an enterprise security information and event management solution that monitors logging from these devices. Furthermore, the Cyber Assets that authorize and/or log access to the PSP have updated anti-virus protection. | When the Standard became mandatory and enforceable to RFC_URE1 | When RFC_URE1 installed all patches | 0 | Self-Report | To mitigate this violation, RFC_URE1: 1) applied all missing security patches and validate that it resolved all vulnerabilities; and 2) transferred cybersecurity and patch management authority to its cybersecurity and critical infrastructure support department to ensure future patching of these devices. | 2012-07-24 | 2013-03-01 | Admits | ReliabilityFirst reviewed RFC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201103027 | Settlement Agreement | WECC_URE1 submitted a Self-Report to WECC stating that it was in violation of CIP-003-1 R1.1 because it had failed to address all the Requirements in Standards CIP-002 through CIP-009 in its cybersecurity policy. Specifically, WECC_URE1 failed to address: CIP-004-1 R4, CIP-005-1 R3, CIP-006-1 R2, CIP-006-1 R3, CIP-007-1 R2, CIP-007-1 R4, CIP-007-1 R6, CIP-009-1 R1, CIP-009-1 R2, CIP-009-1 R3, CIP-009-1 R4, and CIP-009-1 R5. The violation was due to lack of a complete policy map to ensure the controlling polices and procedures addressed all of the CIP-002 through CIP-009 requirements. | CIP-003-1 | R1; R1.1 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although WECC_URE1's Cyber Security Policy did not adequately document a policy map addressing the CIP-002 through CIP-009 requirements, WECC_URE1 stated that all its Critical Cyber Assets (CCAs) are located inside Physical Security Perimeters and Electronic Security Perimeters and are provided the protections specified in CIP-005 and CIP-006. In addition, WECC_URE1 stated that all its employees with access to CCAs are trained as required by CIP-004 R2 and the training program provides a high level overview of the CIP Standards and WECC_URE1's various policies regarding the Reliability Standards. | When the Standard became mandatory and enforceable on WECC_URE1 | Mitigation Plan completion | $53,000 (for WECC2011008640, WECC2011008641, WECC2011008992, WECC2011008993, WECC2011009032, WECC201103026, WECC201103027, WECC201103028, WECC201103029, WECC201103031, WECC201103032, WECC2012010449, and WECC2012010450) | Self-Report | To mitigate this violation, WECC_URE1: 1) completed a thorough policy mapping project; 2) finalized its policy map; 3) updated, reviewed, and approved applicable documentation; and 4) conducted awareness communication to all individuals with cyber or unescorted access to CCAs. | 2011-10-11 | 2012-06-06 | Agrees/ Stipulates | WECC reviewed WECC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201103028 | Settlement Agreement | WECC_URE1 submitted a Self-Report to WECC stating that it was in violation of CIP-003-1 R4 because it had failed to identify its disaster recovery plan as protected information, as required by WECC_URE1's information protection program and the Standard. | CIP-003-1 | R4 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE1's disaster recovery plan was in electronic format only and was protected from unauthorized access. Security measures were in place, including folder share security. Individuals with access to the disaster recovery plan had current training that addressed proper handling of Critical Cyber Asset information. | When the Standard became mandatory and enforceable on WECC_URE1 | Mitigation Plan completion | $53,000 (for WECC2011008640, WECC2011008641, WECC2011008992, WECC2011008993, WECC2011009032, WECC201103026, WECC201103027, WECC201103028, WECC201103029, WECC201103031, WECC201103032, WECC2012010449, and WECC2012010450) | Self-Report | To mitigate this violation, WECC_URE1: 1) updated and classified the disaster recovery plan appropriately; 2) conducted a root cause analysis; and 3) conducted awareness and training on the above corrective actions. | 2011-12-29 | 2012-06-06 | Agrees/ Stipulates | WECC reviewed WECC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201103029 | Settlement Agreement | WECC_URE1 submitted a Self-Report to WECC stating that it was in violation of CIP-004-1 R1 for failing to provide evidence that it provided quarterly refresher security awareness for certain contractors. Specifically, contractors from one company did not receive security awareness updates on a quarterly basis. WECC_URE1’s process for distributing awareness media to these contractors was to email with the awareness media and then use a spreadsheet to track the dates the media was disseminated. The WECC_URE1 employee responsible for tracking awareness reinforcement for these contractors retired. The spreadsheet used to track vendor awareness was located in the employee’s secured home folder, which was inadvertently deleted when she left the company. For this reason, WECC_URE1 could not produce any evidence that would support that awareness media was distributed to these contractors. | CIP-004-1 | R1 | Lower | High | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. All involved individuals had current CIP training and personnel risk assessments. In addition, all devices were in a Physical Security Perimeter and Electronic Security Perimeter, and thus were afforded the protections of CIP-005 and CIP-006 | When the Standard became mandatory and enforceable on WECC_URE1 | Mitigation Plan completion | $53,000 (for WECC2011008640, WECC2011008641, WECC2011008992, WECC2011008993, WECC2011009032, WECC201103026, WECC201103027, WECC201103028, WECC201103029, WECC201103031, WECC201103032, WECC2012010449, and WECC2012010450) | Self-Report | To mitigate this violation, WECC_URE1: 1) re-established formal document detailing security awareness program and security awareness job role functions; 2) created a process to track documentation of indirect communication to contractors to ensure personnel having authorized cyber or authorized unescorted physical access received ongoing security awareness and trained the personnel responsible for this process; and 3) added a section to the applicable monthly status report from the employee responsible for quarterly indirect awareness distribution to the manager documenting completion of duty, thus ensuring management oversight and continuation of duties upon personnel changes. | 2010-09-22 | 2012-04-10 | Agrees/ Stipulates | WECC reviewed WECC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2011008992 | Settlement Agreement | WECC_URE1 submitted a Self-Report to WECC stating that it was in violation of CIP-005-1 R1 because it had failed to identify devices as access points to its Electronic Security Perimeters (ESPs). The devices WECC_URE1 reported are port servers, communication switches, and internal network switches. These devices have externally connected communication end points terminating at devices within the ESP and, as required by CIP 005 R1.1, need to be classified as access points. Additionally, WECC_URE1 reported devices that were not afforded the protections of CIP-005-1 R1.5. Specifically, active directory servers, active control server, intrusion detection system, and security information and event management devices were not afforded the protections of CIP-005-1 R1.5. | CIP-005-1 | R1 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The violation posed a moderate risk because failing to ensure that Cyber Assets used in the access control and monitoring of the ESP are afforded protection measures puts such assets at risk to be manipulated. For instance, if the ports and services required for normal operation of these access control and monitoring assets are not enabled, such ports and services could be utilized to gain unauthorized access to the ESP to go unnoticed and unchecked, potentially allowing malicious access to Cyber Assets contained in the ESP. Such access may then be used to cause harm to Critical Cyber Assets (CCAs) essential to the operation of the BPS, thereby potentially negatively impacting the BPS. The risk was mitigated because all CCAs are located inside an ESP and Physical Security Perimeter and afforded the protections of CIP-005 and CIP-006. The switches in scope are identified and protected as CCAs, and WECC_URE1 only failed to document the switches as access points. Lastly, the active directory servers and active control servers were located in physically secure areas and located in its corporate network which was protected by restrictive firewalls. | When the Standard became mandatory and enforceable on WECC_URE1 | Mitigation Plan completion | $53,000 (for WECC2011008640, WECC2011008641, WECC2011008992, WECC2011008993, WECC2011009032, WECC201103026, WECC201103027, WECC201103028, WECC201103029, WECC201103031, WECC201103032, WECC2012010449, and WECC2012010450) | Self-Report | To mitigate this violation, WECC_URE1 updated its diagrams and inventory lists designating access points to its ESPs. | 2012-07-31 | 2012-08-15 | Agrees/ Stipulates | WECC reviewed WECC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2012010449 | Settlement Agreement | WECC_URE1 submitted a Self-Report to WECC stating that it was in violation of CIP-005-1 R2 because it had failed to update its firewall rules to reflect certain devices that were decommissioned from its network and, as a result, the firewalls were allowing traffic to devices that were no longer on its network. In addition, WECC_URE1 did not have an approved list of ports and services for certain logical access points to its Electronic Security Perimeters (ESPs). WECC_URE1 did have a draft list of approved ports and services; however, the list was never approved by a specific WECC_URE1 director and placed into its document management system as required by WECC_URE1’s procedures. | CIP-005-1 | R2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE1 did have a draft list of required ports and services for all logical access points that was approved by subject matter experts, but not the required director of technology services. All CCAs are protected by an intrusion detection system which will alert on abnormal traffic. All CCAs are within a designated Physical Security Perimeter with restrictive access points which only allows physical access to approved, vetted, and trained individuals. All CCAs had antivirus/malware prevention tools and have unique accounts with strong passwords. Finally, although WECC_URE1 was allowing its network to host traffic, it was only allowing traffic from approved (trusted) networks. | When the Standard became mandatory and enforceable on WECC_URE1 | Mitigation Plan completion | $53,000 (for WECC2011008640, WECC2011008641, WECC2011008992, WECC2011008993, WECC2011009032, WECC201103026, WECC201103027, WECC201103028, WECC201103029, WECC201103031, WECC201103032, WECC2012010449, and WECC2012010450) | Self-Report | To mitigate this violation, WECC_URE1: 1) implemented firewall rules between hosts; 2) removed the network-to-network trust rules; 3) removed unnecessary firewall rules; 4) updated the firewall change processes; 5) required on an ongoing basis a one-year review of rules via the annual Cyber Vulnerability Assessment; 6) established an expiration time for temporary rules; and 7) generated an alert when the time period expires to facilitate timely review and removal of temporary rules. | 2012-11-08 | 2012-12-10 | Agrees/ Stipulates | WECC reviewed WECC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2012010450 | Settlement Agreement | WECC_URE1 submitted a Self-Report to WECC stating that it was in violation of CIP-005-1 R4. WECC_URE1 had deficiencies in its Cyber Vulnerability Assessments (CVAs) for two years. The first year, WECC_URE1 failed to conduct a CVA for logical access points to Electronic Security Perimeters (ESPs). The second year, WECC_URE1 failed to perform a CVA for switches, which are access points to its ESPs. | CIP-005-1 | R4 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The violation posed a moderate risk because a failure to perform a CVA of the electronic access points to the ESPs may allow for unauthorized internal and or external access, which could allow for successful cyber attacks against Critical Cyber Assets (CCAs) essential to the operation of BPS. As compensating measures, WECC_URE1 employs an anomaly-based network intrusion detection system, which will alert upon detecting any abnormal usage of ports and services. In addition, all CCAs implement antivirus/malware prevention tools and have unique accounts and passwords required to gain access. WECC_URE1 also states it monitors and logs all traffic entering the ESP(s) at all times with daily manual reviews of the logs. | When the Standard became mandatory and enforceable on WECC_URE1 | Mitigation Plan completion | $53,000 (for WECC2011008640, WECC2011008641, WECC2011008992, WECC2011008993, WECC2011009032, WECC201103026, WECC201103027, WECC201103028, WECC201103029, WECC201103031, WECC201103032, WECC2012010449, and WECC2012010450) | Self-Report | To mitigate this violation, WECC_URE1: 1) completed the CVA; 2) reviewed the ESP; and 3) documented the results of the review including the process used, the results, and any mitigation steps/resolutions identified in the CVA. | 2012-11-08 | 2013-02-19 | Agrees/ Stipulates | WECC reviewed WECC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201103031 | Settlement Agreement | WECC_URE1 submitted a Self-Report to WECC stating that it was in violation of CIP-006-1 R1 because it had failed to afford certain protections listed in CIP-006-1 R1 to certain of its Cyber Assets used in the access control and monitoring of all of its Physical Security Perimeters (PSPs). The devices are WECC_URE1's application server and database server. Specifically, the CIP-006-1 R1 protections WECC_URE1 failed to afford the devices were: CIP-003-1 R5.2, CIP-004-1 R3, CIP-005-1 R2, CIP-007-1 R2, CIP-007-1 R5, CIP-007-1 R8, CIP-009-1 R1, and CIP-009-1 R4. | CIP-006-1 | R1; R1.8 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The violation posed a moderate risk because the failure to afford the protections in CIP-006-1 R1 to Cyber Assets used in the access control and monitoring of a PSP can hinder an entity's ability to monitor and control access to its PSP, potentially allowing unauthorized individuals access to the PSP. That access can then be used to conduct malicious activities. As compensating measures, WECC_URE1 stated the devices were in a physically secure facility, which is manned and monitored at all times. WECC_URE1 also stated all electronic access to the devices required multi-factor authentication. | When the Standard became mandatory and enforceable on WECC_URE1 | Mitigation Plan completion | $53,000 (for WECC2011008640, WECC2011008641, WECC2011008992, WECC2011008993, WECC2011009032, WECC201103026, WECC201103027, WECC201103028, WECC201103029, WECC201103031, WECC201103032, WECC2012010449, and WECC2012010450) | Self-Report | To mitigate this violation, WECC_URE1: 1) reviewed access privileges for its Physical Access Control (PAC) system; 2) secured computer racks; 3) reviewed ports and services; 4) performed a CIP-004 R4 quarterly audit; and 5) performed a PAC Cyber Vulnerability Assessment. | 2012-08-10 | 2012-12-05 | Agrees/ Stipulates | WECC reviewed WECC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2011008993 | Settlement Agreement | WECC_URE1 submitted a Self-Report to WECC stating that it was in violation of CIP-006-2 R3 because it failed to ensure that certain devices used in the access control and monitoring of its Electronic Security Perimeter (ESP) were located inside a Physical Security Perimeter (PSP). The devices involved in the violation were active directory servers, access control servers (ACS), intrusion detection systems (IDS), and security information and event management devices. These devices are used to monitor users with access to WECC_URE1's ESPs, as well as to grant and verify authentication and authorization of users with access to WECC_URE1's ESPs. | CIP-006-2 | R3 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although the devices were not in a designated PSP, they were provided the protections of CIP 006-2 R4 and R5. All locations were restricted to authorized access by use of card key, and monitored to detect unauthorized access attempts by use of alarm systems and video monitoring. | When the Standard became mandatory and enforceable on WECC_URE1 | Mitigation Plan completion | $53,000 (for WECC2011008640, WECC2011008641, WECC2011008992, WECC2011008993, WECC2011009032, WECC201103026, WECC201103027, WECC201103028, WECC201103029, WECC201103031, WECC201103032, WECC2012010449, and WECC2012010450) | Self-Report | To mitigate this violation, WECC_URE1: 1) installed and configured card readers on its computer racks; 2) established a new management perimeter network environment; and 3) created a PSP for additional devices. | 2012-06-27 | 2012-08-15 | Agrees/ Stipulates | WECC reviewed WECC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201103032 | Settlement Agreement | WECC_URE1 submitted a Self-Report to WECC stating that it was in violation of CIP-007-1 R2 because it had failed to establish and document a process to ensure that only those ports and services required for normal and emergency operations are enabled. WECC_URE1 did use a network mapping scan to view what ports and services were running on all the Cyber Assets within Electronic Security Perimeters (ESPs), but did not document the results of the scan. Additionally, WECC_URE1 did not provide any other evidence that it established and documented a process to ensure that only the ports and services required for normal and emergency operations were enabled. | CIP-007-1 | R2 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The violation posed a moderate risk because failure to ensure that only those ports and services required for normal and emergency operations are enabled may allow for unauthorized internal and/or external access, which could allow for successful cyber attacks against Critical Cyber Assets essential to operation of the BPS. As a compensating measure, WECC_URE1 uses an intrusion detection system, with automated alerting, and manual reviews daily during the work-week, to monitor ports and internal traffic. | When the Standard became mandatory and enforceable on WECC_URE1 | Mitigation Plan completion | $53,000 (for WECC2011008640, WECC2011008641, WECC2011008992, WECC2011008993, WECC2011009032, WECC201103026, WECC201103027, WECC201103028, WECC201103029, WECC201103031, WECC201103032, WECC2012010449, and WECC2012010450) | Self-Report | To mitigate this violation, WECC_URE1 created ports and services processes and documentation. | 2012-05-31 | 2012-07-17 | Agrees/ Stipulates | WECC reviewed WECC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2011009032 | Settlement Agreement | WECC_URE1 submitted a Self-Report to WECC stating that it was in violation of CIP-007-1 R3 because it failed to implement its security patch management program on all of its devices located inside its Electronic Security Perimeters (ESPs). WECC_URE1 was implementing some security patches on 55% of the devices involved, but was not following its documented security patch management program. | CIP-007-1 | R3 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The violation posed a moderate risk because failure to assess security patches could result in vulnerabilities remaining unaddressed for extended periods of time. This increases the risk of a successful cyber attack against Critical Cyber Assets essential to the operation of the BPS. As compensating measures, all devices are located inside ESPs and Physical Security Perimeters, afforded the protections of CIP-005 and CIP-006, and are monitored by a security information and event management protection program. The program logs are reviewed regularly during normal business hours and are configured for automatic alerting upon detecting cybersecurity events. Vulnerability scans are performed regularly on the entity's test system, and all individuals with access to devices located inside ESPs and PSPs have current personnel risk assessments and cybersecurity training. | When the Standard became mandatory and enforceable on WECC_URE1 | Mitigation Plan completion | $53,000 (for WECC2011008640, WECC2011008641, WECC2011008992, WECC2011008993, WECC2011009032, WECC201103026, WECC201103027, WECC201103028, WECC201103029, WECC201103031, WECC201103032, WECC2012010449, and WECC2012010450) | Self-Report | To mitigate this violation, WECC_URE1: 1) enhanced its security patch management procedure to include tracking, gathering, and evaluating patches; 2) expanded security vulnerability threat meetings; and 3) implemented security patches. | 2012-06-21 | 2012-07-20 | Agrees/ Stipulates | WECC reviewed WECC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2011008640 | Settlement Agreement | WECC_URE1 submitted a Self-Report to WECC stating that it was in violation of CIP-007-1 R5 because it had failed to establish, implement, and document technical and procedural controls to ensure passwords consist of a combination of alpha, numeric, and "special" characters. The technical and procedural controls in place required only two of the three criteria specified in the Standard: alpha and numeric characters or alpha and "special" characters. | CIP-007-1 | R5 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE1's password complexity controls require user passwords to be a minimum of eight characters and reset every 60 days. In addition, all remote access requires two-factor authentication and is configured to lockout the user upon five failed login attempts. | When the Standard became mandatory and enforceable on WECC_URE1 | Mitigation Plan completion | $53,000 (for WECC2011008640, WECC2011008641, WECC2011008992, WECC2011008993, WECC2011009032, WECC201103026, WECC201103027, WECC201103028, WECC201103029, WECC201103031, WECC201103032, WECC2012010449, and WECC2012010450) | Self-Report | To mitigate this violation, WECC_URE1: 1) updated its policies and procedures to include annual audit trails; 2) created a logging process; 3) implemented a process to manually log the use of shared accounts; and 4) conducted awareness training for its employees. | 2012-03-30 | 2012-07-17 | Agrees/ Stipulates | WECC reviewed WECC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2011008641 | Settlement Agreement | WECC_URE1 submitted a Self-Report to WECC stating that it was in violation of CIP-007-1 R8 because WECC_URE1 failed to perform a Cyber Vulnerability Assessment (CVA) on all Cyber Assets located in both of its Electronic Security Perimeters (ESPs). The Cyber Assets within the ESPs include workstations, servers, and networking equipment related to the entity's supervisory control and data acquisition (SCADA) system. Specifically, WECC_URE1 identified three failures with respect to its CVA process. First, WECC_URE1 stated that it failed to perform a CVA when the Standard became mandatory and enforceable. Second, WECC_URE1 did not perform a CVA on the Cyber Assets, and instead performed a CVA on the Cyber Assets in its test environment. WECC_URE1's understanding was that, if a testing environment mirrored the production ESP, it could run a CVA on only the Cyber Assets in the test system and, for this reason, WECC_URE1 believed it was not required to conduct a CVA on the Cyber Assets. Finally, the CVA performed did not include a review to verify that only ports and services required for operation of the Cyber Asset within the ESPs are enabled. | CIP-007-1 | R8 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. All devices within the ESPs are monitored with an intrusion detection system that is configured for automated alerting. All devices have antivirus/malware prevention tools software installed and send logs to a centralized log correlation server. | When the Standard became mandatory and enforceable on WECC_URE1 | Mitigation Plan completion | $53,000 (for WECC2011008640, WECC2011008641, WECC2011008992, WECC2011008993, WECC2011009032, WECC201103026, WECC201103027, WECC201103028, WECC201103029, WECC201103031, WECC201103032, WECC2012010449, and WECC2012010450) | Self-Report | To mitigate this violation, WECC_URE1 performed its CVA in accordance with its procedures and documented the results. | 2012-05-31 | 2012-07-17 | Agrees/ Stipulates | WECC reviewed WECC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201103026 | Settlement Agreement | WECC_URE1 submitted a Self-Report to WECC stating that it was in violation of CIP-008-1 R1 because WECC_URE1's incident reporting and response plan (Plan) did not address CIP-008-1 R1.4, R1.5, and R1.6. Specifically, the Plan stipulated that the Plan needed to be updated annually instead of within 90 days as required by R1.4. The Plan also did not include a process for annual review as required by R1.5. Finally, the Plan did not contain a process for testing the Plan as required by R1.6. | CIP-008-1 | R1; R1.4; R1.5; R1.6 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE1's Plan was tested annually, and WECC_URE1 has a small working group responsible for the Plan. Although the processes in scope were not formally documented, the individuals in the working group were familiar with the processes. | When the Standard became mandatory and enforceable on WECC_URE1 | Mitigation Plan completion | $53,000 (for WECC2011008640, WECC2011008641, WECC2011008992, WECC2011008993, WECC2011009032, WECC201103026, WECC201103027, WECC201103028, WECC201103029, WECC201103031, WECC201103032, WECC2012010449, and WECC2012010450) | Self-Report | To mitigate this violation, WECC_URE1: 1) updated its security handling incident procedure to review annually and audit changes; and 2) tested its security incident handling through a full operational exercise. | 2011-10-31 | 2012-04-10 | Agrees/ Stipulates | WECC reviewed WECC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC201103033 | Settlement Agreement | WECC_URE2 submitted a Self-Report to WECC stating that it was in violation of CIP-003-1 R1 because it failed to address all the Requirements in Standards CIP-002 through CIP-009 in its cyber security policy. Specifically, WECC_URE2 failed to address: CIP-004-1 R4, CIP-005-1 R3, CIP-006-1 R2, CIP-006-1 R3, CIP-007-1 R2, CIP-007-1 R4, CIP-007-1 R6, CIP-009-1 R1, CIP-009-1 R2, CIP-009-1 R3, CIP-009-1 R4, and CIP-009-1 R5. The violation was due to the lack of a complete policy map to ensure the controlling polices and procedures addressed all of the CIP-002 through CIP-009 requirements. | CIP-003-1 | R1 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE2 stated that all of its Critical Cyber Assets (CCAs) are located inside Physical Security Perimeters and Electronic Security Perimeters and are provided the protections specified in CIP-005 and CIP-006. In addition, WECC_URE2 stated that all its employees with access to CCAs are trained as required by CIP-004 R2 and the training program provides a high level overview of the CIP Standards, and of WECC_URE2's various policies regarding the Reliability Standards. | When the Standard became mandatory and enforceable on WECC_URE2 | Mitigation Plan completion | $58,000 (for WECC201103025, WECC201103033, WECC201103034, WECC201103035, WECC201103037, WECC201103038, WECC2011008638, WECC2011008639, WECC2011008642, WECC2011008991, WECC2011008994, WECC2011009030, WECC2012010446, and WECC2012010448) | Self-Report | To mitigate this violation, WECC_URE2: 1) finalized its policy map; 2) updated, reviewed, and approved applicable documentation; and 3) conducted awareness communication to all individuals with cyber or unescorted access to CCAs. | 2011-10-11 | 2012-06-06 | Agrees/ Stipulates | WECC reviewed WECC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC201103034 | Settlement Agreement | WECC_URE2 submitted a Self-Report to WECC stating that it was in violation of CIP-003-1 R4 because it had failed to identify its disaster recovery plan as protected information, as required by WECC_URE2's program and the Standard. | CIP-003-1 | R4 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE2's disaster recovery plan was in electronic format only and was protected from unauthorized access. Security measures were in place, including folder share security. Individuals with access to the disaster recovery plan had current training that addressed proper handling of Critical Cyber Asset information. | When the Standard became mandatory and enforceable on WECC_URE2 | Mitigation Plan completion | $58,000 (for WECC201103025, WECC201103033, WECC201103034, WECC201103035, WECC201103037, WECC201103038, WECC2011008638, WECC2011008639, WECC2011008642, WECC2011008991, WECC2011008994, WECC2011009030, WECC2012010446, and WECC2012010448) | Self-Report | To mitigate this violation, WECC_URE2: 1) updated and classified the disaster recovery plan appropriately; 2) conducted a root cause analysis; and 3) conducted awareness and training on the above corrective actions. | 2011-12-29 | 2012-06-06 | Agrees/ Stipulates | WECC reviewed WECC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC201103035 | Settlement Agreement | WECC_URE2 submitted a Self-Report to WECC stating that it was in violation of CIP-004-1 R1 because it had failed to reinforce its security awareness program on at least a quarterly basis, for contractors with authorized cyber or authorized unescorted physical access to Critical Cyber Assets. Specifically, contractors from the Supervisory Control and Data Acquisition (SCADA) vendor did not receive security awareness updates on a quarterly basis. There were six contractors involved with electronic access to the electric reliability center Electronic Security Perimeter (ESP) which contains workstations and servers related to WECC_URE2's SCADA. These contractors did not receive the security awareness reinforcement update in the fourth quarter. In addition, contractors did not receive updated security awareness reinforcement until the next year. There are 11 contractors involved who had authorized unescorted physical access to the electric reliability center and Physical Security Perimeters (PSPs), which contained SCADA workstations, SCADA servers, and Inter-Control Center Communications Protocol servers. | CIP-004-1 | R1 | Lower | High | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. All involved individuals had current CIP training and personnel risk assessments. In addition, all devices were in a Physical Security Perimeter and Electronic Security Perimeter, and thus were afforded the protections of CIP-005 and CIP-006. | When the Standard became mandatory and enforceable on WECC_URE2 | Mitigation Plan completion | $58,000 (for WECC201103025, WECC201103033, WECC201103034, WECC201103035, WECC201103037, WECC201103038, WECC2011008638, WECC2011008639, WECC2011008642, WECC2011008991, WECC2011008994, WECC2011009030, WECC2012010446, and WECC2012010448) | Self-Report | To mitigate this violation, WECC_URE2: 1) re-established formal document detailing security awareness program and security awareness job role functions; 2) created a process to track documentation of indirect communication to contractors to ensure personnel having authorized cyber or authorized unescorted physical access received ongoing security awareness reinforcement, and trained the personnel responsible for this process; and 3) added a section to the applicable monthly status report from the employee responsible for quarterly indirect awareness distribution to the manager documenting completion of duty, thus ensuring management oversight and continuation of duties upon personnel changes. | 2010-09-22 | 2012-04-10 | Agrees/ Stipulates | WECC reviewed WECC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2011008638 | Settlement Agreement | WECC_URE2 submitted a Self-Report to WECC stating that it was in violation of CIP-004-2 R3 because WECC_URE2 failed to ensure one individual had a completed personnel risk assessment (PRA) prior to being granted authorized unescorted physical access to a Physical Security Perimeter (PSP). The PSP contains servers, workstations, and networking equipment comprising its Supervisory Control and Data Acquisition (SCADA) system. The individual was granted access and required physical access as back-up support for WECC_URE2's communications equipment located at a PSP. | CIP-004-2 | R3 | Medium | High | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The individual in scope had completed CIP-004 R2 training and the PSP in scope was manned continuously by operators and monitored continuously by the security operations center. The Critical Cyber Assets in the PSP were protected with intrusion detection software, antivirus, and anti-malware. | When the employee was granted physical access | Mitigation Plan completion | $58,000 (for WECC201103025, WECC201103033, WECC201103034, WECC201103035, WECC201103037, WECC201103038, WECC2011008638, WECC2011008639, WECC2011008642, WECC2011008991, WECC2011008994, WECC2011009030, WECC2012010446, and WECC2012010448) | Self-Report | To mitigate this violation, WECC_URE2: 1) removed the physical access of the individual involved; and 2) completed the PRA. | 2011-10-31 | 2012-03-16 | Agrees/ Stipulates | WECC reviewed WECC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2011008994 | Settlement Agreement | WECC_URE2 submitted a Self-Report to WECC stating that it was in violation of CIP-005-1 R1 because it had failed to identify three types of devices as access points to its Electronic Security Perimeters (ESPs). The devices WECC_URE2 reported are 8 port servers, 2 communication switches, and 6 internal network switches. These devices have externally connected communication end points terminating at devices within the ESP and, as required by CIP-005 R1.1, need to be classified as access points. The port servers and communication switches are located at the perimeter of the defined ESP with one IP routable interface connected inside the ESP and one serially connected interface connected outside of the ESP. The internal switches are located inside the ESP and have IP management interfaces that reside outside of the identified ESP. This connectivity allows devices located outside the ESP to communicate with devices inside the ESP without traversing an identified access point protected as per CIP-005. Additionally, WECC_URE2 reported devices that were not afforded the protections of CIP-005-1 R1.5. Specifically, active directory servers, active control server, intrusion detection system, and security information and event management devices were not afforded the protections of CIP-005-1 R1.5. | CIP-005-1 | R1 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The violation posed a moderate risk because failing to ensure that Cyber Assets used in the access control and monitoring of the ESP are afforded protection measures puts such assets at risk to be manipulated. For instance, if the ports and services required for normal operation of these access control and monitoring assets are not enabled, such ports and services could be utilized to gain unauthorized access to the ESP to go unnoticed and unchecked, potentially allowing malicious access to Cyber Assets contained in the ESP. Such access may then be used to cause harm to Critical Cyber Assets (CCAs) essential to the operation of the BPS, thereby potentially negatively impacting the BPS. The risk was mitigated because all CCAs are located inside an ESP and Physical Security Perimeter and afforded the protections of CIP-005 and CIP-006. The switches in scope are identified and protected as CCAs, and WECC_URE2 only failed to document the switches as access points. Lastly, the active directory servers and active control servers were located in physically secure areas and located in its corporate network which was protected by restrictive firewalls. | When the Standard became mandatory and enforceable on WECC_URE2 | Mitigation Plan completion | $58,000 (for WECC201103025, WECC201103033, WECC201103034, WECC201103035, WECC201103037, WECC201103038, WECC2011008638, WECC2011008639, WECC2011008642, WECC2011008991, WECC2011008994, WECC2011009030, WECC2012010446, and WECC2012010448) | Self-Report | To mitigate this violation, WECC_URE2 updated its diagrams and inventory lists designating access points to the ESPs. | 2012-07-31 | TBD | Agrees/ Stipulates | WECC reviewed WECC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2012010446 | Settlement Agreement | WECC_URE2 submitted a Self-Report to WECC stating that it was in violation of CIP-005-1 R2. WECC conducted a Compliance Audit of WECC_URE2 and reviewed WECC_URE2's Self-Report and determined WECC_URE2 was in violation of the Standard because it failed to ensure that only ports and services required for normal operations were enabled for all Electronic Security Perimeter (ESP) access points. | CIP-005-1 | R2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE2 did have a draft list of required ports and services for all 10 logical (13 physical) access points that was approved by subject matter experts, but not the required director of technology services. All CCAs are protected by an intrusion detection system which will alert on abnormal traffic. All CCAs are within a designated Physical Security Perimeter with restrictive access points which only allows physical access to approved, vetted, and trained individuals. All CCAs had antivirus/malware prevention tools, and have unique accounts with strong passwords. Finally, although WECC_URE2 was allowing its network to host traffic, it was only allowing traffic from approved, trusted networks. | When the Standard became mandatory and enforceable on WECC_URE2 | Mitigation Plan completion | $58,000 (for WECC201103025, WECC201103033, WECC201103034, WECC201103035, WECC201103037, WECC201103038, WECC2011008638, WECC2011008639, WECC2011008642, WECC2011008991, WECC2011008994, WECC2011009030, WECC2012010446, and WECC2012010448) | Self-Report | To mitigate this violation, WECC_URE2: 1) implemented firewall rules; 2) reviewed the rules during the annual Cyber Vulnerability Assessment; 3) required an expiration time for temporary rules; 4) reviewed ports and services; and 5) documented ports and services justification and authentication methods. | 2012-11-08 | 2012-12-21 | Agrees/ Stipulates | WECC reviewed WECC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. WECC did not apply mitigating credit for the Self-Report because WECC_URE2 submitted the Self-Report following the "Notice of Compliance Audit," issued by WECC.
Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2012010448 | Settlement Agreement | WECC_URE2 submitted a Self-Report to WECC stating that it was in violation of CIP-005-1 R4. WECC conducted a Compliance Audit of WECC_URE2 and reviewed WECC_URE2's Self-Report and determined WECC_URE2 was in violation of the Standard because WECC_URE2 failed to perform a complete Cyber Vulnerability Assessment (CVA) of the electronic access points on its Electronic Security Perimeters (ESPs) at certain locations. Specifically, WECC_URE2 failed to fully complete a ports and services review of the following ESPs. In addition, WECC_URE2 failed to discover the access points on the ESPs listed above. Finally, WECC_URE2 did not perform a review of all default accounts, passwords, and network management community strings. | CIP-005-1 | R4 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC determined that the violation posed a moderate risk because failing to perform an annual CVA can result in an entity being unaware of the vulnerabilities on its ESPs or risk the possibility of unidentified vulnerabilities being introduced or exploited. WECC_URE2 did have compensating measures in place. WECC_URE2 had restrictive firewalls, centralized network monitoring, intrusion detection systems, applicable system anti-virus protection, network segmentation, and a monitored physical security infrastructure. | When the Standard became mandatory and enforceable on WECC_URE2 | Mitigation Plan completion | $58,000 (for WECC201103025, WECC201103033, WECC201103034, WECC201103035, WECC201103037, WECC201103038, WECC2011008638, WECC2011008639, WECC2011008642, WECC2011008991, WECC2011008994, WECC2011009030, WECC2012010446, and WECC2012010448) | Self-Report | To mitigate this violation, WECC_URE2: 1) conducted a CVA; 2) reviewed the ESPs; and 3) documented the results, including the process used, the results, and mitigation steps and resolutions identified in the CVA. | 2012-06-29 | 2012-12-21 | Agrees/ Stipulates | WECC reviewed WECC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC201103037 | Settlement Agreement | WECC_URE2 submitted a Self-Report to WECC stating that it was in violation of CIP-006-1 R1 because it had failed to afford certain protections listed in CIP-006-1 R1 to two of its Cyber Assets used in the access control and monitoring of all 13 of its Physical Security Perimeters (PSPs). The two devices are WECC_URE2's application server and database server. Specifically, the CIP-006-1 R1 protections WECC_URE2 failed to afford the devices were: CIP-003-1 R5.2, CIP-004-1 R3, CIP-005-1 R2, CIP-007-1 R2, CIP-007-1 R5, CIP-007-1 R8, CIP-009-1 R1, and CIP-009-1 R4. | CIP-006-1 | R1; R1.8 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The violation posed a moderate risk because the failure to afford the protections in CIP-006-1 R1 to Cyber Assets used in the access control and monitoring of a PSP can hinder an entity's ability to monitor and control access to its PSP, potentially allowing unauthorized individuals access to the PSP. That access can then be used to conduct malicious activities. As compensating measures, WECC_URE2 stated the devices were in a physically secure facility, which is manned and monitored at all times. WECC_URE2 also stated all electronic access to the devices required multi-factor authentication. | When the Standard became mandatory and enforceable on WECC_URE2 | Mitigation Plan completion | $58,000 (for WECC201103025, WECC201103033, WECC201103034, WECC201103035, WECC201103037, WECC201103038, WECC2011008638, WECC2011008639, WECC2011008642, WECC2011008991, WECC2011008994, WECC2011009030, WECC2012010446, and WECC2012010448) | Self-Report | To mitigate this violation, WECC_URE2: 1) reviewed access privileges for its physical access control system; 2) secured computer racks; 3) reviewed WECC_URE2's ports and services; 4) performed a CIP-004 R4 quarterly audit; and 5) performed a physical access control Cyber Vulnerability Assessment. | 2012-08-10 | 2012-12-05 | Agrees/ Stipulates | WECC reviewed WECC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2011008991 | Settlement Agreement | WECC_URE2 submitted a Self-Report to WECC stating that it was in violation of CIP-006-2 R3 because it failed to ensure that certain devices used in the access control and monitoring of its Electronic Security Perimeter (ESP) were located inside a Physical Security Perimeter (PSP). The devices involved in the violation were active directory servers, access control servers (ACS), intrusion detection system (IDS), and security information and event management devices. These devices are used to monitor users with access to WECC_URE2's ESPs, as well as to grant and verify authentication and authorization of users with access to WECC_URE2's ESPs. | CIP-006-2 | R3 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although the devices were not in a designated PSP, they were provided the protections of CIP 006-2 R4 and R5. All locations were restricted to authorized access by use of card key, and monitored to detect unauthorized access attempts by use of alarm systems and video monitoring. | When WECC_URE2 failed to ensure the Cyber Assets involved were located inside a PSP | Mitigation Plan completion | $58,000 (for WECC201103025, WECC201103033, WECC201103034, WECC201103035, WECC201103037, WECC201103038, WECC2011008638, WECC2011008639, WECC2011008642, WECC2011008991, WECC2011008994, WECC2011009030, WECC2012010446, and WECC2012010448) | Self-Report | To mitigate this violation, WECC_URE2: 1) installed and configured card readers on its computer racks; 2) established a new management perimeter network environment; and 3) created a PSP for additional devices. | 2012-06-27 | 2012-08-15 | Agrees/ Stipulates | WECC reviewed WECC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC201103038 | Settlement Agreement | WECC_URE2 submitted a Self-Report to WECC stating that it was in violation of CIP-007-1 R2 because it had failed to establish and document a process to ensure that only those ports and services required for normal and emergency operations are enabled. WECC_URE2 did use a network mapping scan to view that ports and services were running on all the Cyber Assets within Electronic Security Perimeters (ESPs), but did not document the results of the scan. Additionally, WECC_URE2 did not provide any other evidence that it established and documented a process to ensure that only the ports and services required for normal and emergency operations were enabled. | CIP-007-1 | R2 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The violation posed a moderate risk because failure to ensure that only those ports and services required for normal and emergency operations are enabled may allow for unauthorized internal and/or external access, which could allow for successful cyber attacks against Critical Cyber Assets essential to operation of the BPS. As a compensating measure, WECC_URE2 uses an intrusion detection system, with automated alerting, and manual reviews daily during the work-week, to monitor ports and internal traffic. | When the Standard became mandatory and enforceable on WECC_URE2 | Mitigation Plan completion | $58,000 (for WECC201103025, WECC201103033, WECC201103034, WECC201103035, WECC201103037, WECC201103038, WECC2011008638, WECC2011008639, WECC2011008642, WECC2011008991, WECC2011008994, WECC2011009030, WECC2012010446, and WECC2012010448) | Self-Report | To mitigate this violation, WECC_URE2 created ports and services processes and documentation. | 2012-05-31 | 2012-07-10 | Agrees/ Stipulates | WECC reviewed WECC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2011009030 | Settlement Agreement | WECC_URE2 submitted a Self-Report to WECC stating that it was in violation of CIP-007-1 R3 because it failed to implement its security patch management program on all 75 of its devices located inside its five Electronic Security Perimeters (ESPs). WECC_URE2 was implementing some security patches on 55% of the devices involved, but was not following its documented security patch management program. The devices in scope are inter-control center communications protocol servers, energy management system devices, and networking equipment. | CIP-007-1 | R3 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The violation posed a moderate risk because failure to assess security patches could result in vulnerabilities remaining unaddressed for extended periods of time. This increases the risk of a successful cyber attack against Critical Cyber Assets essential to the operation of the BPS. As compensating measures, all devices are located inside ESPs and Physical Security Perimeters, afforded the protections of CIP-005 and CIP-006, and are monitored by a security information and event management protection program. The program logs are reviewed regularly during normal business hours and are configured for automatic alerting upon detecting cybersecurity events. Vulnerability scans are performed regularly on the entity's test system, and all individuals with access to devices located inside ESPs and PSPs have current personnel risk assessments and cybersecurity training. | When the Standard became mandatory and enforceable on WECC_URE2 | Mitigation Plan completion | $58,000 (for WECC201103025, WECC201103033, WECC201103034, WECC201103035, WECC201103037, WECC201103038, WECC2011008638, WECC2011008639, WECC2011008642, WECC2011008991, WECC2011008994, WECC2011009030, WECC2012010446, and WECC2012010448) | Self-Report | To mitigate this violation, WECC_URE2: 1) enhanced its security patch management procedure to include tracking, gathering, and evaluating patches; 2) expanded the scope of security vulnerability threat meetings; and 3) implemented security patches. | 2012-06-21 | 2012-06-28 | Agrees/ Stipulates | WECC reviewed WECC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2011008639 | Settlement Agreement | WECC_URE2 submitted a Self-Report to WECC stating that it was in violation of CIP-007-1 R5 because it had failed to establish, implement, and document technical and procedural controls to ensure passwords consist of a combination of alpha, numeric, and "special" characters. The technical and procedural controls in place required only two of the three criteria specified in the Standard: alpha and numeric characters or alpha and "special" characters. | CIP-007-1 | R5 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE2's password complexity controls require user passwords to be a minimum of eight characters and reset every 60 days. In addition, all remote access requires two-factor authentication and is configured to lockout the user after five failed login attempts. | When the Standard became mandatory and enforceable on WECC_URE2 | Mitigation Plan completion | $58,000 (for WECC201103025, WECC201103033, WECC201103034, WECC201103035, WECC201103037, WECC201103038, WECC2011008638, WECC2011008639, WECC2011008642, WECC2011008991, WECC2011008994, WECC2011009030, WECC2012010446, and WECC2012010448) | Self-Report | To mitigate this violation, WECC_URE2: 1) updated its policies and procedures to include annual audit trails; 2) created a logging process; 3) implemented a process to manually log the use of shared accounts; and 4) conducted awareness training for its employees. | 2012-05-30 | 2012-06-28 | Agrees/ Stipulates | WECC reviewed WECC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2011008642 | Settlement Agreement | WECC_URE2 submitted a Self-Report to WECC stating that it was in violation of CIP-007-1 R8 because WECC_URE2 failed to perform a Cyber Vulnerability Assessment (CVA) on all Cyber Assets located at its Electronic Security Perimeters (ESPs). The Cyber Assets within the ESPs include workstations, servers, and networking equipment related to the entity's supervisory control and data acquisition (SCADA) system. Specifically, WECC_URE2 identified three failures with respect to its CVA process. First, WECC_URE2 stated that it failed to perform a CVA on its ESPs when the Standard became mandatory and enforceable. Second, WECC_URE2 did not perform a CVA on the Cyber Assets in the ESPs, and instead performed a CVA on the Cyber Assets in its test environment for the ESPs. WECC_URE2's understanding was that, if a testing environment mirrored the production ESP, it could run a CVA on only the Cyber Assets in the test system and, for this reason, WECC_URE2 believed it was not required to conduct a CVA on the Cyber Assets ESPs. Finally, one CVA performed did not include a review to verify that only ports and services required for operation of the Cyber Asset within the ESPs are enabled. | CIP-007-1 | R8 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. All devices within the ESPs are monitored with an intrusion detection system that is configured for automated alerting. All devices have antivirus/malware prevention tools software installed, and send logs to a centralized log correlation server. | When the Standard became mandatory and enforceable on WECC_URE2 | Mitigation Plan completion | $58,000 (for WECC201103025, WECC201103033, WECC201103034, WECC201103035, WECC201103037, WECC201103038, WECC2011008638, WECC2011008639, WECC2011008642, WECC2011008991, WECC2011008994, WECC2011009030, WECC2012010446, and WECC2012010448) | Self-Report | To mitigate this violation, WECC_URE2 performed its CVA in accordance with its procedures and documented the results. | 2012-05-31 | 2012-07-10 | Agrees/ Stipulates | WECC reviewed WECC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC201103025 | Settlement Agreement | WECC_URE2 submitted a Self-Report to WECC stating that it was in violation of CIP-008-1 R1 because WECC_URE2's incident reporting and response plan (Plan) did not address CIP-008-1 R1.4, R1.5, and R1.6. Specifically, the Plan stipulated that the Plan needed to be updated annually instead of within 90 days as required by R1.4. The Plan also did not include a process for annual review as required by R1.5. Finally, the Plan did not contain a process for testing the Plan as required by R1.6. | CIP-008-1 | R1; R1.4, R1.5; R1.6 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE2's Plan was tested annually and WECC_URE2 has a small working group responsible for the Plan. Although the processes in scope were not formally documented, the individuals in the working group were familiar with the processes. | When the Standard became mandatory and enforceable on WECC_URE2 | Mitigation Plan completion | $58,000 (for WECC201103025, WECC201103033, WECC201103034, WECC201103035, WECC201103037, WECC201103038, WECC2011008638, WECC2011008639, WECC2011008642, WECC2011008991, WECC2011008994, WECC2011009030, WECC2012010446, and WECC2012010448) | Self-Report | To mitigate this violation, WECC_URE2 updated its Security Handling Incident procedure to review it annually and audit changes every 30 days. | 2011-10-31 | 2012-04-10 | Agrees/ Stipulates | WECC reviewed WECC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2012009100 | Settlement Agreement | WECC_URE3 submitted a Self-Report to WECC stating that it was in violation of CIP-007-1 R3 because there was no process or procedure to implement security patches on some of its network devices. WECC_URE3 failed to document the assessment and implementation of security patches for Cyber Assets within its Electronic Security Perimeters (ESPs). Although WECC_URE3 failed to document the assessment and the implementation of these security patches, WECC_URE3 did assess all security patches. As a result, patches were implemented, but WECC_URE3 failed to document this action. Therefore, WECC determined that WECC_URE3 failed to document the assessment of security patches and security upgrades for applicability within 30 days of availability, as required by CIP-007-1 R3.1. In addition, WECC_URE3 failed to document the implementation of security patches, as required by R3.2. | CIP-007-1 | R3 | Lower | Severe | WECC determined that the violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). WECC determined that the violation posed a moderate risk because a failure to document the assessment of security patches could result in vulnerabilities remaining unaddressed for extended periods of time. The risk was mitigated because the Cyber Assets at issue were located within an ESP and had technical and procedural mechanisms for control of electronic access at all access points. These mechanisms included the enabling of only those ports and services necessary at the access points and on the Cyber Assets. In addition, WECC_URE3 required usernames and passwords on all Cyber Assets and used a continuous monitoring system to monitor changes on the Cyber Assets. In addition, while WECC_URE3 failed to document the assessment and the implementation of these security patches, WECC_URE3 did assess all security patches. As a result, patches were implemented. | When the Standard became mandatory and enforceable on WECC_URE3 | Mitigation Plan completion | $60,000 (for WECC2012009099, WECC2012009100, and WECC2012010375) | Self-Report | To mitigate this violation, WECC_URE3: 1) developed a process flow chart that defines the end-to-end process which describes the steps required to ensure full compliance with the requirements under CIP-007 R3; 2) performed a full review of noncompliance to confirm the scope of the violation; 3) performed a comprehensive review of its existing procedures related to CIP-007 R3 in order to identify any gaps in its existing process; 4) developed and implemented a procedure including controls to monitor compliance and ensure effective escalation of identified issues or concerns for appropriate action; and 5) trained the appropriate personnel on the new CIP-007-1 R3 policies and procedures. | 2012-10-31 | TBD | Agrees/ Stipulates | WECC reviewed WECC_URE3's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2012009099 | Settlement Agreement | WECC_URE3 submitted a Self-Report to WECC stating that it was in violation of CIP-007-1 R5 because it failed to provide account management protections to all Cyber Assets within its Electronic Security Perimeters (ESPs). WECC_URE3 lacked the required account management procedural controls on several workstations, servers, and network devices located within its 50 ESPs. WECC_URE3 did not ensure that a third of its devices' shared accounts had the protections required by CIP-007 R5.1.3, R5.2.1, R5.2.3, and R5.3.3. Specifically, WECC_URE3 failed to: 1) review annually shared accounts to verify access privileges, as required by R5.1.3; 2) remove, disable, or rename accounts where possible, as required by R5.2.1; 3) remove or change the account in the event of personnel changes, as required by R5.2.3; and 4) change passwords at least annually, as required by R5.3.3. | CIP-007-1 | R5; R5.1.3; R5.2.1; R5.2.3; R5.3.3 | Medium | Severe | WECC determined that the violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). WECC determined that the violation posed a moderate risk because WECC_URE3's failure to establish technical and procedural controls to identify and manage shared accounts could have allowed unauthorized access to the Cyber Assets to go unnoticed and unchecked, potentially allowing malicious access to these assets. Such access could then have been used to cause harm to Critical Cyber Assets essential to the operation of the BPS. The shared accounts include administrator, user, and read-only accounts. The administrator accounts provide full system access which allows configuration changes, addition and removal of user accounts, application control, and the starting and stopping of services that are used for the system applications to run properly. A smaller number of the shared accounts provide read-only access which provides limited access to the device and applications. Given the failures described herein, the shared accounts with administrator privileges could have been used by unauthorized personnel to make configuration changes, add unauthorized users to the Cyber Assets within the ESP, and start and stop critical services and applications and potentially misuse the Cyber Assets. Once an unauthorized person has administrator access to a Cyber Asset within the ESP, this person can potentially make changes to the devices and/or applications running, which in turn could impact the reliable operation of those assets which support WECC_URE3's BPS functions. The risk was mitigated because all Cyber Assets were located within an ESP. Additionally, the devices had technical and procedural mechanisms for control of electronic access at all access points, such as enabling only those ports and services necessary at the access points. All of the devices were also located within a Physical Security Perimeter (PSP) and therefore had technical and procedural controls to manage physical access to the PSPs including logging and monitoring of physical access 24 hours a day, seven days a week. Furthermore, WECC_URE3 requires username and passwords on all Cyber Assets and uses a continuous monitoring system to monitor any changes made on the Cyber Assets within the ESPs. | When the Standard became mandatory and enforceable on WECC_URE3 | Mitigation Plan completion | $60,000 (for WECC2012009099, WECC2012009100, and WECC2012010375) | Self-Report | To mitigate this violation, WECC_URE3: 1) performed an assessment to identify an effective strategy to manage passwords not addressed in current standards and processes; 2) performed a detailed review of all accounts within the operational data network (ODN) active directory to identify all accounts that are not related to an individual user; 3) developed and implemented a consolidated process for account access reviews and management of ODN accounts which addresses both user and service shared accounts; 4) produced a detailed list of service or shared accounts which includes who has access to those accounts and what the accounts are used for; 5) modified and/or eliminated accounts or account access as appropriate; 6) performed a review of all users who have any logical access to the ODN by asset area; 7) created a detailed document that establishes the methods, processes and procedures to generate logs of sufficient detail to create historical audit trails of individual user account access activity to all accounts and specific retention requirements; and 8) submitted Technical Feasibility Exceptions as appropriate for passwords that cannot be changed. | 2012-08-31 | TBD | Agrees/ Stipulates | WECC reviewed WECC_URE3's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2012010375 | Settlement Agreement | WECC_URE3 submitted a Self-Report to WECC stating that it was in violation of CIP-007-1 R7. WECC_URE3 did have a process for disposal or redeployment of Cyber Assets within its Electronic Security Perimeters (ESPs); however, this process only tracked assets to destruction. Once storage media was removed from an asset and destroyed, WECC_URE3 did not correlate the destroyed storage media back to the asset it was removed from. Furthermore, WECC_URE3 does not redeploy assets, and as a result, WECC_URE3 was unable to provide evidence of the assets that had been retired. The devices at issue are used to support the supervisory control and data acquisition systems, energy management system, remedial action scheme (RAS), and network and communication equipment. WECC determined that WECC_URE3 failed to have a sufficient security patch management program that documents that it destroyed or erased the data storage media prior to the disposal of a Cyber Asset, as required by CIP-007-1 R7.1, and that documents it erased the data storage media prior to redeployment of a Cyber Asset, as required by R7.2. WECC_URE3 also failed to document that such assets were disposed of or redeployed in accordance with documented procedures, as required by R7.3. | CIP-007-1 | R7 | Lower | Severe | WECC determined that the violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). WECC determined that the violation posed a moderate risk because WECC_URE3's failure to establish controls to dispose of Cyber Assets could allow malicious access to sensitive information related to cybersecurity. Such information could then be used to gain access to Critical Cyber Assets essential to the operation of the BPS. However, the risk was mitigated because the devices at issue were protected through restrictive boundary devices that log and monitor all traffic traveling the ESP. Additionally, WECC_URE3 uses a continuous monitoring system to monitor any changes or configurations that are made to Cyber Assets within the ESPs. | When the Standard became mandatory and enforceable on WECC_URE3 | Present | $60,000 (for WECC2012009099, WECC2012009100, and WECC2012010375) | Self-Report | To mitigate this violation, WECC_URE3: 1) performed an extent of condition evaluation to validate the scope of noncompliance and ensure that non-IT assets (remote terminal units, relays, controllers) are in compliance; 2) completed an assessment and analysis of the existing disposal process; 3) completed and implemented a revised disposal process that includes effective ongoing performance monitoring; and 4) revised its disposal procedure and completed internal reviews of the final processes and procedures prior to the sign-off and submission of the completed Mitigation Plan. | 6/14/2013 (approved completion date) | TBD | Agrees/ Stipulates | WECC reviewed WECC_URE3's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC2011008637 | Settlement Agreement | WECC_URE4 self-reported a violation of CIP-002-1 R3. A few fiber switching devices used to support a fiber channel connection to a storage area network solution (SANS) were found also to be using routable connections within WECC_URE4's control center, which is a Critical Asset. In addition, one modem-connected service processor used in the support and operation of the SANS was found to be dial-up accessible when called from an internal corporate phone extension, and was located within the control center, which is also a Critical Asset. The violation was a result of operational personnel failing, in the process of installing a new SANS in one of WECC_URE4's datacenters, to document the Ethernet connections on the switches, as well as WECC_URE4's SANS documentation not adequately identifying the configuration of WECC_URE4's telephony system. WECC determined that WECC_URE4 was in violation of CIP-002-1 R3.2 (the switches) and R3.3 (the modem-connected service processor) for failing to identify or document appropriately components of SANS as Critical Cyber Assets (CCAs). | CIP-002-1 | R3; R3.2; R3.3 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although WECC_URE4 did not identify these assets as CCAs, WECC_URE4 did have the following compensating measures in place: 1) the fiber switches required terminal access controller access-control system authentication; 2) the fiber switches were located within a Physical Security Perimeter (PSP); 3) those with access to the switches required current personnel risk assessments and CIP cybersecurity training; 4) the modem-connected processor was only accessible from the internal phone system; 5) the modem-connected processor could not be dialed from the outside; 6) the modem-connected processor was located within a PSP; 7) the phone switch that the modem was connected to was configured to dial outbound only; and 8) the modem-connected service processor was configured to dial out only to the SANS vendor. | When the Standard became mandatory and enforceable | Mitigation Plan completion | 4250 | Self-Report | To mitigate this violation, WECC_URE4: 1) updated the change control procedure governing NERC-related CIP Cyber Assets to incorporate new corporate controls to help mitigate the risk of noncompliant changes to NERC environments. These changes included establishing that a member of an IT group will now be included in a corporate advisory board (CAB), which reviews and approves all IT changes at WECC_URE4. The IT security and risk group oversees appropriate IT implementation of compliance associated change controls. The change controls will be routed through the CAB and will not be allowed to be implemented until a sufficient review has been approved by the CAB; 2) documented the SANS completely including all NERC-related and security controls to mitigate the risk that further changes to the solution overlook or omit compliance or security controls; 3) audited for CAB change control samples to validate that item 1 above is mitigating the identified issues as expected; 4) removed CCAs from WECC_URE4’s NERC-related CIP SANS and validated that remaining computer systems are not essential to the operation of WECC_URE4 Critical Assets; 5) disabled the routable connection on the fiber switches and the dial-up inbound connection on the modem; 6) disconnected the SANS from any CCAs and validated that remaining computer systems are not essential to the operation of WECC_URE4 Critical Assets, removing any routable or dial-up path from outside or within the Electronic Security Perimeter and removed essentiality components of the SANS device such that the SANS is not a CCA; and 7) trained all IT personnel on change and incident management. | 2012-07-03 | 2013-03-01 | Agrees/ Stipulates | WECC reviewed WECC_URE4's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.