## PUBLIC_CIP Violations
Region | Registered Entity | NCR_ID | NERC Violation ID # | Notice of Confirmed Violation or Settlement Agreement | Description of the Violation | Reliability Standard | Req. | Violation Risk Factor | Violation Severity Level | Risk Assessment | Violation Start Date | Violation End Date | Total Penalty or Sanction ($) | Method of Discovery | Description of Mitigation Activity | Mitigation Completion Date | Date Regional Entity Verified Completion of Mitigation | "Admits," "Agrees/Stipulates," "Neither Admits nor Denies," or "Does Not Contest" | Other Factors Affecting the Penalty Determination, including Compliance History, Internal Compliance Program and Compliance Culture
Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO201100340 | Notice of Confirmed Violation | During a Compliance Audit MRO discovered that MRO_URE1 was in violation of CIP-002-1 R1. MRO_URE1 failed to have a risk-based assessment methodology (RBAM) that adequately considered control centers, load shedding, and any additional assets that support the reliable operation of the bulk power system (BPS) that MRO_URE1 deems appropriate to include in its assessment. Specifically, MRO_URE1’s RBAM did not contain adequate evaluation criteria for control centers which would justify a classification of an asset as either critical or non-critical. MRO_URE1 performed a new risk-based assessment to update its RBAM documentation. MRO_URE1’s RBAM did not declare any Critical Assets. | CIP-002-1 | R1; R1.2.1 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. MRO determined that this violation posed a minimal risk to the BPS because of MRO_URE1’s security controls, lack of Critical Assets, and its size. After revising its RBAM to comply with its Mitigation Plan, MRO_URE1 did not have any Critical Assets. Additionally, MRO_URE1 performed a vulnerability assessment on its inter-control center communications protocol (ICCP) links connecting its energy management system (EMS) with its Reliability Coordinator’s EMS. The assessment revealed that the security controls in place on those connections during the pendency of the violation included an ICCP configuration on its servers and firewalls for the ICCP links. | when the Standard became mandatory and enforceable on MRO_URE1 | when MRO_URE1 revised its RBAM and did not declare any Critical Assets | $0 (for MR0201100340, MR0201100343, MR0201100344, MR0201100345, MR0201100346,, MR0201100347, MR0201100348, MR0201100349, MR0201100352, MR0201100353, MR0201100354, MR0201100355, MR0201100356, MR0201100357, MR0201100358, MR0201100359) | Compliance Audit | To mitigate this violation, MRO_URE1: 1) reviewed and revised a large portion of its RBAM specifically addresses each of the assets identified in CIP-002-3 R1 CIP Compliance Audit as not being assessed. This new version specifically addresses each of the assets identified in CIP-002-3 R1, even if MRO_URE1 does not own or operate some of those assets; 2) identified additional criteria for its RBAM to delineate more clearly the methodology from the assessment; 3) revised its RBAM based on the results of the evaluation conducted in Step 2. Significant modifications were made to separate the methodology completely from the assessment; and, 4) conducted a risk-based assessment of all applicable facilities by applying the RBAM developed in Step 3. | 2013-02-01 | 2013-02-01 | Admits | MRO reviewed MRO_URE1's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination.
Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO201100343 | Notice of Confirmed Violation | During a Compliance Audit MRO discovered that MRO_URE1 was in violation of CIP-003-1 R6. MRO_URE1 failed to document all entity or vendor-related changes to hardware and software components of Critical Cyber Assets (CCAs) pursuant to the change control process. Although MRO_URE1 had a documented change control program, it did not document all patch changes to CCAs. MRO_URE1 provided samples of the change ticket process. However, MRO determined that security patches were applied to CCAs that were not documented using the change management process as required. MRO_URE1 applied changes to CCAs, but change tickets were not generated for the changes. | CIP-003-1 | R6 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. MRO determined that this violation posed a minimal risk to the BPS because of MRO_URE1’s lack of Critical Assets and its size. MRO_URE1 mitigated this noncompliance prior to the Compliance Audit through revisions to its risk-based assessment methodology (RBAM). Prior to the Compliance Audit, MRO_URE1’s RBAM revealed that MRO_URE1’s had no Critical Assets. MRO determined that security patches were applied to CCAs although they were not documented using the change management process as required. | when the Standard became mandatory and enforceable on MRO_URE1 | when MRO_URE1 revised its RBAM and did not declare any Critical Assets | $0 (for MR0201100340, MR0201100343, MR0201100344, MR0201100345, MR0201100346,, MR0201100347, MR0201100348, MR0201100349, MR0201100352, MR0201100353, MR0201100354, MR0201100355, MR0201100356, MR0201100357, MR0201100358, MR0201100359) | Compliance Audit | Through mitigation of MRO201100340 (CIP-002-1 R1), MRO_URE1 verified that it does not have any Critical Assets. Although there were Critical Assets present at the beginning of the Compliance Audit period, there was no mitigation required because those assets were no longer critical, and therefore no longer subject to this Standard and Requirement. | 2013-02-01 | 2013-02-01 | Admits | MRO reviewed MRO_URE1's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination.
Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO201100344 | Notice of Confirmed Violation | During a Compliance Audit MRO discovered that MRO_URE1 was in violation of CIP-004-1 R3. MRO_URE1 failed to have Personnel Risk Assessments (PRAs) for all personnel with authorized cyber or authorized unescorted access to Critical Cyber Assets (CCAs), in accordance with CIP-004-1 R3. Although MRO_URE1 implemented a PRA program to conduct seven-year criminal background checks and identity verification, one sampled individual was considered "escorted with card access" and was given card access. However, the individual did not receive a PRA until after access was granted. | CIP-004-1 | R3 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. MRO determined that this violation posed a minimal risk to the BPS because of MRO_URE1’s lack of Critical Assets and its size. MRO_URE1 mitigated this noncompliance prior to the Compliance Audit through revisions to its risk-based assessment methodology (RBAM). Prior to the Compliance Audit, MRO_URE1’s RBAM revealed that MRO_URE1 had no Critical Assets. | when the Standard became mandatory and enforceable on MRO_URE1 | when MRO_URE1 revised its RBAM and did not declare any Critical Assets | $0 (for MR0201100340, MR0201100343, MR0201100344, MR0201100345, MR0201100346,, MR0201100347, MR0201100348, MR0201100349, MR0201100352, MR0201100353, MR0201100354, MR0201100355, MR0201100356, MR0201100357, MR0201100358, MR0201100359) | Compliance Audit | Through mitigation of MRO201100340 (CIP-002-1 R1), MRO_URE1 verified that it does not have any Critical Assets. Although there were Critical Assets present at the beginning of the Compliance Audit period, there was no mitigation required because those assets were no longer critical, and therefore no longer subject to this Standard and Requirement. | 2013-02-01 | 2013-02-01 | Admits | MRO reviewed MRO_URE1's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination.
Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO201100345 | Notice of Confirmed Violation | During a Compliance Audit was in violation of CIP-004-1 R4. MRO_URE1 failed to demonstrate that it performed reviews of cyber access privileges in accordance with CIP-004-1 R4.1. MRO_URE1 performed quarterly reviews on physical privileges only, and policy and procedure documents did not demonstrate that electronic access was also reviewed when reviewing physical access. Additionally, MRO_URE1’s access list included individuals with cyber access and no physical access, as well as individuals with identical physical privileges and differing electronic privileges. | CIP-004-1 | R4; R4.1 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. MRO determined that this violation posed a minimal risk to the BPS because of MRO_URE1’s lack of Critical Assets and its size. MRO_URE1 mitigated this noncompliance prior to the Compliance Audit through revisions to its risk-based assessment methodology (RBAM). Prior to the Compliance Audit, MRO_URE1’s RBAM revealed that MRO_URE1 had no Critical Assets. | when the Standard became mandatory and enforceable on MRO_URE1 | when MRO_URE1 revised its RBAM and did not declare any Critical Assets | $0 (for MR0201100340, MR0201100343, MR0201100344, MR0201100345, MR0201100346,, MR0201100347, MR0201100348, MR0201100349, MR0201100352, MR0201100353, MR0201100354, MR0201100355, MR0201100356, MR0201100357, MR0201100358, MR0201100359) | Compliance Audit | Through mitigation of MRO201100340 (CIP-002-1 R1), MRO_URE1 verified that it does not have any Critical Assets. Although there were Critical Assets present at the beginning of the Compliance Audit period, there was no mitigation required because those assets were no longer critical, and therefore no longer subject to this Standard and Requirement. | 2013-02-01 | 2013-02-01 | Admits | MRO reviewed MRO_URE1's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination.
Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO201100346 | Notice of Confirmed Violation | During a Compliance Audit MRO discovered that MRO_URE1 was in violation of CIP-005-1 R1. MRO_URE1 failed to afford Cyber Assets used in the access control and monitoring of the Electronic Security Perimeters (ESPs) with protective measures as specified in Standard CIP-007 R1, in accordance with CIP-005-1 R1.5. Specifically, MRO_URE1 failed to provide documentation of test procedures for review and failed to document that test procedures reflected the MRO_URE1 production environment, in accordance with CIP-007-1 R1.2. | CIP-005-1 | R1; R1.5 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. MRO determined that this violation posed a minimal risk to the BPS because of MRO_URE1’s lack of Critical Assets and its size. MRO_URE1 mitigated this noncompliance prior to the Compliance Audit through revisions to its risk-based assessment methodology (RBAM). Prior to the Compliance Audit, MRO_URE1’s RBAM revealed that MRO_URE1 had no Critical Assets. | when the Standard became mandatory and enforceable on MRO_URE1 | when MRO_URE1 revised its RBAM and did not declare any Critical Assets | $0 (for MR0201100340, MR0201100343, MR0201100344, MR0201100345, MR0201100346,, MR0201100347, MR0201100348, MR0201100349, MR0201100352, MR0201100353, MR0201100354, MR0201100355, MR0201100356, MR0201100357, MR0201100358, MR0201100359) | Compliance Audit | Through mitigation of MRO201100340 (CIP-002-1 R1), MRO_URE1 verified that it does not have any Critical Assets. Although there were Critical Assets present at the beginning of the Compliance Audit period, there was no mitigation required because those assets were no longer critical, and therefore no longer subject to this Standard and Requirement. | 2013-02-01 | 2013-02-01 | Admits | MRO reviewed MRO_URE1's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination.
Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO201100347 | Notice of Confirmed Violation | During a Compliance Audit MRO discovered that MRO_URE1 was in violation of CIP-005-1 R2. MRO_URE1 failed to enable only ports and services required for operations and for monitoring Cyber Assets within the Electronic Security Perimeter in accordance with CIP-005-1 R2. MRO_URE1 performed a cyber vulnerability assessment (CVA). During the review, the list of open ports required did not include the purpose or function of the open ports. Therefore, MRO_URE1 failed to determine whether these ports were needed for normal and emergency operations. Additionally, MRO Audit staff found that multiple CVA recommendations were not identified properly as vulnerabilities. | CIP-005-1 | R2; R2.2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. MRO determined that this violation posed a minimal risk to the BPS because of MRO_URE1’s lack of Critical Assets and its size. MRO_URE1 mitigated this noncompliance prior to the Compliance Audit through revisions to its risk-based assessment methodology (RBAM). Prior to the Compliance Audit, MRO_URE1’s RBAM revealed that MRO_URE1 had no Critical Assets. | when the Standard became mandatory and enforceable on MRO_URE1 | when MRO_URE1 revised its RBAM and did not declare any Critical Assets | $0 (for MR0201100340, MR0201100343, MR0201100344, MR0201100345, MR0201100346,, MR0201100347, MR0201100348, MR0201100349, MR0201100352, MR0201100353, MR0201100354, MR0201100355, MR0201100356, MR0201100357, MR0201100358, MR0201100359) | Compliance Audit | Through mitigation of MRO201100340 (CIP-002-1 R1), MRO_URE1 verified that it does not have any Critical Assets. Although there were Critical Assets present at the beginning of the Compliance Audit period, there was no mitigation required because those assets were no longer critical, and therefore no longer subject to this Standard and Requirement. | 2013-02-01 | 2013-02-01 | Admits | MRO reviewed MRO_URE1's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination.
Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO201100348 | Notice of Confirmed Violation | During a Compliance Audit MRO discovered that MRO_URE1 was in violation of CIP-005-1 R3. MRO_URE1 failed to configure its security monitoring process to detect and alert for attempts at or actual unauthorized access, in accordance with CIP-005-1 R3.2. Additionally, MRO_URE1 failed to review firewall logs every 90 calendar days. MRO_URE1 policy states that reviews will be documented with a sample. However, MRO_URE1 did not provide any documentation to demonstrate that the logs were reviewed. | CIP-005-1 | R3; R3.2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. MRO determined that this violation posed a minimal risk to the BPS because of MRO_URE1’s lack of Critical Assets and its size. MRO_URE1 mitigated this noncompliance prior to the Compliance Audit through revisions to its risk-based assessment methodology (RBAM). Prior to the Compliance Audit, MRO_URE1’s RBAM revealed that MRO_URE1 had no Critical Assets. | when the Standard became mandatory and enforceable on MRO_URE1 | when MRO_URE1 revised its RBAM and did not declare any Critical Assets | $0 (for MR0201100340, MR0201100343, MR0201100344, MR0201100345, MR0201100346,, MR0201100347, MR0201100348, MR0201100349, MR0201100352, MR0201100353, MR0201100354, MR0201100355, MR0201100356, MR0201100357, MR0201100358, MR0201100359) | Compliance Audit | Through mitigation of MRO201100340 (CIP-002-1 R1), MRO_URE1 verified that it does not have any Critical Assets. Although there were Critical Assets present at the beginning of the Compliance Audit period, there was no mitigation required because those assets were no longer critical, and therefore no longer subject to this Standard and Requirement. | 2013-02-01 | 2013-02-01 | Admits | MRO reviewed MRO_URE1's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination.
Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO201100349 | Notice of Confirmed Violation | During a Compliance Audit MRO discovered that MRO_URE1 was in violation of CIP-005-1 R4. MRO_URE1 failed to have a cyber vulnerability assessment (CVA) which included a review to verify that only ports and services required for operations at these access points are enabled, in accordance with CIP-005-1 R4.2. MRO_URE1 performed a CVA. During the review, the list of open ports required did not include the purpose or function of the open ports. Therefore, MRO_URE1 failed to determine whether these ports were needed for normal and emergency operations. Additionally, multiple CVA recommendations were not identified properly as vulnerabilities, including open ports. MRO_URE1 also failed to document the action plan to remediate vulnerabilities and document the execution status in accordance with CIP-005-1 R4.5. | CIP-005-1 | R4.2; R4.5 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. MRO determined that this violation posed a minimal risk to the BPS because of MRO_URE1’s lack of Critical Assets and its size. MRO_URE1 mitigated this noncompliance prior to the Compliance Audit through revisions to its risk-based assessment methodology (RBAM). Prior to the Compliance Audit, MRO_URE1’s RBAM revealed that MRO_URE1 had no Critical Assets. | when the Standard became mandatory and enforceable on MRO_URE1 | when MRO_URE1 revised its RBAM and did not declare any Critical Assets | $0 (for MR0201100340, MR0201100343, MR0201100344, MR0201100345, MR0201100346,, MR0201100347, MR0201100348, MR0201100349, MR0201100352, MR0201100353, MR0201100354, MR0201100355, MR0201100356, MR0201100357, MR0201100358, MR0201100359) | Compliance Audit | Through mitigation of MRO201100340 (CIP-002-1 R1), MRO_URE1 verified that it does not have any Critical Assets. Although there were Critical Assets present at the beginning of the Compliance Audit period, there was no mitigation required because those assets were no longer critical, and therefore no longer subject to this Standard and Requirement. | 2013-02-01 | 2013-02-01 | Admits | MRO reviewed MRO_URE1's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination.
Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO201100352 | Notice of Confirmed Violation | During a Compliance Audit MRO discovered that MRO_URE1 was in violation of CIP-007-1 R1. MRO_URE1 failed to document cybersecurity test procedures in a manner that minimizes adverse effects on the production system or its operation, in accordance with CIP-007-1 R1.1; and failed to document that test procedures by MRO_URE1 or by the application vendor reflected the MRO_URE1 production environment, in accordance with CIP-007-1 R1.2. Additionally, MRO_URE1 did not test all changes to Critical Cyber Assets (CCAs). Although MRO_URE1 provided samples of the change ticket process, the security patches were applied to CCAs without the required testing. MRO_URE1 also failed to document its test results in several cases in accordance with CIP-007-1 R1.3. MRO sampled two server changes. In both cases, configuration changes to the application and server communication ports occurred, but no testing occurred prior to implementation. | CIP-007-1 | R1; R1.1; R1.2; R1.3 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. MRO determined that this violation posed a minimal risk to the BPS because of MRO_URE1’s lack of Critical Assets and its size. MRO_URE1 mitigated this noncompliance prior to the Compliance Audit through revisions to its risk-based assessment methodology (RBAM). Prior to the Compliance Audit, MRO_URE1’s RBAM revealed that MRO_URE1 had no Critical Assets. | when the Standard became mandatory and enforceable on MRO_URE1 | when MRO_URE1 revised its RBAM and did not declare any Critical Assets | $0 (for MR0201100340, MR0201100343, MR0201100344, MR0201100345, MR0201100346,, MR0201100347, MR0201100348, MR0201100349, MR0201100352, MR0201100353, MR0201100354, MR0201100355, MR0201100356, MR0201100357, MR0201100358, MR0201100359) | Compliance Audit | Through mitigation of MRO201100340 (CIP-002-1 R1), MRO_URE1 verified that it does not have any Critical Assets. Although there were Critical Assets present at the beginning of the Compliance Audit period, there was no mitigation required because those assets were no longer critical, and therefore no longer subject to this Standard and Requirement. | 2013-02-01 | 2013-02-01 | Admits | MRO reviewed MRO_URE1's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination.
Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO201100353 | Notice of Confirmed Violation | During a Compliance Audit MRO discovered that MRO_URE1 was in violation of CIP-007-1 R2. MRO_URE1 failed to enable only those ports and services required for normal and emergency operations in accordance with CIP-007-1 R2. MRO_URE1 performed a cyber vulnerability assessment (CVA). During the review, the list of open ports required did not include the purpose or function of the open ports. Additionally, multiple CVA recommendations were not identified properly as vulnerabilities, including open ports. Therefore, MRO_URE1 failed to determine whether these ports were needed for normal and emergency operation. | CIP-007-1 | R2; R2.2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. MRO determined that this violation posed a minimal risk to the BPS because of MRO_URE1’s lack of Critical Assets and its size. MRO_URE1 mitigated this noncompliance prior to the Compliance Audit through revisions to its risk-based assessment methodology (RBAM). Prior to the Compliance Audit, MRO_URE1’s RBAM revealed that MRO_URE1 had no Critical Assets. | when the Standard became mandatory and enforceable on MRO_URE1 | when MRO_URE1 revised its RBAM and did not declare any Critical Assets | $0 (for MR0201100340, MR0201100343, MR0201100344, MR0201100345, MR0201100346,, MR0201100347, MR0201100348, MR0201100349, MR0201100352, MR0201100353, MR0201100354, MR0201100355, MR0201100356, MR0201100357, MR0201100358, MR0201100359) | Compliance Audit | Through mitigation of MRO201100340 (CIP-002-1 R1), MRO_URE1 verified that it does not have any Critical Assets. Although there were Critical Assets present at the beginning of the Compliance Audit period, there was no mitigation required because those assets were no longer critical, and therefore no longer subject to this Standard and Requirement. | 2013-02-01 | 2013-02-01 | Admits | MRO reviewed MRO_URE1's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination.
Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO201100354 | Notice of Confirmed Violation | During a Compliance Audit MRO discovered that MRO_URE1 was in violation of CIP-007-1 R3. MRO_URE1 failed to document the assessment of security patches and security upgrades for applicability within 30 calendar days of availability of the patches or upgrades in accordance with CIP-007-1 R3. MRO_URE1 provided evidence that a third-party contractor had been certifying the security patches, although MRO_URE1 failed to provide any of the supporting documentation, including tracking, evaluating, and testing. MRO also sampled one of MRO_URE1’s Cyber Assets for patches. MRO_URE1 failed to document the assessment and implementation of the patch within 30 days of its release. | CIP-007-1 | R3 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. MRO determined that this violation posed a minimal risk to the BPS because of MRO_URE1’s lack of Critical Assets and its size. MRO_URE1 mitigated this noncompliance prior to the Compliance Audit through revisions to its risk-based assessment methodology (RBAM). Prior to the Compliance Audit, MRO_URE1’s RBAM revealed that MRO_URE1 had no Critical Assets. | when the Standard became mandatory and enforceable on MRO_URE1 | when MRO_URE1 revised its RBAM and did not declare any Critical Assets | $0 (for MR0201100340, MR0201100343, MR0201100344, MR0201100345, MR0201100346,, MR0201100347, MR0201100348, MR0201100349, MR0201100352, MR0201100353, MR0201100354, MR0201100355, MR0201100356, MR0201100357, MR0201100358, MR0201100359) | Compliance Audit | Through mitigation of MRO201100340 (CIP-002-1 R1), MRO_URE1 verified that it does not have any Critical Assets. Although there were Critical Assets present at the beginning of the Compliance Audit period, there was no mitigation required because those assets were no longer critical, and therefore no longer subject to this Standard and Requirement. | 2013-02-01 | 2013-02-01 | Admits | MRO reviewed MRO_URE1's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination.
Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO201100355 | Notice of Confirmed Violation | During a Compliance Audit MRO discovered that MRO_URE1 was in violation of CIP-007-1. MRO_URE1 failed to document and implement a process for the update of anti-virus and malware prevention “signatures” in accordance with CIP-007-1 R4.2. Specifically, MRO_URE1 did not have a documented process for updating the anti-virus signatures of Critical Cyber Assets (CCAs). MRO_URE1 described its process to the MRO Compliance Audit staff verbally, but did not provide any documentation to demonstrate that testing occurred prior to implementation. | CIP-007-1 | R4; R4.2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. MRO determined that this violation posed a minimal risk to the BPS because of MRO_URE1’s lack of Critical Assets and its size. MRO_URE1 mitigated this noncompliance prior to the Compliance Audit through revisions to its risk-based assessment methodology (RBAM). Prior to the Compliance Audit, MRO_URE1’s RBAM revealed that MRO_URE1 had no Critical Assets. | when the Standard became mandatory and enforceable on MRO_URE1 | when MRO_URE1 revised its RBAM and did not declare any Critical Assets | $0 (for MR0201100340, MR0201100343, MR0201100344, MR0201100345, MR0201100346,, MR0201100347, MR0201100348, MR0201100349, MR0201100352, MR0201100353, MR0201100354, MR0201100355, MR0201100356, MR0201100357, MR0201100358, MR0201100359) | Compliance Audit | Through mitigation of MRO201100340 (CIP-002-1 R1), MRO_URE1 verified that it does not have any Critical Assets. Although there were Critical Assets present at the beginning of the Compliance Audit period, there was no mitigation required because those assets were no longer critical, and therefore no longer subject to this Standard and Requirement. | 2013-02-01 | 2013-02-01 | Admits | MRO reviewed MRO_URE1's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination.
Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO201100356 | Notice of Confirmed Violation | During a Compliance Audit MRO discovered that MRO_URE1 was in violation of CIP-007-1 R5. MRO_URE1 failed to establish, implement, and document technical and procedural controls that enforce access authentication of, and accountability for, all user activity, and that minimize the risk of unauthorized system access in accordance with CIP-007-1 R5. MRO_URE1 failed to ensure that user accounts are implemented as approved by designated personnel, in accordance with CIP-007-1 R5.1.1. Specifically, the MRO_URE1 security management controls policy contained four conflicting definitions regarding who is responsible for approval of logical access changes. MRO_URE1 also failed to establish methods, processes, and procedures that generate logs of sufficient detail to create historical audit trails of individual user account access activity for a minimum of ninety 90 days, in accordance with CIP-007-1 R5.1.2. Although MRO_URE1 provided sample logs which contained successful and failed login data, the logs did not contain detail to create historical audit trails of individual user account activity. Also, the sample logs provided did not demonstrate that logs were being reviewed every 90 days. MRO_URE1 also failed to review, at least annually, user accounts to verify access privileges are in accordance with Standards CIP-003 R5 and CIP-004 R4, as required by CIP-007-1 R5.1.3. Quarterly reviews were based on physical privileges only, and policy and procedure documents did not reflect the assertion that electronic access was implicitly reviewed when reviewing physical access. Additionally, the access list included individuals with cyber access and no physical access, as well as individuals with identical physical privileges and differing electronic privileges. MRO_URE1 also failed to implement a policy to minimize and manage the scope and acceptable use of administrator, shared, and other generic account privileges including factory default accounts, in accordance with CIP-007-1 R5.2. Although the MRO_URE1 systems security management policy defined the policy for default accounts and shared online supplier inquiry (OSI) administrator accounts, it did not define the scope and acceptable use of firewall and switch administrator accounts. The systems security management policy also did not require that the enabled firewall and switch shared administrator account passwords must be changed prior to being put into service in accordance with CIP-007-1 R5.2.1; failed to identify those individuals with access to firewall and switch administrator accounts and did not identify a policy to manage these accounts, in accordance with CIP-007-1 R5.2.2; and did not provide manual or automated audit trails on shared accounts in accordance with CIP-007-1 R5.2.3. | CIP-007-1 | R5; R5.1.1; R5.1.2; R5.1.3; R5.2; R5.2.1; R5.2.3 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. MRO determined that this violation posed a minimal risk to the BPS because of MRO_URE1’s lack of Critical Assets and its size. MRO_URE1 mitigated this noncompliance prior to the Compliance Audit through revisions to its risk-based assessment methodology (RBAM). Prior to the Compliance Audit, MRO_URE1’s RBAM revealed that MRO_URE1 had no Critical Assets. control center was no longer a Critical Asset. Additionally, MRO_URE1’s highest voltage level is 161 kV. | when the Standard became mandatory and enforceable on MRO_URE1 | when MRO_URE1 revised its RBAM and did not declare any Critical Assets | $0 (for MR0201100340, MR0201100343, MR0201100344, MR0201100345, MR0201100346,, MR0201100347, MR0201100348, MR0201100349, MR0201100352, MR0201100353, MR0201100354, MR0201100355, MR0201100356, MR0201100357, MR0201100358, MR0201100359) | Compliance Audit | Through mitigation of MRO201100340 (CIP-002-1 R1), MRO_URE1 verified that it does not have any Critical Assets. Although there were Critical Assets present at the beginning of the Compliance Audit period, there was no mitigation required because those assets were no longer critical, and therefore no longer subject to this Standard and Requirement. | 2013-02-01 | 2013-02-01 | Admits | MRO reviewed MRO_URE1's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination.
Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO201100357 | Notice of Confirmed Violation | During a Compliance Audit MRO discovered that MRO_URE1 was in violation of CIP-007-1 R6. MRO_URE1 failed to implement automated tools or process controls which are capable of issuing automated or manual alerts for detected cyber security incidents in accordance with CIP-007-1 R6.2. Per the compensating measures described in a technical feasibility exception, MRO_URE1 is supposed to review logs every 90 days. Although MRO_URE1 provided sample logs with successful and failed login data, the samples did not contain detail to determine whether security incidents had occurred during the period. While the network monitoring screen can detect a Cyber Asset shutdown after a security incident has occurred, the monitoring process did not detect the Cyber Asset intrusion and other security incidents. Also, the logs provided did not demonstrate that logs were being reviewed every 90 days in accordance with CIP-007-1 R6.4. | CIP-007-1 | R6; R6.2; R6.4 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. MRO determined that this violation posed a minimal risk to the BPS because of MRO_URE1’s lack of Critical Assets and its size. MRO_URE1 mitigated this noncompliance prior to the Compliance Audit through revisions to its risk-based assessment methodology (RBAM). Prior to the Compliance Audit, MRO_URE1’s RBAM revealed that MRO_URE1 had no Critical Assets. | when the Standard became mandatory and enforceable on MRO_URE1 | when MRO_URE1 revised its RBAM and did not declare any Critical Assets | $0 (for MR0201100340, MR0201100343, MR0201100344, MR0201100345, MR0201100346,, MR0201100347, MR0201100348, MR0201100349, MR0201100352, MR0201100353, MR0201100354, MR0201100355, MR0201100356, MR0201100357, MR0201100358, MR0201100359) | Compliance Audit | Through mitigation of MRO201100340 (CIP-002-1 R1), MRO_URE1 verified that it does not have any Critical Assets. Although there were Critical Assets present at the beginning of the Compliance Audit period, there was no mitigation required because those assets were no longer critical, and therefore no longer subject to this Standard and Requirement. | 2013-02-01 | 2013-02-01 | Admits | MRO reviewed MRO_URE1's internal compliance program (ICP) and considered it to be a mitigating/neutral factor in the penalty determination.
Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MR02O1100358 | Notice of Confirmed Violation | During a Compliance Audit MRO discovered that MRO_URE1 was in violation of CIP-007-1 R8. MRO_URE1 failed to have a cyber vulnerability assessment (CVA) which: 1) verified that only ports and services required for operation of the Cyber Assets within the Electronic Security Perimeter were enabled, in accordance with CIP-008-1 R8.2; 2) reviewed controls for default accounts, in accordance with CIP-008-1 R8.3; and 3) documented the results of the assessment, the action plan to remediate or mitigate vulnerabilities identified in the assessment, and the execution status of that action plan, in accordance with CIP-008-1 R8.4. MRO_URE1 did not provide documentation to determine whether ports were needed only for normal and emergency operations. Additionally, multiple CVA recommendations were not identified properly as vulnerabilities, including open ports. MRO_URE1 also failed to demonstrate that the default accounts on two servers were reviewed. | CIP-007-1 | R8; R8.2; R8.3; R8.4 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. MRO determined that this violation posed a minimal risk to the BPS because of MRO_URE1’s lack of Critical Assets and its size. MRO_URE1 mitigated this noncompliance prior to the Compliance Audit through revisions to its risk-based assessment methodology (RBAM). Prior to the Compliance Audit, MRO_URE1’s RBAM revealed that MRO_URE1 had no Critical Assets. | when the Standard became mandatory and enforceable on MRO_URE1 | when MRO_URE1 revised its RBAM and did not declare any Critical Assets | $0 (for MR0201100340, MR0201100343, MR0201100344, MR0201100345, MR0201100346,, MR0201100347, MR0201100348, MR0201100349, MR0201100352, MR0201100353, MR0201100354, MR0201100355, MR0201100356, MR0201100357, MR0201100358, MR0201100359) | Compliance Audit | Through mitigation of MRO201100340 (CIP-002-1 R1), MRO_URE1 verified that it does not have any Critical Assets. Although there were Critical Assets present at the beginning of the Compliance Audit period, there was no mitigation required because those assets were no longer critical, and therefore no longer subject to this Standard and Requirement. | 2013-02-01 | 2013-02-01 | Admits | MRO reviewed MRO_URE1's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination.
Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO201100359 | Notice of Confirmed Violation | During a Compliance Audit MRO discovered that MRO_URE1 was in violation of CIP-009-1 R4. MRO_URE1 failed to provide a recovery plan with processes and procedures for the backup and storage of information required to restore Critical Cyber Assets (CCAs). | CIP-009-1 | R4 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. MRO determined that this violation posed a minimal risk to the BPS because of MRO_URE1’s lack of Critical Assets and its size. MRO_URE1 mitigated this noncompliance prior to the Compliance Audit through revisions to its risk-based assessment methodology (RBAM). Prior to the Compliance Audit, MRO_URE1’s RBAM revealed that MRO_URE1 had no Critical Assets. | when the Standard became mandatory and enforceable on MRO_URE1 | when MRO_URE1 revised its RBAM and did not declare any Critical Assets | $0 (for MR0201100340, MR0201100343, MR0201100344, MR0201100345, MR0201100346,, MR0201100347, MR0201100348, MR0201100349, MR0201100352, MR0201100353, MR0201100354, MR0201100355, MR0201100356, MR0201100357, MR0201100358, MR0201100359) | Compliance Audit | Through mitigation of MRO201100340 (CIP-002-1 R1), MRO_URE1 verified that it does not have any Critical Assets. Although there were Critical Assets present at the beginning of the Compliance Audit period, there was no mitigation required because those assets were no longer critical, and therefore no longer subject to this Standard and Requirement. | 2013-02-01 | 2013-02-01 | Admits | MRO reviewed MRO_URE1's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination.
Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPP RE_URE1) | NCRXXXXX | SPP2011008257 | Settlement Agreement | SPP RE_URE1 self-reported a violation of CIP-007-3a R2.1 and R2.2. SPP RE_URE1 discovered that ports were enabled on its Energy Management System (EMS) system that were not required for normal or emergency operations. During a cyber vulnerability assessment (CVA), SPP RE_URE1 identified five enabled ports affecting ten EMS Cyber Assets that were not required for either normal or emergency operations. | CIP-007-3a | R2; 2.1; 2.2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The risk was minimal because the affected Cyber Assets were within an Electronic Security Perimeter (ESP) and thereby afforded the required protective measures. For instance, the EMS Cyber Assets are guarded by electronic access point firewalls, which utilize anti-virus software to scan and block malicious software crossing the firewall. The EMS Cyber Assets are also protected by an intrusion prevention system (IPS), which further prevents malicious inbound and outbound traffic. Furthermore, the EMS Cyber Assets are running anti-virus software, which provides a third layer of protection against malware beyond the firewalls and IPS. Moreover, physical access to all Cyber Assets within the SPP RE_URE1 ESP is limited to authorized personnel via badge access. Finally, no malicious exploitation of the erroneously enabled ports was identified by SPP RE_URE1. | when the five ports were enabled | Mitigation Plan completion | $15,000 (for SPP2011008257, SPP2012009927, SPP2012009936, and SPP20120011103) | Self-Report | To mitigate this violation, SPP RE_URE1: 1) disabled the non-required ports and services identified in its Self-Report; 2) performed an additional review of all enabled ports associated with Cyber Assets within the ESP to ensure the ports were required for either normal or emergency operations; and 3) retained a vendor to complete on-site work for scanning all devices within the ESP. | 7/16/2012 | 8/15/2012 | Neither Admits nor Denies | SPP RE considered the presence and quality of SPP RE_URE1's internal compliance program (ICP) to be a mitigating factor in the penalty determination. Additionally, SPP RE considered the fact that SPP RE_URE1 self-reported the instant violation and cooperated throughout the processing of the possible violation to be a mitigating factor in the penalty determination.
Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPP RE_URE1) | NCRXXXXX | SPP2012009927 | Settlement Agreement | During a Compliance Audit, SPP RE determined that SPP RE_URE1 did not implement access monitoring, access logging, or alerting capabilities for unauthorized access on six devices, in violation of CIP-005-1 R3.2. The devices at issue included four network switches and two security management systems. SPP RE subsequently determined that only the four network switches were Electronic Security Perimeter (ESP) access points and subject to CIP-005-1 R3.2. | CIP-005-1 | R3; R3.2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Other than the four network switches, was monitoring and logging access at all access points to the ESP and had security alerting capability to detect and alert for unauthorized attempts and or access to the ESP. Additionally, the four network switches resided behind two firewalls that filtered all external communications entering the ESP and were continuously monitored, logged, and providing alerts to SPP RE_URE1 personnel. Therefore, any unauthorized external access attempts would have been monitored, logged, and alerts would have been sent to appropriate security personnel. Moreover, SPP RE_URE1's intrusion prevention system (IPS) was monitoring traffic between the firewalls and the four network switches. The IPS is configured to prevent identified malicious communication from entering the switches. | when the Standard became mandatory and enforceable for SPP RE_URE1 | Mitigation Plan completion | $15,000 (for SPP2011008257, SPP2012009927, SPP2012009936, and SPP20120011103) | Compliance Audit | To mitigate this violation, SPP RE_URE1: 1) added the four network switches to the monitoring and logging system provided by its third-party network security provider. The system monitors and logs activity at all times and alerts appropriate security personnel of any unauthorized attempts and access to SPP RE_URE1's ESP. | 2012-09-07 | 2012-10-10 | Neither Admits nor Denies | SPP RE considered the presence and quality of SPP RE_URE1's internal compliance program (ICP) to be a mitigating factor in the penalty determination. Additionally, SPP RE considered the fact that SPP RE_URE1 self-reported the instant violation and cooperated throughout the processing of the possible violation to be a mitigating factor in the penalty determination.
Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPP RE_URE1) | NCRXXXXX | SPP2012009936 | Settlement Agreement | During a Compliance Audit, SPP RE determined that SPP RE_URE1 had not implemented automated tools or organizational process controls to monitor, log, and alert SPP RE_URE1 of possible security events on two Cyber Assets (vulnerability scanners) within its Electronic Security Perimeter (ESP). For the two vulnerability scanners, SPP RE_URE1 did not: 1) document and implement the processes for monitoring (R6.1); 2) institute automated or manual alerting (R6.2); 3) maintain logs in support of incident response (R6.3); 4) retain logs for 90 calendar days (R6.4); and, 5) review logs of security events related to cyber security and maintain records documenting review of logs (R6.5). | CIP-007-1 | R6; R6.1; R6.2; R6.3; R6.4; R6.5 | Medium; | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Except for the two vulnerability scanners, SPP RE_URE1 implemented and documented automated tools or organizational process controls to monitor, log, and alert for possible security events on all Cyber Assets within the ESP. Additionally, SPP RE_URE1's intrusion protection and detection system (IPS/IDS) monitors, alerts, and prevents security events inside the SPP RE_URE1 ESP on a continuous basis and was doing so for the duration of this violation. As a result, malicious traffic impacting the two vulnerability scanners would have been subject to identification and prevention by the IDS/IPS, which would also have alerted SPP RE_URE1 personnel. Additionally, SPP RE_URE1 attested that there were no cyber security system events during the duration of the violation. | when the Standard became mandatory and enforceable for SPP RE_URE1 | Mitigation Plan completion | $15,000 (for SPP2011008257, SPP2012009927, SPP2012009936, and SPP20120011103) | Compliance Audit | To mitigate this violation, SPP RE_URE1: 1) removed the two vulnerability scanners from the ESP and from its Cyber Asset list; and 2) added the devices to its monitoring service, which provides 24- hour, seven days a week monitoring and alerting for unauthorized access attempts. | 2012-07-25 | 2012-08-03 | Neither Admits nor Denies | SPP RE considered the presence and quality of SPP RE_URE1's internal compliance program (ICP) to be a mitigating factor in the penalty determination. Additionally, SPP RE considered the fact that SPP RE_URE1 self-reported the instant violation and cooperated throughout the processing of the possible violation to be a mitigating factor in the penalty determination.
Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPP RE_URE1) | NCRXXXXX | SPP2012011103 | Settlement Agreement | During a Compliance Audit, SPP RE determined that SPP RE_URE1 violated CIP-007-1 R3.2 because it failed to document adequately the application of security patches and compensating measures for 6.0 % of patches published during an approximate three year period. SPP RE subsequently determined that for those patches lacking documentation: 1) the vulnerability posed was remediated by a separately released patch; 2) the patch itself was determined to present a risk to cyber systems, and therefore not installed; or 3) the patch was not a “security” patch. | CIP-007-1 | R3.2 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The risk was minimal because the affected Cyber Assets were within an Electronic Security Perimeter (ESP) and thereby afforded substantial protective measures. For instance, the affected Cyber Assets are guarded by electronic access point firewalls, which utilize anti-virus software to scan and block malicious software crossing the firewall. Additionally, SPP RE_URE1's ESP is continuously monitored and protected by an intrusion prevention and detection system (IPS/IDS), which provided real-time log analysis, event alerting, and blocking of both internal and external malicious transmissions on Cyber Assets within the ESP. Furthermore, the affected Cyber Assets were running anti-virus software, which provided a third layer of protection against malware beyond the firewalls and IPS. Moreover, physical access to all Cyber Assets within the SPP RE_URE1 ESP was limited to authorized personnel via badge access. | when the Standard became mandatory and enforceable for SPP RE_URE1 | Mitigation Plan completion | $15,000 (for SPP2011008257, SPP2012009927, SPP2012009936, and SPP20120011103) | Compliance Audit | To mitigate this violation, SPP RE_URE1: 1) reviewed all patches that lacked documentation of compensating measures or a patch being applied; and 2) ensured all patches were up to date for all Cyber Assets within the scope of this violation. | 2012-04-11 | 2013-04-30 | Neither Admits nor Denies | SPP RE considered the presence and quality of SPP RE_URE1's internal compliance program (ICP) to be a mitigating factor in the penalty determination. Additionally, SPP RE considered the fact that SPP RE_URE1 self-reported the instant violation and cooperated throughout the processing of the possible violation to be a mitigating factor in the penalty determination.
Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2012010414 | Notice of Confirmed Violation | WECC_URE1 submitted a Self-Report to WECC stating that it was in violation of CIP-004-3 R4. WECC_URE1 reported that on five occasions it failed to update Critical Cyber Asset (CCA) access lists within seven days of a change in personnel with access to CCAs, or any change in the access rights of such personnel. Further, WECC_URE1 reported that it failed to revoke access within seven days for personnel who no longer required such access to CCAs. Based on the Self-Report and additional information provided by WECC_URE1, WECC determined that physical access to CCAs was revoked for one WECC_URE1 employee and the access list was updated three months later. In another instance, physical access was granted to two WECC_URE1 employees and the access list was updated two weeks later. In addition, an individual left WECC_URE1 and the individual’s electronic access rights were revoked almost two months later. Finally, an individual left WECC_URE1 and the individual’s electronic access was revoked two weeks later. WECC determined that WECC_URE1’s failure to update access lists within seven days constituted a violation of CIP-004-3 R4.1. WECC also determined that WECC_URE1’s failure to revoke access rights within seven days constituted a violation of CIP-004-3 R4.2. | CIP-004-3 | R4; R4.1; R4.2 | Lower | High | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The scope of the violation was limited to four individuals and all four individuals had completed cybersecurity training and personnel risk assessments. All CCAs to which the individuals had access were secured within Electronic Security Perimeters (ESPs). In addition, electronic access to the ESPs was controlled and monitored. CCAs were monitored for system events and unauthorized access attempts, which trigger alarms. All CCAs, to which individuals had access, were secured within Physical Security Perimeters (PSPs). All PSPs were monitored by security personnel on a continual basis, and unauthorized access attempts would trigger alarms. Further, physical access and physical access attempts were logged per CIP-006 R6. | seven days after WECC_URE1 failed to update the access list | Mitigation Plan completion | $10,000 | Self-Report | To mitigate this violation, WECC_URE1: 1) developed and provided additional procedural training to top managers and administrative officers, as well as supervisors and administrative staff at each facility, to ensure that they understand their responsibilities with regard to NERC Standards compliance; 2) finalized and packaged training materials; 3) provided specialized CIP training to top managers and administrative officers as well as to supervisors and administrative staff; and 4) finalized any associated documentation. | 2012-09-05 | TBD | Does Not Contest | WECC did not review WECC_URE1's internal compliance program (ICP) and therefore did not consider it to be a mitigating factor in the penalty determination.
Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2013011961 | Settlement Agreement | WECC_URE2 submitted a Self-Report to WECC stating that it was in violation of CIP-004-1 R4. WECC_URE2 stated that during a quarterly review it failed to ensure a number of instances of change in personnel were updated on the Critical Cyber Assets (CCAs) access list within seven days of making the change. The instances involved employees that no longer required access and employees that required and obtained access. | CIP-004-1 | R4 | Lower | High | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although WECC_URE2 failed to update its access list within seven days, physical and electronic access was timely revoked for individuals that no longer required access, including accounts disabled, shared passwords changes, and physical access revoked. Additionally, the individuals were not terminated for cause and left in good standing with WECC_URE2. All CCAs were within defined Physical Security Perimeters (PSPs) where access is restricted to individuals with authorization, training, and current personnel risk assessments (PRAs), and all access to PSPs requires valid identification badges. The individuals whose access was granted had valid identification badges which restrict and monitor all physical access. The individuals had authorized physical and cyber access, training, and current PRAs. Additionally, the violation affected less than 5% of authorized WECC_URE2 employees or contractors. Lastly, the required changes with respect to access were made but the administrative task of updating the access list was not performed. | seven days after WECC_URE2 failed to update the access list for the first change in personnel | Mitigation Plan completion | $15,000 | Self-Report | To mitigate this violation, WECC_URE2: 1) updated the access list; and 2) reassigned responsibility for updating the access list to different individuals. | 2013-02-24 | 2013-03-29 | Does Not Contest | WECC reviewed WECC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2012009451 | Settlement Agreement | WECC_URE3 submitted a Self-Certification to WECC stating that it was in violation of CIP-005-3 R1.5. Two firewalls were commissioned that were not afforded all of the protections required under the Standard. The two firewalls commissioned by WECC_URE3 were Electronic Security Perimeter (ESP) access control and monitoring (ACM) devices. Under CIP-005-3a R1.5, entities must afford ACM devices 24 different protective measures. In this case, WECC found that WECC_URE3 afforded two protective measures by securing the ACM devices within a Physical Security Perimeter (PSP) and ensuring that all personnel with access to the two ACM devices completed a personnel risk assessment (PRA). However, WECC also determined that WECC_URE3 failed to afford 22 additional protective measures required under CIP-005-3a R1.5. | CIP-005-3a | R1; R1.5 | Medium | Severe | This violation posed a minimal risk and did not pose a serious and substantial risk to the reliability of the bulk power system (BPS) given the scope of the violation and compensating measures in place during the violation period. The scope of the violation is limited to 2.9% of WECC_URE3's ACM devices. Both of the devices are located within an ESP and a PSP. Physical and electronic access to the 2.9% ACM devices is controlled and monitored and individuals with specific access to the two devices had completed PRAs. | when WECC_URE3 commissioned two firewalls without all of the protections required under CIP-005-3 R1.5 | Mitigation Plan completion | $17,000 (for WECC2012009451, WECC2012009453, and WECC2012009459) | Self-Certification | To mitigate this violation, WECC_URE3: a) reviewed existing CIP documentation as well as the applicable devices to determine which of the protections/controls enumerated in this Requirement have been put into place, and which still need to be applied; b) updated the documentation to reflect current implementation of the two firewalls and implement any missing protections/controls; c) created an install/modify/removal policy to ensure equipment installations, modifications and removals follow appropriate change management procedures in accordance with the CIP requirements; and d) provided training for a network data team on the new process and policy. | 2012-06-28 | 2013-06-25 | Does Not Contest | WECC reviewed WECC_URE3's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2012009453 | Settlement Agreement | WECC_URE3 submitted a Self-Certification to WECC stating that it was in violation of CIP-005-3 R5. WECC_URE3 reported two instances of noncompliance. The first instance occurred when WECC_URE3 implemented a change in its technical and procedural mechanisms for electronic access to access points to ESPs for WECC_URE3's energy management system (EMS). WECC_URE3, however, discovered that it failed to update documentation to reflect modification of network controls within 90 days, in violation of CIP-005-3 R5.2. WECC found that WECC_URE3 implemented significant changes to network controls, without updating network control procedural documentation within 90 days of the change. WECC determined that WECC_URE3 failed to update changes to electronic access control procedures within ninety days, in violation of R5.2. The second instance of noncompliance occurred approximately a year later, when WECC_URE3 implemented a configuration change to its electronic security monitoring system that resulted in a failure to retain electronic access logs for 90 days, in violation of R5.3. WECC determined that WECC_URE3 was in violation of R5.3 for not maintaining electronic access logs for 90 days. | CIP-005-3a | R5; R5.2; R5.3 | Lower | Severe | This violation posed a minimal risk and did not pose a serious and substantial risk to the reliability of the bulk power system (BPS) because of mitigating factors in place during the duration of the violation. Electronic access logs were generated and retained on local cyber assets. In the event of a system event, these local logs would have been available for review. Access to ESPs was controlled and monitored during the duration of the violation. Lastly, WECC_URE3 implemented intrusion detection and prevention controls that would have immediately detected and alerted unauthorized access or malicious activity within the ESP. | when WECC_URE3 implemented significant changes to network controls | Mitigation Plan completion | $17,000 (for WECC2012009451, WECC2012009453, and WECC2012009459) | Self-Certification | To mitigate this violation, WECC_URE3: a) For CIP-005-3 R5.2: 1) conducted a review of the existing documentation against the current processes and procedures. WECC_URE3 identified any discrepancies and updated documentation. Once the documentation was updated and approved, all network data team members were trained on the current processes; 2) created a new documentation review procedure to ensure that documentation related to CIP-005 is reviewed and updated within 90 days of any significant changes and again annually to ensure that WECC_URE3 is compliant with the R5 requirement; b) For CIP-005-3 R5.3: 1) ensured that the CIP-applicable devices are only creating those logs that are necessary and appropriate. There may have been too many legitimate event logs being generated by the CIP-applicable devices and negatively impacting log management. Not all of these log events were necessary for security review and incident response processes. WECC_URE3 reduced the unnecessary log generation to help with log storage, management, and review processes; 2) ensured that its Security Incident and Event Management (SIEM) tools were licensed appropriately. Once the aforementioned process was been completed, WECC_URE3 was able to determine if sufficient license thresholds have been purchased. WECC_URE3 then created alerts that will be triggered if applicable devices are creating an unexpected number of events; and 3) developed better alerting conditions designed to more quickly identify logging levels that threaten WECC_URE3's ability to be alerted to certain security issues or sufficiently retain logs to respond to potential incidents. WECC_URE3 also reviewed its current monitoring process for efficiencies and possible improvements that may help mitigate future risk from similar issues. | 2012-06-28 | 2012-10-08 | Does Not Contest | WECC reviewed WECC_URE3's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2012009459 | Settlement Agreement | WECC_URE3 submitted a Self-Certification to WECC stating that it was in violation of CIP-007-3 R6.3. WECC_URE3 implemented a configuration change to its electronic security monitoring system that resulted in a failure to retain electronic system event logs for 90 days, in violation of CIP-007-3 R6.3. WECC determined that the configuration change made by WECC_URE3 resulted in the generation of approximately 20,000 to 30,000 logs per minute. The space on the two devices used to store logs, the Security Incident and Event Management (SIEM) server and secondary server, was quickly filled. WECC determined that because the two devices were overwhelmed, both devices were not able to retain the logs for 90 days. WECC determined that WECC_URE3's failure to maintain system event logs for 90 days constitutes a violation of CIP-007-3 R6.3. | CIP-007-3a | R6; R6.3 | Medium | Severe | This violation posed a minimal risk and did not pose a serious and substantial risk to the reliability of the bulk power system (BPS) because access logs were generated and retained on local Cyber Assets. In the event of a system event, these local logs would have been available for review. In addition, access to Electronic Security Perimeters (ESPs) and devices therein was controlled and monitored during the duration of the violation. Lastly, WECC_URE3 implemented intrusion detection and prevention controls that would have immediately detected and alerted unauthorized access or malicious activity within the ESP. | when WECC_URE3 implemented the configuration change | Mitigation Plan completion | $17,000 (for WECC2012009451, WECC2012009453, and WECC2012009459) | Self-Certification | To mitigate this violation, WECC_URE3: 1) ensured that the CIP-applicable devices are only creating those logs that are necessary and appropriate. 2) ensured that its SIEM tools were licensed appropriately. 3) Once the aforementioned process has been completed, WECC_URE3 will be able to determine if sufficient license thresholds have been purchased. 4) created alerts that will be triggered if applicable devices are creating an unexpected number of events. In conjunction with the two items listed above, WECC_URE3 developed better alerting conditions designed to more quickly identify logging levels that threaten WECC_URE3's ability to be alerted to certain security issues or sufficiently retain logs to respond to potential incidents. 5) reviewed its current monitoring process for efficiencies and possible improvements that may help mitigate future risk from similar issues. | 2012-06-28 | 2012-08-08 | Does Not Contest | WECC reviewed WECC_URE3's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC2013011953 | Settlement Agreement | WECC_URE4 submitted a Self-Report to WECC stating that it was in violation of CIP-005-3a R1, specifically, R1.5 because it failed to provide CIP-007-3 R1 and CIP-007-3 R5.3.3 protections required by the Standard. WECC_URE4 reported that it failed to change passwords for two electronic access and control monitoring (EACM) devices. In addition, WECC_URE4 reported that it installed four EACM devices without documenting the test procedures and their results. | CIP-005-3a | R1; R1.5 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE4's network is electronically monitored 24 hours a day, 7 days a week. If any suspicious or unusual traffic appears on the network, automatic alerts are sent to WECC_URE4 staff for review. Only authorized personnel with CIP training and Personnel Risk Assessments have access to the devices. The devices reside within a Physical Security Perimeter, which requires employees to have company clearances before physical access is granted. | when WECC_URE4 installed the first EACM device without documenting the test procedures and their results | Mitigation Plan completion | $55,000 (for WECC2013011953, WECC2013011954, WECC2013011959, WECC2013011958, WECC2013012167, and WECC2013012168) | Self-Report | To mitigate this violation,WECC_URE4: 1) modified the Critical Cyber Asset installation job plan to provide better detail on the steps necessary to document CIP-007 R1 test procedures and results adequately ; 2) changed the passwords on the affected devices; 3) revised and updated its password monitoring documents to include password last set date and local accounts; 4) developed an annual password reset job plan that all passwords are changed annually; and 5) created a preventative maintenance work order to remind WECC_URE4 staff of the annual password change requirement and document its completion. | 2013-02-14 | 2013-03-22 | Does Not Contest | WECC reviewed WECC_URE4's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. WECC determined that WECC_URE4’s prior compliance history to be an aggravating factor in the penalty determination.
Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC2013011954 | Settlement Agreement | WECC_URE4 submitted a Self-Report to WECC stating that it was in violation of CIP-006-3c R2, specifically R2.2, because it failed to provide CIP-007-3 R5.3.3 protections as required by the Standard. WECC_URE4 reported that it failed to afford CIP-007-3 R5.3.3 protections to five out of ten Physical Access Control Systems (PACs) devices. WECC_URE4 also reported that it had not changed the passwords on five PACs devices. | CIP-006-3c | R2; R2.2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE4's network is electronically monitored 24 hours a day, 7 days a week. If any suspicious or unusual traffic appears on the network, automatic alerts are sent to WECC_URE4 staff for review. Only authorized personnel with CIP training and Personnel Risk Assessments have access to the devices. The devices reside within a Physical Security Perimeter, which requires employees to have company clearances before physical access is granted. | when WECC_URE4 was required to change passwords on the five PACs devices | Mitigation Plan completion | $55,000 (for WECC2013011953, WECC2013011954, WECC2013011959, WECC2013011958, WECC2013012167, and WECC2013012168) | Self-Report | To mitigate this violation, WECC_URE4: 1) changed the passwords on the affected devices; 2) revised and updated its password monitoring documents to include password last set date and local accounts; 3) developed an annual password reset job plan that all passwords are changed annually; and 4) created a preventative maintenance work order to remind WECC_URE4 staff of the annual password change requirement and document its completion. | 2013-02-13 | 2013-03-22 | Does Not Contest | WECC reviewed WECC_URE4's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. WECC determined that WECC_URE4’s prior compliance history to be an aggravating factor in the penalty determination.
Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC2013011959 | Settlement Agreement | WECC_URE4 submitted a Self-Report to WECC stating that it was in violation of CIP-007-1 R5.3.3 because WECC_URE4 did not change the user account passwords on 17 out of 27 Critical Cyber Assets. | CIP-007-1 | R5; R5.3.3 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE4's network is electronically monitored 24 hours a day, 7 days a week. If any suspicious or unusual traffic appears on the network, automatic alerts are sent to WECC_URE4 staff for review. Only authorized personnel with CIP training and Personnel Risk Assessments have access to the devices. The devices reside within a Physical Security Perimeter, which requires employees to have company clearances before physical access is granted. | when WECC_URE4 was required to change passwords on the devices | Mitigation Plan completion | $55,000 (for WECC2013011953, WECC2013011954, WECC2013011959, WECC2013011958, WECC2013012167, and WECC2013012168) | Self-Report | To mitigate this violation, WECC_URE4: 1) changed the passwords on the affected devices; 2) revised and updated its password monitoring documents to include password last set date and local accounts; and 3) developed an annual password reset job plan that all passwords are changed annually; and 4) created a preventative maintenance work order to remind WECC_URE4 staff of the annual password change requirement and document its completion. | 2013-02-22 | 2013-03-29 | Does Not Contest | WECC reviewed WECC_URE4's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC2013011958 | Settlement Agreement | WECC_URE4 submitted a Self-Report to WECC stating that it was in violation of CIP-007-3a R1. WECC_URE4 failed to document test procedures and their associated results for one Critical Cyber Asset (CCA) and two non critical Cyber Assets. WECC_URE4 tested one device with ad hoc testing procedures and did not follow documented test procedures as required by the Standard. Additionally, WECC_URE4 failed to document properly the results associated with that testing. | CIP-007-3a | R1 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE4 does not allow remote access into its network and the Electronic Security Perimeters in scope are segregated from the corporate network and public internet. Additionally, the devices were installed in an existing CIP managed network where access is controlled and monitored. WECC_URE4 conducted some testing on one of the devices in question prior to installation. The testing included verification that cybersecurity control applications were installed and functioning correctly, that only ports and services required for normal operation were enabled, and default accounts were disabled prior to installation. All devices are located within a Physical Security Perimeter. Furthermore, if any unusual traffic occurs on the network, alerts are sent via email to WECC_URE4 staff. | when the first device was installed | Mitigation Plan completion | $55,000 (for WECC2013011953, WECC2013011954, WECC2013011959, WECC2013011958, WECC2013012167, and WECC2013012168) | Self-Report | To mitigate this violation, WECC_URE4: updated its CCA installation job plan to ensure that devices are installed in accordance with the requirements of CIP-007-3 R1. | 2013-02-14 | 2013-03-22 | Does Not Contest | WECC reviewed WECC_URE4's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC2013012167 | Settlement Agreement | WECC conducted an onsite Compliance Audit of WECC_URE4 and discovered that it was in violation of CIP-005-1 R1. WECC_URE4 did not include five Critical Cyber Assets (CCAs) in its Electronic Security Perimeters. | CIP-005-1 | R1 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE4 has a defense-in-depth architecture of administrative, physical, and logical Cyber Security controls. WECC_URE4 has physical security measures which include guards, special locks, and CCTV for devices which reside within its Physical Security Perimeter. Additionally, WECC_URE4 has implemented various logical controls to protect its CCAs. These controls include firewalls, vulnerability scanning tools, and a security incident and events management program. These programs allow WECC_URE4 to detect promptly any potential threats to its CCAs. Additionally, WECC_URE4's procedures ensure that proper steps are taken following any potential threats. | when the Standard became mandatory and enforceable to WECC_URE4 | when WECC_URE4 decommissioned the ESP | $55,000 (for WECC2013011953, WECC2013011954, WECC2013011959, WECC2013011958, WECC2013012167, and WECC2013012168) | Compliance Audit | To mitigate this violation,WECC_URE4: 1) relocated one CCA; 2) created a new subnet; and 3) updated its CIP SQL database, its network diagram for CIP assets, and other documentation. | 2013-05-03 | TBD | Does Not Contest | WECC reviewed WECC_URE4's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC2013012168 | Settlement Agreement | WECC conducted an onsite Compliance Audit of WECC_URE4 and discovered that it was in violation of CIP-005-3 R2. WECC_URE4 failed to use a proper access control model that denies access by default, such that explicit access permissions must be specified. | CIP-005-3 | R2; R2.1 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE4 has a defense-in-depth architecture of administrative, physical and logical Cyber Security controls. WECC_URE4 has physical security measures which include guards, special locks, and CCTV for devices which reside within its Physical Security Perimeter. Additionally, WECC_URE4 has implemented various logical controls to protect its CCAs. These controls include firewalls, vulnerability scanning tools, and a security incident and events management program. These programs allow WECC_URE4 to promptly detect any potential threats to its CCAs. Additionally, WECC_URE4's procedures ensure that proper steps are taken following any potential threats. | when the Standard became mandatory and enforceable to WECC_URE4 | when WECC_URE4 decommissioned the ESP | $55,000 (for WECC2013011953, WECC2013011954, WECC2013011959, WECC2013011958, WECC2013012167, and WECC2013012168) | Compliance Audit | To mitigate this violation, WECC_URE4: 1) relocated one CCA; 2) created a new subnet; and 3) updated its CIP SQL database, its network diagram for CIP assets, and other documentation. | 2013-05-03 | TBD | Does Not Contest | WECC reviewed WECC_URE4's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. WECC determined that WECC_URE4's compliance history to be an aggravating factor in the penalty determination.