## PUBLIC_CIP Violations
Region | Registered Entity | NCR_ID | NERC Violation ID # | Notice of Confirmed Violation or Settlement Agreement | Description of the Violation | Reliability Standard | Req. | Violation Risk Factor | Violation Severity Level | Risk Assessment | Violation Start Date | Violation End Date | Total Penalty or Sanction ($) | Method of Discovery | Description of Mitigation Activity | Mitigation Completion Date | Date Regional Entity Verified Completion of Mitigation | "Admits," "Agrees/Stipulates," "Neither Admits nor Denies," or "Does Not Contest" | Other Factors Affecting the Penalty Determination, including Compliance History, Internal Compliance Program and Compliance Culture
Florida Reliability Coordinating Council, Inc.(FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2011008323 | Settlement Agreement | FRCC_URE1 submitted a Self-Report to FRCC stating that it was in violation of CIP-005-1 R1.5. FRCC_URE1 did not afford all protective measures, specifically CIP-005 R2.1 and R2.2, for a number of electronic access control and monitoring system (EACMS) Cyber Assets. In addition, FRCC_URE1 reported it lacked documentation listing the approved ports and services required for normal and emergency operation at the access points. Furthermore, FRCC_URE1 failed to identify additional EACMS Cyber Assets and afford the protective measures as required by CIP-005-2 R1.5. The specific protective measures excluded were CIP-003 R5, CIP-005 R2, CIP-005 R3, CIP-007 R1, CIP-007 R3, CIP-007 R4, CIP-007 R5, and CIP-007 R6. | CIP-005-1 | R1.5 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). FRCC determined that the violation posed a moderate risk because EACMS Cyber Assets are critical to ESP protection. Although FRCC_URE1 or the contractor managing them did not document all the afforded security measures, specifically CIP-005 R2.1 and R2.2, that could demonstrate compliance with CIP-005 R1.5, most of the essential secured measures were always enforced, such as monitoring for user access control, intrusion detection, and logging. Furthermore, FRCC_URE1 maintained all EACMS Cyber Assets behind a corporate firewall and within a Physical Security Perimeter (PSP), thereby limiting any potential serious impact from failure of any individual EACMS Cyber Asset reported under this violation. In addition, all personnel with logical and physical access had proper personnel risk assessments (PRAs) and cyber training. The risk for additional EACMS Cyber Asset was mitigated as it was afforded the protective measures from all other CIP requirements. | when the Standard became mandatory and enforceable for FRCC_URE1 | Mitigation Plan completion | $35,000 (for FRCC2011008323, FRCC2011008324, FRCC2011008325, FRCC2011008326, FRCC2012010357, FRCC2012010359, and FRCC2012010358) | Self-Report | To mitigate this violation, FRCC_URE1: 1) created new access points into the ESP by purchasing and installing new firewalls on the outside perimeter of the headquarters energy management system (EMS) and backup EMS switches. This action created two separate ESPs and eliminated the need for any access control on the switches. The new firewalls enabled FRCC_URE1 to establish deny-by-default access methodology to control ports and services at the newly defined access points; 2) changed the firewall rule set to reflect the approved ports and services, as configured on the headquarters EMS firewall, for access to the safe room. This revised rule set is similar to the rule set defined on the headquarters EMS firewall, but with the source and destinations for services and internet protocol (IP) reversed; 3) updated the documents identifying the approved ports and services on the firewalls. These documents list the defined ports and services on the firewalls along with an explanation for their use; 4) moved the old firewalls outside the new firewalls, and thus outside the ESP. FRCC_URE1 had originally planned to update the old firewalls’ configuration to define explicitly the IP addresses allowed for communications, and deny by default all non-defined IP addresses. The new firewalls became the EACM for the ESP, and were configured to define explicitly the IP addresses allowed for communication. Monitoring is performed via syslog to the application already deployed; 5) updated affected NERC CIP-related documentation such as the ESP drawing and CCA list, to reflect these changes; and 6) reviewed FRCC_URE1's recovery plans for firewall recovery in the case of a disaster and updated its recovery plan practice. | 2012-03-14 | 2013-05-09 | Neither Admits nor Denies | FRCC reviewed FRCC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
Florida Reliability Coordinating Council, Inc.(FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2011008324 | Settlement Agreement | FRCC_URE1 submitted a Self-Report to FRCC stating that it was in violation of CIP-006-2 R1.1. FRCC_URE1 did not deploy and document alternative measures for the Cyber Assets (non-FRCC_URE1 owned) along the path of the leased fiber cable where a completely enclosed border could not be established. The fiber cable travels between the two Physical Security Perimeters (PSPs) using a dedicated optical circuit managed by a communications provider. The Cyber Assets on each end of the circuit were not identified nor acting as access points and thus a single Electronic Security Perimeter (ESP) existed between the two PSPs. | CIP-006-1 | R1.1 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). FRCC determined that the violation posed a moderate risk because failure to deploy alternative measures could lead to a potential cyber threat on the unprotected Cyber Assets and the optical circuit between the two PSPs. The risk was reduced as the end points of the communication links were protected by switches that are contained within a defined PSP with machine access control lists (ACLs) and port security. The risk was further reduced as the communication link was a dedicated optical circuit making it difficult to sniff or inject traffic without advanced telecommunications equipment. | when the Standard became mandatory and enforceable for FRCC_URE1 | Mitigation Plan completion | $35,000 (for FRCC2011008323, FRCC2011008324, FRCC2011008325, FRCC2011008326, FRCC2012010357, FRCC2012010359, and FRCC2012010358) | Self-Report | To mitigate this violation, FRCC_URE1: 1) redefined the former single ESP into two distinctly separate ESPs at FRCC_URE1 headquarters and backup facilities. These two locations continue to be connected via the optical carrier 3 (OC-3) circuit, but the leased line is now classified as a data communication link between discrete ESPs. The OC-3 circuit does not require a 6-walled border, since it is no longer part of a defined ESP; 2) purchased and installed firewalls that enable them to establish a deny-by-default access methodology to control ports and services at these newly defined access points; 3) established appropriate electronic access controls on the newly defined ESPs. Since the OC-3 circuit is no longer defined as part of the ESP, FRCC_URE1 implemented protective Cyber Assets to control electronic access at the points of connection between the leased circuit and the two separate energy management system networks; and 4) completed migration of the EMS network. | 2011-12-30 | 2013-02-19 | Neither Admits nor Denies | FRCC reviewed FRCC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
Florida Reliability Coordinating Council, Inc.(FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2011008325 | Settlement Agreement | FRCC_URE1 submitted a Self-Report to FRCC stating that it was in violation of CIP-006-1 R1.8. FRCC_URE1 did not afford all protective measures required by CIP-006-1 R1.8 to a number of deployed physical access control system (PACS) Cyber Assets for almost two years, and additional PACS Cyber Assets for a year. Specifically, the protective measures excluded were CIP-003 R5, CIP-005 R2, CIP-005 R3, CIP-007 R2, CIP-007 R3, CIP-007 R4, and CIP-007 R6.2. | CIP-006-1 | R1.8 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). FRCC determined that the violation posed a moderate risk because failure to properly provide protective measures for the Cyber Assets left them unprotected and vulnerable to a cyber threat. The risk was mitigated, however, as the PACS Cyber Assets were secured behind the corporate firewall and within a required Physical Security Perimeter (PSP). Furthermore the PACS Cyber Assets were accessible only to internal users with appropriate clearance and personnel risk assessments (PRAs). All other CIP requirements were met for these Cyber Assets. | when the Standard became mandatory and enforceable for FRCC_URE1 | Mitigation Plan completion | $35,000 (for FRCC2011008323, FRCC2011008324, FRCC2011008325, FRCC2011008326, FRCC2012010357, FRCC2012010359, and FRCC2012010358) | Self-Report | To mitigate this violation, FRCC_URE1: 1) initiated a project to assess each CIP Reliability Standard and sub-requirement that pertains to the PACS. The project included mitigation initiation, assessment, solution, implementation, operations, and documentation and addressed all standards captured by the CIP-006-1 R1.8 requirement; 2) implemented an information technology infrastructure library ready software application and revised its change control and configuration management practice to address the protective measures required by CIP-003 R6; 3) discussed electronic access point (EAP) architecture and design with third-party vendor, implemented new EAP solution in-house, verified operational readiness, gathered evidence including new EAP diagram to support changes, and revised its ESP practices to address the protective measures required by CIP 005 R2-R3; 4) implemented a vulnerability and patch management software application and revised its test procedures and security patch management practice to address the protective measures required by CIP-007 R1 and R3; 5) documented applications and services using user datagram protocol/ transmission control protocol ports and revised its firewall ports and services practice to address the protective measures required by CIP-007 R2; 6) evaluated and installed malicious software and anti-malware software application, tested and verified application and process, and revised its malicious software prevention practice to address the protective measures required by CIP-007 R4; 7) ensured and documented that all system accounts are compliant with password length, password age, and password complexity requirements. If any of these conditions were not met due to technical infeasibility, a technical feasibility exception (TFE) was submitted with reference to this mitigation plan. Revised its system account management practice to address the protective measures required by CIP-007 R5; 8) implemented a security status monitoring and alerting software application, and revised its monitoring system cybersecurity events practice to address the protective measures required by CIP-007 R6; 9) performed operational readiness exercise on disposal process and revised its disposal/redeployment of Cyber Assets practice to address the protective measures required by CIP-007 R7; 10) revised its cybersecurity incident response and reporting practice to include EAP Cyber Assets addressed in CIP-005 R2 and R3 to address the protective measures required by CIP-008 R1; 11) revised its cyber recovery plans practice to incorporate additional criteria to address varying degree impact or incident to initiate a full recovery, as well as additional roles and responsibilities to address actions taken when responding to a recovery event to address the protective measures required by CIP-009 R1; 12) filed new TFEs, as appropriate, to implement compensating measures to address the access control panels associated with the PACS; and 13) completed final compliance review of activities and evidence. | 2012-10-02 | 2013-05-16 | Neither Admits nor Denies | FRCC reviewed FRCC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
Florida Reliability Coordinating Council, Inc.(FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2011008326 | Settlement Agreement | FRCC_URE1 submitted a Self-Report to FRCC stating that it was in violation of CIP-007-1 R2, R2.1, and R2.2. FRCC_URE1 did not establish and document the process for ensuring that only ports required for normal and emergency operations are enabled for a number of Cyber Assets during the violation period. | CIP-007-1 | R2; R2.1; R2.2 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). FRCC determined that this violation posed a moderate risk because failure to enable only ports and services required for normal and emergency operations can leave the Cyber Assets unprotected and vulnerable to a cyber threat. FRCC_URE1 had mitigated the risk because all workstations and servers had anti-malware for threat detection from services that may be exploited, and all Cyber Assets were behind a corporate firewall. All workstations and servers were also kept up-to-date with operating system security patches. Furthermore, all personnel with access to these Cyber Assets had current personnel risk assessments (PRAs) and cybersecurity training. | when the Standard became mandatory and enforceable for FRCC_URE1 | Mitigation Plan completion | $35,000 (for FRCC2011008323, FRCC2011008324, FRCC2011008325, FRCC2011008326, FRCC2012010357, FRCC2012010359, and FRCC2012010358) | Self-Report | To mitigate this violation, FRCC_URE1: 1) conducted comprehensive port scans on existing Cyber Assets for ports and services; 2) checked all scanned assets against the Cyber Asset document and confirmed by manual inspection to ensure that all Cyber Assets were included and accounted for; 3) included all user datagram protocol ports as well as the entire range of transmission control protocol ports in the port scans; 4) ran scans against all Cyber Assets within the Electronic Security Perimeters (ESP) as well as all ESP access point Cyber Assets; 5) conducted port scans of ESP access point Cyber Assets against internal interfaces; 6) implemented a new energy management system (EMS) and rescanned all equipment for any additional ports and services required for operation; 7) updated the ports and services documentation with the new scan results; 8) analyzed the new scan results to determine which ports and services are required for operation and modified its ports & services documentation to define and describe the purpose of each port or service, which became the revised ports and services baseline; 9) reviewed all services currently running within the EMS local area network; 10) turned off or disabled all unnecessary services and provided justification for all required services; 11) rescanned all servers and workstations for any additional services required for operation and modified services documentation to incorporate changes; and 12) opened a ticket with the firewall vendor and attached a port scan for its review of the required firewall ports and services; the vendor reviewed the ports that were open on the interface and suggested actions for FRCC_URE1 to address; reviewed the rule sets and determined which ports and services were required for operation; and submitted the findings to the vendor to implement only the required ports and services on the firewall’s internal interface. | 2012-08-30 | 2013-06-14 | Neither Admits nor Denies | FRCC reviewed FRCC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
Florida Reliability Coordinating Council, Inc.(FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2012010357 | Settlement Agreement | During a Compliance Audit FRCC determined that FRCC_URE1 was in violation of CIP-005-1 R2, R2.1, R2.2, R2.3, R2.4, and R2.6. FRCC_URE1 failed to demonstrate that its process and mechanisms used an access control model that denies access by default, such that explicit access permissions were specified as required. FRCC_URE1 also failed to demonstrate that only the required ports were enabled. FRCC_URE1 also failed to demonstrate that strong procedural or technical controls at access points to ensure the authenticity of the accessing party were enforced for Cyber Assets used to communicate to analog circuits. Furthermore, a procedure for securing dial-up access to the Electronic Security Perimeters (ESPs) did not exist. | CIP-005-1 | R2; R2.1; R2.2; R2.3; R2.4 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). FRCC determined that this violation posed a moderate risk because failure to establish an access control model of deny by default, and enable only ports and services required for normal and emergency operations can leave the Cyber Assets unprotected and vulnerable to a cyber threat. The risk was reduced because the access points connected down-stream ESPs and were protected to only allow trusted sources to communicate through these access points. Furthermore, the access points were afforded all protective measures from all other CIP requirements. | when the Standard became mandatory and enforceable for FRCC_URE1 | when FRCC_URE1 placed the necessary firewalls, implemented access point rule sets, and wrote a procedure for allowing access to ESP | $35,000 (for FRCC2011008323, FRCC2011008324, FRCC2011008325, FRCC2011008326, FRCC2012010357, FRCC2012010359, and FRCC2012010358) | Compliance Audit | To mitigate this violation, FRCC_URE1: 1) moved the Cyber Assets outside the ESP by placing new firewalls between the routers and energy management system network to ensure that they are no longer access points nor classified as Cyber Assets within the ESP; 2) verified that the new firewalls became the access points and provide a deny-by-default access control model and enable only ports and services required for operation; 3) refined the rule sets on the existing access points specifically to identify the allowed IP addresses to ensure that, unless specifically noted and justified, all access point rule sets explicitly identify the permitted network addresses across the perimeter; and 4) wrote a procedure for securing dial-up access to the ESP. | 2013-02-21 | 2013-06-14 | Neither Admits nor Denies | FRCC reviewed FRCC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
Florida Reliability Coordinating Council, Inc.(FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2012010359 | Settlement Agreement | During a Compliance Audit FRCC determined that FRCC_URE1 was in violation of CIP-005-1 R3, R3.1, and R3.2. FRCC_URE1 failed to implement and document an electronic or manual process(es) for monitoring and logging access at access points to the Electronic Security Perimeters (ESPs) 24 hours a day, seven days a week. Specifically, some Cyber Asset failed to log access for a period of eight hours. In addition, FRCC_URE1 failed to log all the successful attempts at access points for all Cyber Assets. Lastly, FRCC_URE1 failed to detect and alert for attempts at or actual unauthorized accesses for a number of access points; no technical feasibility exceptions (TFE) were filed, and FRCC_URE1 had not performed a manual review of logs every 90 days. | CIP-005-1 | R3; R3.1; R3.2 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). FRCC determined that this violation posed a moderate risk because failure to implement electronic or manual processes for monitoring and logging access can leave the Cyber Assets unprotected and vulnerable to a cyber threat. The risk was mitigated because the lack of logging was limited to successful access at only 30% of the access points and only a few Cyber Assets during an outage for a period of eight hours. Additionally, all the denied attempts were being logged at the IP-accessible access points. | when the Standard became mandatory and enforceable for FRCC_URE1 | when FRCC_URE1 finalized the process for logging and monitoring access | $35,000 (for FRCC2011008323, FRCC2011008324, FRCC2011008325, FRCC2011008326, FRCC2012010357, FRCC2012010359, and FRCC2012010358) | Compliance Audit | To mitigate this violation, FRCC_URE1: 1) developed a process for logging and capturing internal log buffer during logging disruptions for access points; 2) purchased, tested, and implemented backup syslog server; 3) implemented the logging process and tested logging of successful and unsuccessful login attempts at all access points; 4) finalized logging process document and added reference to process in appropriate FRCC_URE1 practice; and 5) performed compliance department final review of mitigation plan completion. | 2013-05-14 | 2013-06-14 | Neither Admits nor Denies | FRCC reviewed FRCC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
Florida Reliability Coordinating Council, Inc.(FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2012010358 | Settlement Agreement | During a Compliance Audit FRCC determined that FRCC_URE1 was in violation of CIP-007-1 R3, R3.1, and R3.2. FRCC_URE1 failed to establish, document, and implement a security patch management program for tracking, evaluating, testing, and installing applicable cybersecurity software patches for all Cyber Assets within the Electronic Security Perimeters (ESPs). Specifically, for some Cyber Assets and workstation/server applications, FRCC_URE1 documentation was insufficient to demonstrate that available patches were evaluated for applicability. Also, FRCC_URE1 did not evaluate new software releases containing security upgrades. Further, FRCC_URE1 documents were insufficient to demonstrate that FRCC_URE1 assessed security patches and security upgrades for applicability within 30 calendar days of availability of the patches or upgrades. | CIP-007-1 | R3; R3.1; R3.2 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). FRCC determined that the violation posed a moderate risk because failure to establish, document, and implement a complete security patch management program can leave the Cyber Assets unprotected and vulnerable to a cyber threat. The risk was mitigated because FRCC_URE1 patched operating systems on all of the servers and workstations, which made up most of the Cyber Assets (between 79% and 94%) over the duration of the violation. | when the Standard became mandatory and enforceable for FRCC_URE1 | present | $35,000 (for FRCC2011008323, FRCC2011008324, FRCC2011008325, FRCC2011008326, FRCC2012010357, FRCC2012010359, and FRCC2012010358) | Compliance Audit | To mitigate this violation, FRCC_URE1: 1) scanned Critical Cyber Assets and Cyber Assets, and generated a list of installed applications running on each asset; 2) reviewed the Cyber Asset application inventory spreadsheet, and identified the applications that could be removed; and 3) had a vendor remove unnecessary applications from the Cyber Assets and hired a vendor to conduct security patch assessment and testing. To mitigate this violation, FRCC_URE1 will: 1) develop interim processes to bring Cyber Assets into compliance and to assess non-vendor-supported security patches; 2) start the process of bringing Cyber Assets into compliance; 3) modify or replace FRCC_URE1 documentation to include new processes for non-vendor security patches; 4) remove all non-approved software from all Cyber Assets; 5) assess all non-vendor security patches for all Cyber Assets; 6) either install security patches or implement compensating measures, and place all Cyber Assets under FRCC_URE1's process documentation; and 7) perform corporate compliance department final review. | 12/20/2013 (approved completion date) | TBD | Neither Admits nor Denies | FRCC reviewed FRCC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO201100371 | Notice of Confirmed Violation | During a Spot Check, MRO discovered that MRO_URE1 was in violation of CIP-002-1 R3. MRO_URE1 failed to develop a list of associated Critical Cyber Assets (CCAs) essential to the operation of Critical Assets. During the Spot Check, MRO_URE1 failed to present sufficient evidence to demonstrate that Cyber Assets outside of a given Critical Asset’s Electronic Security Perimeter (ESP) and not co-located with the Critical Asset were properly evaluated (i.e., determined to be essential or not essential to the operation of the Critical Asset). MRO_URE1 originally identified 130 Cyber Assets that needed to be evaluated for criticality. During mitigation, MRO_URE1 identified 1,296 Cyber Assets that needed to be evaluated for criticality, including all Cyber Assets at substations with routable connectivity to MRO_URE1's control centers (two Critical Assets). The assessment of the new list did not result in the identification of any additional CCAs. | CIP-002-1 | R3 | High | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although there was a large increase in the number of Cyber Assets included in MRO_URE1's evaluation, the additional Cyber Assets consisted of remote terminal units, substation intelligent electronic devices, and substation routers. These devices reside on a network separate from the control centers, with firewalls in place between the networks. Furthermore, these firewalls were sampled in a previous Compliance Audit for another CIP standard, and MRO did not identify any issues with the configuration to protect the control center ESP. Additionally, because MRO_URE1 does not possess any substations that are identified as Critical Assets, the evaluation of the substation Cyber Assets focused only on their impact on the control center's CCAs; these CCAs reside in a different Physical Security Perimeter and in a different ESP than the Cyber Assets added to the evaluation. | when the Standard became mandatory and enforceable for MRO_URE1 | when MRO_URE1 developed a list of associated CCAs essential to the operation of Critical Assets | 6000 | Spot Check | To mitigate this violation, MRO_URE1: 1) developed a list of associated CCAs essential to the operation of Critical Assets; 2) revised its assessment procedure for its next annual risk-based assessment methodology; and 3) provided training to the individuals responsible for implementing the modified procedure. | 2012-09-10 | 2012-09-12 | Admits | MRO reviewed MRO_URE1's internal compliance program and considered it to be a neutral factor in the penalty determination.
Texas Reliability Entity, Inc. (Texas RE) | Unidentified Registered Entity 1 (Texas RE_URE1) | NCRXXXXX | TRE201100470 | Settlement Agreement | Texas RE conducted an on-site Compliance Audit of Texas RE_URE1. During the Compliance Audit, Texas RE discovered Texas RE_URE1 had a violation of CIP-007-2a R2. A review of Texas RE_URE1's CIP-007 policy, required ports and services listings, firewall configuration, and Critical Cyber Asset (CCA) cyber vulnerability assessment (CVA) suggested that despite having an established and documented process, Texas RE_URE1 failed to implement its process fully to ensure that only those ports and services required for normal and emergency operations are enabled, a violation of CIP-007 R2. Texas RE_URE1's Electronic Security Perimeter (ESP) policy states that firewalls are configured to allow for only the ports and services necessary for normal and emergency operations. However, in comparing Texas RE_URE1's listings of required ports and services with its CVA, open ports and services were identified during the CVA that were not documented in the applicable listings. All the required ports and services referenced in the three listings at minimum were expected to be identified in the CVA. The CVA was performed to identify all the open ports and services required to conduct normal and emergency cyber operations. Subsequently, Texas RE_URE1 provided supplemental documentation that identified additional open ports and services that were used for Texas RE_URE1's Supervisory Control and Data Acquisition (SCADA) that were not included in the CVA. This misalignment between the subject documents demonstrates that Texas RE_URE1 failed to follow its process to identify and ensure that only the ports and services required for normal and emergency operations were enabled. | CIP-007-2a | R2 | Medium | Severe | This violation posed a moderate risk but not a serious or substantial risk to the reliability of the bulk power system. The moderate risk was partially mitigated by Texas RE_URE1 providing a layered approach to protecting its Cyber Assets. Texas RE_URE1's layered approach includes firewalls, group user authentication, shared account reviews, infrastructure reviews, employee training, cyber incidence detection, and ESP/Physical Security Perimeter access authentication. Additionally, Texas RE_URE1 has an established CIP-007 program it relies upon, which has been in place since the Standard became mandatory and enforceable. | when the Standard became mandatory and enforceable to Texas RE_URE1 | Mitigation Plan completion | $15,000 (for TRE201100470 and TRE201100472) | Compliance Audit | To mitigate this violation Texas RE_URE1: 1) performed a CVA to include all the applicable open ports and services required to conduct normal and emergency operations; 2) updated its CVA procedures to ensure all open ports and services are included in future assessments; and 3) updated the CVA process version to prevent the likelihood of reoccurrence. | 2011-12-22 | 2013-05-24 | Neither Admits nor Denies | Texas RE reviewed Texas RE_URE1’s internal compliance program (ICP) and considered it to be a mitigating factor in in determining the penalty amount.
Texas Reliability Entity, Inc. (Texas RE) | Unidentified Registered Entity 1 (Texas RE_URE1) | NCRXXXXX | TRE201100472 | Settlement Agreement | Texas RE conducted an on-site Compliance Audit of Texas RE_URE1. During the Compliance Audit, Texas RE discovered Texas RE_URE1 had a violation of CIP-007-2a R8.2. A review of Texas RE_URE1's CIP-007 policy, required ports and services listings, firewall configuration, Critical Cyber Asset cyber vulnerability assessment (CVA), CVA Procedure, and a statement from Texas RE_URE1 revealed that the required user datagram protocol (UDP) ports were not included in the CVA or reviewed, in violation of CIP-007-2a R8.2. CIP-007 R2 required Texas RE_URE1 to perform a CVA on all Cyber Assets within its Electronic Security Perimeter (ESP) at least annually and to verify that only ports and services required for operation of the Cyber Assets within the ESP are enabled. Texas RE_URE1 has a documented process to ensure vulnerabilities are discovered in the equipment residing inside Texas RE_URE1's ESPs. The evidence showed the transport control protocol (TCP) and UDP ports are required for the operation of Cyber Assets residing in the ESP. However, the ports and services scan and CVA report revealed the CVA only included the ports and attached services associated with the TCP ports and not the UDP ports. Pursuant to the Standard, Texas RE_URE1 was also expected to conduct a verification and review on the UDP ports, which it did not. Further, there was no evidence provided to show attempts by Texas RE_URE1 to discover the UDP ports. During the Compliance Audit Texas RE_URE1 stated the UDP ports were inadvertently left off the port scan. | CIP-007-2a | R8; R8.2 | Medium | Severe | This violation posed a moderate risk but not a serious or substantial risk to the reliability of the bulk power system. The moderate risk was partially mitigated by Texas RE_URE1 providing a layered approach to protecting its Cyber Assets. Texas RE_URE1's layered approach includes firewalls, group user authentication, shared account reviews, infrastructure reviews, employee training, cyber incidence detection, and ESP/Physical Security Perimeter access authentication. Additionally, Texas RE_URE1 has an established CIP-007 program it relies upon, which has been in place since the Standard became mandatory and enforceable. | when the Standard became mandatory and enforceable to Texas RE_URE1 | Mitigation Plan completion | $15,000 (for TRE201100470 and TRE201100472) | Compliance Audit | To mitigate this violation Texas RE_URE1: 1) performed a CVA to include all the applicable open ports and services required to conduct normal and emergency operations; 2) updated its CVA procedures to ensure UDP ports are included in future assessments; and 3) updated the CVA process version to prevent the likelihood of reoccurrence. | 2011-12-22 | 2013-05-24 | Neither Admits nor Denies | Texas RE reviewed Texas RE_URE1’s internal compliance program (ICP) and considered it to be a mitigating factor in in determining the penalty amount.
Texas Reliability Entity, Inc. (Texas RE) | Unidentified Registered Entity 2 (Texas RE_URE2) | NCRXXXXX | TRE201100556 | Settlement Agreement | Texas RE concluded an on-site Compliance Audit of Texas RE_URE2 and determined that it had a violation of CIP-005-1 R4.3. Texas RE_URE2 failed to identify multiple Electronic Security Perimeter (ESP) access points as required by CIP-005-1 R4.3. A review of Texas RE_URE2's Cyber Vulnerability Assessment (CVA) procedures, electronic access procedures, the scan report, and the CVA revealed that several routers and network sub sets were absent from the CVA, the scan, and the manual access point identification process. Consequently, the discrepancies between the access point identification methodologies, the access point identification results, the documented access points, and the lack of the discovery of all the ESP access points demonstrates non-compliance with CIP-005-1 R4.3. | CIP-005-1 | R4; R4.3 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The moderate risk was mitigated by Texas RE_URE2 evidencing that an annual CVA and review was conducted on all of the ESP access points except the referenced routers and network sub sets and the report revealed no material issues. A review of the enabled ports and services for operations at the identified access points was conducted. Further, Texas RE_URE2 implemented a CVA program that has been in place since the standard became enforceable. | when the Standard became mandatory and enforceable on Texas RE_URE2 | Mitigation Plan completion | $17,200 (for TRE201100556 and TRE201100559) | Compliance Audit | To mitigate this violation, Texas RE_URE2: 1) conducted a CVA to demonstrate a vulnerability assessment was conducted on all the access points identified within the subject ESP; and 2) conducted training on its updated ESP access point evaluation and identification processes. In addition, Texas RE_URE2 is installing and implementing management software. This software will automate access control processes and enhance access management. | 2011-09-01 | 2013-04-17 | Neither Admits nor Denies | Texas RE reviewed Texas RE_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in in determining the penalty amount.
Texas Reliability Entity, Inc. (Texas RE) | Unidentified Registered Entity 2 (Texas RE_URE2) | NCRXXXXX | TRE201100559 | Settlement Agreement | Texas RE concluded an on-site Compliance Audit of Texas RE_URE2 and determined that it had a violation of CIP-007-1 R8. Texas RE_URE2 performed a cyber vulnerability assessment (CVA) on the Cyber Assets within its defined Electronic Security Perimeter (ESP), but the annual assessment did not include all the Cyber Assets in its two ESPs as identified on its network diagram. Based upon the review of the CVA provided by Texas RE_URE2 during the Compliance Audit, no evidence was provided to demonstrate that a CVA was performed on two Cyber Asset groups residing within the ESP. Several servers and web user interface devices identified by Texas RE_URE2 as Cyber Assets and shown within the ESP on the network diagram were not included in the CVA, the scan report, or manual scan results. This is a violation of CIP-007-1 R8, because the standard requires all Cyber Assets within an ESP to be included in a CVA assessment. | CIP-007-1 | R8 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The moderate risk was mitigated by Texas RE_URE2 evidencing an annual CVA and a review was conducted on all of the Cyber Assets within the ESP except the referenced routers and network sub sets and the report revealed no material issues. A review of the enabled ports and services required for operation of the identified Cyber Assets also was conducted. Further, Texas RE_URE2 has implemented a CVA program that has been in place since the standard became enforceable. | when the Standard became mandatory and enforceable on Texas RE_URE2 | Mitigation Plan completion | $17,200 (for TRE201100556 and TRE201100559) | Compliance Audit | To mitigate this violation, Texas RE_URE2: 1) completed its cyber vulnerability assessment on the missed devices; 2) reviewed and updated the Critical Cyber Asset (CCA) list and the drawing for the CCA ESP during change control meetings; and 3) compared the vulnerability assessment report to the CCA list and the ESP network drawing to ensure that the three documents match and are correct. In addition, Texas RE_URE2 is installing and implementing management software. This software will automate access control processes and enhance access management. | 2013-07-11 | 2013-07-16 | Neither Admits nor Denies | Texas RE reviewed Texas RE_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in in determining the penalty amount.
Texas Reliability Entity, Inc. (Texas RE) | Unidentified Registered Entity 3 (Texas RE_URE3) | NCRXXXXX | TRE2012010292 | Settlement Agreement | Texas RE concluded an on-site Compliance Audit of Texas RE_URE3 and determined that Texas RE_URE3 had a violation of CIP-004-1 R4. Texas RE_URE3 was able to provide evidence that it maintained a list of personnel with authorized cyber or authorized unescorted physical access to Critical Cyber Assets (CCAs). However, Texas RE determined that Texas RE_URE3 did not include the user’s specific electronic and physical access rights to CCAs. Although Texas RE_URE3 provided an Access Control List (List) that listed users with authorized cyber or authorized unescorted physical access to CCAs, Texas RE_URE3's List did not provide dates when: 1) the List was generated; 2) access for users and contractors was effective; and/or 3) specific electronic and physical rights to CCAs were granted to individually approved personnel. | CIP-004-1 | R4 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Although Texas RE_URE3 did not include each user’s specific electronic and physical access rights to CCAs, the Texas RE_URE3 infrastructure is protected from penetration by various layers of protection including firewalls, group user authentication, shared account reviews, infrastructure reviews, employee training, cyber incidence detection, and Electronic Security Perimeter (ESP)/Physical Security Perimeter (PSP) access authentication. | when the Standard became mandatory and enforceable on Texas RE_URE3 | Mitigation Plan completion | 4800 | Compliance Audit | To mitigate this violation, Texas RE_URE3 developed a master spreadsheet to detail the granted access duration dates and to indicate the specific access rights for each user. In addition, Texas RE_URE3 is installing and implementing management software. This software will automate access control processes and enhance access management. | 2010-12-31 | 2013-06-05 | Neither Admits nor Denies | Texas RE reviewed Texas RE_URE3's internal compliance program (ICP) and considered it to be a mitigating factor in in determining the penalty amount.
Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2012010764 | Settlement Agreement | WECC_URE1 submitted a Self-Certification stating that it was in violation of CIP-005-2 R3. Specifically, WECC_URE1 stated that on two separate instances it failed to monitor and log access at all access points to its Electronic Security Perimeters (ESPs) twenty-four hours a day, seven days a week. The first instance occurred for four days, and the second occurred for one day. WECC_URE1's firewalls controlling the sites' ESPs send access logs to a firewall manager device that retains the logs and then sends the logs to another device for analysis and detection. However, during two separate instances, the firewall manager failed, and the firewall logs were not retained and sent to the analysis and detection device. Because of the failure of the firewall manager device, WECC_URE1 was unable to monitor and log access at the access points to its primary and backup ESPs for one day. These access points contain a total of eleven Critical Cyber Assets (CCAs). | CIP-005-2 | R3 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. As compensating measures, WECC_URE1 stated that during these occasions, the firewalls were working to control access at both the sites. In addition, the management system was being monitored by the system personnel for any unusual activity. | when WECC_URE1 failed to monitor and log access at all access points to its ESPs when WECC_URE1 failed to monitor and log access at all access points to its ESPs | when WECC_URE1 replaced the firewall manager and continued to monitor and log access at all access points to its ESPs when WECC_URE1 replaced the firewall manager and continued to monitor and log access at all access points to its ESPs | 20000 | Self-Certification | To mitigate this violation, WECC_URE1 replaced the failed firewall manager with a new unit. | 2012-03-28 | 2013-04-30 | Agrees/Stipulates | WECC reviewed WECC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. WECC considered WECC_URE1's above and beyond measures to be a mitigating factor in the penalty determination. Specifically, WECC_URE1 will: 1) develop a process to track deadlines and mitigate timely minimizing the need for Mitigation Plan extension requests; 2) create a monthly coordination meeting between compliance groups that will focus on increasing communication between entities and centralizing issues stemming from information silos; 3) create an annual compliance awareness training program and measure the degree of understanding; 4) develop a process or improvements to processes that help identify the full scope of violations promptly; and 5) develop a process for detecting what controls are needed when new devices are installed.