## PUBLIC_CIP Violations
Region | Registered Entity | NCR_ID | NERC Violation ID # | Notice of Confirmed Violation or Settlement Agreement | Description of the Violation | Reliability Standard | Req. | Violation Risk Factor | Violation Severity Level | Risk Assessment | Violation Start Date | Violation End Date | Total Penalty or Sanction ($) | Method of Discovery | Description of Mitigation Activity | Mitigation Completion Date | Date Regional Entity Verified Completion of Mitigation | "Admits," "Agrees/Stipulates," "Neither Admits nor Denies," or "Does Not Contest" | Other Factors Affecting the Penalty Determination, including Compliance History, Internal Compliance Program and Compliance Culture
Florida Reliability Coordinating Council, Inc. (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2011008539 | Settlement Agreement | FRCC determined that FRCC_URE1 was in violation of CIP-005-1 R2.1, R2.2. FRCC_URE1 did not apply explicit access permissions at access points such that they are specified for a certain set of source IP addresses. Furthermore, for the same set of configurations, FRCC_URE1 did not ensure only ports necessary for operations and monitoring are enabled. | CIP-005-1 | R2; R2.1; R2.2 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. FRCC determined that the violation posed a moderate risk because failure to apply explicit access permissions and ensure that only ports and services necessary for operations and monitoring are enabled could leave the devices within the Electronic Security Perimeter (ESP) unprotected and vulnerable to a cyber threat. This risk was reduced because the ACLs did limit access from designated FRCC_URE1 trusted hosts by specifying certain source IP addresses. Centralized electronic access control and monitoring systems are in place and configured to detect and alert on security events. Furthermore, FRCC_URE1 requires two-factor authentication for all interactive access into the ESP. | when the Standard became mandatory and enforceable on FRCC_URE1 | completion of milestone updating firewall rules | $100,000 (for FRCC2011008539, FRCC2012011023, FRCC2012010621, FRCC2012010625, FRCC2012010626, FRCC2012011024, and FRCC2012011050) | Spot Check | To mitigate this violation, FRCC_URE1: 1) restricted the use of a parameter with rule reconfigurations and restricted and documented ports and services required for operation and monitoring of Cyber Assets within the ESPs; 2) performed a review of firewall rules on access points to all other Critical Cyber Asset ESPs; 3) performed a review of policies and procedures relating to the control of electronic access at electronic access points to the ESPs; 4) established action plans for policy and procedure enhancements to address areas of improvement identified as a result of the review performed; 5) reported additional findings covered during mitigation plan implementation and consulted with FRCC enforcement; 6) consulted with FRCC with recommendations for the mitigation plan; 7) performed a review of technical controls relating to the control of electronic access at electronic access points to the ESPs; 8) established action plans for technical control enhancements to address areas of improvement identified as a result of the review performed; 9) completed implementation of policy and procedure enhancements previously identified; 10) conducted training and awareness with FRCC_URE1's NERC CIP personnel responsible for managing electronic access points to ESPs; and 11) completed implementation of technical control enhancements identified as a result of the review previously performed. | 2013-02-28 | 2013-04-25 | Neither Admits nor Denies | FRCC reviewed FRCC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
Florida Reliability Coordinating Council, Inc. (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2012011023 | Settlement Agreement | FRCC_URE1 submitted a Self-Report stating that it was in violation of CIP-005-1 R1.5. FRCC_URE1 failed to afford the required protective measures for multiple Cyber Assets that were used for the electronic access control and monitoring system (EACMS) of the Electronic Security Perimeter (ESP). | CIP-005-1 | R1; R1.5; R1.6 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. FRCC determined that the violation posed a moderate risk because failure to afford all required protective measures can leave the Cyber Assets unprotected and vulnerable to a cyber threat. Even with the multiple instances of violation on several Cyber Assets, the risk was reduced as the devices were located within ESPs for which interactive access was limited and required authentication. The devices were also located in a Physical Security Perimeter (PSP), and policy enforcement and training was in place for users to create strong passwords in accordance with the Standards. Additionally, all of the Cyber Assets were afforded the other protective measures required by the Standards. | when the Standard became mandatory and enforceable on FRCC_URE1 | Mitigation Plan completion | $100,000 (for FRCC2011008539, FRCC2012011023, FRCC2012010621, FRCC2012010625, FRCC2012010626, FRCC2012011024, and FRCC2012011050) | Self-Report | To mitigate this violation FRCC_URE1: 1) performed an assessment and extent of condition review of asset type classification for Cyber Assets in scope of CIP-005 R1.5; 2) filed technical feasibility exceptions (TFEs) for the Cyber Assets identified in the Self-Report as they relate to CIP-007 R5.3 requirements; 3) performed a cyber vulnerability assessment (CVA); 4) performed a review of personnel with access to the Cyber Asset. FRCC_URE1 then removed access to applicable Cyber Assets, where necessary; 5) assessed the Personnel Risk Assessment (PRA) program as per CIP-004 R3 to identify possible improvements for validating PRAs prior to granting access to Cyber Assets used in the access control and/or monitoring of the ESPs. Also, FRCC_URE1 assessed the controls defined for updating PRAs pursuant to standard CIP-004 R3.2. FRCC_URE1 also established a corrective action plan to address any issues or improvements identified during the reviews; 6) performed training and education on the applicability of standards and requirements associated with Cyber Assets used in the access control and/or monitoring of the ESPs as per CIP-005 R1.5; 7) performed an assessment of compliance to CIP-005 R1.5 for Cyber Assets subject to NERC CIP requirements identified as Cyber Assets used in electronic access control and/or monitoring of the ESPs but not properly classified in a previous milestone; 8) performed a review of compliance for the Cyber Asset identified in the Self-Report as being improperly classified to ensure that the Cyber Asset is afforded the protective measures as required by CIP-005 R2. Additionally, FRCC_URE1 performed an extent of condition review of CIP-005 R2 and sub-requirements for all applicable Cyber Assets used in the access control and/or monitoring of the ESPs. FRCC_URE1 also established a corrective action plan to address any issues or improvements identified during the reviews; 9) performed an extent of condition review of CIP-007 R3 controls for Cyber Assets used in the access control and/or monitoring of the ESPs. FRCC_URE1 established a corrective action plan to address any issues or improvements identified during the reviews; 10) performed an extent of condition review of account management controls for all applicable Cyber Assets used in the access control and/or monitoring of the ESPs pursuant to CIP-007 R5 (including the need to file additional TFEs), and established a corrective action plan to address any issues or improvements identified during the reviews; 11) performed a review of compliance for the Cyber Asset identified in the Self-Report as being improperly classified to ensure that the Cyber Asset is afforded the protective measures as required by CIP-005 R3. Additionally, FRCC_URE1 performed an extent of condition review of CIP-005 R3 and sub-requirements for all applicable Cyber Assets used in the access control and/or monitoring of the ESPs, and established a corrective action plan to address any issues or improvements identified during the reviews; and 12) implemented corrective actions as identified in action plans created in the Mitigation Plan milestones for applicable Cyber Assets used in the access control and/or monitoring of the ESPs across business units. | 2013-07-11 | 2013-08-14 | Neither Admits nor Denies | FRCC reviewed FRCC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
Florida Reliability Coordinating Council, Inc. (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2012010621 | Settlement Agreement | FRCC_URE1 submitted a Self-Report stating that it was in violation of CIP-007-3 R2.1, R2.2, and R2.3. FRCC_URE1 failed to enable only those ports and services required for normal and emergency operations, disable other ports and services not needed, and apply and document compensating measure(s) to mitigate risk exposure for a number of Cyber Assets. FRCC_URE1 did review configurations of the Cyber Assets for services, but not ports. In addition, a cyber vulnerability assessment (CVA) report revealed a Cyber Asset with two new ports; but no actions were taken to disable the ports or file an appropriate technical feasibility exception (TFE). The CVA report also revealed a power distribution Cyber Asset that relied on a configuration validation; thus, all ports and services were not validated. | CIP-007-3 | R2; R2.1; R2.2; R2.3 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. FRCC determined that the violation posed a moderate risk because failure to document only ports and services required for normal and emergency operations could allow Cyber Assets within the Electronic Security Perimeter (ESP) to be configured incorrectly, and thus leave them unprotected and vulnerable to a cyber threat. The risk was reduced because all Cyber Assets were protected within an ESP and a physical security perimeter, and all personnel with access to the Cyber Assets had current personnel risk assessments and cyber training. Furthermore, external interactive access required authentication and was limited. | annual assessment discovery | completion of Mitigation Plan milestone validating ports and services | $100,000 (for FRCC2011008539, FRCC2012011023, FRCC2012010621, FRCC2012010625, FRCC2012010626, FRCC2012011024, and FRCC2012011050) | Self-Report | To mitigate this violation, FRCC_URE1: 1) ascertained required ports and services for normal and emergency operations; 2) determined if any updates to procedures were needed; 3) updated process documents as needed from prior milestone; 4) trained personnel responsible for assessing ports and services and completing CVAs as to the requirements of the standard and FRCC_URE1's processes; 5) reviewed current CIP assets and validated that required ports for normal and emergency operations of the asset were correctly documented; and 6) reviewed current CIP assets and validated that the CVAs performed were adequate and any discrepancies identified. | 3/31/2013 | 2013-05-01 | Neither Admits nor Denies | FRCC reviewed FRCC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
Florida Reliability Coordinating Council, Inc. (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2012010625 | Settlement Agreement | FRCC_URE1 submitted a Self-Report stating that it was in violation of CIP-007-1 R6, R6.1, R6.2, R6.4, and R6.5. FRCC_URE1 failed to ensure that all Cyber Assets within the Electronic Security Perimeter (ESP), as technically feasible, implement automated tools or organizational process controls to monitor system events that are related to cyber security. Security event logs were not retained for 90 days for several non-Critical Cyber Assets within the ESP. Some of the Cyber Assets were not configured to send log files to the centralized tool used to review security logs, nor issue automated or manual alerts. A Cyber Assets was configured correctly to send security logs to the centralized tool; however, a malfunction occurred resulting in a gap in the activity. Lastly, FRCC_URE1 failed to review logs of system events related to cyber security and maintain records documenting review of logs for several of the Cyber Assets that were logging locally. | CIP-007-1 | R6; R6.1; R6.2; R6.4; R6.5 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. FRCC determined that the violation posed a moderate risk because failure to implement automated tools or organizational process controls to monitor system events that are related to cyber security, not perform manual reviews of logs, and not properly retain such logs can let potential cyber security events go undetected and leave devices vulnerable to a cyber threat. Other Cyber Assets within the ESP which are connected to these Cyber Assets have alerting and logging enabled in addition to the ESP access points. The risk was reduced because these non-critical Cyber Assets are located within an ESP and a Physical Security Perimeter, and external interactive access to the ESP is limited and restricted with authentication. Furthermore, access was limited to authorized personnel with proper cyber training and current personnel risk assessments. | when the Standard became mandatory and enforceable on FRCC_URE1 | completion of Mitigation Plan milestone of updating processing and controls to close the gaps identified | $100,000 (for FRCC2011008539, FRCC2012011023, FRCC2012010621, FRCC2012010625, FRCC2012010626, FRCC2012011024, and FRCC2012011050) | Self-Report | To mitigate this violation, FRCC_URE1: 1) completed inventory of applicable Cyber Assets and validated logging is functional; 2) filed technical feasibility exceptions as necessary; 3) completed a review of current process and controls for remaining Critical Assets to identify gaps; 4) updated processes and controls as necessary to close gaps identified; and 5) trained personnel on updated processes and controls. | 2012-12-14 | 2013-04-25 | Neither Admits nor Denies | FRCC reviewed FRCC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
Florida Reliability Coordinating Council, Inc. (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2012010626 | Settlement Agreement | FRCC_URE1 submitted a Self-Report stating that it was in violation of CIP-007-3 R8.2. FRCC_URE1 failed to properly perform a complete review to verify that only ports and services required for operation for Cyber Assets within the Electronic Security Perimeter (ESP) were enabled during its annual cyber vulnerability assessment (CVA). The review performed was automated and either missed the Cyber Asset entirely or did not address what actions would occur when scans returned unexpected or invalid results or unexpected ports. | CIP-007-3 | R8; R8.2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. This risk was reduced because all Cyber Assets were afforded the protection of the ESP and Physical Security Perimeter (PSP). These Cyber Assets also require authentication, and access was limited to authorized personnel with proper cyber training and current personnel risk assessments. While FRCC_URE1 failed to conduct a proper CVA for ports and services in the required manner, evidence demonstrated that all ESP Cyber Assets were well-hardened and known vulnerabilities were addressed. Ultimately, all open ports and services were ascertained as required. | required completion of annual CVA | Mitigation Plan completion | $100,000 (for FRCC2011008539, FRCC2012011023, FRCC2012010621, FRCC2012010625, FRCC2012010626, FRCC2012011024, and FRCC2012011050) | Self-Report | To mitigate this violation, FRCC_URE1: 1) ascertained required ports for normal and emergency operations of the assets; 2) reviewed processes and procedures related to required ports and services; 3) updated procedures based on results of prior milestone; 4) trained personnel; 5) performed review of current CIP assets and validated required ports for normal and emergency operations are correctly documented; and 6) performed a review of current CIP assets and validated CVAs were adequate and updated discrepancies identified. | 2013-03-31 | 2013-05-01 | Neither Admits nor Denies | FRCC reviewed FRCC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. FRCC_URE1 had a documented ICP that was recently reviewed by FRCC to verify that the program included corrective action processes, internal controls, upper management involvement, and a structure that encourages a culture of compliance within the organization. The evaluation determined that many of the key elements were established and implemented to ensure the entity maintains a robust ICP.
Florida Reliability Coordinating Council, Inc. (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2012011024 | Settlement Agreement | FRCC_URE1 submitted a Self-Report stating that it was in violation of CIP-006-1 R1.8. FRCC_URE1 failed to afford all the required protections to two Cyber Assets. First, both of these Cyber Assets lacked patching controls for CIP-007 R3.1.1; specifically, FRCC_URE1 failed to assess security patches within the required 30 calendar days. Second, for a number of accounts on these Cyber Assets, FRCC_URE1 did not enforce the password controls of CIP-007 R5.3.3 (password annual change frequency). | CIP-006-1 | R1; R1.8 | Lower | Moderate | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. FRCC determined that the violation posed a moderate risk because failure to afford all required protective measures of patching and proper password controls can leave the Cyber Assets unprotected and vulnerable to a cyber threat. In this instance, the patches were properly assessed within 120 days rather than the required 30 days. The risk was reduced because the PACS Cyber Assets were located within an ESP which required authentication for external interactive access and within a Physical Security Perimeter (PSP). Additionally, all of the Cyber Assets were afforded all other protective measures required by the Standards. | when the Standard became mandatory and enforceable on FRCC_URE1 | completion of Mitigation Plan milestone communicating changes | $100,000 (for FRCC2011008539, FRCC2012011023, FRCC2012010621, FRCC2012010625, FRCC2012010626, FRCC2012011024, and FRCC2012011050) | Self-Report | To mitigate this violation, FRCC_URE1: 1) collaborated with manufacturer to confirm the issue is not specific to FRCC_URE1’s environment; 2) created a script that will automatically notify users via email if their password has not been changed in required time frames; 3) created a script that will automatically notify via email the access control administrators if any account password has not been properly changed and request the administrator to terminate and/or disable the account; 4) updated corporate security document to reflect the notifications outlined in previous two milestones. The on-call administrator will delete the account and record in a service ticket upon receipt of the notification of account passwords exceeding the required interval; 5) trained corporate security personnel responsible for the updates made to corporate security systems security management document; 6) communicated to users in the access control the requirement to change their passwords and that failure to change their passwords would result in their accounts being terminated; 7) conducted an extent of condition analysis on all the devices; 8) conducted an extent of condition analysis on all the devices in regards to CIP-006-3 R2.2 (the effective version equivalent) protective measures in CIP-003-3 R6 in relation to the change management procedure/change ticket process and CIP-004-3 R3 PRA process and determined if there were any gaps that needed to be addressed in the outlined protective measures; 9) conducted an extent of condition analysis of the devices in regards to CIP-006-3 R 2.2 of specified protective measures in CIP-007-3 and determined if there were any gaps that needed to be addressed with the outlined protective measures; 10) reviewed the results of the extent of condition analysis in the three previous milestones to develop a corrective action plan to address any identified gaps; 11) completed the corrective action plan developed in previous milestone; 12) communicated to and trained affected personnel on the changes from the corrective action plans completed in the previous milestone; 13) performed an extent of condition review for the devices in relation to CIP-007 R3 controls, and established a corrective action plan to address any issues or improvements identified during the reviews; 14) performed an extent of condition review of account management controls for the devices in regards to CIP-007 R5 (including need to file additional TFE’s), and established a corrective action plan to address any issues or improvements identified during the reviews; and 15) implemented corrective actions as identified in action plans created in previous two milestones for Cyber Assets across business units. | 2013-07-11 | 2013-08-14 | Neither Admits nor Denies | FRCC reviewed FRCC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. .
Florida Reliability Coordinating Council, Inc. (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2012011050 | Settlement Agreement | FRCC_URE1 submitted a Self-Report stating that it was in violation of CIP-005-3a R3.2. FRCC_URE1 failed to implement security monitoring process(es) to detect and alert for attempts at or actual unauthorized accesses at access point; and did not review access logs for attempts at or actual unauthorized accesses at least every ninety calendar days. | CIP-005-3a | R3; R3.2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). This risk was reduced because only users with a proper personnel risk assessment and cyber training were granted physical or cyber access into the Electronic Security Perimeter (ESP). External interactive access to the ESP is limited and requires authentication. Furthermore, users are trained on password complexity requirements and the need to keep their passwords private. These multiple layers (defense in depth) of password controls, physical protections, and monitoring further mitigated the risk to the BPS. | annual assessment discovery | completion of Mitigation Plan milestone submitting TFEs and confirming Cyber Assets in compliance | $100,000 (for FRCC2011008539, FRCC2012011023, FRCC2012010621, FRCC2012010625, FRCC2012010626, FRCC2012011024, and FRCC2012011050) | Self-Report | To mitigate this violation, FRCC_URE1: 1) researched how to implement technically a mechanism to detect and alert for actual unauthorized accesses or determine if a process can be implemented should a technical solution not be available; 2) submitted a Technical Feasibility Exception (TFE); 3) created procedures to detect and alert for actual unauthorized accesses for any Cyber Assets where it is not technically feasible to do so. In addition, FRCC_URE1's remaining departments that operate the rest of its Critical Assets; 4) performed a review of build/test plans for Cyber Assets subject to CIP-005 R3 to ensure that they include steps for validating that the Cyber Assets are configured to detect and alert for attempts at or actual unauthorized accesses 24 hours a day, seven days a week; Additionally, language will be enhanced to ensure that when automated alerting is not technically feasible, a TFE will be filed and the Cyber Assets will be subject to processes and procedures created in the previous milestone to assess access logs for attempts at or actual unauthorized accesses; 5) trained all personnel responsible for performing the new procedures created in the previous milestone as needed; and 6) implemented any new processes created in the previous milestone. | 2013-06-27 | 2013-08-14 | Neither Admits nor Denies | FRCC reviewed FRCC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO201100312 | Settlement Agreement | MRO conducted a compliance audit of MRO_URE1 (Compliance Audit). During the Compliance Audit, MRO_URE1 failed to demonstrate that all personnel having authorized cyber or authorized unescorted physical access were subject to identity verification as required by CIP-004-1 R3.1. Specifically, 28 of the 216 individuals with access to Critical Cyber Assets (CCAs) were not subject to any sort of identity verification. Upon discovering the issue, MRO_URE1 performed Personnel Risk Assessments (PRAs) for the 28 individuals, and it changed its program to utilize an identity verification tool with better documentation of PRAs. Of the 28 individuals with inadequate PRAs, 24 were MRO_URE1 employees with physical access to a single substation, three individuals were third-party security personnel that had physical access to both the primary and secondary control centers (including their associated data centers), as well as electronic access to the physical control system, and one individual was a third-party cleaning contractor that had physical access to the control center (but not to the associated data center). Although MRO_URE1 failed to perform the identity verifications on 28 individuals, it did perform seven-year criminal background checks on those individuals. | CIP-004-1 | R3; R3.1 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). By not performing identity verifications on 28 individuals, MRO_URE1 could not be certain that the individuals with access to its CCAs, including its control centers, had backgrounds appropriate for such access. Of the 28 individuals with inadequate PRAs, three were third-party security contractors that had physical access to both the primary and secondary control centers (including the associated data centers), as well as electronic access to the physical control system. One individual was a third-party cleaning service contractor that had physical access to the control center. MRO_URE1 performed seven-year criminal background checks on each of the 28 individuals, although the background checks were not necessarily as accurate without the identity verification in place to ensure that the correct individual was being assessed. However, out of the 28 individuals with inadequate PRAs, 24 individuals were MRO_URE1 employees. Each of these employees had physical access to one substation. Furthermore, each of the 24 employees has been with the entity for at least two decades. Therefore, the violation posed a moderate risk, but not a serious or substantial risk, to reliability of the BPS. | The date MRO_URE1 was required to comply with the Reliability Standard | When MRO_URE1 performed all of the necessary PRAs | $34,000 (for MRO201100312, MRO201100314, and MRO201100315) | Compliance Audit | To mitigate this violation, MRO_URE1: 1) performed a comprehensive review of PRAs for all personnel having authorized cyber or authorized unescorted physical access to CCAs; 2) conducted full or partial PRAs on personnel found to have discrepancies with the comprehensive review; 3) performed training for human resources personnel to ensure proper steps are followed when initiating PRAs; and 4) revised its PRA procedure to include verification of completion (internal control) of the PRA for all personnel having authorized cyber or authorized unescorted physical access to CCAs. | 2012-05-25 | 2012-05-25 | Admits | In addition to the monetary penalty, MRO determined that it was appropriate for MRO_URE1 to undertake a series of additional remedial actions, including providing additional training and hiring additional personnel.
Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO201100314 | Settlement Agreement | MRO conducted a compliance audit of MRO_URE1 (Compliance Audit). During the Compliance Audit, MRO_URE1 failed to provide evidence of a security patch management program which meets the requirements of CIP-007-1 R3. Specifically, MRO_URE1 failed to provide evidence that all security patches were assessed for applicability within 30 calendar days, and it failed to provide patch documentation for many of its older legacy Energy Management System (EMS) subsystems. Most of MRO_URE1's EMS subsystems require the certification of patches by MRO_URE1's EMS vendor (per MRO_URE1's program) prior to MRO_URE1 assessing or installing third-party patches on the EMS. However, MRO_URE1's EMS vendor refused to certify any patches for mainframe units in use within MRO_URE1's EMS. A review of MRO_URE1's patch management program and legacy devices revealed that most of MRO_URE1's older systems were no longer supported by vendors, and consequently no longer had patches available. For some subsystems such as the primary database for the EMS, the EMS vendor did not certify patches. MRO_URE1, after experiencing system failures when installing non-certified patches, ceased the patching of the database (and any other software not certified by the EMS vendor). MRO_URE1 changed EMS vendors, partially due to problems with patch management. Mitigation focused on revising MRO_URE1's policies and procedures with patching the new EMS, as well as ensuring that all systems were up to date. A comprehensive review of MRO_URE1's software patch levels revealed issues on approximately 24% of its devices. The average length of time these devices went without patch assessments was 13 months, with two devices not having had any patches for several years. Most of the devices without patches were part of MRO_URE1's EMS and associated security subsystems, although the devices with the longest duration between patch assessments involved subsystems such as network monitoring and printing. | CIP-007-1 | R3 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). This violation posed a moderate risk because approximately 24% of MRO_URE1's devices had patch issues, potentially increasing the vulnerability of those devices to new cyber security threats. Many of these devices were part of MRO_URE1's EMS and associated security subsystems. The average length of time these devices went without patch assessments was 13 months, and two devices did not have any patches for several years. The following factors mitigated the risk. First, the EMS servers and consoles themselves were not among the devices that had an extended duration between patch assessments. In addition, MRO_URE1 has network security controls, such as host-based routing and network isolation, as well as an intrusion detection system. However, based upon the duration of the violation and the number and types of devices that required updates, MRO determined that this violation posed a moderate risk to the BPS. | The date MRO_URE1 was required to comply with the Reliability Standard | Mitigation Plan completion | $34,000 (for MRO201100312, MRO201100314, and MRO201100315) | Compliance Audit | To mitigate this violation, MRO_URE1: 1) updated and implemented its security patch management program; 2) performed a comprehensive review of its patch management status; 3) prioritized and addressed discrepancies according to patch management program; and 4) submitted Technical Feasibility Exception requests to MRO, where necessary. | 2012-12-21 | 2013-01-24 | Admits | In addition to the monetary penalty, MRO determined that it was appropriate for MRO_URE1 to undertake a series of additional remedial actions, including providing additional training and hiring additional personnel.
Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO201100315 | Settlement Agreement | MRO conducted a compliance audit of MRO_URE1 (Compliance Audit). During the Compliance Audit, MRO discovered that MRO_URE1 failed to establish, implement, and document technical and procedural controls which enforce access authentication of, and accountability for, all user activity, and that minimize the risk of unauthorized system access in accordance with CIP-007-1 R5. Specifically, MRO discovered inconsistent password complexity and password change controls being implemented on MRO_URE1's Critical Cyber Assets (CCAs). Multiple CCAs did not have technical controls enabled, as required by CIP-007-1 R5. MRO_URE1 performed a comprehensive review of technical controls for accounts subject to CIP-007-1 R5 as part of mitigation. Of the accounts subject to CIP-007-1 R5, approximately 2% did not have passwords changed annually. Most notably, MRO_URE1 did not have evidence of a password change for a shared administrative system account prior to the date of the most recent change, indicating that the passwords were not changed for over three years. These account devices are used in MRO_URE1's Energy Management System (EMS) network system. Additionally, the password for one system administrative account was changed only twice, with the instances being over two years apart. This device is configured to require a digital certificate for Secure Shell remote access, with the password being the primary control for the local console within the Physical Security Perimeter. The password for one system account, a shared administrative account on two devices, was last changed over eighteen months before the start of the Compliance Audit. The devices accessed through this account are used for network segregation, and both devices also required the use of both a digital certificate and key as additional methods of authentication for access. The same five individuals have access to all of these accounts. None of the individuals with access to these accounts has left employment at MRO_URE1 since July 1, 2007, and the Personnel Risk Assessments and training for the five individuals with account access was confirmed. Additionally, a thorough review of MRO_URE1's CCAs resulted in a large number of devices requiring Technical Feasibility Exceptions (TFEs) for the implementation of technical controls for both password complexity and annual change control, in addition to revising MRO_URE1's policies and procedures around account management. | CIP-007-1 | R5 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). This violation posed a moderate risk because the shared administrative system account passwords were not changed for over three years. These accounts have a critical function of monitoring and managing the EMS network. The associated devices did not have any additional compensating authentication controls such as a digital certificate or key. However, MRO did not consider this violation to pose a serious risk to the BPS because the same five individuals have access to all of these accounts, none of the individuals with access to these accounts left employment at MRO_URE1 since July 1, 2007, and each of the individuals had proper Personnel Risk Assessments and CIP training. Additionally, a large number of MRO_URE1's other devices required TFEs for the implementation of technical controls for both password complexity and annual change control. Furthermore, although MRO_URE1 was primarily using a manual process to change passwords, only approximately 2% of accounts did not have their passwords changed at least annually. | The date MRO_URE1 was required to comply with the Reliability Standard | Mitigation Plan completion | $34,000 (for MRO201100312, MRO201100314, and MRO201100315) | Compliance Audit | To mitigate this violation, MRO_URE1: 1) performed a comprehensive review of documentation and Cyber Asset system capability; 2) updated account management processes and procedures; 3) verified and applied password complexity and expiration enforcement; and 4) changed Cyber Asset user account passwords. | 2012-12-31 | 2013-01-24 | Admits | In addition to the monetary penalty, MRO determined that it was appropriate for MRO_URE1 to undertake a series of additional remedial actions, including providing additional training and hiring additional personnel.
ReliabilityFirst Corporation (RF) | Unidentified Registered Entity 1 (RF_URE1) | NCRXXXXX | RFC2012010161 | Settlement Agreement | RF_URE1 submitted a Self-Report to RF stating that it was in violation of CIP-003-3 R6. RF_URE1's control and configuration management process did not have a configuration management program to document current and ongoing hardware and software configurations of Critical Cyber Assets (CCAs). RF_URE1's change control and configuration management process in place at the time of the violation only addressed controlling and documenting future changes made to the configurations of CCAs; it did not establish baseline configurations for all CCAs. | CIP-003-3 | R6 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. RF determined that the violation posed a moderate risk because RF_URE1's of failure to memorialize its baseline configuration as part of the configuration management. Without the baseline RF_URE1 would not be able to accurately predict how change to CCAs could impact the changed CCA or other CCAs and non Critical systems. Further, the duration of the violation stretched out for over 2 years. Finally, although RF_URE1 had an informal process to track changes, RF could not verify the thoroughness or rigor or the process. Although RF_URE1 did not establish baseline configurations for all CCAs, they did have a change control and configuration management process in place during the duration of the violation. Also, RF_URE1 represented that personnel were aware of system changes. Additionally, RF_URE1 reviewed all changes to its CCAs. Further, RF_URE1 conducted cyber vulnerability assessments of the CCAs at issue. | when the Standard became mandatory and enforceable | Mitigation Plan completion | $0 (for RFC2012010161, RFC2012010162, RFC2012010163, RFC2012010164, RFC2012010165, RFC2012010166, RFC2012010172, RFC2012010173, RFC2012010174, RFC2012010175, RFC2012010176, and RFC2012010177) | Self-Report | To mitigate this violation, RF_URE1: 1) altered the change control and configuration management procedures to document initial baseline configurations of applicable Cyber Assets; 2) recorded the configuration of its applicable Cyber Assets and stored the configuration records securely; and 3) established baseline configurations for its Cyber Assets. | 2013-03-18 | 2013-05-02 | Admits | RF reviewed RF_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
ReliabilityFirst Corporation (RF) | Unidentified Registered Entity 1 (RF_URE1) | NCRXXXXX | RFC2012010162 | Settlement Agreement | RF_URE1 submitted a Self-Report to RF that it was in violation of CIP-005-3 R4. RF_URE1 determined that, although it performs a cyber vulnerability assessment (CVA) annually, during the 2010 and 2011 CVAs, it did not verify that the enabled ports and services on each electronic access point to the Electronic Security Perimeter was required for operation. | CIP-005-3 | R4 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. RF determined that the violation posed a minimal risk because the risk to the reliability of the bulk power system was mitigated by the fact that upon completion of the 2012 CVA, RF_URE1 confirmed that only those ports and services required for operation were enabled during the duration of the violation. | when the Standard became mandatory and enforceable | Mitigation Plan completion | $0 (for RFC2012010161, RFC2012010162, RFC2012010163, RFC2012010164, RFC2012010165, RFC2012010166, RFC2012010172, RFC2012010173, RFC2012010174, RFC2012010175, RFC2012010176, and RFC2012010177) | Self-Report | To mitigate this violation, RF_URE1 completed its 2012 CVA. During the 2012 CVA, RF_URE1 verified that only ports and services located on electronic access points and required for operation are enabled. | 2012-12-21 | 2013-05-02 | Admits | RF reviewed RF_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
ReliabilityFirst Corporation (RF) | Unidentified Registered Entity 1 (RF_URE1) | NCRXXXXX | RFC2012010163 | Settlement Agreement | RF_URE1 submitted a Self-Report to RF that it was in violation of CIP-007-3a R1. RF_URE1 discovered that it had not documented its test procedures and therefore could not demonstrate that it performed testing in a manner that reflects the production environment or provide documented test results. | CIP-007-3a | R1 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. RF determined that the violation posed a minimal risk because RF_URE1 represents that it performed testing on all Cyber Assets as required during the duration of the violation and, although undocumented, RF_URE1 followed its informal change management process. RF_URE1 represents that this process required RF_URE1 to perform test procedures and that testing did occur during the duration of the violation. | when the Standard became mandatory and enforceable | Mitigation Plan completion | $0 (for RFC2012010161, RFC2012010162, RFC2012010163, RFC2012010164, RFC2012010165, RFC2012010166, RFC2012010172, RFC2012010173, RFC2012010174, RFC2012010175, RFC2012010176, and RFC2012010177) | Self-Report | To mitigate this violation, RF_URE1 developed specific documented testing procedures for all Cyber Assets located within its Electronic Security Perimeter. | 2012-09-21 | 2012-12-26 | Admits | RF reviewed RF_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
ReliabilityFirst Corporation (RF) | Unidentified Registered Entity 1 (RF_URE1) | NCRXXXXX | RFC2012010164 | Settlement Agreement | RF_URE1 submitted a Self-Report to RF that it was in violation of CIP-007-3a R8. RF_URE1 discovered that during the cyber vulnerability assessments (CVAs), it did not verify that only those ports and services required for operation of Cyber Assets within the Electronic Security Perimeter (ESP) were enabled. | CIP-007-3a | R8.2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. RF determined that the violation posed a minimal risk because upon completion of the CVA, RF_URE1 confirmed that only those ports and services required for operation were enabled during the duration of the violation. | when the Standard became mandatory and enforceable | Mitigation Plan completion | $0 (for RFC2012010161, RFC2012010162, RFC2012010163, RFC2012010164, RFC2012010165, RFC2012010166, RFC2012010172, RFC2012010173, RFC2012010174, RFC2012010175, RFC2012010176, and RFC2012010177) | Self-Report | To mitigate this violation, RF_URE1 conducted its 2012 CVA and verified that only those ports and services required for operation of the Cyber Assets within the ESP were enabled. | 2012-12-21 | 2013-05-02 | Admits | RF reviewed RF_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
ReliabilityFirst Corporation (RF) | Unidentified Registered Entity 1 (RF_URE1) | NCRXXXXX | RFC2012010165 | Settlement Agreement | RF_URE1 submitted a Self-Report to RF that it was in violation of CIP-006-3a R2 because RF_URE1 discovered that it did not afford the protective measures specified in CIP-006-3a R2.2 to its system. Further, RF_URE1 did not address testing of signatures in process for updating anti-virus and malware prevention signatures as applicable to a device. | CIP-006-3a | R2; R2.2 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. RF determined that the violation posed a moderate risk because RF_URE1 did not include the device in the original scope of its CIP compliance effort. Further, RF considered RF_URE1's failure to test signatures on the other device thereby leaving it vulnerable to virus and malware. However, the risk was mitigated because the devices were located within a Physical Security Perimeter for the duration of the violation. Further, the one device is password protected and further restricted through the use of local, as well as domain, firewall, and security policies. Finally, throughout the duration of the violation, access to the device authentication. | when the Standard became mandatory and enforceable | Mitigation Plan completion | $0 (for RFC2012010161, RFC2012010162, RFC2012010163, RFC2012010164, RFC2012010165, RFC2012010166, RFC2012010172, RFC2012010173, RFC2012010174, RFC2012010175, RFC2012010176, and RFC2012010177) | Self-Report | To mitigate this violation, RF_URE1: 1) filed the necessary technical feasibility exception (TFE) requests; 2) modified the device to a serial connection, thereby removing network access to the device; and 3) moved the software on the other device to a protected asset within the Electronic Security Perimeter capable of performing testing of anti-virus and malware signatures. | 2013-03-18 | 2013-05-02 | Admits | RF reviewed RF_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
ReliabilityFirst Corporation (RF) | Unidentified Registered Entity 1 (RF_URE1) | NCRXXXXX | RFC2012010166 | Settlement Agreement | RF_URE1 submitted a Self-Report to RF that it was in violation of CIP-007-3a R3. RF_URE1 discovered it did not establish, document, or implement a security patch management process for all Cyber Assets within its Electronic Security Perimeter (ESP). | CIP-007-3a | R3 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. RF determined that the violation posed a moderate risk because it demonstrated a general lack of awareness about the requirements of CIP-007-3a R3. Further, RF could not verify the effectiveness of RF_URE1's informal security patch management program. Additionally, the violation involved Cyber Assets within the ESP which concerned RF due to the increased vulnerability of those assets to infiltration of unauthorized network traffic. Finally, the duration of the violation was over two years. RF_URE1 implemented an informal procedure for reviewing updates to its servers throughout the duration of the violation. RF_URE1 tracked available and applicable updates for its assets and accessed various online vendors for tracking non-windows updates throughout the duration of the violation. | when the Standard became mandatory and enforceable | Mitigation Plan completion | $0 (for RFC2012010161, RFC2012010162, RFC2012010163, RFC2012010164, RFC2012010165, RFC2012010166, RFC2012010172, RFC2012010173, RFC2012010174, RFC2012010175, RFC2012010176, and RFC2012010177) | Self-Report | To mitigate this violation, RF_URE1 documented a security patch management program and filed technical feasibility exception (TFE) requests for all Cyber Assets that could not be patched. | 2012-12-11 | 2013-05-02 | Admits | RF reviewed RF_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
ReliabilityFirst Corporation (RF) | Unidentified Registered Entity 1 (RF_URE1) | NCRXXXXX | RFC2012010172 | Settlement Agreement | RF_URE1 submitted a Self-Report to RF that it was in violation of CIP-007-3a R3. RF_URE1 discovered it did not establish, document, or implement a security patch management process for all Cyber Assets within its Electronic Security Perimeter (ESP). | CIP-007-3a | R3 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. RF determined that the violation posed a moderate risk because it demonstrated a general lack of awareness about the requirements of CIP-007-3a R3. Further, RF could not verify the effectiveness of RF_URE1's informal security patch management program. Additionally, the violation involved Cyber Assets within the ESP which concerned RF due to the increased vulnerability of those assets to infiltration of unauthorized network traffic. Finally, the duration of the violation was over two years. RF_URE1 implemented an informal procedure for reviewing updates to its servers throughout the duration of the violation. RF_URE1 tracked available and applicable updates for its assets and accessed various online vendors for tracking non-windows updates throughout the duration of the violation. | when the Standard became mandatory and enforceable | Mitigation Plan completion | $0 (for RFC2012010161, RFC2012010162, RFC2012010163, RFC2012010164, RFC2012010165, RFC2012010166, RFC2012010172, RFC2012010173, RFC2012010174, RFC2012010175, RFC2012010176, and RFC2012010177) | Self-Report | To mitigate this violation, RF_URE1 documented a security patch management program and filed technical feasibility exception requests for all Cyber Assets that could not be patched. | 2012-12-21 | 2013-03-22 | Admits | RF reviewed RF_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
ReliabilityFirst Corporation (RF) | Unidentified Registered Entity 1 (RF_URE1) | NCRXXXXX | RFC2012010173 | Settlement Agreement | RF_URE1 submitted a Self-Report to RF that, as a Generator Operator, it was in violation of CIP-007-3a R8. RF_URE1 discovered that during the cyber vulnerability assessments (CVAs), it did not verify that only those ports and services required for operation of Cyber Assets within the Electronic Security Perimeter (ESP) were enabled. | CIP-007-3a | R8.2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. RF determined that the violation posed a minimal risk because upon completion of the CVA, RF_URE1 confirmed that only those ports and services required for operation were enabled during the duration of the violation. | when the Standard became mandatory and enforceable | Mitigation Plan completion | $0 (for RFC2012010161, RFC2012010162, RFC2012010163, RFC2012010164, RFC2012010165, RFC2012010166, RFC2012010172, RFC2012010173, RFC2012010174, RFC2012010175, RFC2012010176, and RFC2012010177) | Self-Report | To mitigate this violation, RF_URE1 conducted its CVA and verified that only those ports and services required for operation of the Cyber Assets within the ESP were enabled. | 2012-12-21 | 2013-03-21 | Admits | RF reviewed RF_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
ReliabilityFirst Corporation (RF) | Unidentified Registered Entity 1 (RF_URE1) | NCRXXXXX | RFC2012010174 | Settlement Agreement | RF_URE1 submitted a Self-Report to RF that it was in violation of CIP-003-3 R6. RF_URE1 change control and configuration management process did not have a configuration management program to document current and ongoing hardware and software configurations of Critical Cyber Assets (CCAs). RF_URE1's change control and configuration management process in place at the time of the violation only addressed controlling and documenting future changes made to the configurations of CCAs; it did not establish baseline configurations for all CCAs. | CIP-003-3 | R6 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. RF determined that the violation posed a moderate risk because RF_URE1's failure to memorialize its baseline configuration as part of the configuration management. Without the baseline RF_URE1 would not be able to accurately predict how change to CCAs could impact the changed CCA or other CCAs and non Critical systems. Further, the duration of the violation stretched out for over 2 years. Finally, although RF_URE1 had an informal process to track changes, RF could not verify the thoroughness or rigor or the process. RF_URE1 did have a change control and configuration management process in place during the duration of the violation. Also, RF_URE1 represented that personnel were aware of system changes. Additionally, RF_URE1 reviewed all changes to its CCAs. Further, RF_URE1 conducted cyber vulnerability assessments of the CCAs at issue. | when the Standard became mandatory and enforceable | Mitigation Plan completion | $0 (for RFC2012010161, RFC2012010162, RFC2012010163, RFC2012010164, RFC2012010165, RFC2012010166, RFC2012010172, RFC2012010173, RFC2012010174, RFC2012010175, RFC2012010176, and RFC2012010177) | Self-Report | To mitigate this violation, RF_URE1: 1) altered the change control and configuration management procedures to document initial baseline configurations of applicable Cyber Assets; 2) recorded the configuration of its applicable Cyber Assets and stored the configuration records securely; and 3) established baseline configurations for its Cyber Assets. | 2013-03-18 | 2013-04-25 | Admits | RF reviewed RF_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
ReliabilityFirst Corporation (RF) | Unidentified Registered Entity 1 (RF_URE1) | NCRXXXXX | RFC2012010175 | Settlement Agreement | RF_URE1 submitted a Self-Report to RF that it was in violation of CIP-005-3 R4. RF_URE1 determined that, although it performs a cyber vulnerability assessment (CVA) annually, during past CVAs, it did not verify that the enabled ports and services on each electronic access point to the Electronic Security Perimeter were required for operation. | CIP-005-3 | R4 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. RF determined that the violation posed a minimal risk because the risk to the reliability of the bulk power system was mitigated by the fact that upon completion of the recent CVA, RF_URE1 confirmed that only those ports and services required for operation were enabled during the duration of the violation. | when the Standard became mandatory and enforceable | Mitigation Plan completion | $0 (for RFC2012010161, RFC2012010162, RFC2012010163, RFC2012010164, RFC2012010165, RFC2012010166, RFC2012010172, RFC2012010173, RFC2012010174, RFC2012010175, RFC2012010176, and RFC2012010177) | Self-Report | To mitigate this violation, RF_URE1 completed its CVA. During the CVA, RF_URE1 verified that only ports and services located on electronic access points and required for operation were enabled. | 2012-12-21 | 2013-03-22 | Admits | RF reviewed RF_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
ReliabilityFirst Corporation (RF) | Unidentified Registered Entity 1 (RF_URE1) | NCRXXXXX | RFC2012010176 | Settlement Agreement | RF_URE1 submitted a Self-Report to RF that it was in violation of CIP-006-3a R2. RF_URE1 discovered that it did not afford the protective measures specified in CIP-006-3a R2.2 to its system. RF_URE1 did not include the one device in the original scope of its CIP compliance effort. Further, RF_URE1 did not address testing of signatures in their process for updating anti-virus and malware prevention signatures as applicable to the other device. | CIP-006-3a | R2; R2.2 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. RF determined that the violation posed a moderate risk because RF_URE1 did not include the device in the original scope of its CIP compliance effort. Further, RF considered RF_URE1's failure to test signatures on its other device thereby leaving it vulnerable to virus and malware. However, the risk was mitigated because the devices were located within a Physical Security Perimeter for the duration of the violation. Further, one device is password protected and further restricted through the use of local, as well as domain, firewall and security policies. Finally, throughout the duration of the violation, access to the device required authentication. | when the Standard became mandatory and enforceable | Mitigation Plan completion | $0 (for RFC2012010161, RFC2012010162, RFC2012010163, RFC2012010164, RFC2012010165, RFC2012010166, RFC2012010172, RFC2012010173, RFC2012010174, RFC2012010175, RFC2012010176, and RFC2012010177) | Self-Report | To mitigate this violation, RF_URE1: 1) filed the necessary technical feasibility exception requests; 2) modified the device to a serial connection thereby removing network access to the device; and 3) moved the software on the other device to a protected asset within the Electronic Security Perimeter capable of performing testing of anti-virus and malware signatures. | 2013-03-18 | 2013-05-02 | Admits | RF reviewed RF_URE1 internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
ReliabilityFirst Corporation (RF) | Unidentified Registered Entity 1 (RF_URE1) | NCRXXXXX | RFC2012010177 | Settlement Agreement | RF_URE1 submitted a Self-Report to RF that it was in violation of CIP-007-3a R1. RF_URE1 discovered that it had not documented its test procedures and therefore could not demonstrate that it performed testing in a manner that reflects the production environment or provide documented test results. | CIP-007-3a | R1 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. RF determined that the violation posed a minimal risk because RF_URE1 performed testing on all Cyber Assets as required during the duration of the violation and, although undocumented, RF_URE1 followed its informal change management process. RF_URE1 performed test procedures and that testing did occur during the duration of the violation. | when the Standard became mandatory and enforceable | Mitigation Plan completion | $0 (for RFC2012010161, RFC2012010162, RFC2012010163, RFC2012010164, RFC2012010165, RFC2012010166, RFC2012010172, RFC2012010173, RFC2012010174, RFC2012010175, RFC2012010176, and RFC2012010177) | Self-Report | To mitigate this violation, RF_URE1 developed specific documented testing procedures for all Cyber Assets located within its Electronic Security Perimeter. | 2012-09-21 | 2012-12-18 | Admits | RF reviewed RF_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2013012045 | Settlement Agreement | WECC_URE1 submitted a Self-Certification to WECC stating that it was in violation of CIP-007-3a R2. WECC_URE1 reported that it failed to complete assessment and documentation for the review of ports and services on two servers, in violation of CIP-007-3a R2.1 and R2.2. For each device, WECC_URE1 failed to ensure that only those ports and services required for normal and emergency operations were enabled. | CIP-007-3a | R2; R2.1; R2.2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. All devices in scope resided within a Physical Security Perimeter (PSP) where physical access was restricted. All individuals with access to the PSP had current training, personnel risk assessments, and had approved authorized access. In addition, the devices were in an Electronic Security Perimeter (ESP) and were logged and monitored. All network traffic to the ESP is logged and monitored by a system that sends alerts to WECC_URE1 personnel after any unusual traffic is detected. | when WECC_URE1 commissioned the devices | Mitigation Plan completion | $25,000 (for WECC2013012045 and WECC2013012047) | Self-Certification | To mitigate this violation, WECC_URE1: 1) developed and conducted a change control training for personnel with NERC CIP responsibilities; and 2) completed a ports and services review for applicable devices. | 2013-06-28 | TBD | Does Not Contest | WECC_URE1 was cooperative throughout the process. WECC_URE1 did not fail to complete any applicable compliance directives. There was no evidence of any attempt by WECC_URE1 to conceal the violation. There was no evidence that WECC_URE1’s violation was intentional.
Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2013012047 | Settlement Agreement | WECC_URE1 submitted a Self-Certification to WECC stating that it was in violation of CIP-007-1 R5. WECC_URE1 failed to remove, disable, or rename administrator accounts and failed to change passwords prior to putting systems into service. Specifically, WECC_URE1 failed to ensure that one factory default shared administrator account on each of eight devices was removed, disabled, or renamed. It also failed to ensure the default password was changed prior to putting the equipment into production. In addition, WECC_URE1 failed to change the passwords on eight accounts in scope during the 2010, 2011, and 2012 calendar years. | CIP-007-1 | R5 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC determined that the violation posed a moderate risk because the generating units associated with this violation are blackstart units that are critical for system restoration. Although WECC_URE1 did have a policy in place for these devices, the personnel responsible for implementing the policy did not know how to properly manage these types of switches. The risk was mitigated because the devices resided within a Physical Security Perimeter where access was restricted to individuals with current training, approved personnel risk assessments, and approved authorized access. Electronic Security Perimeter (ESP) and access attempts were logged and monitored. All network traffic to the ESP is logged an monitored by a system that sends alerts to WECC_URE1 personnel after any unusual traffic is detected. | when the Standard became mandatory and enforceable | Mitigation Plan completion | $25,000 (for WECC2013012045 and WECC2013012047) | Self-Certification | To mitigate this violation, WECC_URE1: 1) reviewed the device accounts and supplied documentation of the review and password changes; 2) developed and conducted supplemental change control and account management refresher training for personnel; and 3) reassigned workflow tasks for the devices to the IT network support team. | 2013-06-28 | TBD | Does Not Contest | WECC_URE1 was cooperative throughout the process. WECC_URE1 did not fail to complete any applicable compliance directives. There was no evidence of any attempt by WECC_URE1 to conceal the violation. There was no evidence that WECC_URE1 ’s violation was intentional.
Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2013012055 | Settlement Agreement | WECC_URE2 submitted a Self-Certification to WECC stating that it was in violation of CIP-007-3a R2. WECC_URE2 failed to establish, document and implement a process to ensure that only those ports and services required for normal and emergency operations were enabled. Specifically, two devices were commissioned that did not undergo testing or change control prior to implementation. WECC_URE2 failed to appropriately identify a server as a Critical Cyber Asst (CCA). Additionally, because of the misclassification, WECC_URE2 failed to ensure that the second server, which resided on the same network, was afforded CCA protections. WECC discovered a third device which should have been afforded CCA protection. Therefore, WECC_URE2 commissioned one CCA and two Cyber Assets residing within an Electronic Security Perimeter (ESP) without testing, change control, or verifying that only ports and services required for normal and emergency operations were enabled,. | CIP-007-3a | R2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. All devices within scope resided within a Physical Security Perimeter where physical access was restricted to individuals with current training, approved Personal Risk Assessments, and approved authorized access. The devices also were protected by an Electronic Security Perimeter (ESP) and behind a device that logs, monitors, and restricts all access in and out of the ESP. In addition, all network traffic that is within the ESP is logged and monitored by its system log server which is configured to send alerts to WECC_URE2 personnel after any unusual traffic is suspected. | when WECC_URE2 commissioned the devices | Mitigation Plan completion | 10000 | Self-Certification | To mitigate this violation, WECC_URE2: 1) completed review of ports and services to ensure that only those ports and services required for normal and emergency operation are enabled; and 2) developed and conducted supplemental training for personnel with NERC CIP responsibilities. | 2013-06-28 | TBD | Does Not Contest | WECC_URE2 was cooperative throughout the process. WECC_URE2 did not fail to complete any applicable compliance directives. There was no evidence of any attempt by WECC_URE2 to conceal the violation. WECC determined that a prior violation should serve as a basis for aggravating the penalty .
Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2012009389 | Settlement Agreement | WECC_URE3 submitted a Self-Certification stating that it was in violation of CIP-004-1 R4. Specifically, WECC_URE3 stated there were three incidents where individuals whose physical access rights to Physical Security Perimeters (PSPs) were not revoked as required by the Standard. WECC_URE3 failed to revoke access to Critical Cyber Assets (CCAs) within seven days for eight individuals who no longer require such access. The first incident occurred when a contingent worker WECC_URE3 did not have physical access rights revoked within seven days of his separation with WECC_URE3. The contingent worker had authorized physical access rights to WECC_URE3's PSPs which should have been revoked. However, due to an administrative oversight, the access was not revoked until approximately eight months later. WECC_URE3 identified the second incident when a manager was reviewing documentation related to two contract security guards who had been given authorized unescorted physical access to PSPs. The security guards were terminated; however, the access was not revoked until approximately one month and three months after the security guards were terminated. The third incident involved five WECC_URE3 employees who had physical access to CCAs. For the five employees, WECC_URE3 did not have records for when access was no longer required, and therefore did not have dates for when access should have been revoked. It was determined that the five individuals were terminated and access was revoked for the five employees approximately for eight months, three weeks, three months and one month after termination. | CIP-004-1 | R4 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although these individuals had physical access, they did not have electronic access to CCAs. Moreover, all the individuals in scope had Personnel Risk Assessments and all of the PSPs are monitored by human observation 24 hours a day seven days a week, including security video monitoring. Also, each PSP access point is configured to generate an alarm for any unauthorized physical access and no alarms occurred during the incidents. | when the access should have been revoked for the first incident | Mitigation Plan completion | $20,000 (for WECC2012009389, WECC2012009391, and WECC2012009392) | Self-Certification | To mitigate this violation, WECC_URE3: 1) revoked access for the affected employees; 2) conducts regular training sessions on its procedure regarding physical access revocations with employees; and 3) conducts regular monthly meetings with vendors to reinforce the contractual requirements related to terminations. | 2011-06-09 | 2013-08-21 | Does Not Contest | WECC reviewed WECC_URE3's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. WECC determined that WECC_URE3's compliance history and determined it to be an aggravating factor in the penalty determination.
Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2012009391 | Settlement Agreement | WECC_URE3 submitted a Self-Certification stating that it was in violation of CIP-006-3c R5. WECC_URE3 stated that on seven instances it failed to maintain 24-hour physical monitoring of all 35 of its Physical Security Perimeters (PSPs). Specifically, WECC_URE3 experienced seven monitoring outages over a period of an approximate year. During each outage, WECC_URE3 maintained local logs at each PSP to log physical access attempts. In addition, with the exception of one substation, all of WECC_URE3's substations where the outages occurred were manned 24 hours a day. The substation that was not manned is WECC_URE3's facility which contains various devices used to support WECC_URE3's energy management system such as servers, firewalls and switches. The outage at this facility lasted more than four hours. During the outage, WECC_URE3 did not dispatch personnel to the facility. | CIP-006-3a | R5 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The PSP in scope is located in a remote substation and is manned by operators approximately 15 hours of the day and the PSP access points are locked and require card key access even if monitoring is down. Further, all PSP access points are located to default to "fail-safe" and all doors and cabinets are locked and secured. | when the first of seven outages occurred at the facility | Mitigation Plan completion | $20,000 (for WECC2012009389, WECC2012009391, and WECC2012009392) | Self-Certification | To mitigate this violation, WECC_URE3 developed a procedure to address unplanned CCURE outages involving WECC_URE3 substations. Pursuant to the procedure, corporate security is to contact specific personnel and notify them when manual monitoring at the PSPs is required. | 2012-06-27 | 2013-06-10 | Does Not Contest | WECC reviewed WECC_URE3's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2012009392 | Settlement Agreement | WECC_URE3 submitted a Self-Certification stating that it was in violation of CIP-007-1 R5. WECC_URE3 stated that on three occasions a trainee was allowed by his supervisor to access an energy management system (EMS) using another operator's account. Specifically, the operator, at the direction of the supervisor, left his workstation unlocked to allow the trainee to work on the EMS workstation. The EMS workstation is a Critical Cyber Asset (CCA) located in the control substation facility within an Electronic Security Perimeter (ESP) and Physical Security Perimeter (PSP). | CIP-007-1 | R5; R5.2.3 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The person in scope had a current Personnel Risk Assessment, cybersecurity training, and was required to access the EMS workstation to perform work duties. Also, this person was in training and was under complete supervision the entire time during all three instances. Finally, the ESP and PSP were monitored and manned 24 hours a day. | when access to the account was obtained by the trainee | Mitigation Plan completion | $20,000 (for WECC2012009389, WECC2012009391, and WECC2012009392) | Self-Certification | To mitigate this violation, WECC_URE3: 1) affixed a sign to the EMS workstation to remind employees to log-off after their shifts and not to share log-in tokens or passwords with others; 2) secured log-in credentials for the in-scope trainee; and 3) reinforced the cybersecurity policy with the supervisor. | 2012-06-28 | TBD | Does Not Contest | WECC reviewed WECC_URE3's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.