## PUBLIC_CIP Violations
Region | Registered Entity | NCR_ID | NERC Violation ID # | Notice of Confirmed Violation or Settlement Agreement | Description of the Violation | Reliability Standard | Req. | Violation Risk Factor | Violation Severity Level | Risk Assessment | Violation Start Date | Violation End Date | Total Penalty or Sanction ($) | Method of Discovery | Description of Mitigation Activity | Mitigation Completion Date | Date Regional Entity Verified Completion of Mitigation | "Admits," "Agrees/Stipulates," "Neither Admits nor Denies," or "Does Not Contest" | Other Factors Affecting the Penalty Determination, including Compliance History, Internal Compliance Program and Compliance Culture
ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RF_URE1) | NCRXXXXX | RFC2011001224 | Settlement Agreement | ReliabilityFirst conducted a Compliance Audit and discovered that RF_URE1 was in violation of CIP-003-1 R6. During the Compliance Audit, RF reviewed documentation related to RF_URE1's change and configuration management procedures, promulgated pursuant to CIP-003-1 R6. While RF_URE1 presented several documents related to configuration, RF_URE1 did not provide evidence supporting its application of configuration management procedures to identify, control, and document all changes to Critical Cyber Asset hardware and software. | CIP-003-1 | R6 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Specifically, configuration management ensures the network and environment are properly managed with consistent versions and settings so that the environment remains secure. Insufficient implementation and support of configuration management can introduce unwanted security vulnerabilities, unauthorized access points, and impact the availability of critical systems up to and including the BPS. The risk to the reliability of the BPS was mitigated by the following factors. RF_URE1 had a configuration management process and maintained some documentation of that process. Although RF_URE1 was unable to produce detailed documentation demonstrating that the process was followed in all cases, ReliabilityFirst did not identify any instances of RF_URE1 failing to implement this process. | when the Standard become mandatory and enforceable as to RF_URE1 | when RF_URE1 enacted new configuration management processes | $0 (for RFC2011001224, RFC2011001225, RFC2011001230, RFC2011001237, RFC2012011566, and RFC2013012173) | Compliance Audit | To mitigate this violation, RF_URE1: 1) consolidated its processes related to configuration management into a single, high-level, corporate-wide document; and 2) enhanced its configuration management procedures at the Cyber Asset level. | 2012-06-20 | TBD | Neither Admits nor Denies | ReliabilityFirst considered certain aspects of RF_URE1's compliance program as a mitigating factor in penalty determination. RF_URE1 also invested in computer software to assist in the tracking and monitoring of Reliability Standards. RF_URE1 has sought to improve its compliance program after the Compliance Audit, dedicating significant resources to developing programs that will ensure continued observance of the NERC Reliability Standards. ReliabilityFirst considered that it discovered this violation through the Compliance Audit, and, accordingly, applied no mitigating credit to this violation. ReliabilityFirst assessed a $0 penalty because although most of the violations were discovered at a Compliance Audit, they were issues that represented non-compliance based on thresholds of compliance, as opposed to complete failures to comply with the NERC Standards. In this particular violation, ReliabilityFirst considered that although this violation of CIP-003 R6 posed a moderate risk, RF_URE1's implementation of its configuration management process was short only in documentation and ReliabilityFirst did not find any instances of failure to implement the process.
ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RF_URE1) | NCRXXXXX | RFC2011001225 | Settlement Agreement | ReliabilityFirst conducted a Compliance Audit and discovered that RF_URE1 was in violation of CIP-005-1 R1. First, ReliabilityFirst discovered that RF_URE1 had granted a vendor access to its Electronic Security Perimeters (ESPs) through a virtual private network (VPN) without documenting that VPN as an access point to the ESPs, as required by CIP-005-1 R1.1. The vendor required access to service RF_URE1's Supervisory Control and Data Acquisition (SCADA) system. Second, RF_URE1 maintained Cyber Assets used in the access control and monitoring of its ESPs that were incapable of implementing antivirus or malware prevention tools, as required by CIP-007-1 R4. These Cyber Assets are within the scope of CIP-005-1 R1 and, therefore, in accordance with CIP-005-1 R1.5 RF_URE1 must afford them the protections specified in CIP-007-1 R4. Because these Cyber Assets could not implement antivirus or malware prevention tools, RF_URE1 was required to submit Technical Feasibility Exceptions (TFEs) detailing these technical limitations but failed to do so timely. | CIP-005-1 | R1; R1.1, R1.5 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. ReliabilityFirst determined that the violation of CIP-005-1 R1.1 posed a moderate risk because the individual worked for a reputable SCADA vendor that provides security training and conducts Personnel Risk Assessments on its employees, in addition to RF_URE1's processes. RF_URE1 only enabled the VPN at issue when specifically requested to do so by its SCADA support team, and RF_URE1's corporate firewalls further controlled access to this VPN. In addition, the mitigating and compensating measures described in the TFE were in place throughout the entire period of time at issue. | For R1.1: when the Standard become mandatory and enforceable as to RF_URE1; for R1.5: when RF_URE1 should have submitted the TFE | For R1.1: when RF_URE1 revoked the vendor’s VPN access; for R1.5: when RF_URE1 submitted a TFE for the Cyber Assets at issue | $0 (for RFC2011001224, RFC2011001225, RFC2011001230, RFC2011001237, RFC2012011566, and RFC2013012173) | Compliance Audit | To mitigate this violation, RF_URE1: 1) revoked the vendor’s VPN access that had previously served as an undocumented access point to an ESP; 2) enhanced its inspections of its ESPs to document more fully access points to ESPs; and 3) submitted an acceptable TFE for the Cyber Assets incapable of having antivirus and malware prevention tools implemented. | 2012-03-16 | TBD | Neither Admits nor Denies | ReliabilityFirst considered certain aspects of RF_URE1's compliance program as a mitigating factor in penalty determination. RF_URE1 also invested in computer software to assist in the tracking and monitoring of Reliability Standards. RF_URE1 has sought to improve its compliance program after the Compliance Audit, dedicating significant resources to developing programs that will ensure continued observance of the NERC Reliability Standards. RF considered that it discovered this violation through the Compliance Audit, and, accordingly, applied no mitigating credit to this violation. ReliabilityFirst assessed a $0 penalty because although most of the violations were discovered at a Compliance Audit, they were issues that represented non-compliance based on thresholds of compliance, as opposed to complete failures to comply with the NERC Standards. In this particular violation, although RF_URE1 failed to fully comply with CIP-005 R1 at all times, the violation constituted exceptions to an otherwise strong compliance program. For example, although TFEs were not timely submitted for devices that are incapable of implementing antivirus and malware prevention tools, the mitigating and compensating measures were in place at all times.
ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RF_URE1) | NCRXXXXX | RFC2011001230 | Settlement Agreement | ReliabilityFirst conducted a Compliance Audit and discovered that RF_URE1 was in violation of CIP-007-1 R1. ReliabilityFirst reviewed evidence of RF_URE1's program for testing new Cyber Assets and significant changes to existing Cyber Assets within Electronic Security Perimeters (ESPs) to ensure that such changes do not adversely impact existing cyber security controls, as required pursuant to CIP-007-1 R1. ReliabilityFirst discovered that three devices lacked test procedures for certain periods of time: 1) one device lacked test procedures prior to September 28, 2011; 2) another device lacked test procedures prior to March 4, 2011; and 3) the third lacked test procedures prior to September 22, 2011. Additionally, ReliabilityFirst reviewed RF_URE1's documentation of test results retained pursuant to CIP-007-1 R1.3. Specifically, ReliabilityFirst reviewed three test procedures provided by RF_URE1. In reviewing documentation of RF_URE1's implementation of these procedures, ReliabilityFirst discovered that all three procedures included Cyber Assets for which no documentation of test results existed. | CIP-007-1 | R1; R1.3 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Specifically, a violation of CIP-007-1 R1 has the potential to affect the reliable operation of the BPS by providing the opportunity for new Cyber Assets within the ESP and significant changes to existing Cyber Assets within the ESP to adversely affect existing cyber security controls. The risk to the reliability of the BPS was mitigated by the following factors. During the entire period subject to the Compliance Audit, the devices in question were located in ESPs protected by firewalls and physically protected from unauthorized access. Additionally, RF_URE1 has automated monitoring and notifications in place with respect to the firewall logs to detect and respond to unauthorized access or unauthorized access attempts. Furthermore, only a small subset of the entire list of Cyber Assets lacked test results, namely substation field devices that provide telemetry for the Supervisory Control and Data Acquisition (SCADA) system. These devices had related Technical Feasibility Exceptions, evidencing RF_URE1's awareness of the devices. Any significant changes to these devices would have required trained technicians and an outage scheduled to perform the necessary work. Firmware updates to these devices cannot be applied through automated processes, and the updates are closely controlled through internal databases. | when the Standard become mandatory and enforceable as to RF_URE1 | when RF_URE1 completed and documented testing for each Cyber Asset at issue | $0 (for RFC2011001224, RFC2011001225, RFC2011001230, RFC2011001237, RFC2012011566, and RFC2013012173) | Compliance Audit | To mitigate this violation, RF_URE1: 1) reviewed its test procedures for Cyber Assets and recognized that improvements were necessary; 2) created its CIP-007 Cyber Security test procedure, which provides a guideline and checklist to verify that the proper security controls are in place for new or significant changes to existing Cyber Assets; 3) provided sample test results, including results from the testing of monthly patching for security patches and also completed an inventory of all Cyber Assets and ESPs to ensure that all Cyber Asset device types have documented test procedures; and 4) provided training to relevant information technology personnel. | 2012-05-14 | TBD | Neither Admits nor Denies | ReliabilityFirst considered certain aspects of RF_URE1's compliance program as a mitigating factor in penalty determination. RF_URE1 also invested in computer software to assist in the tracking and monitoring of Reliability Standards. RF_URE1 has sought to improve its compliance program after the Compliance Audit, dedicating significant resources to developing programs that will ensure continued observance of the NERC Reliability Standards. ReliabilityFirst considered that it discovered this violation through the Compliance Audit, and, accordingly, applied no mitigating credit to this violation. ReliabilityFirst assessed a $0 penalty because although most of the violations were discovered at a Compliance Audit, they were issues that represented non-compliance based on thresholds of compliance, as opposed to complete failures to comply with the NERC Standards. In this particular violation, although RF_URE1 failed to have test procedures for certain devices, RF_URE1 demonstrated that it had proper awareness of the devices at issue in this violation, and had afforded other protections such as firewall, physical protection, and automated monitoring to the devices.
ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RF_URE1) | NCRXXXXX | RFC2011001237 | Settlement Agreement | ReliabilityFirst conducted a Compliance Audit and discovered that RF_URE1 was in violation of CIP-007-1 R8. Specifically, RF_URE1 failed to perform cyber vulnerability assessments (CVAs) on Cyber Assets within the Electronic Security Perimeters (ESPs) at RF_URE1's substations, as required by CIP-007-1 R8. Instead, RF_URE1 performed only limited scans on those devices; the scans did not meet the requirements of CIP-007-1 R8. Although RF_URE1 previously performed scans that met the requirements of CIP-007-1 R8 on Cyber Assets in substation ESPs; experienced operational issues on scanned devices and, as a result, began performing the limited scans. | CIP-007-1 | R8 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Specifically, failure to perform CVAs on Cyber Assets in the ESPs increase the risk of weaknesses in the security of the Cyber Assets going undetected. The lack of assessment increase the risk to Critical Cyber Assets being compromised and/or rendered inoperable. During the entire period subject to the Compliance Audit, the devices in question were located in ESPs protected by firewalls and physically protected from unauthorized access. Additionally, RF_URE1 has automated monitoring and notifications in place with respect to the firewall logs to detect and respond to unauthorized access or unauthorized access attempts. The lack of CVA test involved a small subset of the RF_URE1's Cyber Assets, namely substation field devices that provide telemetry for the Supervisory Control and Data Acquisition (SCADA) system. These devices had related Technical Feasibility Exceptions, evidencing RF_URE1's awareness of the devices. Any significant changes to these devices would have required trained technicians and an outage scheduled to perform the necessary work. Firmware updates to these devices cannot be applied through automated processes, and the updates are closely controlled through internal databases. RF_URE1 represents that these devices could not have been easily modified to introduce new vulnerabilities. Furthermore, when RF_URE1 performed CVAs on these devices in a test environment (the CVAs were performed in a test environment due to the operational issues previously experience by RF_URE1), the test results were accurate and provided assurance to RF_URE1 regarding the functioning of these devices. | when the Standard become mandatory and enforceable as to RF_URE1 | when RF_URE1 submitted its revised procedures for performing CVAs to RF | $0 (for RFC2011001224, RFC2011001225, RFC2011001230, RFC2011001237, RFC2012011566, and RFC2013012173) | Compliance Audit | To mitigate this violation, RF_URE1 drafted a new interim process for manual testing of field devices. RF_URE1's CVA addressed the issues identified at the Compliance Audit and was a comprehensive process completed within the scope of the new interim process. This interim process incorporated a physical inspection component, which will be added to the CVA process each year. | 2012-05-14 | TBD | Neither Admits nor Denies | ReliabilityFirst considered certain aspects of RF_URE1's compliance program as a mitigating factor in penalty determination. RF_URE1 also invested in computer software to assist in the tracking and monitoring of Reliability Standards. RF_URE1 has sought to improve its compliance program after the Compliance Audit, dedicating significant resources to developing programs that will ensure continued observance of the NERC Reliability Standards. ReliabilityFirst considered that it discovered this violation through the Compliance Audit, and, accordingly, applied no mitigating credit to this violation. ReliabilityFirst assessed a $0 penalty because although most of the violations were discovered at a Compliance Audit, they were issues that represented non-compliance based on thresholds of compliance, as opposed to complete failures to comply with the NERC Standards. In this particular violation, although RF_URE1 failed to conduct CVAs on certain devices, RF_URE1 demonstrated that it had proper awareness of the devices at issue in this violation, and had afforded other protections such as firewall, physical protection, and automated monitoring to the devices.
ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RF_URE1) | NCRXXXXX | RFC2012011566 | Settlement Agreement | RF_URE1 submitted a Self-Report to RF stating that it was in violation of CIP-004-3 R4. RF_URE1 had not timely revoked an individual’s access to Critical Cyber Assets (CCAs) and had not timely updated its list of personnel with access to CCAs. Specifically, RF_URE1 discovered that it had not revoked an employee’s physical access to certain CCAs. The employee at issue passed away. This employee did not have electronic access to CCAs. Upon discovering this issue, RF_URE1 immediately revoked the access and documented the revocation of access. RF_URE1 submitted an additional Self-Report, stating that it failed to revoke physical access to certain CCAs and failed to update its list of personnel with access to account for an employee who transferred to a position within RF_URE1 that did not require such access. This transfer occurred, but RF_URE1 did not revoke access eight days later, one day after it was required to do so pursuant to CIP-004-1 R4.2. This delay in revocation was due to RF_URE1's human resources department not receiving timely notice of the transfer. | CIP-004-3 | R4; R4.1, R4.2 | Lower | High | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The first instance of the violation related to the deceased employee was an isolated incident. Given that the individual was deceased, he had no ability to access RF_URE1's facilities, and RF_URE1 determined that his identification badge was secure during the relevant period. As to the second instance of the violation, the employee at issue remained a RF_URE1 employee in good standing throughout the period of the violation. In both cases, the individuals at issue had undergone personnel risk assessments and cyber security training. | when RF_URE1 should have revoked access for the individual at issue in the first occurrence; when access should have been removed for the transferred individual | when access was removed for the deceased individual; when RF_URE1 revoked access for the transferred individual | $0 (for RFC2011001224, RFC2011001225, RFC2011001230, RFC2011001237, RFC2012011566, and RFC2013012173) | Self-Report | To mitigate this violation, RF_URE1 transferred responsibility for CIP-004 compliance to its human resources department. To mitigate this violation, RF_URE1 will implement procedural and technological enhancements to ensure timely access revocations and updates to access lists. | 2013-07-31 | TBD | Neither Admits nor Denies | ReliabilityFirst considered certain aspects of RF_URE1's compliance program as a mitigating factor in penalty determination. RF_URE1 also invested in computer software to assist in the tracking and monitoring of Reliability Standards. RF_URE1 has sought to improve its compliance program after the Compliance Audit, dedicating significant resources to developing programs that will ensure its continued observance of the NERC Reliability Standards. ReliabilityFirst also applied mitigating credit to RF_URE1's self-reported violations. RF_URE1's Self-Reports evidence a full understanding of the issues presented, described the immediate steps taken by RF_URE1 to minimize reliability risks, and provided RF with sufficient information to analyze the violations. Such timely and robust Self-Reports are essential to maintaining the continued reliability of the BPS. ReliabilityFirst assessed a $0 penalty because although most of the violations were discovered at a Compliance Audit, they were issues that represented non-compliance based on thresholds of compliance, as opposed to complete failures to comply with the NERC Standards. In this particular violation, although RF_URE1 failed to fully comply with CIP-004 R4 at all times, the violation constituted an exception to an otherwise strong compliance program. For example, one failure to revoke access involved a deceased employee and in both cases the employees in question had undergone personnel risk assessments and cyber security training.
ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RF_URE1) | NCRXXXXX | RFC2013012173 | Settlement Agreement | RF_URE1 submitted a Self-Report to RF stating that it was in violation of CIP-006-3 R5. RF_URE1's communications group was performing work at a substation identified as a Critical Asset. This work required RF_URE1 to shut down power to its security system used to monitor access to the Physical Security Perimeter (PSP) protecting this substation. The security system operated on backup battery power until ultimately failing. The failure generated an error message to RF_URE1's security group, but RF_URE1 did not recognize the cause as a loss of power. Upon returning to work three days later, RF_URE1's security group discovered that the security system had lost power, and RF_URE1 took prompt corrective actions. While this security system was inoperable, RF_URE1 failed to monitor the access points to the PSP surrounding the substation. | CIP-006-3c | R5 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). RF determined that the violation of CIP-006-3c R5 posed a minimal risk because the security system at issue failed to a secure state, where physical access was locked. Therefore, despite RF_URE1's inability to monitor access to the substation, the substation was nevertheless protected from physical intrusion. Furthermore, RF_URE1 investigated for evidence of physical and logical intrusions at the substation and discovered no evidence of any. | when the security system failed due to power loss | when RF_URE1 restored power to the security system) | $0 (for RFC2011001224, RFC2011001225, RFC2011001230, RFC2011001237, RFC2012011566, and RFC2013012173) | Self-Report | To mitigate this violation, RF_URE1 will: 1) detail the steps it took to restore power to the security system at issue; 2) investigate the error message; 3) ensure that power is not inadvertently shut off in the future; and 4) implement procedural controls to prevent a similar issue from occurring in the future. | 2013-08-30 | TBD | Neither Admits nor Denies | ReliabilityFirst considered certain aspects of RF_URE1's compliance program as a mitigating factor in penalty determination. RF_URE1 also invested in computer software to assist in the tracking and monitoring of Reliability Standards. RF_URE1 has sought to improve its compliance program after the Compliance Audit, dedicating significant resources to developing programs that will ensure its continued observance of the NERC Reliability Standards. ReliabilityFirst also applied mitigating credit to RF_URE1's self-reported violations. RF_URE1's Self-Reports evidence a full understanding of the issues presented, described the immediate steps taken by RF_URE1 to minimize reliability risks, and provided ReliabilityFirst with sufficient information to analyze the violations. Such timely and robust Self-Reports are essential to maintaining the continued reliability of the BPS. ReliabilityFirst assessed a $0 penalty because although most of the violations were discovered at a Compliance Audit, they were issues that represented non-compliance based on thresholds of compliance, as opposed to complete failures to comply with the NERC Standards. In this particular violation, although RF_URE1 failed to fully comply with CIP-006 R5 at all times, the violation constituted an exception to an otherwise strong compliance program. For example, although RF_URE1 failed to monitor access points to a PSP during an equipment failure, the equipment was configured to fail to a secure state and RF_URE1 took prompt corrective action once aware of the problem.
ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RF_URE2) | NCRXXXXX | RFC2012010103 | Settlement Agreement | RF_URE2 submitted a Self-Report stating that it was in violation of CIP-006-3c R2. RF_URE2 discovered that it did not afford the protective measures specified in CIP-006-1 R2.2 to its Physical Control System. RF_URE2 did not include the device in its original scope of its CIP compliance effort. Further, RF_URE2 did not address testing of signatures in its process for updating antivirus and malware prevention signatures as applicable to the device. | CIP-006-1 | R2 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). ReliabilityFirst determined that the violation posed a moderate risk because if Cyber Assets that authorize and log access to the Physical Security Perimeter (PSP) do not receive the required protective measures, the Critical Cyber Assets within the PSP are at an increased risk of unauthorized access. The risk was mitigated in this case because the devices were located within a PSP during the duration of the violation. Further, one device is password protected and further restricted through the use of local, as well as domain, firewall and security policies. | when the Standard became mandatory and enforceable on RF_URE2 | Mitigation Plan completion | $0 (for RFC2012010103, RFC2012010167, RFC2012010168, RFC2012010169, RFC2012010170, and RFC2012010171) | Self-Report | To mitigate this violation, RF_URE2: 1) filed the necessary technical feasibility exception (TFE) requests; 2) modified the one device to a serial connection thereby removing network access to the device; and 3) moved the software on the other device to a protected asset within the Electronic Security Perimeter (ESP) capable of performing testing of antivirus and malware signatures. | 2012-12-14 | 2013-03-28 | Admits | ReliabilityFirst considered certain aspects of RF_URE2's internal compliance program (ICP) as mitigating factors.
ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RF_URE2) | NCRXXXXX | RFC2012010167 | Settlement Agreement | RF_URE2 submitted a Self-Report stating that it was in violation of CIP-007-1 R8. RF_URE2 determined that it did not conduct a review of ports and services associated with non-critical Cyber Assets located within an Electronic Security Perimeter (ESP) as part of its annual Cyber Vulnerability Assessments (CVAs). | CIP-007-1 | R8; R8.2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). ReliabilityFirst determined that the violation posed a minimal risk because RF_URE2 confirmed that only those ports and services required for operation were enabled during the duration of the violation. | when the Standard became mandatory and enforceable on RF_URE2 | Mitigation Plan completion | $0 (for RFC2012010103, RFC2012010167, RFC2012010168, RFC2012010169, RFC2012010170, and RFC2012010171) | Self-Report | To mitigate this violation, RF_URE2 conducted its CVA at the earliest possible date and verified that only those ports and services required for operation of the Cyber Assets within the ESP were enabled. RF_URE2 now includes a review of all ports and services in its annual Cyber Vulnerability Assessment. | 2012-07-31 | 2013-06-03 | Admits | ReliabilityFirst considered certain aspects of RF_URE2's internal compliance program (ICP) as mitigating factors.
ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RF_URE2) | NCRXXXXX | RFC2012010168 | Settlement Agreement | RF_URE2 submitted a Self-Report stating that it was in violation of CIP-003-1 R6. RF_URE2 determined that it did not have a configuration management program to document all entity or vendor-related changes to hardware and software components of Critical Cyber Assets (CCAs). | CIP-003-1 | R6 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). ReliabilityFirst determined that the violation posed a moderate risk because a violation of CIP-003-1 R6 has the potential to affect the reliable operation of the BPS, by providing the opportunity to exploit vulnerable CCAs after a Responsible Entity applies undocumented change control or configuration management activities to those CCAs. The risk was mitigated because RF_URE2 had a change control process in place during the duration of the violation. Additionally, RF_URE2 represents that personnel were aware of system changes and that it reviewed all changes to its CCAs. | when the Standard became mandatory and enforceable on RF_URE2 | Mitigation Plan completion | $0 (for RFC2012010103, RFC2012010167, RFC2012010168, RFC2012010169, RFC2012010170, and RFC2012010171) | Self-Report | To mitigate this violation, RF_URE2: 1) documented a configuration management process that includes initial baseline configurations of applicable Cyber Assets; 2) recorded the configuration of its applicable Cyber Assets and stored the configuration records securely; and 3) established baseline configurations for its Cyber Assets. | 2013-05-08 | 2013-05-29 | Admits | ReliabilityFirst considered certain aspects of RF_URE2's internal compliance program (ICP) as mitigating factors.
ReliabilityFirst Corporation (ReliabilityFirst) | Unidentitfied Registered Entity 2 (RF_URE2) | NCRXXXXX | RFC2012010169 | Settlement Agreement | RF_URE2 submitted a Self-Report stating that it was in violation of CIP-005-1 R4. RF_URE2 determined that it did not verify that the enabled ports and services on each electronic access point to the Electronic Security Perimeter (ESP) were required for operation when it performed its Cyber Vulnerability Assessments (CVAs). RF_URE2 could provide a list of running ports and services for its CVA, but it could not verify that these ports and services were required for operation. Additionally, RF_URE2 could only provide a table indicating that it completed a review of all ports and services during its later CVA. | CIP-005-1 | R4 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). ReliabilityFirst determined that the violation posed a minimal risk because RF_URE2 confirmed upon completion of the CVA that only those ports and services required for operation were enabled during the duration of the violation. | when the Standard became mandatory and enforceable on RF_URE2 | Mitigation Plan completion | $0 (for RFC2012010103, RFC2012010167, RFC2012010168, RFC2012010169, RFC2012010170, and RFC2012010171) | Self-Report | To mitigate this violation, RF_URE2 completed its CVA during which it verified that only ports and services located on electronic access points and required for operation were enabled. | 2012-05-31 | 2013-06-03 | Admits | ReliabilityFirst considered certain aspects of RF_URE2's internal compliance program (ICP) as mitigating factors.
ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RF_URE2) | NCRXXXXX | RFC2012010170 | Settlement Agreement | RF_URE2 submitted a Self-Report stating that it was in violation of CIP-007-3a R3. RF_URE2 determined that it had not established, documented, or implemented a security patch management program for tracking, evaluating, testing and installing applicable cybersecurity software patches for all Cyber Assets within an Electronic Security Perimeter (ESP). | CIP-007-1 | R3 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). ReliabilityFirst determined that the violation posed a minimal risk because RF_URE2 implemented a security patch management program for its CCAs during the duration of the violation. | when the Standard became mandatory and enforceable on RF_URE2 | Mitigation Plan completion | $0 (for RFC2012010103, RFC2012010167, RFC2012010168, RFC2012010169, RFC2012010170, and RFC2012010171) | Self-Report | To mitigate this violation, RF_URE2 documented a security patch management program and filed Technical Feasibility Exception requests for those Cyber Assets that could not be patched. | 2012-07-31 | 2013-05-02 | Admits | ReliabilityFirst considered certain aspects of RF_URE2's internal compliance program (ICP) as mitigating factors.
ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RF_URE2) | NCRXXXXX | RFC2012010171 | Settlement Agreement | RF_URE2 submitted a Self-Report stating that it was in violation of CIP-007-1 R1. RF_URE2 determined it did not create, implement or maintain test procedures for Cyber Assets residing within one Electronic Security Perimeter (ESP). RF_URE2 did have test procedures for Critical Cyber Assets (CCAs) residing with the ESP during the duration of the violation. | CIP-007-1 | R1 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). ReliabilityFirst determined that the violation posed a minimal risk because the Cyber Assets for which RF_URE2 did not have test procedures were non-critical Cyber Assets. Further, during the duration of the violation, none of the non-critical Cyber Assets at issue experienced significant changes that would have necessitated RF_URE2 to implement the test procedures mandated by CIP-007-1 R1. | when the Standard became mandatory and enforceable on RF_URE2 | Mitigation Plan completion | $0 (for RFC2012010103, RFC2012010167, RFC2012010168, RFC2012010169, RFC2012010170, and RFC2012010171) | Self-Report | To mitigate this violation, RF_URE2 developed specific documented testing procedures for all Cyber Assets located within its ESP. | 2012-08-20 | 2013-06-03 | Admits | ReliabilityFirst considered certain aspects of RF_URE2's internal compliance program (ICP) as mitigating factors.
ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RF_URE3) | NCRXXXXX | RFC2011001271 | Settlement Agreement | RF_URE3 submitted a Self-Report to ReliabilityFirst stating that it was in violation of CIP-006-1 R2. RF_URE3 discovered that it did not afford the protective measures specified in CIP-006-1 R2.2 to its Physical Control System. RF_URE3 did not include the device in its original scope of its CIP compliance effort. Further, RF_URE3 did not address testing of signatures in its process for updating anti-virus and malware prevention signatures as applicable to the device. | CIP-006-1 | R2; R2.2 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. ReliabilityFirst determined that the violation posed a moderate risk because if Cyber Assets that authorize and log access to the Physical Security Perimeter (PSP) do not receive the required protective measures, the Critical Cyber Assets within the PSP are at an increased risk of unauthorized access. The risk was mitigated in this case because the devices were located within a Physical Security Perimeter (PSP) during the duration of the violation. Further, the one device is password protected and further restricted through the use of local, as well as domain, firewall and security policies. | when the Standard became mandatory and enforceable on RF_URE3 | Mitigation Plan completion | $0 (for RFC2011001271, RFC2012010104, RFC2012010105, RFC2012010106, RFC2012010107, and RFC2012010109 | Self-Report | To mitigate this violation, RF_URE3: 1) filed the necessary technical feasibility exception (TFE) requests; 2) modified the one device to a serial connection thereby removing network access to the device; and 3) moved the software on the other device to a protected asset within the Electronic Security Perimeter (ESP) capable of performing testing of anti-virus and malware signatures. | 2012-12-14 | 2013-03-28 | Admits | ReliabilityFirst reviewed RF_URE3's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RF_URE3) | NCRXXXXX | RFC2012010104 | Settlement Agreement | During a Compliance Audit, ReliabilityFirst determined that RF_URE3 was in violation of CIP-003-1 R6. ReliabilityFirst discovered that RF_URE3 did not have a configuration management program to document all entity or vendor related changes to hardware and software components of Critical Cyber Assets (CCAs). RF_URE3 did provide an established change control process to ReliabilityFirst during the Compliance Audit. | CIP-003-1 | R6 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. ReliabilityFirst determined that the violation posed a moderate risk because a violation of CIP-003-1 R6 has the potential to affect the reliable operation of the BPS, by providing the opportunity to exploit vulnerable CCAs after a Responsible Entity applies undocumented change control or configuration management activities to those CCAs.The risk was mitigated because RF_URE3 had a change control process in place during the duration of the violation. Additionally, RF_URE3 represents that personnel were aware of system changes and that it reviewed all changes to its CCAs. | when the Standard became mandatory and enforceable on RF_URE3 | Mitigation Plan completion | $0 (for RFC2011001271, RFC2012010104, RFC2012010105, RFC2012010106, RFC2012010107, and RFC2012010109 | Compliance-Audit | To mitigate this violation, RF_URE3: 1) documented a configuration management process that includes initial baseline configurations of applicable Cyber Assets: 2) recorded the configuration of its applicable Cyber Assets and stored the configuration records securely; and 3) established baseline configurations for its Cyber Assets. | 2013-05-08 | 2013-06-03 | Admits | ReliabilityFirst reviewed RF_URE3's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RF_URE3) | NCRXXXXX | RFC2012010105 | Settlement Agreement | During a Compliance Audit, ReliabilityFirst determined that RF_URE3 was in violation of CIP-005-1 R4. ReliabilityFirst determined that RF_URE3 did not verify that the enabled ports and services on each electronic access point to the Electronic Security Perimeter (ESP) were required for operation when it performed its cyber vulnerability assessment (CVA). RF_URE3 provided a list of running ports and services for its CVA, but could not verify that these ports and services were required for operation. RF_URE3 did not provide a list of running ports and services for its CVA, but rather a table indicating that it completed a review. | CIP-005-1 | R4; R4.2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. ReliabilityFirst determined that the violation posed a minimal risk because RF_URE3 confirmed upon completion of the CVA that only those ports and services required for operation were enabled during the duration of the violation. | when the Standard became mandatory and enforceable on RF_URE3 | Mitigation Plan completion | $0 (for RFC2011001271, RFC2012010104, RFC2012010105, RFC2012010106, RFC2012010107, and RFC2012010109 | Compliance Audit | To mitigate this violation, RF_URE3 completed its CVA and verified that only ports and services located on electronic access points and required for operation are enabled. | 2012-05-31 | 2013-06-03 | Admits | ReliabilityFirst reviewed RF_URE3's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RF_URE3) | NCRXXXXX | RFC2012010106 | Settlement Agreement | During a Compliance Audit, ReliabilityFirst determined that RF_URE3 was in violation of CIP-007-1 R1. ReliabilityFirst determined that RF_URE3 did not create, implement or maintain test procedures for Cyber Assets residing within one Electronic Security Perimeter (ESP). During the Compliance Audit, RF_URE3 was able to provide test procedures to ReliabilityFirst for Critical Cyber Assets (CCAs) residing with the ESP. | CIP-007-1 | R1 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. ReliabilityFirst determined that the violation posed a minimal risk because the Cyber Assets for which RF_URE3 did not have test procedures were non-CCAs. Further, during the duration of the violation none of the non-CCAs at issue experienced significant changes that would have necessitated RF_URE3 to implement the test procedures mandated by CIP-007-1 R1. | when the Standard became mandatory and enforceable on RF_URE3 | Mitigation Plan completion | $0 (for RFC2011001271, RFC2012010104, RFC2012010105, RFC2012010106, RFC2012010107, and RFC2012010109 | Compliance Audit | To mitigate this violation, RF_URE3 developed, implemented, and maintains specific documented testing procedures for all Cyber Assets located within its ESP. | 2012-08-20 | 2013-06-03 | Admits | ReliabilityFirst reviewed RF_URE3's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RF_URE3) | NCRXXXXX | RFC2012010107 | Settlement Agreement | During a Compliance Audit, ReliabilityFirst determined that RF_URE3 was in violation of CIP-007-1 R3. ReliabilityFirst discovered that RF_URE3 did not establish, document, or implement a security patch management program for tracking, evaluating, testing and installing applicable cyber security software patches for all Cyber Assets within an Electronic Security Perimeter (ESP). | CIP-007-1 | R3 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. ReliabilityFirst determined that the violation posed a minimal risk because RF_URE3 implemented security patch management program for its CCAs during the duration of the violation. | when the Standard became mandatory and enforceable on RF_URE3 | Mitigation Plan completion | $0 (for RFC2011001271, RFC2012010104, RFC2012010105, RFC2012010106, RFC2012010107, and RFC2012010109 | Compliance Audit | To mitigate this violation, RF_URE3 documented a security patch management program and filed Technical Feasibility Exception requests for those Cyber Assets that cannot be patched. | 2012-07-31 | 2013-05-02 | Admits | ReliabilityFirst reviewed RF_URE3's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RF_URE3) | NCRXXXXX | RFC2012010109 | Settlement Agreement | During a Compliance Audit, ReliabilityFirst determined that RF_URE3 was in violation of CIP-007-1 R8. ReliabilityFirst determined that RF_URE3 could not provide evidence that it conducted a review of ports and services associated with non-Critical Cyber Assets located within an Electronic Security Perimeter (ESP) as part of its annual cyber vulnerability assessments (CVAs). | CIP-007-1 | R8 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. ReliabilityFirst determined that the violation posed a minimal risk because RF_URE3 confirmed that only those ports and services required for operation were enabled during the duration of the violation. | when the Standard became mandatory and enforceable on RF_URE3 | Mitigation Plan completion | $0 (for RFC2011001271, RFC2012010104, RFC2012010105, RFC2012010106, RFC2012010107, and RFC2012010109 | Compliance Audit | To mitigate this violation, RF_URE3 conducted its CVA and verified that only those ports and services required for operation of the Cyber Assets within the ESP are enabled. | 2012-06-04 | 2013-06-03 | Admits | ReliabilityFirst reviewed RF_URE3's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC201000743 | Settlement Agreement | SERC_URE1 submitted a Self-Report to SERC stating that it was in violation of CIP-007-1 R4.1. SERC_URE1 failed to implement anti-virus and malware prevention tools on all Cyber Assets within the Electronic Security Perimeter (ESP). SERC_URE1 had a process in place for updating malware signatures as required by CIP-007-1 R4.2. While conducting a single on-demand scan of Cyber Assets within an ESP in an effort to enhance security, SERC_URE1 discovered that the malware prevention software was not performing as expected on one Cyber Asset, a server used to exchange data with a neighboring utility. After the discovery of the problem with the malware prevention software, SERC_URE1 initiated an immediate investigation. SERC_URE1 preliminarily concluded that the malware prevention software package had been loaded onto the Cyber Asset but the installation package had not been executed to complete the installation. SERC_URE1 rebooted the server and successfully loaded the malware prevention signatures. SERC_URE1 scanned all other Cyber Assets within the control center ESPs and discovered no other security problems. All of SERC_URE1’s remaining Cyber Assets had malware prevention software loaded properly (as technically feasible) and all signatures were found to be current. | CIP-007-1 | R4, R4.1 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC_URE1 had secured ports and services through its electronic access control and monitoring (EACM) devices to only those required for normal and emergency operations. SERC_URE1 reviewed the access logs from the EACM devices and found they contained no malicious activity that would have created alerts for investigation. All access from outside the ESP requires two-factor (strong) authentication and no internet access is permitted for these isolated networks. SERC_URE1 conducted a full scan of the network after successfully loading the anti-malware software and found no infections or potentially unwanted programs present. | when the Standard became mandatory and enforceable on SERC_URE1 | Mitigation Plan completion | $41,000 (for SERC201000743, SERC201000751, SERC2011008285, SERC2011008331, SERC2012009651, SERC2012010509, SERC2012011334, SERC2013011760, SERC2013011762, SERC2013011764, SERC2013011766, and SERC2013011767) | Self-Report | To mitigate this violation, SERC_URE1: 1) revised its malware prevention software implementation and monitoring process to ensure that malware prevention software is verified to be functioning as required following installation. IT administrators subsequently monitor the malware prevention software for proper operation, and appropriate IT personnel are promptly notified of any functional concerns; and 2) instituted a quarterly review to verify that the list of Cyber Assets monitored by malware prevention software administrators includes all Cyber Assets within the ESP that, where technically feasible, are required to comply with CIP-007 R4. To accomplish this, SERC_URE1 compared Cyber Asset lists and reconciled discrepancies as appropriate. | 2/28/2011 | 2013-06-27 | Neither Admits nor Denies | SERC reviewed SERC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC201000751 | Settlement Agreement | SERC_URE1 submitted a Self-Report to SERC stating that it was in violation of CIP-005-1 R1.6. SERC_URE1 failed to maintain documentation of all interconnected Cyber Assets and Critical Cyber Assets (CCAs) within the Electronic Security Perimeter (ESP). SERC_URE1 conducted an internal review of its ESP documentation. During that review, SERC_URE1 discovered four types of Cyber Assets within the ESPs that were not documented on the ESP diagrams. The four types of Cyber Assets were: 1) keyboard/video/mouse (KVM) switches (used to toggle between the device interfaces) in one control center ESP; 2) a tape library; 3) routers; and 4) Voice over Internet Protocol (VoIP) phones. While the routers were located within an ESP and Physical Security Perimeter (PSP), the VoIP phones were not. After this discovery, SERC_URE1 conducted a full scan for all devices on its ESPs and found no additional devices. SERC determined that SERC_URE1 failed to maintain the required documentation of all Cyber Assets within the ESP. SERC_URE1 had a process for creating and maintaining ESP documentation, but the process lacked the level of detail required for an employee to know what to include and what to exclude in the ESP documentation. As a result, SERC_URE1 missed four types of Cyber Assets when it created the original list of CCAs and Cyber Assets within the ESP. | CIP-005-1 | R1, R1.6 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC determined that the violation posed a moderate risk because SERC_URE1’s failure to maintain documentation of the overlooked Cyber Assets could have left those affected Cyber Assets without proper security measures and presented an attack path for potential hackers. However, the KVM switches, the tape library, and phone system routers resided within a secured PSP and ESP. The VoIP telephones, although not secured within the official PSP and ESP, were in a secured facility that was staffed 24 hours a day, seven days a week, monitored by cameras, and secured with restricted card key access. SERC_URE1's electronic access control and monitoring devices did not detect any conditions for the involved ESPs that required investigation. | when the Standard became mandatory and enforceable on SERC_URE1 | when SERC_URE1 removed the overlooked Cyber Assets from the ESPs | $41,000 (for SERC201000743, SERC201000751, SERC2011008285, SERC2011008331, SERC2012009651, SERC2012010509, SERC2012011334, SERC2013011760, SERC2013011762, SERC2013011764, SERC2013011766, and SERC2013011767) | Self-Report | To mitigate this violation, SERC_URE1: 1) revised the existing control center ESP documentation process to ensure that all interconnected non-critical Cyber Assets and CCAs within control center ESPs are addressed in ESP diagrams; 2) modified scan tools to instruct performers directly on how to perform full network scans instead of partial network scans; and 3) relocated the non-essential Cyber Assets that were in the ESP outside of the ESP. | 2011-02-28 | 2012-09-20 | Neither Admits nor Denies | SERC reviewed SERC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2011008285 | Settlement Agreement | SERC_URE1 submitted a Self-Report to SERC stating that it was in violation of CIP-004 R4.2. SERC_URE1 failed in two instances to revoke an individual’s access to Critical Cyber Assets (CCAs) within seven calendar days when the access was no longer required. In the first instance, an employee’s NERC training qualification expired due to a failure to renew the training by the SERC_URE1 specified deadline. This employee had access to the physical access control system (PACS) via remote token access, which in turn required active directory access. SERC_URE1 had an automated system in place to alert the IT security group responsible for revocation of CCA access to the expiration of the employee's NERC training. Due to human error, SERC_URE1 did not remove the employee’s remote token access until 16 days after the revocation was requested, causing it to be nine days late. The employee's active directory rights had been removed within the required timeframe. Without the active directory rights, the employee would not be able to access the PACS using the remote token. During this period, the employee did not attempt to use his or her access to the PACS. In addition, the employee continued to be in good standing with SERC_URE1 and had a valid Personal Risk Assessment (PRA). In the second instance, SERC_URE1 had an automated process in place to alert the IT security group responsible for revocation of CCA access when an employee with CCA access had a job duties change. The IT security group would be responsible for reviewing and removing CCA access as required. This automated process failed due to the server freezing and did not resume until 15 days later when regular maintenance tasks were performed and the server was rebooted. At this time, SERC_URE1 did not have any means of remotely monitoring whether the server was operating normally. Upon reboot, pending revocation alerts that were hung-up in the server were sent and acted on the same day. One alert required SERC_URE1 to remove an employee’s CCA access due to a job change that did not require CCA access. This employee had access to three Physical Security Perimeters that contained Cyber Assets used as electronic access control and monitoring devices and PACS. SERC_URE1 did not remove the employee’s access until 15 days after the date the revocation was requested, causing it to be eight days late. During this period, the employee did not use his or her physical access privileges. In addition, the employee continues to be in good standing with SERC_URE1 and had a valid PRA. | CIP-004-1 | R4, R4.2 | Lower | Moderate | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. These failures were limited to two separate instances, and the employees involved were in good standing with the company for the entire period in question, and remained in good standing after the violation end date. Both employees had current PRAs. In the first incident, the employee's active directory rights had been removed within the required timeframe. Without the active directory rights, the employee would not be able to access the PACS using the remote token. Neither individual at issue used or attempted to use his or her access during the violation. | eight days after the first individual no longer needed access | when SERC_URE1 revoked access for the second individual | $41,000 (for SERC201000743, SERC201000751, SERC2011008285, SERC2011008331, SERC2012009651, SERC2012010509, SERC2012011334, SERC2013011760, SERC2013011762, SERC2013011764, SERC2013011766, and SERC2013011767) | Self-Report | To mitigate this violation, SERC_URE1: For the first instance: 1) implemented a new access revocation application that lists each task required to be performed; and 2) re-trained the group responsible for completing the revocation on the process and the associated responsibilities and reminded of the critical nature of removing NERC access within the allowed window of time. For the second instance: 1) confirmed that the delayed notifications were processed on the same day they were received; 2) ensured that the process for sending notifications was monitored; 3) determined the scope of the problem resulting from the hung system processes; 4) determined if there were any other previous incidents; 5) ensured that automated monitoring with alerting was in place for access revocation workflows within the future access revocation application; and 6) implemented the rewritten access revocation application and retired the old application. New functionality exists in the rewritten application to provide real-time visibility into the state of revocation tasks associated with NERC assets through automated reports, and through the user interface. | 2011-03-17 | 2012-09-20 | Neither Admits nor Denies | SERC reviewed SERC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2011008331 | Settlement Agreement | SERC_URE1 submitted a Self-Report to SERC stating that, as a Load Serving Entity and Transmission Owner, it was in violation of CIP-007-1 R3.1. SERC_URE1 failed to assess security patches within 30 calendar days. SERC_URE1 had a program that required the assessment of security patches and security upgrades for applicability within 30 calendar days of availability. SERC_URE1 discovered the identified security patches in three separate investigations which found that the missed security patches affected Critical Cyber Assets (CCAs) and non-critical Cyber Assets within the Electronic Security Perimeter (ESP). SERC_URE1 conducted an internal review of its patch management process. SERC_URE1 discovered that it had assessed the applicability of ten security patches for seven software products outside of the 30-day window. SERC_URE1 determined that it had taken between 81 and 313 days from the release dates of these ten security patches to assess their applicability. The individual responsible for conducting the security patch assessment failed to match the released security patches to the software inventory spreadsheet correctly. SERC_URE1 made a second discovery when a subject matter expert familiar with the product realized it was not running the latest software package. SERC_URE1 conducted an immediate review and found that the software in question was not on the software inventory spreadsheet at all. SERC_URE1 determined that it had not assessed the applicability of five security patches within 30 calendar days of their availability. SERC_URE1 assessed the applicability of the five security patches on the same day and determined that it had taken between 41 and 333 days from the release of the five security patches to assess their applicability. SERC_URE1 made a third discovery when a subject matter expert reviewed the software inventory spreadsheet and identified that software for one device was not current. In this case, the individual responsible for the review of newly released security patches incorrectly assessed that the security patch was not applicable. SERC_URE1 determined that it had taken 41 days from the release of the security patch to correctly assess the applicability of the patch. SERC_URE1 submitted a second Self-Report to SERC stating that it was in violation of CIP-007-3 R3.1 because it had failed to include a software application in its inventory of software applications when it was installed. SERC determined that this violation was related to the initial Self-Report and decided to treat the Self-Report as an expansion of scope of the violation. SERC_URE1 discovered this violation during an internal review of the security patch alert process. SERC_URE1 determined that it had not assessed the applicability of two software releases addressing three security vulnerabilities within 30 calendar days as required. The next day SERC_URE1 assessed both security patches for applicability and determined that it had taken between 64 and 275 days from the release of the two security patches to assess their applicability. In total, SERC_URE1 failed to assess 18 security patches for ten different software products within 30 days of the release of the security patches. | CIP-007-1 | R3, R3.1 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). SERC determined that the violation posed a moderate risk because SERC_URE1’s failure timely to assess 18 security patches and updates on ten different software products left software on the involved Cyber Assets vulnerable for extended periods of time, increasing the risk of a successful cyber attack against CCAs or Cyber Assets that could have resulted in operational impacts and potential degradation of the BPS. However, all of SERC_URE1’s Cyber Assets resided within secured ESPs and Physical Security Perimeters and access to Cyber Assets from outside the ESP required two-factor (strong) authentication. SERC_URE1’s electronic access control and monitoring devices did not identify any malicious activity during the violation that would have impacted the involved Cyber Assets. | 31 calendar days after the release of the first security patch | Mitigation Plan completion | $41,000 (for SERC201000743, SERC201000751, SERC2011008285, SERC2011008331, SERC2012009651, SERC2012010509, SERC2012011334, SERC2013011760, SERC2013011762, SERC2013011764, SERC2013011766, and SERC2013011767) | Self-Report | To mitigate this violation, SERC_URE1: For the first Self-Report: 1) modified its patch management alert process procedure to provide additional guidance to check for the version shown or any later versions to ensure that security patch applicability is correctly determined; 2) verified that all security patches issued were assessed based on the software inventory for the affected CCAs and all other Cyber Assets within the ESP; 3) assessed the missed patches identified and documented the assessment. In addition, it reviewed and augmented the software inventory methodology and then ran the new software inventory methodology against the current Cyber Asset list; 4) assessed and implemented the missing patch identified and scheduled the implementation of the missing patch; and 5) modified the patch management alert process procedure to provide additional instructions regarding the alert process and ensured that subject matter experts were made aware of the change. For the second Self-Report: 1) improved the patch assessment process by automating the patch assessment alert process; 2) modified the change management procedures to include a step for adding newly installed software to the NERC patch management inventory and assessing applicable security patches prior to commissioning the asset; 3) enhanced the patch assessment procedures to ensure that all applicable security patches or upgrades were assessed prior to the installation of new software on an existing device; and 4) communicated the changes in the patch assessment procedures to all supporting personnel. | 2012-03-27 | 2013-06-28 | Neither Admits nor Denies | SERC reviewed SERC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. SERC determined that SERC_URE1's prior compliance history was an aggravating factor in the penalty determination
SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2012009651 | Settlement Agreement | SERC_URE1 submitted a Self-Certification to SERC stating that it was in violation of CIP-007-3 R2.1. SERC_URE1 discovered three ports and two services not used for normal and emergency operations that were enabled on a device. SERC_URE1 had a process in place for ensuring only ports and services required for normal and emergency operations were enabled that involved using the discovery command provided by the vendor of the Cyber Assets. However, SERC_URE1 had three switches in separate Electronic Security Perimeters (ESPs) that retained three default open ports associated with three services that were not required for normal or emergency operations. In addition, SERC_URE1 had four routers in additional ESPs that had the same ports and services enabled as the switches, plus two additional services with no associated ports that were not required for normal or emergency operations. All of the switches and routers were protected by a Physical Security Perimeter (PSP). SERC_URE1 was unaware of these ports and services until it ran a user datagram protocol port scan. SERC_URE1 had disabled all unused ports and services or, in the case where such unused ports and services could not be disabled due to technical limitations, adopted compensating measures and filed a Technical Feasibility Exception request. In addition, SERC_URE1 modified the process for identification of open ports and services to use different tools for the discovery of enabled ports and services. | CIP-007-1 | R2, R2.1 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The affected Cyber Assets resided behind secured firewalls which restricted any outside remote electronic access, meaning any compromise would have to occur from within the secured ESP and PSP. The routers and switches were subject to logging and monitoring for cybersecurity events. Firewalls protecting the affected ESPs employed intrusion detection prevention (IDP) controls which monitored the firewall for cybersecurity events. IDP triggered events were sent to the firewall management station in real-time for monitoring and analysis. IDP signatures were downloaded from the firewall vendor daily to ensure they were up-to-date. | when the Standard became mandatory and enforceable on SERC_URE1 | Mitigation Plan completion | $41,000 (for SERC201000743, SERC201000751, SERC2011008285, SERC2011008331, SERC2012009651, SERC2012010509, SERC2012011334, SERC2013011760, SERC2013011762, SERC2013011764, SERC2013011766, and SERC2013011767) | Self-Certification | To mitigate this violation, SERC_URE1: 1) disabled unused ports and services on the three identified devices; 2) applied an access control list to block the unnecessary port on the three identified devices; 3) disabled unused services on the four identified routers; and 4) revised and implemented procedure enhancements to the network operations testing process document, which now includes commands used to verify ports. | 2012-05-08 | 2013-06-27 | Neither Admits nor Denies | SERC reviewed SERC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2012010509 | Settlement Agreement | SERC_URE1 submitted a Self-Report to SERC stating that it was in violation of CIP-004-2 R4.2. SERC_URE1 failed to revoke five contract employees’ access to Critical Cyber Assets (CCAs) within seven calendar days of when the access was no longer required. SERC_URE1 subsequently determined that one of the contractors required ongoing access and should not have been included in the Self-Report. Thus, SERC_URE1 failed to revoke four contractors’ access to CCAs within seven calendar days of when the access was no longer required. SERC_URE1 had a process in place for the revocation of physical access to CCAs for employees by deactivating their enterprise ID, consisting of a username and password, leaving them unable to attain a key card required for physical access. However, this process did not adequately address the contingent workforce (e.g., contractors) utilized by SERC_URE1. SERC_URE1 discovered that it had not revoked a contractor’s physical access to CCAs within seven days of the date on which the contractor no longer required such access. During an internal assessment, SERC_URE1 found that it had not revoked the physical access to CCAs of three other contractors within the required seven days. SERC_URE1 removed the four contractors' physical access to CCAs between 20 and 244 days late. SERC_URE1 determined that its process did not clearly delineate whether SERC_URE1 management or the contingent workforce company should contact SERC_URE1’s access control office to notify it to deactivate the workers’ access at the end of the workers’ assignments. SERC_URE1 collected the contractors’ key cards that gave them physical access to CCAs on or prior to their respective end dates. | CIP-004-2 | R4, R4.2 | Lower | Moderate | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. These failures were limited to four separate instances, and the contractors involved did not attempt to obtain a key card that would be required to gain physical access to CCAs. The contractors had valid personal risk assessments, were current in their NERC CIP training, and were in good standing with SERC_URE1 during the periods in question and after the violation was resolved. | eight days after the first contractor no longer needed physical access to CCAs | Mitigation Plan completion | $41,000 (for SERC201000743, SERC201000751, SERC2011008285, SERC2011008331, SERC2012009651, SERC2012010509, SERC2012011334, SERC2013011760, SERC2013011762, SERC2013011764, SERC2013011766, and SERC2013011767) | Self-Report | To mitigate this violation, SERC_URE1: 1) established a procedure to run a report twice a week to review all open assignment date requisitions. If an employee's reporting manager does not respond within three days, the employee's enterprise ID will be deactivated, thereby revoking access; 2) changed email notifications to define more clearly the steps the reporting managers must take to end the assignment; and 3) placed a new banner on an internal website to raise awareness and help managers understand what actions are required of them when ending contractor assignments. | 2012-03-16 | 2013-06-27 | Neither Admits nor Denies | SERC reviewed SERC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2012011334 | Settlement Agreement | SERC_URE1 submitted a Self-Report to SERC stating that it was in violation of CIP-006-1 R1.8. SERC_URE1 failed to adequately test and ensure that the upgrade of its physical access control system (PACS) did not adversely affect existing Cyber Assets within the Electronic Security Perimeter (ESP). SERC_URE1 had previously submitted a Self-Report to SERC addressing this violation, but stated that it was in violation of CIP-007-1 R1. After a preliminary review, SERC determined that the violation was more appropriately addressed under CIP-006-1 R1.8. SERC_URE1 had a testing program and procedures for adding new Cyber Assets and for significant changes to existing Cyber Assets within the ESP to ensure that significant changes do not affect existing cybersecurity controls. SERC_URE1 did not test the cybersecurity controls during an upgrade of the PACS. It did, however, confirm that the individuals with physical access to Critical Cyber Assets (CCAs) did not change as a result of the PACS upgrade. SERC_URE1, in following the advice of the vendor, incorrectly classified significant changes to the PACS systems as minor. SERC_URE1 has a process in place that monitors and alerts IT when any change is made to the PACS. This process alerted IT that there had been a change to the PACS as a result of an upgrade. An internal subject matter expert followed up on an inquiry from IT regarding the change and reviewed the change that was implemented. The internal subject matter expert determined that the change was significant and that SERC_URE1 should have tested and documented the PACS upgrade to ensure it did not adversely impact the existing cybersecurity controls. This violation affected five PACS servers used by SERC_URE1 to log and monitor its Physical Security Perimeters (PSPs) and impacted both production and failover systems. Despite this failure, SERC_URE1 completed a review and comparison of security controls after the changes had been implemented. While gathering information to respond to SERC questions regarding the scope of the violation, SERC_URE1 discovered seven earlier instances in which it implemented significant changes to the PACS without testing to ensure the changes did not adversely affect the existing cybersecurity controls. In these prior instances, SERC_URE1 determined that the significant changes to the PACS had no effect on its cybersecurity controls. | CIP-006-1 | R1, R1.8 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC determined that the violation posed a moderate risk because SERC_URE1’s failure to test significant changes made to PACS devices allowed undocumented changes to be implemented, potentially altering the existing cybersecurity controls. If the PACS servers were compromised due to an undocumented significant change, unauthorized individuals could gain physical access to CCAs and non-critical Cyber Assets and modify or disrupt their normal operation. However, in all eight instances in which SERC_URE1 implemented significant changes to the PACS without testing, it performed some functional testing on the PACS after implementation on the production environment that demonstrated the PACS’ operational functions were intact. SERC_URE1 utilizes a tool that alerts its IT in real time when changes in cybersecurity controls are detected. The seven earlier significant changes to the PACS had no impact on SERC_URE1’s cybersecurity controls. | when SERC_URE1 implemented the first significant change to the PACS system without testing | Mitigation Plan completion | $41,000 (for SERC201000743, SERC201000751, SERC2011008285, SERC2011008331, SERC2012009651, SERC2012010509, SERC2012011334, SERC2013011760, SERC2013011762, SERC2013011764, SERC2013011766, and SERC2013011767) | Self-Report | To mitigate this violation, SERC_URE1: 1) enhanced its cybersecurity test procedures to incorporate specific steps related to the testing of cybersecurity controls, including user account configuration changes and password configuration and parameter changes; 2) enhanced its cybersecurity test procedures to include a ports and service scan and comparison in coordination with any change that is made to the PACS baseline, regardless of the significance of the change; and 3) implemented a new testing threshold that characterizes all subsequent changes to PACS as significant by default, regardless of the change type, and requires the execution of the cybersecurity test procedures to confirm that cybersecurity controls have not been adversely affected by the changes. | 2012-03-30 | 2013-06-27 | Neither Admits nor Denies | SERC reviewed SERC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2013011760 | Settlement Agreement | SERC_URE1 submitted a Self-Report to SERC stating that it was in violation of CIP-007-3 R3.1. SERC_URE1 failed to assess the applicability of security patches within 30 calendar days of their availability. SERC_URE1 had a security patch management program that required the assessment of security patches and security upgrades for applicability within 30 calendar days of their availability. SERC_URE1 identified a security upgrade that was not reviewed for applicability within 30 days. The security upgrade was applicable to four servers that were non-critical Cyber Assets within an Electronic Security Perimeter (ESP). SERC_URE1 assessed the security upgrade 64 days after the vendor released it and 34 days after the required date. SERC_URE1 determined that the root cause of this violation was a human performance failure. While this specific security upgrade was correctly identified and associated with a number of other Cyber Assets, the SERC_URE1 IT security staff responsible for the review and assessment of security patches failed to associate this single security upgrade properly with all associated Cyber Assets. | CIP-007-3a | R3, R3.1 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). SERC determined that this violation posed a moderate risk because SERC_URE1’s failure to assess security patches and updates within 30 days of their availability left software on the affected Cyber Assets vulnerable for an extended period, increasing the risk of a cyber attack that could have resulted in operational impacts and potential degradation of the BPS. However, all the affected Cyber Assets resided within secured ESPs and Physical Security Perimeters and access from outside the ESP was limited and restricted. SERC_URE1’s electronic access control and monitoring devices were monitoring and alerting for unusual activity and did not identify any malicious activity that would have impacted the affected Cyber Assets. This violation affected only one security upgrade on four servers that were non-critical Cyber Assets | 31 days after the security patches were available | when SERC_URE1 assessed the applicability of the security patch | $41,000 (for SERC201000743, SERC201000751, SERC2011008285, SERC2011008331, SERC2012009651, SERC2012010509, SERC2012011334, SERC2013011760, SERC2013011762, SERC2013011764, SERC2013011766, and SERC2013011767) | Self-Report | To mitigate this violation, SERC_URE1 implemented an automatic risk alert solution which matches asset inventory to the monitored software products and automatically creates alerts for the asset owners to assess within the 30-day requirement. | 2012-10-18 | 2013-06-27 | Neither Admits nor Denies | SERC reviewed SERC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2013011762 | Settlement Agreement | SERC_URE1 submitted a Self-Report to SERC stating that it was in violation of CIP-004-3 R4.2. SERC_URE1 failed to revoke access to Critical Cyber Assets (CCAs) within seven calendar days of when the access was no longer required for four personnel. SERC_URE1 had an internally developed application to facilitate the revocation of physical access to CCAs for personnel who no longer required such access. SERC_URE1 discovered that this application had a bug in the code which resulted in a large number of duplicate records. The volume of duplicate records being processed by the application resulted in the production database failing to process alert emails, leaving the emails in a pending state. Once SERC_URE1 discovered and resolved this violation, it discovered that it had not revoked four SERC_URE1 employees’ physical access to CCAs within seven days of when that access was no longer required. Three employees retained access to all substation Physical Security Perimeters (PSPs) containing CCAs and one employee retained access to two substation PSPs containing CCAs. The employees retained access from one day to eight days beyond the seven days allowed by CIP-004-3 R4. | CIP-004-3 | R4, R4.2 | Lower | Moderate | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The affected individuals did not attempt to access the PSPs containing CCAs after they no longer required access. All involved personnel had valid personnel risk assessments and were current in their NERC CIP training. This violation was limited to four individuals who were in good standing with SERC_URE1 for the entire period in question and remained in good standing after this violation was resolved. | eight days after the employees no longer required access to CCAs | when SERC_URE1 revoked the final employee’s access | $41,000 (for SERC201000743, SERC201000751, SERC2011008285, SERC2011008331, SERC2012009651, SERC2012010509, SERC2012011334, SERC2013011760, SERC2013011762, SERC2013011764, SERC2013011766, and SERC2013011767) | Self-Report | To mitigate this violation, SERC_URE1: 1) created and implemented a script to remove duplicate records from the application which facilitates the revocation of access to CCAs; 2) enhanced the access revocation application to attempt to resend all failed notifications; and 3) optimized the access revocation database to reduce the likelihood of a notification time-out condition. | 4/6/2013 | 2013-07-17 | Neither Admits nor Denies | SERC reviewed SERC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2013011764 | Settlement Agreement | SERC_URE1 submitted a Self-Report to SERC stating that it was in violation of CIP-006-1 R1.8. SERC_URE1 had failed to afford Cyber Assets used in the access control and monitoring of the Physical Security Perimeters (PSPs) the protective measures specified in R1.8 in two instances. In the first instance SERC_URE1 discovered five dial-up modems that were being used to provide communications to the Physical Access Control System (PACS) server. As such, the five modems were Cyber Assets used in the access control and monitoring of the PSP. The communication between the five modems and the PACS server was a serial connection. However, SERC_URE1 failed to afford the five dial-up modems the protective measures specified in CIP-005-1 R2.3. SERC_URE1 failed to maintain a procedure for securing dial-up access to the PACS devices. Upon identification of this violation, SERC_URE1 investigated to ensure and confirm that the newly discovered dial-up connections were secured. SERC_URE1 also verified that no other dial-up connections existed in its broader CIP program. In the second instance, SERC_URE1 learned that its existing interpretation of what Cyber Assets should be included in a PACS was incomplete. A third-party consultant concluded a review of SERC_URE1’s CIP compliance program. After reviewing the consultant’s recommendations, SERC_URE1 determined that it had not been sufficiently inclusive in its assessment of what Cyber Assets made up its PACS. Originally, SERC_URE1 identified the PACS server as the only Cyber Asset associated with the PACS that fell within the scope of the CIP Standards. After the consultant’s review, SERC_URE1 identified additional card reader control panels and PACS workstations that should have been considered as PACS devices. SERC determined that SERC_URE1 was in violation of CIP-006-1 R1.8 because it failed to afford the card readers control panels and workstations used to manage the PACS devices the protective measures specified in CIP-006-1 R2. Specifically, SERC_URE1 could not implement operational and procedural controls to manage physical access at all access points to the PSP without identifying these Cyber Assets as PACS devices. | CIP-006-1 | R1, R1.8 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. All dial-up communications between the five modems and the PACS server were encrypted and secured using a passcode that was securely maintained by technical security personnel. SERC_URE1 knew of the existence of the Cyber Assets that were newly identified as PACS devices and afforded them defense-in-depth security under a broader corporate security initiative. All card reader control panels were located inside PSPs and were within secured cabinets with tamper alarms. All workstations used to manage the PACS devices were subject to corporate policies for change management, patch management, and access control. System monitoring logs indicated no attempts to compromise or actual compromise of any PACS panels. | when the Standard became mandatory and enforceable on SERC_URE1 | Mitigation Plan completion | $41,000 (for SERC201000743, SERC201000751, SERC2011008285, SERC2011008331, SERC2012009651, SERC2012010509, SERC2012011334, SERC2013011760, SERC2013011762, SERC2013011764, SERC2013011766, and SERC2013011767) | Self-Report | To mitigate this violation, SERC_URE1: 1) submitted technical feasibility exceptions where it was not technically possible to comply with standards regarding the protections applicable to the PACS panels and dial-up access to the electronic perimeter; 2) implemented primary and secondary dedicated workstations within the PACS PSP and electronic security perimeter (ESP); 3) developed and implemented a procedure for securing dial-up access for modems accessing the PACS ESP or remove the dial-up access points from the ESP altogether; and 4) implemented changes necessary to ensure that PACS panels are afforded the protective measures identified in CIP 006-3 R2.2 where technically feasible. | 8/1/2013 | 2013-10-23 | Neither Admits nor Denies | SERC reviewed SERC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2013011766 | Settlement Agreement | SERC_URE1 submitted two Self-Reports to SERC stating that it was in violation of CIP-006-3 R2.2. SERC_URE1 failed to afford its Physical Access Control Systems (PACS) the protective measures specified in R2.2. In the first instance a support vendor for the SERC_URE1 PACS system failed to test appropriately a change to the PACS system prior to implementing the change into production. SERC_URE1 had previously decided that all changes to PACS would be considered significant and would be tested and approved prior to implementation. SERC_URE1 had explained its change control process to the PACS support vendor. The PACS support vendor misunderstood the SERC_URE1 requirements and believed that simple parameter changes in the PACS were not considered significant. A SERC_URE1 subject matter expert (SME) became aware of the implemented change through regular communications with the PACS support vendor. SERC_URE1 rolled back the change in order to ensure the integrity of the PACS system and allow proper testing of the change to occur. However, SERC_URE1 had the untested and unapproved change in service on the production PACS system for three days. SERC determined that SERC_URE1 was in violation of CIP-006-3 R2.2 because it failed to afford its PACS devices the protective measures specified in CIP-007-3 R1. After a review by the SERC_URE1 SME and the support vendor, SERC_URE1 determined that no other changes had been implemented outside of the established change management process. In the second instance SERC_URE1 discovered that it had not assessed a security patch for a PACS server for 96 days. The patch was released by the vendor but was not assessed for applicability to the PACS server until 96 days after it was made available by the vendor and 66 days after the required date. This second instance was initially reported under CIP-007-3 R3.1 (NERC Violation ID SERC2013011760), but SERC determined that the violation was more appropriately addressed under CIP-006-3 R2.2 because it involved PACS devices. SERC determined that SERC_URE1 was in violation of CIP-006-3 R2.2 because it failed to afford its PACS devices the protective measures specified in CIP-007-3 R3.1. | CIP-006-3c | R2, R2.2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The unauthorized change was to a parameter file that affected reporting capabilities only, and did not impact or affect the security controls of the PACS. Remote panels at the Physical Security Perimeter (PSP) locations would have continued to operate autonomously and any alarms generated would have been queued by the panels and sent to the central server when it became available. SERC_URE1 utilizes a tool for real time alerting when changes in cybersecurity controls are detected. All personnel working for the PACS support vendor had received the required cybersecurity training, had a current personnel risk assessment, and were authorized by SERC_URE1 to work on its PACS. The failure to assess a security patch for the PACS server within 30 days affected only one security upgrade on a single PACS server. The PACS server resided within a secured Electronic Security Perimeter (ESP) and PSP and access from outside the ESP was limited and restricted. SERC_URE1’s electronic access control and monitoring devices did not identify any malicious activity that would have impacted the involved PACS server. | when the SERC_URE1 support vendor made the untested and unauthorized change to the PACS and 31 days after the missed security patch was available for assessment | when SERC_URE1 rolled back the untested and unauthorized change and when SERC_URE1 assessed the security patch | $41,000 (for SERC201000743, SERC201000751, SERC2011008285, SERC2011008331, SERC2012009651, SERC2012010509, SERC2012011334, SERC2013011760, SERC2013011762, SERC2013011764, SERC2013011766, and SERC2013011767) | Self-Report | To mitigate this violation, SERC_URE1: 1) sent notification via email to the support vendor informing them to return SERC_URE1's issued laptops and tokens. The email further described that SERC_URE1's IT personnel would be the proxy if any remote access was required going forward; 2) received all three SERC_URE1's issued laptops and tokens from support vendor and submitted requests to have the laptops decommissioned; and 3) implemented an automatic risk alert solution which matches asset inventory to the monitored software products and automatically creates alerts for the asset owners to assess within the 30-day requirement. | 2012-10-18 | 2013-06-27 | Neither Admits nor Denies | SERC reviewed SERC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2013011767 | Settlement Agreement | SERC_URE1 submitted a Self-Report to SERC stating that it was in violation of CIP-007-1 R2.1. SERC_URE1 failed to enable only those ports required for normal and emergency operations. SERC_URE1 identified four Critical Cyber Assets (CCAs) that had open ports that were not required for normal or emergency operations. SERC_URE1 discovered this violation as a result of its cyber vulnerability assessment. Three of the four routers were located within a SERC_URE1 Electronic Security Perimeter (ESP). The fourth router was located within another ESP. Each router had eight serial interfaces, and each serial interface contained four open transmission control protocol (TCP) ports, resulting in 32 open ports on each router, for a total of 128 open ports. SERC_URE1 started mitigating activities in its testing environment, which included blocking the unused and unneeded ports. SERC_URE1 initiated a review of all other ESPs. SERC_URE1 determined that no other similar violations existed within SERC_URE1 or its affiliates. SERC_URE1 updated the first three production and disabled the unused and unneeded ports. SERC_URE1 updated the fourth router and disabled the unused and unneeded ports. | CIP-007-1 | R2, R2.1 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). SERC determined that the violation posed a moderate risk because SERC_URE1’s failure to disable open ports on CCAs within the ESP could have allowed access to and the exploitation of the CCAs. This failure could limit, or render inoperable, SERC_URE1’s operational capabilities, remote control of Critical Assets, and situational awareness of BPS components into the energy management system. However, SERC_URE1 provided the devices involved in this violation with a defense-in-depth strategy. The devices resided behind secured firewalls that had a “deny by default” rule and restricted any outside remote electronic access, meaning any compromise would have to occur from within the secured ESP and Physical Security Perimeter. The firewalls protecting the devices also employed intrusion detection prevention (IDP) controls that monitored the firewalls for cybersecurity events. IDP-triggered events were sent to the firewall management station in real-time for monitoring and analysis. SERC_URE1 downloaded IDP signatures from the firewall vendor on a daily basis to keep them up-to-date. In addition, the devices were subject to logging and monitoring for cybersecurity events. Where technically feasible, all Cyber Assets within the ESP were running malware protection. There are no known vulnerabilities or exploits associated with the open ports that could be used to disrupt, degrade or otherwise misuse the routers or terminal servers connected to these devices. | when the Standard became mandatory and enforceable on SERC_URE1 | Mitigation Plan completion | $41,000 (for SERC201000743, SERC201000751, SERC2011008285, SERC2011008331, SERC2012009651, SERC2012010509, SERC2012011334, SERC2013011760, SERC2013011762, SERC2013011764, SERC2013011766, and SERC2013011767) | Self-Report | To mitigate this violation, SERC_URE1: 1) determined the ports and services necessary for normal and emergency operations; 2) performed a TCP port scan; 3) developed an access control list (ACL) which blocked access to unused ports; 4) applied the ACL to the test device, performed a port scan, and verified the unused ports were blocked; 5) applied configuration changes in production which blocked the unused ports; 6) completed production configuration changes which blocked the unused ports; 7) added a task to the network operations group's CIP-007 annual review; 8) communicated the changes in the systems security management procedure to all affected personnel; and 9) completed production configuration changes which blocked the unused ports. | 2013-03-14 | 2013-06-27 | Neither Admits nor Denies | SERC reviewed SERC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
SERC Reliability Corporation (SERC) | Unidentified Registered Entity 2 (SERC_URE2) | NCRXXXXX | SERC201000603 | Settlement Agreement | SERC_URE2 submitted a Self-Report to SERC stating that it was in violation of CIP-007-1 R6.4. SERC_URE2 failed to retain all system event logs related to cybersecurity for 90 calendar days. SERC_URE2 had implemented and documented organizational processes and technical and procedural tools to monitor for cybersecurity events on all Cyber Assets within the Electronic Security Perimeter (ESP). The automated tools alert on any cybersecurity event detected and would allow for retention of logs associated with any cybersecurity event and for further review as required. However, some device logs were configured to capture all event logs, not just cyber events. Due to the large amount of logs generated by patching, the local memory filled and began to overwrite existing data. SERC_URE2 discovered the violation during an internal review of the 90-day retention requirement and immediately initiated an internal investigation. SERC_URE2 concluded its investigation, and found that six Critical Cyber Assets (CCAs) and four non-critical Cyber Assets, in several ESPs, were missing log data for various periods. SERC_URE2 modified the maximum file size for its cybersecurity logs and the overwrite thresholds on all CCAs and Cyber Assets to prevent overwriting logged events that were less than 90 days old. SERC_URE2 determined that the logs for the ten devices in question had been overwritten and were unrecoverable. SERC_URE2 started conducting daily manual backups of the logs to prevent further overwrites and alleviate any more potential non-compliance. | CIP-007-1 | R6; R6.4 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC determined that the violation posed a moderate risk because, in the event of a cybersecurity incident, SERC_URE2’s failure to retain logs related to security events for 90 calendar days on the 10 CCAs and Cyber Assets could have resulted in the loss of important security information required for a thorough investigation. However, this failure was limited to CCAs and Cyber Assets that were spread across four separate ESPs, which further reduced potential attack vectors and impacts. SERC_URE2 reviewed all accesses to the ESP and Physical Security Perimeters and found no unauthorized accesses or access attempts. Malware prevention and other security controls remained operational and up-to-date for the time period in question. SERC_URE2 did not discover or detect any cybersecurity events, including the discovery of malware, during the violation period. | the first day logs were overwritten | Mitigation Plan completion | $14,000 (for SERC201000603, SERC2011008287, SERC2012009650, SERC2012010581, SERC2012011335, SERC2013011755, and SERC2013011757) | Self-Report | To mitigate this violation, SERC_URE2: 1) reviewed and modified, as necessary, the local audit policies associated with the logging of cybersecurity to ensure that only events related to cybersecurity are written to the cybersecurity log; 2) developed automated processes to verify log configuration settings, monitor log events related to cybersecurity, and perform cybersecurity log backup and retention; 3) communicated the intended automated processes changes to the process control vendor, verified with the vendor that the changes would not impact the reliability function of the Cyber Assets, and documented the vendor's review; and 4) implemented the new automated processes, verified that they are functioning as intended, documented the changes to the affected Cyber Assets, and revised documentation as necessary to incorporate the new automated processes. | 2010-11-29 | 2012-08-23 | Neither Admits nor Denies | SERC reviewed SERC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
SERC Reliability Corporation (SERC) | Unidentified Registered Entity 2 (SERC_URE2) | NCRXXXXX | SERC2011008287 | Settlement Agreement | SERC_URE2 submitted a Self-Report to SERC stating that it was in violation of CIP-004 R4.2. SERC_URE2 failed in two instances to revoke an individual’s access to Critical Cyber Assets (CCAs) within seven calendar days when the access was no longer required. In the first instance, an employee’s NERC training qualification expired due to a failure to renew the training by the SERC_URE2-specified deadline. This employee had access to the physical access control system (PACS) via remote token access, which in turn required active directory access. SERC_URE2 had an automated system in place to alert the IT security group responsible for revocation of CCA access to the expiration of the employee's NERC training. Due to human error, SERC_URE2 did not remove the employee’s remote token access until 16 days after the revocation was requested, causing it to be nine days late. The employee's active directory rights had been removed within the required timeframe. Without the active directory rights, the employee would not be able to access the PACS using the remote token. During this period, the employee did not attempt to use his or her access to the PACS. In addition, the employee continued to be in good standing with SERC_URE2 and had a valid Personal Risk Assessment (PRA). In the second instance, SERC_URE2 had an automated process in place to alert the IT security group responsible for revocation of CCA access when an employee with CCA access had a change in job duties. The IT security group would be responsible for reviewing and removing CCA access as required. This automated process failed due to the server freezing and did not resume until 15 days later when regular maintenance tasks were performed and the server was rebooted. At this time, SERC_URE2 did not have any means of remotely monitoring whether the server was operating normally. Upon reboot, pending revocation alerts that were hung-up in the server were sent and acted on the same day. One alert required that SERC_URE2 remove an employee’s CCA access due to a job change that did not require CCA access. This employee had access to three Physical Security Perimeters that contained Cyber Assets used as electronic access control and monitoring devices and PACS. SERC_URE2 did not remove the employee's access until 15 days after the date the revocation was requested, causing it to be eight days late. During this period, the employee did not use his or her physical access privileges. In addition, the employee continues to be in good standing with SERC_URE2 and had a valid PRA. | CIP-004-1 | R4; R4.2 | Lower | Moderate | This violation posed a minimal risk to the reliability of the bulk power system. These failures were limited to two separate instances, and the employees involved were in good standing with the company for the entire period in question and remained in good standing after this violation end date. Both employees had current PRAs. In the first incident, the employee's active directory rights had been removed within the required timeframe. Without the active directory rights, the employee would not be able to access the PACS using the remote token. Neither individual used or attempted to use his or her access during the violation. | eight days after the first individual no longer needed access | when SERC_URE2 revoked access for the second individual | $14,000 (for SERC201000603, SERC2011008287, SERC2012009650, SERC2012010581, SERC2012011335, SERC2013011755, and SERC2013011757) | Self-Report | To mitigate this violation, SERC_URE2: 1) confirmed that the delayed notifications were processed in a timely manner; 2) ensured that the process for sending access revocation notifications was monitored; 3) determined the scope of the problem resulting from the hung systems processes; 4) performed an extent of condition review to determine if there were any other instances that previously went un-recognized and could have resulted in non-compliance; 5) ensured that automated monitoring with alerting was in place for access revocation workflows within the future access revocation application; 6) implemented the rewritten access revocation application and retired the old application; 7) implemented a new access revocation application that lists each task required to be performed; and 8) re-trained the group responsible for access revocation on the revocation process and associated responsibilities. | 2011-03-17 | 2012-09-20 | Neither Admits nor Denies | SERC reviewed SERC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
SERC Reliability Corporation (SERC) | Unidentified Registered Entity 2 (SERC_URE2) | NCRXXXXX | SERC2012009650 | Settlement Agreement | SERC_URE2 submitted a Self-Certification to SERC stating that it was in violation of CIP-007-3 R2.1. SERC_URE2 discovered three ports and three services not used for normal and emergency operations enabled on a device. SERC_URE2 had a process in place for ensuring only ports and services required for normal and emergency operations were enabled that involved using the discovery command provided by the vendor of the Cyber Assets. However, SERC_URE2 had four switches in four separate Electronic Security Perimeters (ESPs) that retained three default open ports associated with three services that were not required for normal or emergency operations. All of the switches were protected by a Physical Security Perimeter (PSP). SERC_URE2 was unaware of these ports and services until it ran a user datagram protocol port scan. SERC_URE2 had disabled all unused ports and services or, in the case where such unused ports and services could not be disabled due to technical limitations, adopted compensating measures and filed a Technical Feasibility Exception request. In addition, SERC_URE2 modified the process for identification of open ports and services to use different tools for discovery of enabled ports and services. | CIP-007-1 | R2; R2.1 | Medium | Severe | This violation posed a minimal risk and did not pose a severe risk to the reliability of the bulk power system. The affected Cyber Assets resided behind secured firewalls which restricted any outside remote electronic access, meaning any compromise would have to occur from within the secured ESP and PSP. The routers and switches were subject to logging and monitoring for cybersecurity events. Firewalls protecting the four affected ESPs employed intrusion detection prevention (IDP) controls which monitored the firewall for cybersecurity events. IDP-triggered events were sent to the firewall management station in real time for monitoring and analysis. IDP signatures were downloaded from the firewall vendor daily to maintain currency. | when the Standard became mandatory and enforceable on SERC_URE2 | Mitigation Plan completion | $14,000 (for SERC201000603, SERC2011008287, SERC2012009650, SERC2012010581, SERC2012011335, SERC2013011755, and SERC2013011757) | Self-Certification | To mitigate this violation, SERC_URE2: 1) disabled unused ports and services on identified devices; 2) applied an access control list to block the unnecessary ports on the device; and 3) revised and implemented an updated network operations testing process document to include procedures to find and disable unused ports and services. | 2012-01-18 | 2013-06-27 | Neither Admits nor Denies | SERC reviewed SERC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
SERC Reliability Corporation (SERC) | Unidentified Registered Entity 2 (SERC_URE2) | NCRXXXXX | SERC2012010581 | Settlement Agreement | SERC_URE2 submitted a Self-Report to SERC stating that it was in violation of CIP-007-1 R3.1. SERC_URE2 failed to document its assessment of a security patch within 30 calendar days of the availability of the security patch. SERC_URE2 had a program that required the documentation of its assessment of security patches and security upgrades for applicability within 30 calendar days of the availability of such patches and upgrades. SERC learned that SERC_URE2 relied on an automated email alert from a security vendor to make it aware of available and applicable security patches. There was no confirmation step to ensure that all required security patch updates had been sent. A SERC_URE2 subject matter expert identified a security patch that had been released by a software vendor and had not been assessed within 30 days. Forty-four days after the security patch was released, SERC_URE2 completed its assessment of the security patch and retained all necessary documentation. SERC_URE2 implemented the patch on all impacted CCAs. | CIP-007-3a | R3; R3.1 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. This violation affected one security patch for one software product on several CCAs. Access to the CCAs from outside the ESP required strong two-factor authentication. SERC_URE2’s electronic access control and monitoring systems did not identify any malicious activity during the violation that would have impacted the CCAs. | 31 calendar days after the release of the security patch | when SERC_URE2 assessed the security patch and documented its assessment | $14,000 (for SERC201000603, SERC2011008287, SERC2012009650, SERC2012010581, SERC2012011335, SERC2013011755, and SERC2013011757) | Self-Report | To mitigate this violation, SERC_URE2: 1) conducted a comprehensive review and comparison of the patches/upgrades to look for related problems; and 2) enhanced the patch management procedure to require a daily review of the website that served as the source of patch and upgrade notifications. | 2011-11-18 | 2013-04-23 | Neither Admits nor Denies | SERC reviewed SERC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
SERC Reliability Corporation (SERC) | Unidentified Registered Entity 2 (SERC_URE2) | NCRXXXXX | SERC2012011335 | Settlement Agreement | SERC_URE2 submitted a Self-Report to SERC stating that it was in violation of CIP-006-1 R1.8. SERC_URE2 failed to adequately test and ensure that the upgrade of its physical access control system (PACS) did not adversely affect existing Cyber Assets within the Electronic Security Perimeter (ESP). SERC_URE2 had previously submitted a Self-Report to SERC addressing this violation but stated that it was in violation of CIP-007-1 R1. After a preliminary review, SERC determined that the violation was more appropriately addressed under CIP-006-1 R1.8. SERC_URE2 had a testing program and procedures for adding new Cyber Assets and for significant changes to existing Cyber Assets within the ESP to ensure that significant changes do not affect existing cybersecurity controls. SERC_URE2 did not test the cybersecurity controls during an upgrade of the PACS. It did, however, confirm that the individuals with physical access to Critical Cyber Assets (CCAs) did not change as a result of the PACS upgrade. SERC_URE2, in following the advice of the vendor, incorrectly classified significant changes to the PACS systems as minor. SERC_URE2 has a process in place that monitors and alerts IT when any change is made to the PACS. This process alerted IT that there had been a change to the PACS as a result of an upgrade. An internal subject matter expert followed up on an inquiry from IT regarding the change and reviewed the change that was implemented. The internal subject matter expert determined that the change was significant and that SERC_URE2 should have tested and documented the PACS upgrade to ensure that it did not adversely impact the existing cybersecurity controls. This violation affected five PACS servers used by SERC_URE2 to log and monitor its Physical Security Perimeters (PSPs) and impacted both production and failover systems. Despite this failure SERC_URE2 completed a review and comparison of security controls after the changes had been implemented. While gathering information to respond to SERC questions regarding the scope of the violation, SERC_URE2 discovered seven earlier instances in which it implemented significant changes to the PACS without testing to ensure the changes did not adversely impact the existing cybersecurity controls. In these prior instances, SERC_URE2 determined that the significant changes to the PACS had no impact on its cybersecurity controls. | CIP-006-1 | R1; R1.8 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC determined that the violation posed a moderate risk because SERC_URE2’s failure to test significant changes made to PACS devices allowed undocumented changes to be implemented, potentially altering the existing cybersecurity controls. If the PACS servers were compromised due to an undocumented significant change, unauthorized individuals could gain physical access to CCAs and non-critical Cyber Assets and modify or disrupt their normal operation. However, in all eight instances in which SERC_URE2 implemented significant changes to the PACS without testing, it performed some functional testing on the PACS after implementation on the production environment that demonstrated the PACS’ operational functions were intact. SERC_URE2 utilizes a tool that alerts its IT in real time when changes in cybersecurity controls are detected. The seven earlier significant changes to the PACS had no impact on SERC_URE2's cybersecurity controls. | when SERC_URE2 implemented the first significant change to the PACS system without testing | Mitigation Plan completion | $14,000 (for SERC201000603, SERC2011008287, SERC2012009650, SERC2012010581, SERC2012011335, SERC2013011755, and SERC2013011757) | Self-Report | To mitigate this violation, SERC_URE2: 1) enhanced test procedures; 2) added ports and service scans to testing process; and 3) invoked a new testing threshold. | 2012-03-30 | 2013-06-27 | Neither Admits nor Denies | SERC reviewed SERC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
SERC Reliability Corporation (SERC) | Unidentified Registered Entity 2 (SERC_URE2) | NCRXXXXX | SERC2013011755 | Settlement Agreement | SERC_URE2 submitted a Self-Report to SERC stating that it was in violation of CIP-006-1 R1.8 . SERC_URE2 failed to afford Cyber Assets used in the access control and monitoring of the Physical Security Perimeter(s) (PSPs) the protective measures specified in R1.8 in two instances. In the first instance SERC_URE2 discovered five dial-up modems that were being used to provide communications to the physical access control system (PACS) server. As such, the five modems were Cyber Assets used in the access control and monitoring of the PSP. The communication between the five modems and the PACS server was a serial connection. However, SERC_URE2 failed to afford the five dial-up modems the protective measures specified in CIP-005-1 R2.3. SERC_URE2 failed to maintain a procedure for securing dial-up access to the PACS devices. Upon identification of this violation, SERC_URE2 investigated to ensure and confirm that the newly discovered dial-up connections were secured. SERC_URE2 also verified that no other dial-up connections existed in its broader CIP program. In the second instance, SERC_URE2 learned that its existing interpretation of what Cyber Assets should be included in a PACS was incomplete. A third-party consultant concluded a review of SERC_URE2’s CIP compliance program. After reviewing the consultant’s recommendations, SERC_URE2 determined that it had not been sufficiently inclusive in its assessment of what Cyber Assets made up its PACS. Originally, SERC_URE2 identified the PACS server as the only Cyber Asset that fell within the scope of the CIP Standards. After the consultant’s review, SERC_URE2 identified additional card reader control panels and PACS workstations that should have been considered as PACS devices. SERC determined that SERC_URE2 was in violation of CIP-006-1 R1.8 because it failed to afford the card reader control panels and workstations used to managed the PACS devices the protective measures specified in CIP-006-1 R2. Specifically, SERC_URE2 could not implement operational and procedural controls to manage physical access to all access points to the PSP without identifying these Cyber Assets as PACS devices. | CIP-006-1 | R1; R1.8 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. All dial-up communications between the five modems and the PACS server were encrypted and secured using a passcode that was securely maintained by technical security personnel. SERC_URE2 knew of the existence of the Cyber Assets that were newly identified as PACS devices and afforded them defense-in-depth security under a broader corporate security initiative. All card reader control panels were located inside PSPs and within secured cabinets with tamper alarms. All workstations used to manage the PACS devices were subject to corporate policies for change management, patch management, and access control. System monitoring logs indicated no attempts or actual compromise of any PACS panels. | when the Standard became mandatory and enforceable for SERC_URE2 | Mitigation Plan completion | $14,000 (for SERC201000603, SERC2011008287, SERC2012009650, SERC2012010581, SERC2012011335, SERC2013011755, and SERC2013011757) | Self-Report | To mitigate this violation, SERC_URE2 implemented an off-cycle RBAM and determined that it does not have any CCAs. | 2012-06-26 | 2013-06-27 | Neither Admits nor Denies | SERC reviewed SERC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
SERC Reliability Corporation (SERC) | Unidentified Registered Entity 2 (SERC_URE2) | NCRXXXXX | SERC2013011757 | Settlement Agreement | SERC_URE2 submitted a Self-Report to SERC stating that it was in violation of CIP-006-3 R2.2. SERC_URE2 failed to afford its Physical Access Control Systems (PACS) the protective measures specified in R2.2. A support vendor for the SERC_URE2 PACS system failed to appropriately test a change to the PACS system prior to implementing the change into production. SERC_URE2 had previously decided that all changes to PACS would be considered significant and would be tested and approved prior to implementation. SERC_URE2 had explained its change control process to the PACS support vendor. The PACS support vendor misunderstood the SERC_URE2 requirements and believed that simple parameter changes in the PACS were not considered significant. A SERC_URE2 subject matter expert (SME) became aware of the implemented change through regular communications with the PACS support vendor. SERC_URE2 rolled back the change in order to ensure the integrity of the PACS system and allow proper testing of the change to occur. However, SERC_URE2 had the untested and unapproved change in service on the production PACS system for three days. SERC determined that SERC_URE2 was in violation of CIP-006-3 R2.2 because it failed to afford its PACS devices the protective measures specified in CIP-007-3 R1. After a review by the SERC_URE2 SME and the support vendor, SERC_URE2 determined that no other changes had been implemented outside of the established change management process. | CIP-006-3c | R2; R2.2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. This unauthorized change was to a parameter file that affected reporting capabilities only, and did not impact or affect the security controls of the PACS. Remote panels at the Physical Security Perimeter locations would have continued to operate autonomously and any alarms generated would have been queued by the panels and sent to the central server when it was available. SERC_URE2 utilizes a tool for real time alerting when changes in cybersecurity controls are detected. All personnel working for the PACS support vendor had received the required cybersecurity training, had a current personnel risk assessment, and were authorized by SERC_URE2 to work on its PACS. | when the SERC_URE2 support vendor made the untested and unauthorized change to the PACS | when SERC_URE2 rolled back the untested and unauthorized change | $14,000 (for SERC201000603, SERC2011008287, SERC2012009650, SERC2012010581, SERC2012011335, SERC2013011755, and SERC2013011757) | Self-Report | To mitigate this violation, SERC_URE2 implemented an off-cycle RBAM and determined that it does not have any CCAs. | 2012-06-26 | 2013-06-27 | Neither Admits nor Denies | SERC reviewed SERC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.