## PUBLIC_CIP Violations
Region | Registered Entity | NCR_ID | NERC Violation ID # | Notice of Confirmed Violation or Settlement Agreement | Description of the Violation | Reliability Standard | Req. | Violation Risk Factor | Violation Severity Level | Risk Assessment | Violation Start Date | Violation End Date | Total Penalty or Sanction ($) | Method of Discovery | Description of Mitigation Activity | Mitigation Completion Date | Date Regional Entity Verified Completion of Mitigation | "Admits," "Agrees/Stipulates," "Neither Admits nor Denies," or "Does Not Contest" | Other Factors Affecting the Penalty Determination, including Compliance History, Internal Compliance Program and Compliance Culture
Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2012009748 | Notice of Confirmed Violation | During a Compliance Audit MRO determined that MRO_URE1 was in violation of CIP-005-1 R1. Specifically, MRO_URE1 failed to afford Cyber Assets used in the access control and monitoring of the Electronic Security Perimeter (ESP) the protective measures as specified in CIP-007-1 R1.3, R8.2, and R8.4. While reviewing MRO_URE1's Cyber Vulnerability Assessment documentation, MRO discovered that an ESP device had an open port, and the port was not listed in the device baseline. MRO_URE1 did not document any action items to correct this discrepancy. Therefore, MRO_URE1 failed to verify that only ports and services required for operation of the Cyber Assets within the ESP were enabled as required by CIP-007-1 R8.2, and failed to document the action plan to mitigate vulnerabilities identified in the assessment as required by CIP-007-1 R8.4. Additionally, MRO_URE1 failed to provide evidence of testing when the a device was commissioned, as required by CIP 007-1 R1.3. | CIP-005-1 | R1; R1.5 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The device is a supplemental security protection measure and it is located outside of the ESP within a demilitarized zone. Therefore, a potential unauthorized user could not use the device to access devices within the ESP. Additionally, although the port was not documented properly, the port was properly enabled. Furthermore, MRO_URE1 provided baseline profiles to indicate that at least some level of security control testing was performed. | when the Standard became mandatory and enforceable on MRO_URE1 | when MRO_URE1 updated its cyber baseline profile and completed the testing as required by CIP-007-1 R1.3 | $10,000 (for MRO2012009748; MRO2012009749; MRO2012009751; MRO2012009752; and MRO2012009753) | Compliance Audit | To mitigate this violation, MRO_URE1: 1) updated its Cyber Asset profile documentation for the device; 2) performed a comprehensive review of all devices used for the access control and monitoring of the ESP to confirm that configurations are correct and to verify that the access points are consistent with documentation; and 3) updated documentation for all devices used for the access control and monitoring of the ESP. | 2013-08-26 | 2013-09-30 | Admits | MRO reviewed MRO_URE1's internal compliance program and considered it to be a neutral factor in the penalty determination. MRO considered the duration of the Mitigation Plan as an aggravating factor that affected the penalty. After the Compliance Audit, MRO_URE1 invested in equipment to improve their compliance with the CIP Standards. MRO considered this as a mitigating factor in the penalty determination.
Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2012009749 | Notice of Confirmed Violation | During a Compliance Audit MRO determined that MRO_URE1 was in violation of CIP-005-1 R2. Specifically, MRO_URE1 failed to document the configuration of one port at an access point required for operation and monitoring Cyber Assets within the Electronic Security Perimeter (ESP) as required by CIP-005-1 R2.2. The port was properly enabled, but the port was not documented in the baseline. During mitigation, MRO_URE1 performed a comprehensive review of its ports and services documentation. | CIP-005-1 | R2; R2.2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although MRO_URE1 failed to document the configuration of one port at an access point, MRO_URE1's process for determining which ports to enable was not deficient. Additionally, the port at issue was properly enabled and required for operation. MRO_URE1 failed to document the port in the baseline document. Therefore, this violation was limited to a documentation deficiency for one port subject to CIP-005-1 R2.2. | when the Standard became mandatory and enforceable on MRO_URE1 | when MRO_URE1 documented the configuration of its port | $10,000 (for MRO2012009748; MRO2012009749; MRO2012009751; MRO2012009752; and MRO2012009753) | Compliance Audit | To mitigate this violation, MRO_URE1: 1) updated the Cyber Asset profile documentation for the device; 2) performed a comprehensive review of all ESP access points to confirm that configurations are correct and to verify that the access points are consistent with documentation; and 3) updated documentation for all devices classified as ESP access points. | 2013-08-21 | 2013-09-11 | Admits | MRO reviewed MRO_URE1's internal compliance program and considered it to be a neutral factor in the penalty determination. MRO considered the duration of the Mitigation Plan as an aggravating factor that affected the penalty. After the Compliance Audit, MRO_URE1 invested in equipment to improve their compliance with the CIP Standards. MRO considered this as a mitigating factor in the penalty determination.
Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2012009751 | Notice of Confirmed Violation | During a Compliance Audit MRO determined that MRO_URE1 was in violation of CIP-006-1 R1.8. Specifically, MRO_URE1 failed to afford the protective measures as described in CIP-007-1 R2 for Cyber Assets used in the access control and monitoring of the Physical Security Perimeter (PSP). MRO_URE1 failed to document a process to ensure that only ports and services required for normal and emergency operations were enabled as required by CIP-007-1 R2. MRO_URE1's Cyber Vulnerability Assessment identified open ports that were not identified in the associated baseline documentation. Upon discovering the ports, MRO_URE1 did not update its baseline documentation. During mitigation, MRO_URE1 performed a comprehensive review of its ports and services and did not identify any other discrepancies in its ports and services documentation. | CIP-006-1 | R1; R1.8 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although MRO_URE1 failed to document its ports, MRO_URE1's process for determining which ports to enable was not deficient. All of MRO_URE1's ports and services subject to CIP-006-1 R1.8 were properly enabled for normal and emergency operations. Furthermore, the PACS devices are afforded the protections of being located within the Electronic Security Perimeter. | when the Standard became mandatory and enforceable on MRO_URE1 | when MRO_URE1 documented ports and services for normal and emergency operation | $10,000 (for MRO2012009748; MRO2012009749; MRO2012009751; MRO2012009752; and MRO2012009753) | Compliance Audit | To mitigate this violation, MRO_URE1: 1) updated the Cyber Asset profile document for the device; 2) performed a comprehensive review of the procedures; and 3) updated its Cyber Asset profile documentation template to include more accurate reporting of port and service status. | 2013-08-21 | 2013-09-16 | Admits | MRO reviewed MRO_URE1's internal compliance program and considered it to be a neutral factor in the penalty determination. MRO considered the duration of the Mitigation Plan as an aggravating factor that affected the penalty. After the Compliance Audit, MRO_URE1 invested in equipment to improve their compliance with the CIP Standards. MRO considered this as a mitigating factor in the penalty determination.
Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2012009752 | Notice of Confirmed Violation | During a Compliance Audit MRO determined that MRO_URE1 was in violation of CIP-007-1 R4. Specifically, MRO_URE1 failed to have a process for updating antivirus and malware prevention signatures that addressed testing the signatures prior to installation, as required by CIP-007-1 R4.2. MRO_URE1 installed updated antivirus and malware signatures before it installed the same signatures within the Electronic Security Perimeter (ESP). However, this process was not documented. Additionally, MRO_URE1 only applied this process to some devices. | CIP-007-1 | R4; R4.2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although MRO_URE1 failed to document its testing process for antivirus and malware signatures, MRO_URE1 first tested the signatures on outside of the ESP. Therefore, if a failure would have occurred, MRO_URE1 would have discovered the issue prior to installing the update on the devices within the ESP. Additionally, although the process for testing was not documented for the other device, the manual nature of the updating process provided MRO_URE1 an opportunity to stop the update if problems were discovered prior to installation of the update. | when the Standard became mandatory and enforceable on MRO_URE1 | when MRO_URE1 documented and implemented a process for updating antivirus and malware signatures | $10,000 (for MRO2012009748; MRO2012009749; MRO2012009751; MRO2012009752; and MRO2012009753) | Compliance Audit | To mitigate this violation, MRO_URE1: 1) performed a comprehensive review of the anti-malware environment and procedures to ensure the documents are accurate and an up-to-date reflection of the technology and management processes; 2) updated documentation for antivirus signature updates and testing procedures; 3) evaluated a new signature testing module from an antivirus vendor; and 4) designed and implemented procedures and technology to provide more robust testing of antivirus signatures. | 2013-08-23 | 2013-09-26 | Admits | MRO reviewed MRO_URE1's internal compliance program and considered it to be a neutral factor in the penalty determination. MRO considered the duration of the Mitigation Plan as an aggravating factor that affected the penalty.
Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2012009753 | Notice of Confirmed Violation | During a Compliance Audit MRO determined that MRO_URE1 was in violation of CIP-007-1 R8. Specifically, MRO_URE1 failed to document and track the execution status of its action plan for remediation of one vulnerability identified during its Cyber Vulnerability Assessment (CVA), as required by CIP-007-1 R8.4. During the annual CVA, MRO_URE1 discovered that a service and associated port were enabled in two Cyber Assets, but they were not included in the baseline documentation. As a result, an action item was created to disable the service on both Cyber Assets. The status of the action item at the time of the Compliance Audit was closed. However, the ticket provided as evidence of completion only indicated that one of the Cyber Assets was corrected. When MRO_URE1 went to disable the other service, it determined that the service was necessary and did not disable it as specified in the action item. However, MRO_URE1 did not revise the action item to reflect the erroneous inclusion. | CIP-007-1 | R8; R8.4 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although MRO_URE1 originally listed disabling the service as an action item, during the execution of the task, MRO_URE1 determined that the service was necessary. Therefore, the service should not have been listed as an action item and the violation is based on erroneous inclusion. Additionally, the Cyber Asset was protected by the Electronic Security Perimeter and the Physical Security Perimeter. | when MRO_URE1 failed to document the execution status of the CVA | when MRO_URE1 documented the status of its action plan for the vulnerability identified in the CVA | $10,000 (for MRO2012009748; MRO2012009749; MRO2012009751; MRO2012009752; and MRO2012009753) | Compliance Audit | To mitigate this violation, MRO_URE1: 1) performed a comprehensive review of the CVA program to identify procedural gaps relative to CIP-007-3 R8; 2) revised the 2010 CVA spreadsheet to indicate the actual actions taken; 3) reviewed the action plans for the 2010 and 2011 iterations of the CVA and confirmed that all action items were completed and documented correctly; and 4) added two columns to the CVA findings template to capture additional information for future assessments. | 2013-08-21 | 2013-09-25 | Admits | MRO reviewed MRO_URE1's internal compliance program and considered it to be a neutral factor in the penalty determination. MRO considered the duration of the Mitigation Plan as an aggravating factor that affected the penalty.
SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC201000442 | Settlement Agreement | SERC_URE1 submitted a Self-Report to SERC stating that it was in violation of CIP-006-1 R1.8 because the physical access control system (PACS) was not afforded all the protective measures required pursuant to CIP-006-1 R1.8. Specifically, SERC_URE1 reported that it had not afforded the PACS the protective measures described in CIP-007-1 R3 related to security patch management. SERC_URE1 discovered that it was not assessing security patches for all the assets comprising the PACS. The subset of PACS assets at issue in this violation consisted of a total of seven Cyber Assets, three servers and four workstations. SERC_URE1 reported that the PACS assets at issue were deployed in an isolated Electronic Security Perimeter (ESP) with no communication paths to SERC_URE1's Critical Cyber Assets (CCAs), corporate assets, or the internet. While analyzing this issue, SERC learned that SERC_URE1 had a procedure requiring it to assess and apply security patches. SERC_URE1 did assess and apply security patches on its deployed CCAs and other non-critical Cyber Assets, as required. SERC_URE1 had classified all its PACS assets as CIP-protected Cyber Assets, thereby bringing them within the scope of this procedure. SERC_URE1 however, had no evidence that assessments were being performed for the seven PACS assets described above. In total, SERC_URE1 failed to document its assessment of 19 security patches released during a five month period for the seven PACS asset at issue. A month and half later, SERC_URE1 applied these 19 security patches on the seven PACS assets. SERC sent SERC_URE1 an initial notice of a Compliance Audit. During this Compliance Audit, SERC found that SERC_URE1's Physical Security Plan, which details SERC_URE1's organizational processes and technical and procedural mechanisms for controlling access at physical access points to Physical Security Perimeters (PSPs), including the protections required for the PACS assets, failed to address the following protective measures as required by CIP-006-1 R1.8: 1) SERC_URE1 failed to document the enabled ports and services required for operations and monitoring of Cyber Assets within the ESP, as described in CIP-005 R2.2; 2) SERC_URE1 permitted external interactive access to the PACS without authentication, thereby failing to demonstrate strong procedural or technical controls to ensure authenticity of the accessing party at access points, as described in CIP-005 R2.4; 3) SERC_URE1 failed to log authorized traffic through its firewall to the PACS, as described in CIP-005 R3; 4) SERC_URE1 failed to document test results for significant changes to the PACS to ensure the changes did not adversely affect existing cybersecurity controls, as described in CIP-007 R1.3; 5) Despite providing evidence that a third-party vendor tested anti-virus and malware prevention signatures for the PACS, SERC_URE1 failed to document a process for such testing, as described in CIP-007 R3.1; and 6) SERC_URE1 failed to document a backup and recovery process for its physical access control panels, as described in CIP-009 R4. | CIP-006-1 | R1 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). SERC determined that the violation posed a moderate risk because SERC_URE1's failure to afford PACS devices and logging systems the measures listed in CIP-006-1 R1.8, could have made those devices more easily compromised, allowing malicious access to Cyber Assets within the PSP to go unnoticed and unchecked. Such access may then be used to cause harm to CCAs essential to the operation of the BPS. Failure to test significant changes made to PACS devices allowed undocumented changes to be implemented, altering, and possibly weakening, the existing cybersecurity controls and making SERC_URE1 more vulnerable to physical intrusion. SERC_URE1's failure to timely assess 19 security patches on seven different PACS assets left those Cyber Assets vulnerable for extended periods of time, increasing the risk of a successful cyber intrusion. However, SERC_URE1's PACS assets were deployed within a secured ESP and PSP and there was no electronic access to PACS assets from outside their isolated ESP, significantly decreasing the risk of a successful cyber intrusion. Although the PSP access points did not log authorized traffic, as described in CIP-005 R3, the access points would log unauthorized access attempts; however, no unauthorized access attempts occurred during this period. | when the Standard became mandatory and enforceable on SERC_URE1 | Mitigation Plan completion | $70,000 (for SERC201000442, SERC2011006644, SERC2011006645, SERC2011006646, SERC2011006647, SERC2011007279, SERC2011008318, SERC2011008319, SERC2011008320, SERC2011009000, SERC2011009003, SERC2011009004, SERC2011009005, SERC2011009006, SERC2011009007, SERC2011009008, SERC2011009009, and SERC2013012823) | Self-Report | To mitigate this violation, SERC_URE1: 1) established an operations security patch coordinator position; 2) modified the existing SERC_URE1 system security plan to reflect the assignment of a security patch coordinator, the increase in internal compliance monitoring, and the modifications to the documentation processes; 3) provided additional guidance and directions to the system administrators by expanding the Security Patch Management section of the SERC_URE1 plan to include step-by-step processes in the following areas: a) obtaining security patches from each vendor; b) assessing patches and documenting the assessment on each system.; c) implementation and documentation of compensating measures if a patch cannot be applied; d) testing and documentation of security patches on each system; e) installing and documenting the application of patches to the production environment on each system; and f) routine internal confirmation that security patches have been assessed and applied to each system; 4) conducted additional security patch process training session with system administrators; 5) validated the improved process through internal auditing; and 6) confirmed compliance with patch management policies, guidelines, and procedures (PGPs) that: a) the operations' security patch coordinator collects evidence on one-third of the systems each month; b) the operations security patch coordinator verifies monthly evidence meets the requirements of SERC_URE1's PGPs and supplies this evidence to Critical Infrastructure Compliance; and c) Critical Infrastructure Compliance conducts an independent confirmation of compliance. | 2012-12-21 | TBD | Admits | SERC reviewed SERC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2011006644 | Settlement Agreement | SERC_URE1 submitted a Self-Report stating that it was in violation of CIP-005-1 R2.2 because it failed to ensure that only ports and services required for operations and for monitoring Cyber Assets within the Electronic Security Perimeter (ESP) were enabled. SERC learned that one electronic access control and monitoring system (EACMS), a firewall, serving as an electronic access point to a SERC_URE1 ESP, had undocumented ports and services enabled that were not required for operations or monitoring of Cyber Assets within the ESP. SERC_URE1 acknowledged that two firewall rules allowed unnecessary network traffic. The first rule allowed unrestricted access from SERC_URE1's internal protected network segments to the CIP protected network segment on ports that were not required for operations or for monitoring of Cyber Assets within the ESP. As a result, 66.67% of SERC_URE1's Critical Cyber Assets were potentially accessible. The second rule allowed access from SERC_URE1's CIP protected network segment to unrestricted destinations on ports not required for operations or for monitoring of Cyber Assets within the ESP. | CIP-005-1 | R2; R2.2 | Medium | Severe | This violation posed a moderate risk and not a serious or substantial risk to the reliability of the bulk power system (BPS). SERC determined that the violation posed a moderate risk because the failure to restrict ports and services at access points to only those required for operations could increase the attack surface into the ESP and result in access out of the ESP to low-trust assets that could be leveraged or compromised. In addition, SERC_URE1's failure to implement restrictive rules for inbound and outbound traffic could result in internal compromise or vulnerabilities that propagate between the CIP and non-CIP networks without restriction. However, the risk to the BPS was mitigated because SERC_URE1's vendor was monitoring SERC_URE1's ESP and would have alerted SERC_URE1 of any unauthorized attempts or access to its ESP. The EACMS assets were located within a Physical Security Perimeter and thus afforded physical access controls. Finally, no unauthorized attempts were detected during the violation period. | when the Standard became mandatory and enforceable on SERC_URE1 | Mitigation Plan completion | $70,000 (for SERC201000442, SERC2011006644, SERC2011006645, SERC2011006646, SERC2011006647, SERC2011007279, SERC2011008318, SERC2011008319, SERC2011008320, SERC2011009000, SERC2011009003, SERC2011009004, SERC2011009005, SERC2011009006, SERC2011009007, SERC2011009008, SERC2011009009, and SERC2013012823) | Self-Report | To mitigate this issue, SERC_URE1: 1) documented the authorized ports/services configuration (baseline); 2) closed all ports not currently in use; 3) conducted a new vulnerability assessment; and 4) updated change control training to include assessment of the ports and services, default accounts, and malware instructions for capturing before and after screen shots. | 2012-04-03 | TBD | Admits | SERC reviewed SERC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2011006645 | Settlement Agreement | SERC_URE1 submitted a Self-Report to SERC stating that it was in violation of CIP-007-1 R2 because it failed to establish and document a process to ensure that only those ports and services required for normal and emergency operations are enabled. SERC_URE1 reported that it conducted its annual Cyber Vulnerability Assessment (CVA) and discovered that ports and services were enabled on 31 servers that SERC_URE1 could not show were required for operations out of 397 total Cyber Assets. Specifically, SERC_URE1 did not have documentation stating the enabled ports and services were required for normal and/or emergency operations. | CIP-007-1 | R2; R2.1: R2.2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failure to disable ports and services that were not required for normal or emergency operations could allow unauthorized individuals or malware to exploit these ports and thereby disrupt operations or gain unauthorized access to or control of Critical Cyber Assets (CCAs). However, the servers are protected by two levels of firewalls that prevent the enabled services from being accessed by an outside entity, and services have been disabled where SERC_URE1 could confirm that it was safe to do so. SERC_URE1 made an affirmative decision to allow the ports and services in question to remain open in an effort to ensure the continued functionality of its servers. Where technically feasible, all Cyber Assets within the Electronic Security Perimeter(s) were running malware protection. | when the Standard became mandatory and enforceable on SERC_URE1 | Mitigation Plan completion | $70,000 (for SERC201000442, SERC2011006644, SERC2011006645, SERC2011006646, SERC2011006647, SERC2011007279, SERC2011008318, SERC2011008319, SERC2011008320, SERC2011009000, SERC2011009003, SERC2011009004, SERC2011009005, SERC2011009006, SERC2011009007, SERC2011009008, SERC2011009009, and SERC2013012823) | Self-Report | To mitigate this issue, SERC_URE1: 1) filed a technical feasibility exception for 47 servers; 2) documented an authorized ports/services list (baseline); and 3) completed a vulnerability assessment that included a scan of firewalls and a comparison to the authorized ports and services list (baseline). | 2012-12-28 | TBD | Admits | SERC reviewed SERC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2011006646 | Settlement Agreement | SERC_URE1 submitted a Self-Report to SERC stating that it was in violation of CIP-007-1 R8.3 because it failed to perform a review of the controls for default accounts during its annual Cyber Vulnerability Assessment (CVA). Upon reviewing the results from the CVA SERC_URE1 discovered that it failed to perform a review of controls on default accounts and passwords, as required by CIP-007-1 R8.3. SERC reviewed documentation for default accounts and evidence demonstrating that the accounts were quarterly reviewed. SERC_URE1 also provided evidence demonstrating its use of password controls software, as well as change management tickets, illustrating that the default account passwords were required to be changed annually. In addition, SERC_URE1's policy implementing CIP-007 R5.2 required the proper handling, review, and management of default accounts, including the requirements for password controls. Despite the presence of these controls, SERC_URE1 failed to review these controls as part of its annual CVA. SERC learned that this violation involved nine default accounts enabled on SERC_URE1's Cyber Assets. | CIP-007-1 | R8; R8.3 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC_URE1 documented its default account controls in established policies. SERC_URE1 performed quarterly reviews of the default accounts themselves, but it failed to include a review of its controls for those accounts as part of its annual CVA. The devices in question are protected by multiple levels of security, including corporate firewalls, intrusion detection systems, and cybersecurity monitoring software with twenty-four hour a day, seven days a week off-site monitoring and alerting. | when the Standard became mandatory and enforceable on SERC_URE1 | when a comprehensive CVA was conducted, which included reviewing controls for default accounts | $70,000 (for SERC201000442, SERC2011006644, SERC2011006645, SERC2011006646, SERC2011006647, SERC2011007279, SERC2011008318, SERC2011008319, SERC2011008320, SERC2011009000, SERC2011009003, SERC2011009004, SERC2011009005, SERC2011009006, SERC2011009007, SERC2011009008, SERC2011009009, and SERC2013012823) | Self-Report | To mitigate this issue, SERC_URE1: 1) conducted a review of controls for default accounts; 2) conducted a comprehensive CVA; and 3) provided awareness on the CVA process to the appropriate personnel. | 2012-04-12 | TBD | Admits | SERC reviewed SERC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2011006647 | Settlement Agreement | SERC_URE1 submitted a Self-Report stating that it had a violation of CIP-005-1 R4 because it failed to perform annual Cyber Vulnerability Assessments (CVAs) that discovered all access points to Electronic Security Perimeters (ESPs) and the completed CVAs were otherwise not adequate. SERC_URE1 discovered that its CVA did not meet the requirements of CIP-005-1 R4, while reviewing its firewall access control rules in conjunction with a prior Self-Report. The CVA failed to verify that only ports and services required for operations were enabled, as required by CIP-005-1 R4.2. The CVA also failed to include a comprehensive list of all SERC_URE1 ESP access points, and the CVA was not performed on all access points, as required by CIP-005-1 R4.3. Finally, the CVA failed to document a review of controls for default accounts, passwords, and network management community strings, as required by CIP-005-1 R4.4. SERC learned that the unidentified access points were utilized to isolate SERC_URE1's assets from the substation communication network, and were deployed on a dedicated leased communication circuit with no public accessibility. The CVA report addressed the discovery of access points to the ESP, generally. However, this report failed to include the discovery of the access points in question. | CIP-005-1 | R4; R4.2; R4.3; R4.4; R4.5 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC determined that the violation posed a moderate risk because SERC_URE1's failure to identify and protect open ports and services, access points to its ESPs, and shared passwords, could have made SERC_URE1 more vulnerable to a cyber attack. However, SERC_URE1 utilized a network intrusion detection system to analyze network traffic for known and suspect malicious activity. SERC_URE1's Cyber Assets were located within a Physical Security Perimeter and thus afforded physical access controls. In addition, SERC_URE1's vendor was monitoring electronic access to SERC_URE1's ESP and would have alerted SERC_URE1 of any unauthorized attempts to access to its ESP during the time of the violation. Finally, SERC_URE1 reported no unauthorized access attempts to the ESP during the time of the violation. | when the Standard became mandatory and enforceable on SERC_URE1 | Mitigation Plan completion | $70,000 (for SERC201000442, SERC2011006644, SERC2011006645, SERC2011006646, SERC2011006647, SERC2011007279, SERC2011008318, SERC2011008319, SERC2011008320, SERC2011009000, SERC2011009003, SERC2011009004, SERC2011009005, SERC2011009006, SERC2011009007, SERC2011009008, SERC2011009009, and SERC2013012823) | Self-Report | To mitigate this issue, SERC_URE1: 1) issued detailed request for proposal to include all requirements of the CIP Standards; and 2) performed a new and more comprehensive CVA. To prevent reoccurrence, SERC_URE1 held a meeting to review the vulnerability assessment report in preparation for the next year's vulnerability assessment. | 2012-04-12 | TBD | Admits | SERC reviewed SERC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2011007279 | Settlement Agreement | SERC_URE1 submitted a Self-Report stating that it was in violation of CIP-005-1 R1.5 because it failed to afford all the required protective measures to Cyber Assets used in the electronic access control and monitoring (EACM) of the Electronic Security Perimeter (ESP). SERC_URE1 submitted a second Self-Report stating that it was in violation of CIP-005-2 R5.3 because it failed to maintain electronic access logs for one Cyber Asset used as an EACM device, as required. SERC determined that these facts actually constituted a violation of CIP-005-1 R1.5 and, therefore, consolidated the two Self-Reports into a single violation. SERC sent SERC_URE1 an initial notice of a Compliance Audit. During this Compliance Audit, SERC discovered that SERC_URE1 failed to identify and document two EACM devices and their associated access points to SERC_URE1's ESP. As a consequence, the devices were not afforded the protective measures specified in CIP-005-1 R1.5. As to the first issue, the EACM device at issue was a firewall that protected a network segment containing 40 Critical Cyber Assets. While performing an internal review of its access lists, SERC_URE1 discovered an unapproved administrative account on this device. This account was created without adherence to SERC_URE1's change control and configuration management process, as described in CIP-003-1 R6. Therefore, the use and privileges of the account were not managed in accordance with CIP-007-1 R5, despite SERC_URE1's documented procedures requiring such. Additionally, SERC_URE1 assigned a generic password to the administrative account that did not meet the complexity requirements described in CIP-007-1 R5.3. SERC_URE1 also failed to ensure that it changed this password at least annually, also as described in CIP-007-1 R5.3. As to the second issue, SERC_URE1 discovered that the electronic access logs for one EACM device were not retained. SERC_URE1 determined that it misconfigured a Cyber Asset thus preventing the logs from reaching the centralized log server. As a result of this misconfiguration, SERC_URE1 could not provide evidence that its documented processes for monitoring and logging access at the EACM were implemented twenty-four hours a day, seven days a week. Although, SERC_URE1 initially reported this issue as a violation of CIP-005-2 R5.3, SERC determined that it was in fact a violation of CIP-005-1 R1.5 because SERC_URE1 failed to maintain access logs for an EACM device, as described in CIP-007-1 R5.1.2. As to third issue, SERC determined that SERC_URE1 was in violation of CIP-005-1 R1.5 because it failed to identify and document two EACM devices as access points to its ESP and afford the EACM devices the protective measures specified in CIP-005-1 R1.5. Specifically, SERC_URE1 failed to: 1) document test results of significant changes to EACM devices within its ESP, as described in CIP-007-1 R1.3; 2) document assessments of cybersecurity patches for Cyber Assets within its ESP, as described in CIP-007-1 R3.1; 3) ensure that only ports and services required for operations and monitoring of Cyber Assets within the ESP were enabled, as described in CIP-005-1 R2.2; and 4) implement strong procedural or technical controls at the access points to the ESP to ensure authenticity of the accessing party, despite a requirement to do so in its CIP Cyber Security Policy, as described in CIP-005-1 R2.4. SERC_URE1's failure to ensure that only required ports and services were open included a failure to provide documentation detailing the business need for its open source and destination ports and services at access points. SERC_URE1 also allowed traffic from any source to an excessive number of ports on its EACM devices. SERC learned that SERC_URE1 utilized an off-site third-party vendor to monitor logs and provide alerts for the access points. SERC_URE1, however, failed to identify and document the third-party EACM devices. In addition, SERC_URE1 could not produce evidence that the assets were being afforded the protection of CIP-005-1 R1.5, as required. | CIP-005-1 | R1; R1.5 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC determined that the violation posed a moderate risk because failing to identify and protect electronic access points associated with EACM devices and the devices themselves presented a risk of unauthorized access to SERC_URE1's ESP. However, the administrative account was known only to a SERC_URE1's maintenance group, consisting of just two individuals. To access the administrative account, a user would have had to have authorized physical access to SERC_URE1's Physical Security Perimeter (PSP). SERC_URE1 used a network intrusion detection system to analyze network traffic for known and suspect malicious activity. All the EACM devices at issue were located within a PSP and thus afforded physical access controls. SERC_URE1's vendor was monitoring SERC_URE1's ESP and would have alerted SERC_URE1 of any unauthorized attempts or access to its ESP. Finally, SERC_URE1 attested that there were no security alerts or cyber attacks during the violation duration. | when the Standard became mandatory and enforceable on SERC_URE1 | Mitigation Plan completion | $70,000 (for SERC201000442, SERC2011006644, SERC2011006645, SERC2011006646, SERC2011006647, SERC2011007279, SERC2011008318, SERC2011008319, SERC2011008320, SERC2011009000, SERC2011009003, SERC2011009004, SERC2011009005, SERC2011009006, SERC2011009007, SERC2011009008, SERC2011009009, and SERC2013012823) | Self-Report | To mitigate this issue, SERC_URE1: 1) changed the password in question; 2) disabled the account; 3) enhanced the change control training to include: a) appropriate security questions are documented including the assessment of the ports and services to be opened, default accounts and malware; and b) instructions for capturing before and after screen shots; 4) documented a new process to properly identify and categorized EACM assets; 5) installed Cyber Assets used in the access control and/or monitoring of the ESP in order to setup authentication at the access points for Cyber Assets within the ESP. 6) set up an in-house solution for monitoring and alerting of its CIP-protected Cyber Assets. All devices related to this solution are properly classified; 7) retired devices identified during the Audit from service due to the cutover of the new energy management system; 8) established a checklist to ensure that only ports and services needed for operations and monitoring are enabled; 9) established technical controls to ensure authenticity of all accessing parties by implementing two factor authentications for external interactive access. 10) corrected the misconfiguration by changing the Secure Shell settings to allow the network device logs to reach the log archiving server and configured an additional log server for redundancy; and 11) established a system in which a confirmation is made on a monthly basis that all CIP-protected Cyber Assets are actively sending logs to the logging server via SERC_URE1's monthly compliance report. | 2013-09-17 | TBD | Admits | SERC reviewed SERC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2011008318 | Settlement Agreement | SERC sent SERC_URE1 an initial notice of a Compliance Audit. SERC_URE1 submitted a Self-Report to SERC stating that it was in violation of CIP-007-3a R5.1 because it failed to implement a user account as approved. SERC_URE1 reported that it created a user account on a Critical Cyber Asset (CCA) for an employee who had not been authorized for electronic access to that CCA. According to SERC_URE1, the individual was authorized for electronic access to a server, classified as a CCA, within an Electronic Security Perimeter (ESP). The ESP at issue contained three CCAs: two servers and a network switch. Despite only being authorized for one of the servers, SERC_URE1 granted the individual access to two both servers. SERC_URE1 determined that the servers at issue are utilized as repositories for CCA information, specifically, Remote Terminal Unit (RTU) configuration information and relay settings and maintenance records. Therefore, SERC_URE1 determined that they were improperly classified as CCAs and subsequently removed them from its list of CCAs. SERC_URE1 discovered this unauthorized user account during a quarterly review of user account access privileges. | CIP-007-3a | R5; R5.1 | Medium | Severe | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The individual had a completed personnel risk assessment and cybersecurity training. The account was created on the asset but the credentials were never distributed to the individual. The individual was not authorized or granted physical access to the Physical Security Perimeter in which these assets resided. The individual had electronic access to other CCAs within the ESP. | when the user account was added | when the user account was removed from the CCA | $70,000 (for SERC201000442, SERC2011006644, SERC2011006645, SERC2011006646, SERC2011006647, SERC2011007279, SERC2011008318, SERC2011008319, SERC2011008320, SERC2011009000, SERC2011009003, SERC2011009004, SERC2011009005, SERC2011009006, SERC2011009007, SERC2011009008, SERC2011009009, and SERC2013012823) | Self-Report | To mitigate this issue, SERC_URE1: 1) clarified the existing procedure with more detailed steps on how to properly grant access to CIP-protected Cyber Assets; 2) provided appropriate personnel with additional training; and 3) removed the individual's account from the second CCA after a quarterly review of access rights determined the individual had not been approved for access to that device. | 2012-09-28 | TBD | Admits | SERC reviewed SERC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2011008319 | Settlement Agreement | SERC sent SERC_URE1 an initial notice of a Compliance Audit. SERC_URE1 submitted a Self-Report that it was in violation of CIP-005-1 R2.5 because it failed to document all authentication methods used for interactive access into the Electronic Security Perimeter (ESP). SERC_URE1 reported that it utilized three different authentication methods for accessing Critical Cyber Assets (CCAs) through its ESP. SERC_URE1, however, failed to identify and describe two of the methods in the required documentation. SERC_URE1 stated that the documentation addressed only the primary authentication method and omitted the two alternate approaches that were used less frequently. SERC reviewed SERC_URE1's Electronic Security Program documentation and determined that it failed to adequately detail the authentication methods employed at the electronic access points to the ESP. SERC_URE1's program required that at least two authentication methods be used simultaneously when accessing the ESP. However, it did not describe all the authentication methods deployed, as required by CIP-005-1 R2.5. Specifically, SERC learned that SERC_URE1 utilized three methods of authentication for accessing the ESP: 1) A CIP compliant user name and password; 2) two factor authentication utilizing a secure token; and 3) internet protocol (IP) restricted source and destination addressing. SERC_URE1 documented only the first authentication method. SERC also determined that the third authentication method, utilizing IP restricted source and destination addressing, did not sufficiently ensure the authenticity of the individual accessing the ESP. As a result, SERC determined that this method did not constitute a strong procedural or technical control at an access point to the ESP to ensure authenticity of the accessing party, as required by CIP-005-1 R2.4. SERC learned SERC_URE1 used the third authentication method to allow control room operators to update deployed remote terminal units (RTU) from a workstation within the Physical Security Perimeter (PSP), but not an ESP. The operators would authenticate to access the workstation, and then use the workstation to access an identified CCA within an ESP to update the RTUs. The operators, however, did not authenticate at the ESP access point. | CIP-005-1 | R2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although SERC_URE1 only described one authentication method in its required documentation, it represented to SERC that it was using multiple methods, thereby restricting access to its ESPs. The workstation used to update RTUs was located within the PSP where only authorized personnel with completed personnel risk assessments and cybersecurity training had access. Although SERC_URE1 was utilizing IP restricted source and destination addresses to restrict access, this authentication method was limited to a single workstation with a static IP address and a firewall that limited its access. | when the Standard became mandatory and enforceable on SERC_URE1 | Mitigation Plan completion | $70,000 (for SERC201000442, SERC2011006644, SERC2011006645, SERC2011006646, SERC2011006647, SERC2011007279, SERC2011008318, SERC2011008319, SERC2011008320, SERC2011009000, SERC2011009003, SERC2011009004, SERC2011009005, SERC2011009006, SERC2011009007, SERC2011009008, SERC2011009009, and SERC2013012823) | Self-Report | To mitigate this issue, SERC_URE1: 1) enhanced documentation to describe all methods used to authenticate users into the ESP and maintain list of methods used for authentication; and 2) created an on-boarding checklist to determine if Cyber Assets being added to the CIP environment introduce a new authentication method. | 2012-12-10 | TBD | Admits | SERC reviewed SERC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2011008320 | Settlement Agreement | SERC sent SERC_URE1 an initial notice of a Compliance Audit. SERC_URE1 submitted a Self-Report stating that it was in violation of CIP-004-3 R4 because it failed to remove physical access to Critical Cyber Assets (CCAs) within seven calendar days of personnel no longer requiring access. While SERC was performing its assessment and determining the scope of the violation, the following additional issues were found: 1) SERC_URE1 self-reported three non-related instances where it failed to follow documented policies and procedures to control physical and electronic access to CCAs. First, an individual was granted access to a Physical Security Perimeter (PSP) prior to being approved for such access. Second, an individual was authorized access to one PSP; however, the individual was granted access to a different PSP which had not been approved. Finally, an individual was granted electronic access to an Electronic Security Perimeter (ESP) prior to approval; 2) the SERC audit team reported that SERC_URE1 was in violation of CIP-004-3 R4.2 because it did not revoke a contractor’s authorized cyber access rights to CCAs within seven calendar days after such access was no longer required. As to the issue disclosed in the first Self-Report, during its second quarter access list review, SERC_URE1 discovered that a temporary employee who was on a leave of absence maintained unescorted physical access to two Physical Security Perimeters (PSPs). The temporary employee's leave of absence was due to the individual returning to coursework and was not for cause. SERC_URE1 revoked the temporary employee' access. The individual returned to work at SERC_URE1 approximately two months later, and SERC_URE1 reauthorized the temporary employee's access privileges and reinstated them two days later. SERC_URE1's access policies in place at the time of the violation did not address leaves of absence or access revocation during leaves of absence. The temporary employee had been granted authorized unescorted physical access to two PSPs, a transmission room and an office area, and was authorized to have unescorted physical access to another two PSPs. The temporary employee' had no electronic access to any CCAs. Although SERC_URE1 discovered this issue, SERC_URE1 did not report it until approximately a year and four months later because the individual who originally discovered it was not aware of the compliance implications of a failure to revoke access within seven calendar days of an individual no longer requiring such access. The three issues disclosed in the second Self-Report, and subsequent investigation, are described below: 1) SERC_URE1 contracted with a temporary employee to serve as a system administrator for the data historian application on non-critical Cyber Assets within the server room PSP. SERC_URE1 required completion and approval of a Bulk Electric System Cyber Authorized (BESCA) request form prior to granting access to PSPs. In this case, SERC_URE1 inadvertently left one server room, related to the energy control and metering systems (ECMS), off the BESCA request form. Knowing that this temporary employee would need access to the ECMS server room, SERC_URE1 granted the individual access to this server room. SERC_URE1 discovered this unauthorized access during a quarterly review of its access lists and revoked it; 2) SERC_URE1 initially granted an individual authorized unescorted physical access to the transmission room PSP. The individual required a badge replacement, which required SERC_URE1 to re-activate the badge for CIP-related access privileges. SERC_URE1 failed to re-activate the individual’s badge, and the individual was denied access to a PSP to which access had previously been authorized. Upon this denial, the individual contacted SERC_URE1's CIP access administrator requesting that access be reinstated. In response to this request, SERC_URE1 inadvertently granted the individual access to a PSP for which the individual lacked authorization. During a quarterly access list review SERC_URE1 discovered the error and revoked the access. SERC_URE1 staff verified through access log review that the individual did not access the unauthorized PSP. The PSP to which the individual was inadvertently granted access contained no CCAs; and 3) SERC_URE1 created an account granting electronic access to one access point to the SERC_URE1 ESP prior to the individual in question being approved for such an account. A SERC_URE1 administrator created the account prior to receiving the necessary approvals, knowing that the account would be needed in the near future. SERC_URE1, however, never shared the account username and password with the user, effectively limiting the possibility of unauthorized access. Upon discovering that the account had been created without the proper authorization, SERC_URE1 disabled the account and verified that it had never been used. SERC_URE1 created the account to allow access to a firewall, thereby enabling access to an ESP but not the CCAs protected by that ESP. The relevant ESP contained two CCAs. SERC_URE1 discovered this issue during a quarterly access list review and disabled the account approximately a month and a half later. As to the issue discovered during the Compliance Audit, SERC_URE1 owns and maintains two servers classified as CCAs which are also utilized by an affiliated entity. SERC_URE1 is the entity responsible for ensuring that the two servers are protected in accordance with the CIP Standards. The affiliated entity contracted with a vendor to provide technical support for an application running on one of these CCAs. One of the vendor’s employees that had provided technical support voluntarily terminated the employment relationship with the vendor. The contractor sent a package to the affiliated entity informing the affiliated entity of the need to revoke this employee’s access, including in the package the virtual private network (VPN) token that enabled remote cyber access to SERC_URE1's CCAs. The affiliated entity received this package six days after the contractor sent the package. The affiliated entity notified SERC_URE1 of the vendor employee’s termination, and SERC_URE1 revoked this individual’s access to the CCA within 24 hours of notification. However, SERC_URE1 failed to revoke the individual’s access within seven calendar days of that individual no longer requiring such access. | CIP-004-3 | R4; R4.2 | Lower | Lower | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC_URE1 conducted personnel risk assessments on the individuals in question and ensured that they had received cybersecurity training prior to granting them access to CCAs. The temporary employee described in the first Self-Report was not authorized nor granted electronic access to any CCAs, SERC_URE1 revoked physical access approximately four weeks after the start of the leave of absence, and SERC_URE1 reinstated access privileges upon the individual’s return. As to the first issue from second Self-Report, the individual in question had no access to CCAs. As to the second issue from the second Self-Report, the individual’s unauthorized access granted access to a PSP in a basement hallway that did not contain any CCAs. As to the third issue from the second Self-Report, SERC_URE1 never distributed the improperly created account information, and the account did not grant access to CCAs. As to the issue discovered during the Compliance Audit, the vendor maintained its relationship with SERC_URE1 after the vendor employee terminated employment with the vendor, indicating a trusted relationship between SERC_URE1 and the vendor. SERC_URE1 identified and promptly remedied these issues through its quarterly review of its access lists, indicating the presence and efficacy of SERC_URE1's internal controls. | seven days following the start of the leave of absence for the first instance of non-compliance | when access was revoked | $70,000 (for SERC201000442, SERC2011006644, SERC2011006645, SERC2011006646, SERC2011006647, SERC2011007279, SERC2011008318, SERC2011008319, SERC2011008320, SERC2011009000, SERC2011009003, SERC2011009004, SERC2011009005, SERC2011009006, SERC2011009007, SERC2011009008, SERC2011009009, and SERC2013012823) | Self-Report | To mitigate this issue, SERC_URE1: 1) clarified the existing procedure with more detailed steps on how to properly grant access to CIP-protected Cyber Assets; 2) provided the revised Security Requirements Certification Agreement to the vendor and contract agencies for their review and signatures; and 3) provided appropriate personnel with additional training. | 2012-11-07 | TBD | Admits | SERC reviewed SERC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. SERC_URE1 did not complete the mitigation plan for this violation on time and SERC considered this an aggravating factor when determining the penalty.
SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2011009000 | Settlement Agreement | SERC sent SERC_URE1 an initial notice of a Compliance Audit. The SERC audit team reported that SERC_URE1 was in violation of CIP-005-1 R3 because it failed to provide evidence that it implemented security monitoring processes to detect and alert for actual unauthorized access into its Electronic Security Perimeters (ESP). SERC learned that SERC_URE1 failed to implement security monitoring processes to detect and alert for actual unauthorized access into one of its ESP access points. SERC reviewed SERC_URE1's electronic security program policy and found that it detailed the requirement to detect and alert for unauthorized access, or attempts at such access. However, SERC_URE1 failed to implement the policy on the identified electronic access point. As part of this failure, SERC_URE1 failed to log traffic that is permitted through its firewall that would be needed to detect and alert on actual unauthorized accesses. The access logs would have been needed to investigate and identify, through automated or manual reviews, successful unauthorized access into the ESP. | CIP-005-1 | R3 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC determined that the violation posed a moderate risk because a violation of CIP-005-1 R3 presents a risk of unauthorized access and exploitable vulnerabilities to Critical Cyber Assets (CCAs) and/or other Cyber Assets located within the ESP. SERC_URE1, however, was logging denied traffic at access points to the ESP during the time of the violation. SERC_URE1 also utilized a network intrusion detection system to analyze network traffic for known and suspected malicious activity. SERC_URE1's vendor was monitoring electronic access to SERC_URE1's ESP and would have alerted SERC_URE1 of any unauthorized attempts and/or access to its ESP. SERC_URE1 attested that there were no security alerts or cyber attacks during the violation duration. | when the Standard became mandatory and enforceable on SERC_URE1 | Mitigation Plan completion | $70,000 (for SERC201000442, SERC2011006644, SERC2011006645, SERC2011006646, SERC2011006647, SERC2011007279, SERC2011008318, SERC2011008319, SERC2011008320, SERC2011009000, SERC2011009003, SERC2011009004, SERC2011009005, SERC2011009006, SERC2011009007, SERC2011009008, SERC2011009009, and SERC2013012823) | Compliance Audit | To mitigate this issue, SERC_URE1: 1) retired router when the new energy management system was upgraded with replacement of hardware and software; 2) verified logging was configured correctly; and 3) developed an on-boarding checklist to be completed prior to placing an asset into production environment. | 2012-11-29 | TBD | Admits | SERC reviewed SERC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2011009003 | Settlement Agreement | SERC sent SERC_URE1 an initial notice of a Compliance Audit. The SERC audit team reported that SERC_URE1 was in violation of CIP-006-1 R3 because SERC_URE1's documented and implemented technical and procedural controls for monitoring physical access to its Physical Security Perimeters (PSPs) did not require monitoring twenty-four hours a day, seven days a week, and SERC_URE1 was unable to provide evidence to demonstrate that all unauthorized access attempts to the PSPs were reviewed immediately and handled in accordance with CIP-008. SERC_URE1 utilized a physical access control system (PACS) for access control and monitoring at its primary control center (PCC) and backup control center (BCC). The two facilities housed separate PSPs and were subject to the CIP requirements and the SERC_URE1 physical security plan. Pursuant to this plan, from 6:00 a.m. through 6:00 p.m., seven days a week, SERC_URE1 had dedicated security operators who monitored security consoles at workstations at both the PCC and the BCC. Any unauthorized access attempts to either PSP facility would have triggered an audible alarm by the PACS, which was also displayed at the security console within the affected control center. The security operators were then able to provide an immediate response and investigate any unauthorized access attempts to the PSPs. Outside of these hours, however, the security workstations were not continuously manned, and therefore SERC_URE1 system operators relied upon audible alarms to initiate an immediate response to investigate an unauthorized access attempt. SERC learned that the audible alarm was muted when a forced or held open door was closed, meaning that the system operators did not need to immediately investigate the alarm in order to silence it. Consequently, an unauthorized access attempt to a PSP could go undetected by the on-duty system operator. In addition, the logs of alarms occurring outside of 6:00 a.m. through 6:00 p.m. were distributed via email for management review the following day, further preventing SERC_URE1 from investigating unauthorized access attempts immediately. | CIP-006-1 | R3 | Medium | Severe | This violation posed a moderate risk and not a serious or substantial risk to the reliability of the bulk power system. SERC determined that the violation posed a moderate risk because failure to continuously monitor all access points to the PSPs twenty-four hours a day, seven days a week, presented a risk of unauthorized access and exploitable vulnerabilities to CCAs. SERC_URE1, however, had implemented exterior and interior access controls to reduce the risk of unauthorized access to its two PSP facilities, including video surveillance, security officers, and electronic badge access controls. Additionally, to access the PCC, all individuals were required to pass through an electronically controlled gate. Furthermore, SERC_URE1 would have monitored for and immediately responded to alarms by its PACS occurring from 6:00 a.m. through 6:00 p.m., seven days a week. Finally, there were no security issues regarding SERC_URE1's PSPs for the duration of the violation. | when the Standard became mandatory and enforceable on SERC_URE1 | Mitigation Plan completion | $70,000 (for SERC201000442, SERC2011006644, SERC2011006645, SERC2011006646, SERC2011006647, SERC2011007279, SERC2011008318, SERC2011008319, SERC2011008320, SERC2011009000, SERC2011009003, SERC2011009004, SERC2011009005, SERC2011009006, SERC2011009007, SERC2011009008, SERC2011009009, and SERC2013012823) | Compliance Audit | To mitigate this issue, SERC_URE1: 1) identified and implemented technical and procedural controls at all access points to the PSP twenty-four hours per day, seven days per week. The action items taken to accomplish this include: a) created a detailed step-by-step procedure to address technical and procedural controls for monitoring physical access at all access points to the PSP twenty-four hours per day, seven days per week; b) prepared a CIP Compliant area; c) hired security personnel; d) trained security personnel; e) established monitoring twenty-four hours per day, seven days per week; and f) assessed evidence to determine if compliance to the standards and procedures have been achieved. | 2012-12-15 | TBD | Admits | SERC reviewed SERC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2011009004 | Settlement Agreement | SERC sent SERC_URE1 an initial notice of a Compliance Audit. The SERC audit team reported that SERC_URE1 was in violation of CIP-006-1 R6 because it failed to implement a maintenance and testing program to ensure that all physical security systems under requirements CIP-006-1 R2, R3, and R4 function properly. The SERC audit team found that SERC_URE1 failed to document or implement a maintenance and testing program on its physical security systems. SERC_URE1 demonstrated evidence that it performed limited testing of select doors, but it failed to provide evidence for all physical security systems. In addition, SERC_URE1 did not provide evidence that it performed testing of the physical security mechanisms on a cycle no longer than three years, as required by CIP-006-1 R6.1. SERC reviewed SERC_URE1's CIP Cyber Security Policy, which required that all physical access controls, monitoring, and logging equipment be tested and maintained at least every three years, and the logs of the testing kept until the next test. SERC also analyzed SERC_URE1's CIP Physical Security Plan, which required that maintenance and testing be performed every three years, and that documentation of maintenance and testing be maintained by the supervisor of CIP compliance, or a designee. SERC_URE1 provided a change management ticket demonstrating that limited testing was completed. Despite SERC_URE1's policies requiring it to maintain documentation of testing, SERC_URE1 failed to maintain this documentation. | CIP-006-1 | R6 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). SERC determined that the violation posed a moderate risk because the failure to implement a maintenance and testing program of the physical security systems could allow a degradation of the security mechanisms that provide access control, monitoring, and logging of access points to the Physical Security Perimeter. Failure to identify possible deficiencies in the physical security systems could allow unauthorized or unmonitored access to Critical Cyber Assets which could impact SERC_URE1's ability to monitor and control the BPS. However, SERC_URE1 did show evidence of a limited test of select doors during the audit period that demonstrated some functionality but did not meet the requirements of CIP-006-1 R6. The audit team performed a functional test of physical security mechanisms associated with all access points during its PSP sampling and found that all security mechanisms under requirements CIP-006-1 R2, R3 and R4 were functioning properly. | when the Standard became mandatory and enforceable on SERC_URE1 | Mitigation Plan Completion | $70,000 (for SERC201000442, SERC2011006644, SERC2011006645, SERC2011006646, SERC2011006647, SERC2011007279, SERC2011008318, SERC2011008319, SERC2011008320, SERC2011009000, SERC2011009003, SERC2011009004, SERC2011009005, SERC2011009006, SERC2011009007, SERC2011009008, SERC2011009009, and SERC2013012823) | Compliance Audit | To mitigate this issue, SERC_URE1: 1) expand its physical security testing plan to include all access control and monitoring devices that collectively control and monitor physical security to SERC_URE1's CIP restricted areas; 2) created an updated checklist to identify the devices, locations, and the functionality of all physical access control and monitoring devices; 3) conducted a comprehensive test according to its physical security testing plan. The test documentation consisted of the following: a) documentation of any defects discovered during the test; b) notification to SERC_URE1's CIP compliance group of test results; and 4) performed a review for completeness is made on a monthly basis | 2012-08-31 | TBD | Admits | SERC reviewed SERC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2011009005 | Settlement Agreement | SERC sent SERC_URE1 an initial notice of a Compliance Audit. The audit team reported that SERC_URE1 was in violation of CIP-006-2 R3 because it failed to deploy its electronic access control and monitoring (EACM) devices used for access control and/or monitoring of the Electronic Security Perimeter (ESP) within an identified Physical Security Perimeter (PSP). The SERC audit team found that SERC_URE1 utilized an off-site third party to monitor EACM logs and provide alerts. SERC_URE1 failed to identify the third-party assets used in the monitoring of the SERC_URE1 EACM devices, and failed to present evidence demonstrating that the third-party assets were deployed within an identified PSP. SERC learned that the devices utilized for monitoring were deployed at an off-site location and received forwarded copies of the ESP access point logs. The third-party scanned the logs for possible security intrusions and alerted SERC_URE1. SERC reviewed the SERC_URE1 CIP Physical Security Plan and its details that the manager, energy control and metering systems is responsible for ensuring that all SERC_URE1 CIP-protected Cyber Assets reside within a defined PSP. In addition, the SERC_URE1 Electronic Security Program document states that the log management systems are considered CIP-protected Cyber Assets. | CIP-006-2 | R3 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). SERC determined that the violation posed a moderate risk because failure to afford protective measures to EACM devices could result in successful unauthorized access or unauthorized access attempts going undetected by logging and monitoring systems. SERC_URE1 relied on a third-party vendor to provide timely notification of security-related incidents, and provided no evidence that the assets utilized for the monitoring were adequately protected pursuant to the CIP Standards. Failure to adequately monitor ESP access point logs presented a risk that unauthorized intruders could access and possibly compromise SERC_URE1 Critical Cyber Assets (CCAs) undetected. Such access to the CCAs may then be used to cause harm to CCAs essential to the operation of the BPS. SERC, however, found no evidence indicating that SERC_URE1's vendor failed to protect the Cyber Assets at issue, and the vendor was an established vendor with experience providing offsite monitoring. SERC_URE1 identified no known security breaches during the time frame in question. | when the Standard became mandatory and enforceable on SERC_URE1 | Mitigation Plan completion | $70,000 (for SERC201000442, SERC2011006644, SERC2011006645, SERC2011006646, SERC2011006647, SERC2011007279, SERC2011008318, SERC2011008319, SERC2011008320, SERC2011009000, SERC2011009003, SERC2011009004, SERC2011009005, SERC2011009006, SERC2011009007, SERC2011009008, SERC2011009009, and SERC2013012823) | Compliance Audit | To mitigate this issue, SERC_URE1: 1) installed Cyber Assets used in the access control and/or monitoring of the ESP in order to setup authentication at the access points for cyber assets within the ESP; 2) changed procedures to use an in house solution for monitoring and alerting of its CIP-Protected Cyber Assets and located all monitoring and alerting devices within a PSP; 3) implemented an enhanced on-boarding checklist to ensure that all systems are classified, placed in the appropriate environment, and afforded the appropriate protective measures; and 4) provided formal training for system administrators on the on-boarding checklist. | 2013-09-17 | TBD | Admits | SERC reviewed SERC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2011009006 | Settlement Agreement | SERC sent SERC_URE1 an initial notice of a Compliance Audit. The SERC audit team reported that SERC_URE1 was in violation of CIP-007-1 R1 because it failed to document cybersecurity test results for significant changes to Critical Cyber Assets (CCAs) and other Cyber Assets within the Electronic Security Perimeter (ESP). The SERC audit team found that SERC_URE1 failed to adequately document the results of the cybersecurity testing performed while implementing significant changes to CCAs and other Cyber Assets within the ESP. SERC_URE1's change control policies and procedures did require testing prior to implementing any additions to, modifications to, replacements of, or removal of CIP-protected Cyber Assets, including significant changes, as described in CIP-007-1 R1. SERC_URE1 provided change tickets generated pursuant to these policies, indicating that it performed testing in accordance with those policies. Finally, the workflow process required the workflow ticket owner to attest that the cybersecurity testing was performed before closing the ticket, and SERC_URE1 provided these attestations. SERC_URE1 failed to document the results of testing as required by CIP-007-1 R1.3. | CIP-007-1 | R1; R1.3 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC determined that the violation posed a moderate risk because failure to document cybersecurity test results could lead to undocumented changes being implemented on Cyber Assets within the ESP, resulting in possible unauthorized access and the introduction of additional unidentified vulnerabilities. However, SERC_URE1 provided attestations from its personnel implementing the changes indicating that testing was completed. SERC_URE1's change process requires cybersecurity testing to be performed and documented prior to implementation. | when the Standard became mandatory and enforceable on SERC_URE1 | Mitigation Plan completion | $70,000 (for SERC201000442, SERC2011006644, SERC2011006645, SERC2011006646, SERC2011006647, SERC2011007279, SERC2011008318, SERC2011008319, SERC2011008320, SERC2011009000, SERC2011009003, SERC2011009004, SERC2011009005, SERC2011009006, SERC2011009007, SERC2011009008, SERC2011009009, and SERC2013012823) | Compliance Audit | To mitigate this issue, SERC_URE1: 1) created an action plan to enhance the existing Request for Change process to correct and prevent this issue from reoccurring; 2) created instructions on what to document within the Request for Change to capture the completion of security testing; 3) captured test results (pre-scan and post-scans) in the change management tool; 4) structured the process so that the change cannot be completed until test results are documented; and 5) trained system administrators upon completion of the process enhancement. | 2012-04-03 | TBD | Admits | SERC reviewed SERC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2011009007 | Settlement Agreement | SERC sent SERC_URE1 an initial notice of a Compliance Audit. The SERC audit team reported that SERC_URE1 was in violation of CIP-007-1 R4.2 because it failed to document a process for testing antivirus and malware prevention signatures. The SERC audit team discovered that SERC_URE1 did not document a process to test antivirus and malware prevention signatures prior to deploying them on Cyber Assets. SERC_URE1 presented evidence demonstrating that a third-party vendor would test malware prevention signatures in its own systems and certify that the signatures caused no issues. SERC_URE1, however, failed to document its own process for conducting testing on its own resources prior to deployment on production assets. SERC reviewed the SERC_URE1 Critical Infrastructure Cyber Security Policy and found that it did have a requirement for installation of antivirus signatures. The Cyber Security Plan states that SERC_URE1 will utilize approved anti-malware software and that the signatures will be updated from the central servers. The central servers are automatically updated with the certified virus definitions from the third-party vendor. This policy was insufficient because it did not contain procedures for SERC_URE1 to test signatures prior to installation on the production environment. | CIP-007-1 | R4; R4.2 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC determined that the violation posed a moderate risk because failure to have a process to test signatures could result in untested signatures being installed, which could introduce vulnerabilities to the network or adversely affect operational functionality. However, the vendor distributing these antivirus and malware signatures tested and certified that they were tested on all supported security products across all operating systems. SERC_URE1 maintained protective measures, such as multiple layers of firewalls and security status monitoring throughout the duration of the violation. | when the Standard became mandatory and enforceable on SERC_URE1 | Mitigation Plan completion | $70,000 (for SERC201000442, SERC2011006644, SERC2011006645, SERC2011006646, SERC2011006647, SERC2011007279, SERC2011008318, SERC2011008319, SERC2011008320, SERC2011009000, SERC2011009003, SERC2011009004, SERC2011009005, SERC2011009006, SERC2011009007, SERC2011009008, SERC2011009009, and SERC2013012823) | Compliance Audit | To mitigate this issue, SERC_URE1: 1) documented test processes that apply to CIP-protected Cyber Assets; 2) reviewed and approved a test process; 3) trained appropriate personnel on the new process; and 4) implemented and configured the new test process. | 2012-08-15 | TBD | Admits | SERC reviewed SERC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2011009008 | Settlement Agreement | SERC sent SERC_URE1 an initial notice of a Compliance Audit. The SERC audit team reported that SERC_URE1 was in violation of CIP-007-1 R5.2.1 because it failed to change the default password for a generic account on a Critical Cyber Asset (CCA) prior to putting the system into service. The SERC audit team found that SERC_URE1 failed to change the password for one factory default account on a CCA prior to putting the system into service, despite the ability to do so. The generic account was associated with a File Transfer Protocol (FTP) account and provided access to the FTP directory on the server, but the account did not have the permissions to upload, delete, or execute files. SERC analyzed SERC_URE1's Cyber Vulnerability Assessment (CVA) and learned that there were two default accounts with unchanged passwords, associated with an enabled FTP service, and impacting eight Cyber Assets. SERC also reviewed the CVA and found that it included the same issue. The default accounts in question were titled “ftp” and “anonymous,” and both had unchanged default passwords. SERC_URE1 reported that the two accounts were restricted to an FTP directory and had no ability to upload, delete, or execute files. SERC_URE1 deployed these systems without changing the default password for the default accounts. SERC_URE1's energy management system (EMS) vendor would not provide guidance on whether the accounts could be disabled or the passwords modified without losing the systems’ functionality. SERC reviewed the access logs for the systems at issue and discovered no other uses of the “ftp” or “anonymous” user accounts, other than scheduled CVAs and a test during the audit. | CIP-007-1 | R5; R5.2.1 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC determined that the violation posed a moderate risk because the default password on a generic account had not been changed on a CCA, making it possible that unauthorized access could be obtained by a malicious party. However, access to the FTP directory at issue enabled individuals to view files in the directory, but they could not upload or execute files, limiting the potential impact of unknown persons having access. SERC_URE1 maintained protective measures such as multiple layers of firewalls and security status monitoring throughout the duration of the violation. Finally, FTP logs from the time period of this violation showed no use of the service other than the CVA scans and a test during the Compliance Audit. | when the Standard became mandatory and enforceable on SERC_URE1 | Mitigation Plan completion | $70,000 (for SERC201000442, SERC2011006644, SERC2011006645, SERC2011006646, SERC2011006647, SERC2011007279, SERC2011008318, SERC2011008319, SERC2011008320, SERC2011009000, SERC2011009003, SERC2011009004, SERC2011009005, SERC2011009006, SERC2011009007, SERC2011009008, SERC2011009009, and SERC2013012823) | Compliance Audit | To mitigate this issue, SERC_URE1: 1) replaced the EMS in production at the time of the audit with new hardware and software; 2) disabled the generic accounts identified as “anonymous" and "ftp,” which were used on the old system; 3) retired all hardware and software on the previous EMS; and 4) developed an on-boarding checklist to be completed prior to placing an asset into production environment. This checklist includes numerous items to ensure strict compliance with CIP Standards. | 2013-09-17 | TBD | Admits | SERC reviewed SERC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2011009009 | Settlement Agreement | SERC sent SERC_URE1 an initial notice of a Compliance Audit. The SERC audit team reported that SERC_URE1 was in violation of CIP-007-3a R3 because it failed to document the assessment of security patches and security upgrades for applicability within 30 calendar days of availability. SERC_URE1's security patch assessment process in place during the compliance period resulted in third-party patches not being assessed within the required 30 days. According to this process, SERC_URE1 held monthly patch assessment meetings, during which it assessed newly released patches and created change management tickets for patches as applicable. If SERC_URE1 failed to schedule this meeting within 30 calendar days of the last meeting, it would not meet the 30 day assessment requirement for certain patches. SERC reviewed SERC_URE1's Change Control and Configuration Management documentation and found that it detailed that the security patches were classified as significant changes and requires the patches to be tested in an environment that reflects the production environment. In addition, the documentation requires that the changes have testing performed, documented, and confirmed. SERC_URE1 first failed to assess security patches within 30 calendar days. The patch in question was released, but SERC_URE1 did not assess it within the 30 day requirement. In total, SERC_URE1 failed to assess 22 patches within 30 calendar days. Upon assessment, however, SERC_URE1 determined that only two of these patches applied to 12.3% of SERC_URE1's Cyber Assets, the remaining patches were not associated with Cyber Assets. | CIP-007-3a | R3; R3.1 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failure to assess patches within 30 calendar days creates the potential that patches for Critical Cyber Assets may not be installed in a timely manner, potentially resulting in an increased risk that those Cyber Assets could be compromised or exploited by unauthorized personnel or software. While using monthly meetings to assess security patches resulted in late assessments, SERC_URE1 was able to assess any missed patches at the next scheduled meeting. Only two of the assessed patches applied to 49 deployed SERC_URE1 Cyber Assets. SERC_URE1 maintained protective measures such as multiple layers of firewalls and security status monitoring throughout the duration of the violation. | when SERC_URE1 failed to assess a patch 30 days following the patch release | Mitigation Plan completion | $70,000 (for SERC201000442, SERC2011006644, SERC2011006645, SERC2011006646, SERC2011006647, SERC2011007279, SERC2011008318, SERC2011008319, SERC2011008320, SERC2011009000, SERC2011009003, SERC2011009004, SERC2011009005, SERC2011009006, SERC2011009007, SERC2011009008, SERC2011009009, and SERC2013012823) | Compliance Audit | To mitigate this issue, SERC_URE1: 1) created a step-by-step procedure that instructs system administrators how to: a) track security patches using Patch Tracking Logs; b) assess released patches on an ongoing basis throughout the month; c) test patches prior to installing into the production environment; and d) schedule installation of the patch; 2 collected evidence of patch assessments which was reviewed by the CIP compliance administrator monthly; 3) performed an assessment to determine which patches were missing and from what assets; and 4) determined that two patches were still missed and assessed them as applicable to a total of four assets. The patches were not installed because the cyber system containing these assets was retired. | 2013-01-10 | TBD | Admits | SERC reviewed SERC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2013012823 | Settlement Agreement | SERC sent SERC_URE1 an initial notice of a Compliance Audit. The SERC audit team reported that SERC_URE1 was in violation of CIP-002-3 R3 because it failed to include an asset in its list of Critical Cyber Assets (CCAs). SERC determined that this was a violation of CIP-005-3a R1.4 instead of CIP-002-3 R3. As a result, SERC dismissed the violation of CIP-002-3 R3 and initiated a violation of CIP-005-3a R1.4. The audit team found that during a SERC_URE1 Cyber Vulnerability Assessment (CVA), SERC_URE1 allowed a vendor to connect a laptop to the Electronic Security Perimeter (ESP) to perform the CVA without first providing evidence that it was protected in accordance with the CIP Standards. The laptop was connected to the ESP for various periods of time during a five day period. The audit team identified this issue as a violation of CIP-002-3 R3. SERC subsequently determined that the laptop was not essential to the operation of any Critical Asset, and, therefore, was not required to be identified as a CCA. SERC determined that the laptop should have been identified as a non-critical Cyber Asset within an ESP and protected pursuant to the requirements of Reliability Standard CIP-005-3. SERC learned that there were 79 CCAs accessible from the laptop during the CVA. | CIP-005-3a | R1; R1.4 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC determined that the violation posed a moderate risk because without proper identification of non-critical Cyber Assets within the ESP, SERC_URE1 may have not provided the appropriate levels of protection to its ESP, potentially leading to malware and other vulnerabilities being introduced inside the ESP. However, in this case, the vendor laptop met SERC_URE1's security requirements which require implementing virus and malicious software protection. The laptop was behind a firewall limiting internet access. The vendor performed the CVA on site and under constant supervision of an authorized SERC_URE1 cyber security engineer. The vendor had a completed personnel risk assessment. The vendor had completed cybersecurity awareness training. The vendor never had unescorted physical access to SERC_URE1's Cyber Assets. The vendor’s electronic access was limited since the vendor was not given any accounts or passwords. SERC_URE1 has an intrusion detection system which alerts of any unauthorized activity. | when the laptop was first connected to the ESP | when the laptop was disconnected from the ESP for the last time | $70,000 (for SERC201000442, SERC2011006644, SERC2011006645, SERC2011006646, SERC2011006647, SERC2011007279, SERC2011008318, SERC2011008319, SERC2011008320, SERC2011009000, SERC2011009003, SERC2011009004, SERC2011009005, SERC2011009006, SERC2011009007, SERC2011009008, SERC2011009009, and SERC2013012823) | Compliance Audit | To mitigate this issue, SERC_URE1: 1) contacted the vendor and requested verification that all the information obtained during the CVA has been erased from the laptop in accordance with SERC_URE1's General Services Agreement; 2) procured a laptop to perform security and administration functions on CIP-protected Cyber Assets and enhanced its procedures to require that only these devices be used for the performance of vulnerability assessments; and 3) provided training to remind personnel of the proper protocol for connecting all Cyber Assets within an ESP. | 2012-04-12 | TBD | Admits | SERC reviewed SERC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
SERC Reliability Corporation (SERC) | Unidentified Registered Entity 2 (SERC_URE2) | NCRXXXXX | SERC201000512 | Settlement Agreement | During a Spot Check the SERC Spot Check team reported that SERC_URE2 was in violation of CIP-002-1 R3. SERC_URE2 failed to identify all Cyber Assets essential to the operation of Critical Assets as Critical Cyber Assets (CCAs). After reviewing the SERC_URE2 risk-based assessment methodology (RBAM) and Critical Asset list, SERC determined that the violation was more appropriately addressed under CIP-002-1 R2 as a failure to identify all Critical Assets. During the Spot Check, SERC_URE2 did not identify the Automatic Generation Control (AGC) as a CCA. AGC is used by the energy management system (EMS) support personnel and possesses the capability of controlling the Bulk Electric System. SERC determined that SERC_URE2 failed to identify a generation facility, where the AGC system is located, as a Critical Asset. The facility was the primary generation control location for SERC_URE2. As such, the facility should have been identified as a Critical Asset. SERC_URE2 had identified a second facility, a control center, as a Critical Asset, but SERC_URE2 should have also identified the first facility where the AGC was located as a Critical Asset. Due to its failure to identify the first facility as a Critical Asset, the Cyber Assets and CCAs associated with it were not afforded all of the protections of the CIP Standards. | CIP-002-1 | R2 | High | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). SERC determined the violation posed a moderate risk because SERC_URE2's failure to correctly identify all Critical Assets could leave any associated CCAs without the protections specified in the CIP Standards, which could allow an attacker to disrupt SERC_URE2's control of its portion of the BPS. However, although it did not afford the Cyber Assets at the facility with all of the protections of the CIP Standards, SERC_URE2 did protect those Cyber Assets with both physical and cybersecurity measures. The facility had card readers at the entry points to the facility. All users of the Cyber Assets at the facility were required to have personnel risk assessments and cyber security training. In addition, the Cyber Assets at the facility are separated from the control center EMS by a firewall with a single port allowing access. Cyber Assets used at the facility were configured to block functions not needed for the applicable function, including Telnet network protocol, secure shell network protocol, hypertext transfer protocol, and remote desktop protocol. None of the facility's Cyber Assets could perform switching. In addition, the AGC at the facility was afforded protections such as security patch management, antivirus software, and account management controls. | when the Standard became mandatory and enforceable on SERC_URE2 | Mitigation Plan completion | 15000 | Spot Check | To mitigate this violation, SERC_URE2: 1) updated the Critical Asset list of SERC_URE2's parent company to include the facility as a Critical Asset; 2) enclosed the AGC operations within an identified Physical Security Perimeter; and 3) merged the secure network protecting the AGC into an existing identified Electronic Security Perimeter. | 2012-07-19 | TBD | Neither Admits Nor Denies | SERC considered SERC_URE2's internal compliance program (ICP) a mitigating factor in the penalty determination.
SERC Reliability Corporation (SERC) | Unidentified Registered Entity 3 (SERC_URE3) | NCRXXXXX | SERC2011006608 | Settlement Agreement | During a Compliance Audit, the SERC audit team reported that SERC_URE3 was in violation of CIP-006-2 R3. SERC_URE3 was unable to provide evidence demonstrating that Cyber Assets used in the Electronic Access Control and/or Monitoring (EACM) of the Electronic Security Perimeter (ESP) resided within an identified Physical Security Perimeter (PSP). SERC_URE3 had EACM Cyber Assets that were located within a data center that met the physical design criteria required to be classified as a PSP. However, SERC_URE3 failed to identify a PSP in or around the data center in its physical security plan or any other documentation. Therefore, EACM Cyber Assets within the data center did not reside within an identified PSP. There were no Critical Cyber Assets (CCAs) within the data center. | CIP-006-2 | R3 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although the EACM devices were not inside of an identified PSP, they resided within a secure facility that contained access control, monitoring, alarming, and video surveillance. There were no CCAs within the data center. | when the Standard became mandatory and enforceable | Mitigation Plan completion | $45,000 (for SERC2011006608, SERC2011006610, SERC2011006612, SERC2011006613, SERC2011006614, SERC2011006615, SERC2011006616, SERC2011006617, SERC2012010737, SERC2013011815, and SERC2013011825) | Compliance Audit | To mitigate this violation, SERC_URE3: 1) consolidated its EACM devices located within its data centers into an authentication monitoring zone (AMZ) secure rack PSP; and 2) updated its physical security plan to include the secure rack PSP. | 2011-03-09 | 2013-12-09 | Admits | SERC reviewed SERC_URE3's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. Additionally, SERC_URE3 completed or will complete the following above and beyond actions, which SERC considered to be a mitigating factor in the penalty determination. SERC_URE3's compliance department coordinates and conducts internal audits of the CIP Standards at least annually. These audits include a review of updated Reliability Standard Audit Worksheets (RSAWs), evidence sampling and review, the presentation of evidence by subject matter experts (SMEs), interviews with SMEs, and audit recommendations. SERC_URE3 also utilizes a third-party vendor on an annual basis to conduct cyber penetration testing on CIP and non-CIP networks and assets, including internal and external firewalls and servers, outside of the required annual Cyber Vulnerability Assessment (CVA) process. The cyber penetration testing is used to identify areas for improvement and provide an additional analysis of SERC_URE3's security posture. SERC_URE3 also spent approximately $1 million to create a dedicated authentication and monitoring zone (AMZ) for CIP activities and upgrades to its physical access control system. In addition, SERC_URE3 has hired a trainer, which will allow more specific and detailed approach to CIP training. SERC_URE3 has spent approximately $2 million on a new energy management system (EMS) that includes cybersecurity improvements that will allow for the termination of three Technical Feasibility Exceptions associated with password management. SERC_URE3 also spent approximately $1 million on a Historian that will allow SERC_URE3 to remove read-only electronic access to the EMS for a large customer.
SERC Reliability Corporation (SERC) | Unidentified Registered Entity 3 (SERC_URE3) | NCRXXXXX | SERC2011006610 | Settlement Agreement | During a Compliance Audit, the SERC audit team reported that SERC_URE3 was in violation of CIP-007-1 R5.2.2 because it failed to document the individuals with access to shared accounts. On the same day, the SERC audit team reported that SERC_URE3 was in violation of CIP-007-1 R5.2.1 because it failed to change passwords for some default accounts prior to putting systems into service. SERC_URE3 submitted a Self-Certification to SERC stating that it was in violation of CIP-004-3 R4. SERC_URE3 discovered that its vendor with access to SERC_URE3 Critical Cyber Assets (CCAs) had a change in personnel with access to CCAs through a shared account. Although the CCA access list was updated within seven days, SERC_URE3 failed to change the password on the shared account within seven days as required by SERC_URE3's procedures. SERC determined that this violation was actually a violation of CIP-007 R5.2.3 and not a violation of CIP-004 R4 as originally indicated in SERC_URE3's Self-Certification. SERC determined that this violation involved the same Standard and Requirement as the two SERC audit team reports and decided to treat the Self-Certification as an expansion of scope. In total, SERC determined that SERC_URE3 had three separate incidents involving CIP-007 R5.2. In the first incident, which involved CIP-007-1 R5.2.2, SERC_URE3 maintained a policy for managing the use of shared accounts that limited the access to individuals with authorized access. SERC_URE3 documented the departments that had access to the shared operator accounts, but failed to document the individuals with access to a single shared operator account. This single shared account was used on 32.1% CCA servers and several non-critical Cyber Asset servers within the Electronic Security Perimeter (ESP). In the second incident, which involved CIP-007-1 R5.2.1, SERC_URE3's Cyber Vulnerability Assessment (CVA) showed that three Cyber Assets (two CCA database servers and one non-critical Cyber Asset server) within the ESP had default accounts and that SERC_URE3 had not renamed, disabled, or changed the passwords on those default accounts prior to putting the Cyber Assets into service. These Cyber Assets were put into service prior to the enforcement date of the CIP Standards. This violation affected two default database accounts on the three servers which had no password set and one anonymous file transfer protocol (FTP) account enabled for the FTP service on all three servers. After a review, SERC_URE3 determined that the anonymous FTP account could be accessed and used by 53.7% of the accounts on the three servers. SERC_URE3 had two approved Technical Feasibility Exceptions (TFEs) pursuant to CIP-007 R5.3.3 for the three servers. The TFEs stated that changing the account passwords on these three servers on an annual basis was not possible because the changes had not been tested and could adversely impact reliable operations. SERC_URE3 was concerned that changing the account passwords could disrupt the operation of the emergency management system (EMS) because the FTP accounts were used by several applications and scripts. However, TFEs are not available for CIP-007 R5.2.1, and SERC_URE3 was required to change the passwords for default accounts prior to putting them into service. In the third incident, which involved CIP-007-1 R5.2.3, SERC_URE3 permitted its EMS vendor authorized cyber access to CCAs within one of its ESPs through the use of a shared account. SERC_URE3 coordinated with the vendor to maintain a list of the authorized vendor personnel who had approved access and had completed the cyber security training, personnel risk assessment (PRA), and received security awareness reinforcement. SERC_URE3 granted electronic access through the ESP to the vendor personnel via a two-factor authentication process. The first factor was a user name and personal identification number that was known by the vendor. The second factor was a passcode from a regularly changing key fob token which was in the possession of SERC_URE3 personnel at all times. Thus, vendor personnel had to obtain the second factor from SERC_URE3 personnel in order to gain access to CCAs. Once inside the ESP, vendor personnel utilized the shared account to electronically access CCAs and non-critical Cyber Assets within the SERC_URE3 ESPs. The vendor had a change in personnel with a need for access to CCAs and notified SERC_URE3. Although SERC_URE3 removed the vendor employee from its CCA access list within seven days, SERC_URE3 failed to change the password known to the vendor on the shared account within seven days of the change as required by its shared account procedures. SERC_URE3 changed the shared account password 22 days after it should have changed the password. The vendor employee would not have been able to access the CCAs or non-critical Cyber Assets within the ESPs because SERC_URE3 personnel would not have provided the passcode from the key fob token that was required to gain access through the ESP after the vendor employee was removed from the CCA access list. | CIP-007-1 | R5; R5.2 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). SERC determined that the violation posed a moderate risk because SERC_URE3's failure to implement its policy to minimize and manage the scope and acceptable use of shared and default accounts could have allowed malicious individuals to exploit the shared or default accounts in order to disrupt SERC_URE3 operations and the reliability of the BPS. However, the first incident involved one shared accounts. This account was present on 32.1% of CCAs and several non-critical servers within its ESPs. Access was limited to operators with valid PRAs and annual cyber security training. For the second incident, SERC_URE3 did not allow remote login to the affected Cyber Assets and had physical security controls in place including man-traps, key cards, active monitoring of access that would prevent local logins to those Cyber Assets, and restricted access to these servers to administrators with PRAs and cybersecurity training. Additionally, ESP controls included dual-factor authentication, intrusion detection systems, third-party monitoring, and security event alerting. The third incident involved a single EMS vendor whose personnel were in good standing with SERC_URE3. Authorized remote EMS vendor access was made through the use of a two-factor authentication process. The EMS vendor was required to contact SERC_URE3 in order to obtain the key fob token passcode. All EMS vendor personnel with access to the shared account had valid PRAs and annual cybersecurity training. | when the Standard became mandatory and enforceable on SERC_URE3 | present | $45,000 (for SERC2011006608, SERC2011006610, SERC2011006612, SERC2011006613, SERC2011006614, SERC2011006615, SERC2011006616, SERC2011006617, SERC2012010737, SERC2013011815, and SERC2013011825) | Compliance Audit | To mitigate this violation, SERC_URE3: 1) employed an additional step in the vendor shared account access process whereby, on session completion, SERC_URE3 changes the password and locks the shared account until the vendor's authorized personnel again need access to the ESP(s) for support purposes; 2) supplemented its processes for changing shared account passwords by ensuring the vendor's program manager sends update lists to the applicable SERC_URE3 email distribution list so SERC_URE3 personnel receive updates simultaneously and vendor changes are known by relevant SERC_URE3 personnel; and 3) finalized its updated process to address both enabling and disabling access. To mitigate this violation, SERC_URE3 will: 1) update the list of shared accounts and the specific individuals with access to those share accounts, instead of the departments with access; and 2) terminate the TFEs by modifying or upgrading its current database management software, which removes the hardcoded passwords. | 12/31/2013 (approved completion date) | TBD | Admits | SERC reviewed SERC_URE3's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. Additionally, SERC_URE3 completed or will complete the following above and beyond actions, which SERC considered to be a mitigating factor in the penalty determination. SERC_URE3's compliance department coordinates and conducts internal audits of the CIP Standards at least annually. These audits include a review of updated Reliability Standard Audit Worksheets (RSAWs), evidence sampling and review, the presentation of evidence by subject matter experts (SMEs), interviews with SMEs, and audit recommendations. SERC_URE3 also utilizes a third-party vendor on an annual basis to conduct cyber penetration testing on CIP and non-CIP networks and assets, including internal and external firewalls and servers, outside of the required annual Cyber Vulnerability Assessment (CVA) process. The cyber penetration testing is used to identify areas for improvement and provide an additional analysis of SERC_URE3's security posture. SERC_URE3 also spent approximately $1 million to create a dedicated authentication and monitoring zone (AMZ) for CIP activities and upgrades to its physical access control system. In addition, SERC_URE3 has hired a trainer, which will allow more specific and detailed approach to CIP training. SERC_URE3 has spent approximately $2 million on a new energy management system (EMS) that includes cybersecurity improvements that will allow for the termination of three Technical Feasibility Exceptions associated with password management. SERC_URE3 also spent approximately $1 million on a Historian that will allow SERC_URE3 to remove read-only electronic access to the EMS for a large customer.
SERC Reliability Corporation (SERC) | Unidentified Registered Entity 3 (SERC_URE3) | NCRXXXXX | SERC2011006612 | Settlement Agreement | During a Compliance Audit, the SERC audit team reported that SERC_URE3 was in violation of CIP-007-1 R3 because SERC_URE3 did not document compensating measures applied to mitigate risk exposure in cases where applicable security patches were not installed. SERC_URE3 has a documented security patch management program for tracking, evaluating, testing, and installing cyber security patches for Cyber Assets within Electronic Security Perimeters (ESPs). SERC_URE3 system administrators are responsible for the control, coordination, assessment, and implementation of the security patch management program. SERC_URE3 received security patch advisories from two sources in an attempt to keep abreast of any security vulnerabilities and associated patches. SERC_URE3's system administrators monitor advisories received regarding software security patches and determine the applicability of the security patches and track their evaluation, testing, and installation. The SERC audit team reviewed SERC_URE3's Cyber Vulnerability Assessment (CVA) results and identified several operating system security patches that were not installed. Some of these patches were identified as critical security patches and dated before the time when CIP-007-1 became mandatory and enforceable. SERC_URE3 had not submitted any Technical Feasibility Exceptions (TFEs) that documented compensating measures for the vulnerabilities associated with the security patches that it had not installed. The security patches were applicable to 84.9% of the total Critical Cyber Assets (CCAs), and several non-critical Cyber Assets. SERC_URE3 restricted the software installed on all Cyber Assets inside of the ESP so that operating system and primary function software were the only software installed on each device, thereby limiting the possible vulnerabilities and security patches requiring assessment and installation. SERC_URE3 did not maintain an assessment log that tracked each security patch assessment but instead used an assessment ticket for each security patch, which made it difficult to verify how many patch assessments were missed. | CIP-007-1 | R3 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC determined that the violation posed a moderate risk because SERC_URE3's failure to install a significant number of missing security patches on CCAs and non-critical Cyber Assets and to document compensating measures resulted in a increased risk that those Cyber Assets could be compromised or exploited by unauthorized personnel or software. However, SERC_URE3 limited the software that were installed on the devices to operating systems and primary function software. SERC_URE3 restricted electronic and physical access to the affected Cyber Assets to only approved screened and trained personnel, and the affected Cyber Assets were protected within an ESP and Physical Security Perimeter. | when the Standard became mandatory and enforceable on SERC_URE3 | present | $45,000 (for SERC2011006608, SERC2011006610, SERC2011006612, SERC2011006613, SERC2011006614, SERC2011006615, SERC2011006616, SERC2011006617, SERC2012010737, SERC2013011815, and SERC2013011825) | Compliance Audit | To mitigate this violation, SERC_URE3 will: 1) test and determine whether it will apply the applicable security patches for the first operating system. If SERC_URE3 decides not to apply any of these applicable operating system patches, it will utilize the TFE process to document compensating measures that have been applied to mitigate risk exposure; 2) implement a newer version of the second operating system as part of an upgrade to the energy management system (EMS). As a result of this upgrade, the missing operating system patches will no longer be necessary. Any applicable operating system patches after the upgrade will be installed on the servers. If SERC_URE3 determines that an applicable patch cannot be implemented, it will utilize the TFE process to document the compensating measures that have been applied to mitigate risk exposure; and 3) revise its security patch management process to include a step to file a TFE to document the compensating measures that are applied whenever an applicable security patch is not installed. | 12/31/2013 (approved completion date) | TBD | Admits | SERC reviewed SERC_URE3's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. Additionally, SERC_URE3 completed or will complete the following above and beyond actions, which SERC considered to be a mitigating factor in the penalty determination. SERC_URE3's compliance department coordinates and conducts internal audits of the CIP Standards at least annually. These audits include a review of updated Reliability Standard Audit Worksheets (RSAWs), evidence sampling and review, the presentation of evidence by subject matter experts (SMEs), interviews with SMEs, and audit recommendations. SERC_URE3 also utilizes a third-party vendor on an annual basis to conduct cyber penetration testing on CIP and non-CIP networks and assets, including internal and external firewalls and servers, outside of the required annual Cyber Vulnerability Assessment (CVA) process. The cyber penetration testing is used to identify areas for improvement and provide an additional analysis of SERC_URE3's security posture. SERC_URE3 also spent approximately $1 million to create a dedicated authentication and monitoring zone (AMZ) for CIP activities and upgrades to its physical access control system. In addition, SERC_URE3 has hired a trainer, which will allow more specific and detailed approach to CIP training. SERC_URE3 has spent approximately $2 million on a new energy management system (EMS) that includes cybersecurity improvements that will allow for the termination of three Technical Feasibility Exceptions associated with password management. SERC_URE3 also spent approximately $1 million on a Historian that will allow SERC_URE3 to remove read-only electronic access to the EMS for a large customer.
SERC Reliability Corporation (SERC) | Unidentified Registered Entity 3 (SERC_URE3) | NCRXXXXX | SERC2011006613 | Settlement Agreement | During a Compliance Audit, the SERC audit team reported that SERC_URE3 was in violation of CIP-006-1 R1.8 because it failed to afford its Physical Access Control System (PACS) devices with the protective measures specified in CIP-005 R2 and R3, and CIP-007 R1, R4.2, and R5.3.3. Specifically, the audit team found that SERC_URE3 failed to present evidence showing that there was electronic access control protection to an Electronic Security Perimeter (ESP) from the corporate network (CIP-005 R2 and R3); cybersecurity controls testing after significant changes (CIP-007 R1); testing of antivirus signatures prior to deployment (CIP-007 R4.2); and shared passwords were being changed at least annually (CIP-007 R5.3.3). The SERC audit team identified PACS devices that were not afforded the protective measures listed in CIP-006-1 R1.8. SERC_URE3 subsequently completed an annual internal assessment of compliance to verify that the scope of the violation was limited to the four PACS devices. SERC later determined that the violation also included additional PACS devices, thereby impacting all the PACS devices that SERC_URE3 had. SERC_URE3 provided no evidence to demonstrate that there was access control protection from an untrusted network to the PACS devices. SERC determined that SERC_URE3 was in violation of CIP-006-1 R1.8 because it failed to provide its PACS devices with the protective measures specified in CIP-005 R2 and R3. SERC_URE3's maintenance and testing procedures did not address the testing of PACS devices after significant changes to ensure that no degradation of cyber security controls occurred. SERC_URE3 only tested significant changes to the PACS devices at a functional level to ensure that the changes did not stop the PACS devices from working. SERC_URE3 did not test a total of 49 significant changes to 77.8% of its PACS devices made during a five month period to ensure that those changes did not adversely affect the existing cyber security controls. SERC determined that SERC_URE3 was in violation of CIP-006-1 R1.8 because it failed to provide its PACS devices with the protective measures specified in CIP-007-1 R1. SERC_URE3's corporate security patch management policy and malicious software tools procedure called for the application of virus definition files immediately upon receipt, but neither addressed the testing of those signatures. SERC_URE3 provided no evidence that it tested the antivirus or malware prevention signatures. SERC determined that SERC_URE3 was in violation of CIP-006-1 R1.8 because it failed to provide its PACS devices with the protective measures specified in CIP-007-1 R4.2. SERC_URE3's account management documentation addressed the annual changing of passwords as well as logging and monitoring. SERC_URE3's corporate password standards policy required annual password changes on all company Cyber Assets. Lastly, SERC_URE3's default active directory domain account policies for all Windows devices had controls in place that required the changing of account passwords associated with the PACS devices in question every 60 days. SERC_URE3 did not provide evidence of password controls in place. SERC determined that SERC_URE3 was in violation of CIP-006-1 R1.8 because it failed to provide its PACS devices with the protective measures specified in CIP-007-1 R5.3.3. SERC_URE3 completed a system upgrade that addressed the cyber security controls testing of the PACS devices in question. This system upgrade ended SERC_URE3's failure to afford its PACS devices the protective measures specified in CIP-05 R2 and R3 and CIP-007 R1, R4.2, and R5.3.3. | CIP-006-1 | R1; R1.8 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC determined that the violation posed a moderate risk because SERC_URE3's failure to protect its PACS devices adequately could lead to the disabling or degradation of physical security protections, which could allow unauthorized physical access to Critical Cyber Assets (CCAs) inside Physical Security Perimeters (PSPs). However, 44.4% of the PACS devices in question were located inside of PSPs, and all personnel with physical access to the PACS devices had valid personnel risk assessments and current cyber security training. Live video feed would allow identification of individuals physically accessing the PACS devices. In addition, access controls and access rules limited electronic access to the PACS devices and denied access by default. SERC_URE3 implemented intrusion detection systems, antivirus and malware software, and network security logging and monitoring within the ESP, as technically feasible, to detect unusual activities. SERC_URE3 used a third-party security services provider as a secondary means of monitoring to ensure that all network activity was monitored for security risks and threats. This third-party security services provider had no access to SERC_URE3 ESPs or CCAs. | when the Standard became mandatory and enforceable on SERC_URE3 | Mitigation Plan completion | $45,000 (for SERC2011006608, SERC2011006610, SERC2011006612, SERC2011006613, SERC2011006614, SERC2011006615, SERC2011006616, SERC2011006617, SERC2012010737, SERC2013011815, and SERC2013011825) | Compliance Audit | To mitigate this violation, SERC_URE3: 1) implemented its PACS devices into an authentication monitoring zone (AMZ) environment within a secure rack PSP; 2) evaluated, identified, and selected automated security control tools that can be employed to conduct security control testing to verify whether any modifications to the existing cyber security controls are made following significant changes to PACS devices; 3) implemented and developed testing procedures for testing against existing security controls on PACS devices after the selection of automated security control tools; and 4) updated its physical security plan to document the addition of the secure rack PSP. | 2012-06-28 | 2013-12-10 | Admits | SERC reviewed SERC_URE3's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. Additionally, SERC_URE3 completed or will complete the following above and beyond actions, which SERC considered to be a mitigating factor in the penalty determination. SERC_URE3's compliance department coordinates and conducts internal audits of the CIP Standards at least annually. These audits include a review of updated Reliability Standard Audit Worksheets (RSAWs), evidence sampling and review, the presentation of evidence by subject matter experts (SMEs), interviews with SMEs, and audit recommendations. SERC_URE3 also utilizes a third-party vendor on an annual basis to conduct cyber penetration testing on CIP and non-CIP networks and assets, including internal and external firewalls and servers, outside of the required annual Cyber Vulnerability Assessment (CVA) process. The cyber penetration testing is used to identify areas for improvement and provide an additional analysis of SERC_URE3's security posture. SERC_URE3 also spent approximately $1 million to create a dedicated authentication and monitoring zone (AMZ) for CIP activities and upgrades to its physical access control system. In addition, SERC_URE3 has hired a trainer, which will allow more specific and detailed approach to CIP training. SERC_URE3 has spent approximately $2 million on a new energy management system (EMS) that includes cybersecurity improvements that will allow for the termination of three Technical Feasibility Exceptions associated with password management. SERC_URE3 also spent approximately $1 million on a Historian that will allow SERC_URE3 to remove read-only electronic access to the EMS for a large customer.
SERC Reliability Corporation (SERC) | Unidentified Registered Entity 3 (SERC_URE3) | NCRXXXXX | SERC2011006614 | Settlement Agreement | During a Compliance Audit, the SERC audit team reported that SERC_URE3 was in violation of CIP-005-1 R2.2. SERC_URE3 failed to enable only the ports and services required for operations and for monitoring Cyber Assets within the Electronic Security Perimeter (ESP). SERC reviewed the firewall rules in place at the time of the audit and learned that SERC_URE3 had two Electronic Access Control and Monitoring (EACM) firewalls in place with eight firewall rules that allowed any port or service from the main energy management system (EMS) ESP to communicate with the backup EMS ESP for nine server hosts. SERC_URE3 claimed that these rules allowed the two EMS systems to communicate and replicate each other, providing complete redundancy and fail over capability. SERC_URE3 did not restrict the ports and services at the time because it was concerned that doing so could cause negative operational impacts. As a result, SERC_URE3 was unable to provide documented justification for the firewall rules at the time of the Compliance Audit. Outside of the eight firewall rules in question, SERC_URE3 used an access control model that denied access by default. SERC_URE3 was also unable to provide documentation, individually or by specified grouping, of the configuration of the enabled ports and services. | CIP-005-1 | R2; R2.2 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC determined that the violation posed a moderate risk because SERC_URE3's failure to restrict ports and services on access control devices could allow the exploitation of vulnerabilities and result in unauthorized access to Critical Cyber Assets (CCAs) inside of the ESP. However, outside of the eight firewall rules in question, SERC_URE3 used an access control model that denied access by default and did not allow traffic from external networks, including the SERC_URE3 corporate network. SERC_URE3 implemented intrusion detection systems, antivirus and malware software, and network security logging and monitoring within the ESP, as technically feasible, to detect unusual activities. SERC_URE3 used a third-party security services provider as a secondary means of monitoring, to ensure that all network activity was monitored for security risk and threats. This third-party security services provider had no access to SERC_URE3 ESPs or CCAs. | when the Standard became mandatory and enforceable on SERC_URE3 | Mitigation Plan completion | $45,000 (for SERC2011006608, SERC2011006610, SERC2011006612, SERC2011006613, SERC2011006614, SERC2011006615, SERC2011006616, SERC2011006617, SERC2012010737, SERC2013011815, and SERC2013011825) | Compliance Audit | To mitigate this violation, SERC_URE3: 1) implemented additional firewall rules to allow only acceptable network traffic that it required for normal business activities; 2) evaluated current traffic through vital firewall interfaces to ensure that the allowed traffic is that which is only required and justified based on business needs; 3) reconfigured access control lists to restrict inbound and outbound traffic to only the justified business traffic; and 4) updated firewall policies with justification of enabled access control lists. | 2011-09-29 | TBD | Admits | SERC reviewed SERC_URE3's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. Additionally, SERC_URE3 completed or will complete the following above and beyond actions, which SERC considered to be a mitigating factor in the penalty determination. SERC_URE3's compliance department coordinates and conducts internal audits of the CIP Standards at least annually. These audits include a review of updated Reliability Standard Audit Worksheets (RSAWs), evidence sampling and review, the presentation of evidence by subject matter experts (SMEs), interviews with SMEs, and audit recommendations. SERC_URE3 also utilizes a third-party vendor on an annual basis to conduct cyber penetration testing on CIP and non-CIP networks and assets, including internal and external firewalls and servers, outside of the required annual Cyber Vulnerability Assessment (CVA) process. The cyber penetration testing is used to identify areas for improvement and provide an additional analysis of SERC_URE3's security posture. SERC_URE3 also spent approximately $1 million to create a dedicated authentication and monitoring zone (AMZ) for CIP activities and upgrades to its physical access control system. In addition, SERC_URE3 has hired a trainer, which will allow more specific and detailed approach to CIP training. SERC_URE3 has spent approximately $2 million on a new energy management system (EMS) that includes cybersecurity improvements that will allow for the termination of three Technical Feasibility Exceptions associated with password management. SERC_URE3 also spent approximately $1 million on a Historian that will allow SERC_URE3 to remove read-only electronic access to the EMS for a large customer.
SERC Reliability Corporation (SERC) | Unidentified Registered Entity 3 (SERC_URE3) | NCRXXXXX | SERC2011006615 | Settlement Agreement | During a Compliance Audit, the SERC audit team reported that SERC_URE3 was in violation of CIP-005-1 R2, specifically R2.4 and R2.5. SERC_URE3 did not implement organizational and technical processes and/or procedural mechanisms for control of electronic access at electronic access points to the Electronic Security Perimeter (ESP) for some user groups. SERC_URE3 allows personnel from a customer to have read-only access to a man-machine interface (MMI) which was classified as a Critical Cyber Asset (CCA). The connection to the ESP is established through a dedicated communication line owned by SERC_URE3. Access to the ESP is granted using a shared account via a secure virtual private network (VPN) connection. Eight individuals at the customer used the shared account. SERC_URE3 logged access to the MMI at the firewall, but SERC_URE3 could not ensure the authenticity of each individual using that shared account. SERC_URE3 also failed to have organizational documentation that described and identified the process for the customer’s access requests and authorization, authentication methods, and the review process for authorization rights associated with the allowed customer access. | CIP-005-1 | R2; R2.4, R2.5 | Medium | Severe | This violation posed a minimal and did not pose a serious or substantial risk to the reliability of the bulk power system. The customer allowed only eight individuals to use the shared account and managed a list of individuals that used the shared account. The shared account had read-only electronic access and the customer did not have physical access to CCAs. ESP firewalls were logging access. SERC_URE3 subsequently reviewed the logs and found no Cyber Security Incidents or attempts to breach security during the violation. The connection was a dedicated connection owned by SERC_URE3 and only provided access to one ESP access point. | when the Standard became mandatory and enforceable on SERC_URE3 | Mitigation Plan completion | $45,000 (for SERC2011006608, SERC2011006610, SERC2011006612, SERC2011006613, SERC2011006614, SERC2011006615, SERC2011006616, SERC2011006617, SERC2012010737, SERC2013011815, and SERC2013011825) | Compliance Audit | To mitigate this violation, SERC_URE3: 1) reviewed the firewall rules and restricted the allowed network addresses from the large customer's site; 2) implemented an authentication scheme that enforces individual, two-factor authentication upon login; 3) implemented a corporate appropriate use banner that will be displayed upon login; 4) reviewed the ports and services on the firewall and disabled any ports and services that were not required for normal or emergency operations; 5) documented each port and service that is necessary to allow the large customer to view its required real-time distribution system information; 6) created individual user accounts for the large customer's personnel to be used in conjunction with two-factor authentication to allow authorized users cyber access through the firewall. In addition, SERC_URE3 employed a time-out feature that suspends user access after a fixed number of hours; and 7) worked with the large customer to complete personnel risk assessments for its employees with cyber access through the SERC_URE3 firewall. | 2012-09-21 | TBD | Admits | SERC reviewed SERC_URE3's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. Additionally, SERC_URE3 completed or will complete the following above and beyond actions, which SERC considered to be a mitigating factor in the penalty determination. SERC_URE3's compliance department coordinates and conducts internal audits of the CIP Standards at least annually. These audits include a review of updated Reliability Standard Audit Worksheets (RSAWs), evidence sampling and review, the presentation of evidence by subject matter experts (SMEs), interviews with SMEs, and audit recommendations. SERC_URE3 also utilizes a third-party vendor on an annual basis to conduct cyber penetration testing on CIP and non-CIP networks and assets, including internal and external firewalls and servers, outside of the required annual Cyber Vulnerability Assessment (CVA) process. The cyber penetration testing is used to identify areas for improvement and provide an additional analysis of SERC_URE3's security posture. SERC_URE3 also spent approximately $1 million to create a dedicated authentication and monitoring zone (AMZ) for CIP activities and upgrades to its physical access control system. In addition, SERC_URE3 has hired a trainer, which will allow more specific and detailed approach to CIP training. SERC_URE3 has spent approximately $2 million on a new energy management system (EMS) that includes cybersecurity improvements that will allow for the termination of three Technical Feasibility Exceptions associated with password management. SERC_URE3 also spent approximately $1 million on a Historian that will allow SERC_URE3 to remove read-only electronic access to the EMS for a large customer.
SERC Reliability Corporation (SERC) | Unidentified Registered Entity 3 (SERC_URE3) | NCRXXXXX | SERC2011006616 | Settlement Agreement | During a Compliance Audit, the SERC audit team reported that SERC_URE3 was in violation of CIP-005-1 R1.5. SERC_URE3 did not afford the protective measures specified in CIP-004 R3, CIP-005 R2 and R3, CIP-006 R3, and CIP-007 R1 to its Electronic Access Control and Monitoring (EACM) devices. SERC later determined that SERC_URE3 had also failed to address the testing of virus definition files on EACM devices (CIP-007 R4.2). SERC determined that 52.2% of EACM devices currently in place were in production prior to when the Standard became mandatory and enforceable for SERC_URE3. SERC_URE3 did not provide evidence to show that all personnel with physical access to the data center containing its EACM devices, which was not a defined Physical Security Perimeter (PSP) at the time, had valid personnel risk assessments (PRAs) completed successfully (CIP-004 R3); that there was access control protection from an untrusted network to EACMs (CIP-005 R2); that electronic security monitoring was being conducted (CIP-005 R3); and did not identify the PSP in which the EACM devices resided (CIP-006-2 R3, addressed in NERC Violation ID SERC2011006608). SERC_URE3 addressed the failure to provide its EACM devices with the protective measures specified in CIP-004 R3, CIP-005 R2 and R3, and CIP-006-2 R3 when it installed an authentication monitoring zone (AMZ) within a secure rack PSP that contained all of SERC_URE3's EACM devices. In addition, SERC_URE3 only tested significant changes to the EACM devices at a functional level to ensure that the changes did not stop the EACM devices from working. SERC_URE3 did not test a total of 21 significant changes to 13.0% of its EACM devices made over a five month period to ensure that those changes did not adversely affect the existing cyber security controls. SERC determined that SERC_URE3 was in violation of CIP-005-1 R1.5 because it failed to provide its EACM devices with the protective measures specified in CIP-007-1 R1. SERC_URE3's corporate patch management policy and malicious software tools procedure called for the application of virus definition files immediately upon receipt, but neither addressed the testing of those signatures. SERC_URE3 provided no evidence that it tested antivirus or malware prevention signatures. SERC determined that SERC_URE3 was in violation of CIP-006-1 R1.8 because it failed to provide its EACM devices with the protective measures specified in CIP-007-1 R4.2. | CIP-005-1 | R1; R1.5 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC determined that the violation posed a moderate risk because SERC_URE3's failure to protect its EACM devices adequately could lead to the disabling or degradation of electronic security protections, which could allow unauthorized electronic access to Critical Cyber Assets (CCAs) inside Electronic Security Perimeters (ESPs). However, of the employees with access to the EACM devices, 36.8% had valid PRAs and training, and the remaining employees had been subject to corporate pre-employment background checks. SERC_URE3 segmented the associated network and added additional controls to protect the EACM devices therein by isolating them physically and logically from the rest of the corporate network. SERC_URE3 implemented intrusion detection systems, antivirus and malware software, and network security logging and monitoring within the ESP, as technically feasible, to detect unusual activities. SERC_URE3 used a third-party security services provider as a secondary means of monitoring to ensure that all network activity was monitored for security risks and threats. This third-party security services provider had no access to SERC_URE3 ESPs or CCAs. | when the Standard became mandatory and enforceable on SERC_URE3 | Mitigation Plan completion | $45,000 (for SERC2011006608, SERC2011006610, SERC2011006612, SERC2011006613, SERC2011006614, SERC2011006615, SERC2011006616, SERC2011006617, SERC2012010737, SERC2013011815, and SERC2013011825) | Compliance Audit | To mitigate this violation, SERC_URE3: 1) implemented an authentication monitoring zone (AMZ) within a secure rack PSP; 2) evaluated, identified, and selected automated security control tools that can be employed to conduct security control testing to verify whether any modifications to the existing cyber security controls are made following significant changes to EACM devices; 3) implemented and developed testing procedures for testing against existing security controls on EACM devices after the selection of automated security control tools; and 4) updated its physical security plan to document the addition of the secure rack PSP. | 2012-06-28 | TBD | Admits | SERC reviewed SERC_URE3's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. Additionally, SERC_URE3 completed or will complete the following above and beyond actions, which SERC considered to be a mitigating factor in the penalty determination. SERC_URE3's compliance department coordinates and conducts internal audits of the CIP Standards at least annually. These audits include a review of updated Reliability Standard Audit Worksheets (RSAWs), evidence sampling and review, the presentation of evidence by subject matter experts (SMEs), interviews with SMEs, and audit recommendations. SERC_URE3 also utilizes a third-party vendor on an annual basis to conduct cyber penetration testing on CIP and non-CIP networks and assets, including internal and external firewalls and servers, outside of the required annual Cyber Vulnerability Assessment (CVA) process. The cyber penetration testing is used to identify areas for improvement and provide an additional analysis of SERC_URE3's security posture. SERC_URE3 also spent approximately $1 million to create a dedicated authentication and monitoring zone (AMZ) for CIP activities and upgrades to its physical access control system. In addition, SERC_URE3 has hired a trainer, which will allow more specific and detailed approach to CIP training. SERC_URE3 has spent approximately $2 million on a new energy management system (EMS) that includes cybersecurity improvements that will allow for the termination of three Technical Feasibility Exceptions associated with password management. SERC_URE3 also spent approximately $1 million on a Historian that will allow SERC_URE3 to remove read-only electronic access to the EMS for a large customer.
SERC Reliability Corporation (SERC) | Unidentified Registered Entity 3 (SERC_URE3) | NCRXXXXX | SERC2011006617 | Settlement Agreement | During a Compliance Audit, the SERC audit team reported that SERC_URE3 was in violation of CIP-005-1 R1.1. SERC_URE3 did not identify an externally connected communication end point terminating at a Critical Cyber Asset (CCA) as an access point to the Electronic Security Perimeter (ESP). After the Compliance Audit, SERC_URE3 conducted an internal review of all externally connected communication end points and discovered an identical device in addition to the device identified by the SERC audit. The identical device was located outside of the backup energy management system (EMS) ESP and terminated at a CCA inside of the ESP. SERC determined that the violation involved two intrusion detection system (IDS) devices, both of which were outside of an ESP. Each IDS device was connected to a switched port analyzer (SPAN) (mirroring) port on a corresponding switch inside an ESP. The IDS devices were also connected to a management interface that was located in the corporate network. The SPAN ports on both switches were configured to monitoring mode, which allowed information to travel out of the ESP to the IDS devices, but did not allow information to travel into the ESP via the IDS devices. SERC_URE3 did not identify these IDS devices as access points to the ESP, did not protect them as such, and therefore did not include these devices in the CIP-005 R4 Cyber Vulnerability Assessment of access points. SERC_URE3 moved the IDS management interface into a protected ESP. | CIP-005-1 | R1; R1.1 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The IDS devices used a SPAN port (mirrored) configured to prevent any ingress traffic to the EMS network. Ten individuals had physical or cyber access to the IDS management interface, which could configure the IDS devices. All 10 individuals had valid personnel risk assessments and were current in their annual cyber security training. The management console located outside of the ESP had physical and cyber security controls and protections in place. Security controls were in place on the corporate network including IDS, alerting, monitoring, video surveillance, third-party ESP monitoring, and strong access control restrictions on corporate firewalls. | when the Standard became mandatory and enforceable on SERC_URE3 | Mitigation Plan completion | $45,000 (for SERC2011006608, SERC2011006610, SERC2011006612, SERC2011006613, SERC2011006614, SERC2011006615, SERC2011006616, SERC2011006617, SERC2012010737, SERC2013011815, and SERC2013011825) | Compliance Audit | To mitigate this violation, SERC_URE3: 1) removed the IDS management interface from the corporate network and placed it behind the primary and backup EMS network firewalls; and 2) moved the management interfaces for the IDS that monitors the primary EMS network and the backup EMS network behind ESP firewalls. These IDS devices can now only be accessed from within an ESP though the specific ESP's firewall. | 2011-05-31 | TBD | Admits | SERC reviewed SERC_URE3's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. Additionally, SERC_URE3 completed or will complete the following above and beyond actions, which SERC considered to be a mitigating factor in the penalty determination. SERC_URE3's compliance department coordinates and conducts internal audits of the CIP Standards at least annually. These audits include a review of updated Reliability Standard Audit Worksheets (RSAWs), evidence sampling and review, the presentation of evidence by subject matter experts (SMEs), interviews with SMEs, and audit recommendations. SERC_URE3 also utilizes a third-party vendor on an annual basis to conduct cyber penetration testing on CIP and non-CIP networks and assets, including internal and external firewalls and servers, outside of the required annual Cyber Vulnerability Assessment (CVA) process. The cyber penetration testing is used to identify areas for improvement and provide an additional analysis of SERC_URE3's security posture. SERC_URE3 also spent approximately $1 million to create a dedicated authentication and monitoring zone (AMZ) for CIP activities and upgrades to its physical access control system. In addition, SERC_URE3 has hired a trainer, which will allow more specific and detailed approach to CIP training. SERC_URE3 has spent approximately $2 million on a new energy management system (EMS) that includes cybersecurity improvements that will allow for the termination of three Technical Feasibility Exceptions associated with password management. SERC_URE3 also spent approximately $1 million on a Historian that will allow SERC_URE3 to remove read-only electronic access to the EMS for a large customer.
SERC Reliability Corporation (SERC) | Unidentified Registered Entity 3 (SERC_URE3) | NCRXXXXX | SERC2012010737 | Settlement Agreement | SERC_URE3 submitted a Self-Certification to SERC stating that it was in violation of CIP-005-3a R1.5. SERC_URE3 did not afford one Electronic Access Control and Monitoring (EACM) device the protective measures specified in CIP-007 R8. Specifically, SERC_URE3 excluded one EACM device from its annual Cyber Vulnerability Assessment (CVA). SERC_URE3 had planned to replace one old Cyber Asset used as an EACM device before the end of the year 2011. SERC_URE3 excluded the old EACM device from its annual CVA and instead included the new EACM device, which was scheduled to replace the old EACM device, in the CVA. SERC reviewed the SERC_URE3 CVA and determined that the CVA covered the new EACM device that was replacing the old EACM device. SERC independently confirmed that the old EACM device was not included in the CVA. Both the old and new EACM devices were logging and monitoring during the period that they were running in parallel. SERC_URE3 put the new EACM device into service and approximately three weeks later SERC_URE3 decommissioned the old EACM device. SERC_URE3 installed the new EACM device in the summer, after which it was running in parallel with the old EACM device. SERC_URE3 completed its CVA in the winter. SERC_URE3 completed its CVA for the following year in the winter of that year and it assessed all applicable Cyber Assets during that CVA. | CIP-005-3a | R1; R1.5 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The old EACM device that was not assessed in the CVA was running in parallel with the new EACM device that was included in the CVA. SERC_URE3 removed the old EACM device from operation. The old and new EACM devices were installed in a demilitarized zone (DMZ), a secure network that contained all the EACM devices, and were running in parallel at the time of the CVA. The DMZ network was also segregated from SERC_URE3's corporate network. The secure DMZ network has electronic access controls, electronic logging and monitoring, intrusion detection systems, and anti-malware. | the first day after SERC_URE3 should have conducted the CVA including the old EACM device | when SERC_URE3 removed the old EACM device from the secure DMZ network | $45,000 (for SERC2011006608, SERC2011006610, SERC2011006612, SERC2011006613, SERC2011006614, SERC2011006615, SERC2011006616, SERC2011006617, SERC2012010737, SERC2013011815, and SERC2013011825) | Self-Certification | To mitigate this violation, SERC_URE3: 1) supplemented internal CVA procedures with more detailed specifics that require, at least annually, that the EACMs and PACs inventory and classification is confirmed; and 2) ensured that, in addition to Cyber Assets within Electronic Security Perimeters (ESPs) and access points to the ESPs, all EACM and PACS devices are included in the internal CVA procedures and are subject to and included in an annual CVA. | 2012-06-30 | TBD | Admits | SERC reviewed SERC_URE3's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. Additionally, SERC_URE3 completed or will complete the following above and beyond actions, which SERC considered to be a mitigating factor in the penalty determination. SERC_URE3's compliance department coordinates and conducts internal audits of the CIP Standards at least annually. These audits include a review of updated Reliability Standard Audit Worksheets (RSAWs), evidence sampling and review, the presentation of evidence by subject matter experts (SMEs), interviews with SMEs, and audit recommendations. SERC_URE3 also utilizes a third-party vendor on an annual basis to conduct cyber penetration testing on CIP and non-CIP networks and assets, including internal and external firewalls and servers, outside of the required annual Cyber Vulnerability Assessment (CVA) process. The cyber penetration testing is used to identify areas for improvement and provide an additional analysis of SERC_URE3's security posture. SERC_URE3 also spent approximately $1 million to create a dedicated authentication and monitoring zone (AMZ) for CIP activities and upgrades to its physical access control system. In addition, SERC_URE3 has hired a trainer, which will allow more specific and detailed approach to CIP training. SERC_URE3 has spent approximately $2 million on a new energy management system (EMS) that includes cybersecurity improvements that will allow for the termination of three Technical Feasibility Exceptions associated with password management. SERC_URE3 also spent approximately $1 million on a Historian that will allow SERC_URE3 to remove read-only electronic access to the EMS for a large customer.
SERC Reliability Corporation (SERC) | Unidentified Registered Entity 3 (SERC_URE3) | NCRXXXXX | SERC2013011815 | Settlement Agreement | SERC_URE3 submitted a Self-Certification to SERC stating that it was in violation of CIP-006-3c R2.2. SERC_URE3 failed to afford all of its Physical Access Control Systems (PACS) devices with the protective measures specified in CIP-007. SERC_URE3 maintains an authentication monitoring zone (AMZ) at its data center that consists of Electronic Access Control and Monitoring (EACM) devices and PACS devices all secured inside of a locked rack. SERC_URE3 identified the secure rack as a Physical Security Perimeter and protects it as such. The AMZ conducts all the logging and monitoring of all PACS devices and Cyber Assets and uses virtual machines to accomplish the various tasks associated with SERC_URE3's EACM and PACS devices. As part of an internal review, SERC_URE3 determined that it did not apply the CIP-007 requirements to host servers that ran several virtual machines, which in turn were running the virtual PACS database. SERC_URE3 failed to ensure protective measures specified in CIP-007, such as antivirus, monitoring and logging, Cyber Vulnerability Assessments, and testing, were applied to the host servers on which the virtual machines were running. The virtual machines that were running on the host servers were afforded the protective measures specified in CIP-007. | CIP-006-3c | R2; R2.2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The virtual machines housed on the host servers were afforded the protections of CIP-007. The host servers resided within a segmented AMZ network that has access control and monitoring and required two-factor authentication to access. Access to the host servers was limited to a total of 14 SERC_URE3 personnel, all of whom had active personnel risk assessments and current cyber security training. | when SERC_URE3 moved to virtual PACS devices running on the host servers | Mitigation Plan completion | $45,000 (for SERC2011006608, SERC2011006610, SERC2011006612, SERC2011006613, SERC2011006614, SERC2011006615, SERC2011006616, SERC2011006617, SERC2012010737, SERC2013011815, and SERC2013011825) | Self-Certification | To mitigate this violation, SERC_URE3: 1) implemented security control testing; 2) identified and evaluated ports and services associated with the PACS virtual machine host servers; 3) evaluated and assessed all security patches associated with the PACS virtual machine host servers; 4) added the PACS virtual machine host servers to a technical feasibility exception; 5) applied all password requirements to PACS virtual machine host servers; and 6) implemented local logging on the PACS virtual machine host servers. | 2013-02-28 | TBD | Admits | SERC reviewed SERC_URE3's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. Additionally, SERC_URE3 completed or will complete the following above and beyond actions, which SERC considered to be a mitigating factor in the penalty determination. SERC_URE3's compliance department coordinates and conducts internal audits of the CIP Standards at least annually. These audits include a review of updated Reliability Standard Audit Worksheets (RSAWs), evidence sampling and review, the presentation of evidence by subject matter experts (SMEs), interviews with SMEs, and audit recommendations. SERC_URE3 also utilizes a third-party vendor on an annual basis to conduct cyber penetration testing on CIP and non-CIP networks and assets, including internal and external firewalls and servers, outside of the required annual Cyber Vulnerability Assessment (CVA) process. The cyber penetration testing is used to identify areas for improvement and provide an additional analysis of SERC_URE3's security posture. SERC_URE3 also spent approximately $1 million to create a dedicated authentication and monitoring zone (AMZ) for CIP activities and upgrades to its physical access control system. In addition, SERC_URE3 has hired a trainer, which will allow more specific and detailed approach to CIP training. SERC_URE3 has spent approximately $2 million on a new energy management system (EMS) that includes cybersecurity improvements that will allow for the termination of three Technical Feasibility Exceptions associated with password management. SERC_URE3 also spent approximately $1 million on a Historian that will allow SERC_URE3 to remove read-only electronic access to the EMS for a large customer.
SERC Reliability Corporation (SERC) | Unidentified Registered Entity 3 (SERC_URE3) | NCRXXXXX | SERC2013011825 | Settlement Agreement | SERC_URE3 submitted a Self-Certification to SERC stating that it was in violation of CIP-005-3a R1.5. SERC_URE3 failed to afford its Electronic Access Control and Monitoring (EACM) devices with the protective measures specified in CIP-007. SERC_URE3 maintains an authentication monitoring zone (AMZ) at its data center that consists of EACM devices and Physical Access Control System (PACS) devices all secured inside of a locked rack. SERC_URE3 identified the secure rack as a Physical Security Perimeter and protects it as such. The AMZ conducts all the logging and monitoring of all EACM devices and Cyber Assets and uses virtual machines to accomplish the various tasks associated with SERC_URE3's EACM and PACS devices. As part of an internal review, SERC_URE3 determined that it did not apply the CIP-007 requirements to the host servers that ran virtual machines, which in turn were running virtual EACM devices. SERC_URE3 failed to ensure protective measures specified in CIP-007, such as antivirus, monitoring and logging, Cyber Vulnerability Assessments, and testing, were applied to the host servers on which the virtual machines were running. The virtual machines that were running on the host servers were afforded the protective measures specified in CIP-007. | CIP-005-3 | R1; R1.5 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The virtual machines housed on the host servers were afforded the protections of CIP-007. The host servers resided within a segmented AMZ network that has access control and monitoring and required two-factor authentication to access. Access to the host servers was limited to a total of 14 SERC_URE3 personnel, all of whom had active personnel risk assessments and current cyber security training. | when SERC_URE3 moved to virtual EACM devices running on the host server | Mitigation Plan completion | $45,000 (for SERC2011006608, SERC2011006610, SERC2011006612, SERC2011006613, SERC2011006614, SERC2011006615, SERC2011006616, SERC2011006617, SERC2012010737, SERC2013011815, and SERC2013011825) | Self-Certification | To mitigate this violation, SERC_URE3: 1) implemented security control testing; 2) identified and evaluated ports and services associated with the EACM virtual machine host servers; 3) evaluated and assessed all security patches associated with the EACM virtual machine host servers; 4) added the EACM virtual machine host servers to a technical feasibility exception; 5) applied all password requirements to EACM virtual machine host servers; and 6) implemented local logging on the EACM virtual machine host servers. | 2013-02-28 | TBD | Admits | SERC reviewed SERC_URE3's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. Additionally, SERC_URE3 completed or will complete the following above and beyond actions, which SERC considered to be a mitigating factor in the penalty determination. SERC_URE3's compliance department coordinates and conducts internal audits of the CIP Standards at least annually. These audits include a review of updated Reliability Standard Audit Worksheets (RSAWs), evidence sampling and review, the presentation of evidence by subject matter experts (SMEs), interviews with SMEs, and audit recommendations. SERC_URE3 also utilizes a third-party vendor on an annual basis to conduct cyber penetration testing on CIP and non-CIP networks and assets, including internal and external firewalls and servers, outside of the required annual Cyber Vulnerability Assessment (CVA) process. The cyber penetration testing is used to identify areas for improvement and provide an additional analysis of SERC_URE3's security posture. SERC_URE3 also spent approximately $1 million to create a dedicated authentication and monitoring zone (AMZ) for CIP activities and upgrades to its physical access control system. In addition, SERC_URE3 has hired a trainer, which will allow more specific and detailed approach to CIP training. SERC_URE3 has spent approximately $2 million on a new energy management system (EMS) that includes cybersecurity improvements that will allow for the termination of three Technical Feasibility Exceptions associated with password management. SERC_URE3 also spent approximately $1 million on a Historian that will allow SERC_URE3 to remove read-only electronic access to the EMS for a large customer.
Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPP RE_URE1) | NCRXXXXX | SPP2013012176 | Settlement Agreement | During a Compliance Audit of SPP RE_URE1, SPP RE discovered a possible violation of CIP-005-1 R2.4. SPP RE_URE1, did not implement strong procedural or technical controls to authenticate interactive access into the Electronic Security Perimeter (ESP) at two points that serve as access points to the ESP. Users initiating external access to the ESP must authenticate using a single-factor authentication method. Once authenticated, users have unrestricted access to all Cyber Assets within the ESP. Use of only a username and password does not constitute strong authentication. | CIP-005-1 | R2, R2.4 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. While only utilizing single-factor authentication, the affected devices reside on a network that is protected by a corporate firewall that limits access to the devices. Additionally, the domain and user accounts used to authenticate to the affected devices are different from the corporate domain user accounts initially authenticating access to SPP RE_URE1’s corporate network. Further, the violation did not include instances when SPP RE_URE1 staff connected to the ESP remotely from outside the office. In such instances, VPN was utilized, therefore providing strong authentication. | when the Standard became mandatory and enforceable on SPP RE_URE1 | Mitigation Plan completion | $15,000 (for SPP20130012176, SPP20130012178, SPP20130012181, and SPP20130012182) | Compliance Audit | To mitigate this violation, SPP RE_URE1: modified its method of authenticating users onto the ESP so that all users are strongly authenticated before gaining access to the ESP. | 6/14/13 | 7/11/2013 | Neither Admits nor Denies | SPP reviewed SPP RE_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPP RE_URE1) | NCRXXXXX | SPP2013012178 | Settlement Agreement | During a Compliance Audit of SPP RE_URE1 SPP RE discovered that SPP RE_URE1 was in violation of CIP-006-1 R1. SPP RE_URE1 did not create and maintain a written physical security plan addressing all the requirements of R1. SPP RE_URE’s physical security plan primarily restated the language of the requirements rather than outlining specifically how SPP RE_URE1 implemented the requirements. SPP RE_URE1 lacked documentation on the processes, tools, and procedures it used to monitor physical access to its Physical Security Perimeters (PSP) as required by R1.3 and the appropriate use of physical access controls as required by R1.4. Further, SPP RE_URE1 was in violation of R1.5 because its process for issuing temporary physical access badges did not require confirmation that the requester still had authorized, unescorted access to the PSP. SPP RE_URE1 was unable to produce documentation that it reviewed its physical access controls in 2011 as required by R1.9. Additionally, URE failed to identify four devices as Cyber Assets used in the access control and monitoring of the PSP, and as a result did not apply the protective measures enumerated in R1.8 to the devices. SPP RE also found that SPP RE_URE1 failed to include an application and its underlying Database used in provisioning access to the PSP in its 2011 annual Cyber Vulnerability Assessment (CVA) per R1.8. Additionally, in 2012, although SPP RE_URE1 included the application in the CVA, the CVA did not include the Database as required by R1.8. | CIP-006-1 | R1, R1.3; R1.4; R1.5; R1.8; R1.9 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. While SPP RE_URE1 did not fully document its physical security plan, SPP RE_URE1 had processes in place to monitor physical access to the PSP and for the physical protection of Critical Cyber Assets. Regarding R1.8, the relevant devices reside within an access-controlled facility. The devices require a username and password that is different from the domain user account and the employee population at the facility containing the devices is small and well-known, thereby reducing the risk that unauthorized access on the devices would go unnoticed. | when the Standard became mandatory and enforceable on SPP RE_URE1 | TBD | $15,000 (for SPP20130012176, SPP20130012178, SPP20130012181, and SPP20130012182) | Compliance Audit | To mitigate this violation, SPP RE_URE1: 1) revised its physical security plan so that it now documents how SPP RE_URE1 physically secures its Cyber Assets and meets the requirements of CIP-006; 2) split the PACS into two separate environments; one for the corporate non-CIP related doors and the other for CIP related doors managed by the contractor; 3) procured, received, and built-up necessary hardware and licensing for software for the new PACS environments; and 4) had its contractors coordinate and implement the split of the PACS environment with the SPP RE_URE1 IT staff. | 11/22/13 (Proposed Completion date) | TBD | Neither admits nor Denies | SPP reviewed SPP RE_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPP RE_URE1) | NCRXXXXX | SPP2013012181 | Settlement Agreement | During a Compliance Audit of SPP RE_URE1, SPP RE discovered that SPP RE_URE1 was in violation of CIP-007-3a R2. SPP RE_URE1 had partially documented the baseline of required ports and services. The port utilized by a device was not documented. Also, all ports and their associated services listening on an IP address were excluded from the list. As a result the documented baselines did not provide information regarding whether these ports and services were required for normal and emergency operations. SPP RE_URE1 documented only services with externally reachable listening ports and thus did not document all required services. | CIP-007-3a | R2, R2.1, R2.2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failure to fully document port and service configurations can present a risk of incorrect configurations and port vulnerability, port failure, or port inaccessibility in certain situations. However, SPP RE_URE1 documented a ports and services baseline and managed all listening ports and associated services that are externally reachable. The Cyber Assets within the Electronic Security Perimeter (ESP) are behind multiple firewalls, which limited the chance that they could be compromised because of a failure to document all ports and services. | when SPP RE_URE1 deployed the assets at issue in this violation | Mitigation Plan completion | $15,000 (for SPP20130012176, SPP20130012178, SPP20130012181, and SPP20130012182) | Compliance Audit | To mitigate this violation, SPP RE_URE1: 1) revised its ports and services management procedure to include steps to ensure that all ports and services are documented and that unnecessary ports and services are disabled as technically feasible; 2) performed an annual cyber vulnerability assessment on the Cyber Assets located within the ESPs; and. 3) added the missing ports and services to its baseline documentation. | 2013-06-14 | 2013-09-06 | Neither Admits nor Denies | SPP reviewed SPP RE_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPP RE_URE1) | NCRXXXXX | SPP2013012182 | Settlement Agreement | During a Compliance Audit of SPP RE_URE1, SPP RE discovered that SPP RE_URE1 was in violation of CIP-007-3a R3.2. Although SPP RE_URE1 had documented and implemented a security patch management program for tracking, evaluating, testing, and installing applicable cyber security patches, SPP RE_URE1 did not apply security patches to all its devices within a reasonable timeframe after the evaluation process determined that they were applicable. Overall, 23 patches were not installed to the devices until 11 to 24 months after being deemed applicable. Additionally, no compensating measures were documented for any of these patches until the patches were installed. | CIP-007-3a | R3, R3.2 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Failure to test and implement all available security patches or updates for Cyber Assets within the Electronic Security Perimeter (ESP) presented a risk that out-of-date security patches could allow unauthorized electronic access and potential compromise of Critical Cyber Assets that support BPS reliability. The risk posed by SPP RE_URE1’s noncompliance was lessened because the affected Cyber Assets and Critical Cyber Assets were within SPP RE_URE1’s ESP and were afforded protective measures, including firewall protection, malware prevention pursuant to CIP-007-3a R4, account management controls pursuant to CIP-007-3a R5, and security status monitoring pursuant to CIP-007-3a R6. | when SPP RE_URE1 deployed the assets at issue in this violation | Mitigation Plan completion | $15,000 (for SPP20130012176, SPP20130012178, SPP20130012181, and SPP20130012182) | Compliance Audit | To mitigate this violation, SPP RE_URE1 revised its patch management procedure to require that (1) applicable security patches be installed at least on a quarterly basis and (2) development, implementation, and documentation of compensating measures if an applicable security patch cannot be installed within the required timeframe. All patches identified in this violation have been installed. | 2013-06-14 | 2013-07-29 | Neither Admits nor Denies | SPP reviewed SPP RE_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPP RE_URE2) | NCRXXXXX | SPP201100642 | Settlement Agreement | SPP RE_URE2 submitted a Self-Report stating that it was in violation of CIP-007-1 R1. SPP RE_URE2 did not ensure that all significant changes to existing Cyber Assets within the Electronic Security Perimeter (ESP) did not adversely affect existing cyber security controls. Additionally, not all Cyber Assets within the ESP were tested in a manner that reflects the production environment (R1.2). SPP RE_URE2’s cyber security testing procedures did not apply to all Cyber Assets within the ESP, as required by R1 and R.1. The testing procedures required only functional testing after significant changes were implemented on the associated devices, instead of testing to ensure the significant changes did not adversely affect existing cyber security controls, as required by R1 and R1.1. Although not included in the testing procedures, after significant changes were implemented to SPP RE_URE2’s devices, SPP RE_URE2 did test in a manner that reflected the production environment to ensure that the significant changes did not adversely affect existing cyber security controls. However, testing in a production environment was not applied to all Cyber Assets located within the ESP per R1.2. | CIP-007-1 | R1; R1.1; R1.2 | Medium | Severe | This violation posed a moderate risk and not a serious or substantial risk to the reliability of the bulk power system (BPS). SPP RE determined that the violation posed a moderate risk because failing to test significant changes to existing Cyber Assets located within SPP RE_URE2’s ESP presented a risk that the significant changes would introduce exploitable vulnerabilities in SPP RE_URE2’s Cyber Assets without its knowledge. Such vulnerabilities, if exploited, could result in loss of sensitive data, corruption of data, manipulation of applications or data, or complete system failure, thereby placing the reliability of the BPS at risk. SPP RE_URE2 did, however, conduct compliant cybersecurity testing for most of its Cyber Assets located within the ESP, including the devices involved in the violation. Additionally, some changes related to security control systems were protected by antivirus software. Further, SPP RE_URE2’s Cyber Assets are protected by a firewall. SPP RE_URE2 also uses a network intrusion detection system to analyze network traffic at access points to the ESP for known and suspect malicious activity. Moreover, access to Critical Cyber Assets is limited to only those individuals with authorized physical and/or electronic access rights. SPP RE_URE2 attested that there were no cyber security incidents during the violation duration. | when the Standard became mandatory and enforceable on SPP RE URE2 | Mitigation Plan completion | $74,500 (for SPP201100642, SPP201100643, SPP2011008244, SPP2011008247, SPP2011008248, SPP2011008249, SPP2011008250, SPP2011008252, SPP2011008253, SPP2011008254, SPP2011008255, and SPP2011008291) | Self-Report | To mitigate this violation, SPP RE_URE2: 1) revised its cybersecurity testing procedures to include all the requirements of R1; 2) documented that testing is performed in a manner that reflects the full production environment to include all Cyber Assets; and 3) trained all affected personnel on the revised procedures. | 7/19/2013 | 7/31/2013 | Neither Admits nor Denies | SPP RE reviewed SPP RE_URE2's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination.
Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPP RE_URE2) | NCRXXXXX | SPP201100643 | Settlement Agreement | SPP RE_URE2 submitted a Self-Report stating that it was in violation of CIP-007-1 R3 because its security patch management program was not compliant with R3, R3.1, and R3.2. Specifically, SPP RE_URE2’s program did not apply to all Cyber Assets within the Electronic Security Perimeter (ESP). Additionally, SPP RE_URE2’s program relied on SPP RE_URE2’s vendor to track, evaluate, test, and assess cybersecurity software patches and, only some patches were included in the program. As a result, other security patches were not being tracked, evaluated, tested, or assessed. Further, because SPP RE_URE2’s program did not include procedures to address its reliance upon its vendor, SPP RE_URE2 was unable to verify that the vendor actually tracked, evaluated, tested, and assessed all applicable security patches. Moreover, SPP RE_URE2’s security patch management program did not include a process for documenting compensating measures for mitigating risk exposure or accepting risk when security patches or upgrades were not implemented. | CIP-007-1 | R3; R3.1; R3.2 | Lower | Severe | This violation posed a moderate risk and not a serious or substantial risk to the reliability of the bulk power system (BPS). SPP RE determined that the violation posed a moderate risk because failing to maintain a compliant security patch management program presented a risk of introducing exploitable vulnerabilities in SPP RE_URE2’s Cyber Assets without its knowledge. Such vulnerabilities, if exploited, could result in loss of sensitive data, corruption of data, manipulation of applications or data, or complete system failure, thereby placing the reliability of the BPS at risk. While SPP RE_URE2 was unable to verify that its vender tracked, evaluated, tested, and assessed patches for applicability within thirty (30) calendar days from the date of availability for all devices, SPP RE_URE2 did install available patches and conducted compliant CIP-007 R1 cybersecurity testing. For instance, after implementation of security patches, SPP RE_URE2 tested the devices in a manner that reflected the production environment to ensure that the security patches did not adversely affect existing cybersecurity controls. Additionally, SPP RE_URE2’s Cyber Assets are protected by a firewall. SPP RE_URE2 also uses a network intrusion detection system to analyze network traffic at access points to the ESP for known and suspect malicious activity. Moreover, access to Critical Cyber Assets is limited to only those individuals with authorized physical and/or electronic access rights. SPP RE_URE2 attested that there were no cybersecurity incidents during the violation duration. | when the Standard became mandatory and enforceable on SPP RE URE2 | Mitigation Plan completion | $74,500 (for SPP201100642, SPP201100643, SPP2011008244, SPP2011008247, SPP2011008248, SPP2011008249, SPP2011008250, SPP2011008252, SPP2011008253, SPP2011008254, SPP2011008255, and SPP2011008291) | Self-Report | To mitigate this violation, SPP RE_URE2: 1) purchased and installed a security patch management and network security scanner to assist in the: (i) identification of all security software that needs to be tracked, evaluated, tested, and assessed; (ii) assessments of applicable security patches and upgrades; (iii) implementation of automated downloading and installation of applicable patches; and 2) revised its security patch management program to: (i) include all Cyber Assets within the ESP; (ii) reflect the patch management and network security scanner and automated functions for security patches; (iii) include manual procedures for tracking, evaluating, testing, and assessing patches; (iv) ensure vendor confirmation and testing (where applicable) of all available security patches; and (v) include a process for documenting compensating measures when security patches are not implemented. | 2013-07-01 | 2013-08-22 | Neither Admits nor Denies | SPP RE reviewed SPP RE_URE2's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination.
Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPP RE_URE2) | NCRXXXXX | SPP2011008244 | Settlement Agreement | SPP RE_URE2 submitted a Self-Report stating that it was in violation of CIP-003-1 R5. SPP RE_URE2 did not annually (i) review access privileges to protected Critical Cyber Asset (CCA) information to confirm that the privileges are correct and that they correspond with current needs and current personnel roles and responsibilities as required by R5.2, and (ii) assess and document its processes for controlling access privileges to protected information as required by R5.3. During an ensuing Compliance Audit SPP RE determined that SPP RE_URE2 was also in violation of R5 because it did not document or implement a program for managing access to protected CCA information. | CIP-003-1 | R5; R5.2; R5.3 | Lower | Severe | This violation posed a moderate risk and not a serious or substantial risk to the reliability of the bulk power system. SPP RE determined that the violation posed a moderate risk because failure to document and annually assess its information protection program could have exposed sensitive information related to CCAs. Though SPP RE_URE2 did not document a program for managing access to CCA information, access to the information was controlled. For instance, the information was located and protected within SPP RE_URE2’s Physical Security Perimeter (PSP). As a result, physical and electronic access to the protected information was restricted to those individuals with authorized access. Additionally, SPP RE_URE2 maintained lists of personnel with access to CCA information and personnel with the authority to grant access to such information. | when the Standard became mandatory and enforceable on SPP RE URE2 | Mitigation Plan completion | $74,500 (for SPP201100642, SPP201100643, SPP2011008244, SPP2011008247, SPP2011008248, SPP2011008249, SPP2011008250, SPP2011008252, SPP2011008253, SPP2011008254, SPP2011008255, and SPP2011008291) | Self-Report; Compliance Audit | To mitigate this violation, SPP RE_URE2 developed, documented and implemented procedures for managing access to protected CCA information, which includes a provision for annual review of access privileges, as well as an annual review of the process itself. | 2013-07-01 | 2013-07-10 | Neither Admits nor Denies | SPP RE reviewed SPP RE_URE2's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination.
Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPP RE_URE2) | NCRXXXXX | SPP2011008247 | Settlement Agreement | SPP RE_URE2 submitted a Self-Report stating that it was in violation of CIP-005-1 R1 because it had not properly documented its Electronic Security Perimeter (ESP) in accordance with R1.1 and R1.4 through R1.6. SPP RE_URE2 did not: (i) identify and document two of its access points; (ii) identify and document all non-critical Cyber Assets within the ESP; and (iii) address protective measures for systems in its CIP-005-1 policy. During an ensuing Compliance Audit, SPP RE determined that SPP RE_URE2 also failed to maintain a complete list of devices, which led to two devices not being afforded the protective measures of R1.5. | CIP-005-1 | R1; R1.1; R1.4; R1.5; R1.6 | Medium | Severe | This violation posed a moderate risk and not a serious or substantial risk to the reliability of the bulk power system (BPS). SPP RE determined that the violation posed a moderate risk because the violation presented a risk of unauthorized access and exploitable vulnerabilities to Critical Cyber Assets (CCAs) and/or other Cyber Assets located within SPP RE_URE2’s ESP without its knowledge. Such access and vulnerabilities, if exploited, could result in loss of sensitive data, corruption of data, manipulation of applications or data, or complete system failure, thereby placing the reliability of the BPS at risk. Regarding R1.1, one of the access points was a serial connection and therefore less prone to compromise, and the other was configured to allow only outgoing communication. Regarding R1.5, while the two devices were within a secure area, they were not within a defined Physical Security Perimeter. The risk to the BPS was reduced because SPP RE_URE2 was utilizing an intrusion detection system to analyze network traffic for known and suspect malicious activity. Regarding R1.4 and R1.6, access to CCAs is limited to only those individuals with authorized physical and/or electronic access rights. SPP RE_URE2 attested that there were no cybersecurity incidents during the violation duration. | when the Standard became mandatory and enforceable on SPP RE URE2 | Mitigation Plan completion | $74,500 (for SPP201100642, SPP201100643, SPP2011008244, SPP2011008247, SPP2011008248, SPP2011008249, SPP2011008250, SPP2011008252, SPP2011008253, SPP2011008254, SPP2011008255, and SPP2011008291) | Self-Report; Compliance Audit | To mitigate this violation, SPP RE_URE2: 1) developed and implemented new procedures for identifying, documenting, and providing access control measures for all access points; 2) re-inventoried its networks and revised its ESP-related lists to ensure they are complete and in accordance with CIP-005; and 3) trained all affected personnel on the new procedures. | 2013-07-25 | 2013-08-28 | Neither Admits nor Denies | SPP RE reviewed SPP RE_URE2's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination.
Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPP RE_URE2) | NCRXXXXX | SPP2011008248 | Settlement Agreement | SPP RE_URE2 submitted a Self-Report stating that it was in violation of CIP-005-1 R2. SPP RE_URE2 did not document all of the organizational processes and technical and procedural mechanisms for control of electronic access at all electronic access points to the Electronic Security Perimeter (ESP) as required by R2.2, R2.5.3, and R2.6. Regarding R2.2, SPP RE_URE2 did not have an electronic access control process for documenting and approving open ports and services for each device used for operations and monitoring of Cyber Assets located within the ESP. Therefore, SPP RE_URE2 was unable to ensure that only ports and services required for operations and monitoring Cyber Assets within the ESP were enabled. Regarding R2.5.3, SPP RE_URE2 did not have a review process for authorization rights in accordance with CIP-004 R4. As a result, SPP RE_URE2 was unable to locate any documentation to demonstrate that any such reviews had been conducted. Regarding R2.6, SPP RE_URE2 failed to implement its documented appropriate use banner on all electronic access control systems. During an ensuing Compliance Audit, SPP RE determined that SPP RE_URE2 was also in violation of R2.5.2 because a form of authentication was not included in its documented authentication methods. SPP RE consolidated the Self-Report findings with the audit findings. | CIP-005-1 | R2; R2.2; R2.5.2; R2.5.3; R2.6 | Medium | Severe | This violation posed a moderate risk and not a serious or substantial risk to the reliability of the bulk power system. SPP RE determined that the violation posed a moderate risk because the failure to provide all the access control measures specified in CIP-005-1 R2 presented a risk of unauthorized electronic access to Cyber Assets located within SPP RE_URE2’s ESP. SPP RE_URE2 did, however, have compliant CIP-005-1 R2 electronic access control processes and mechanisms in place during the violation duration, including the implementation of an access control model that denies access by default; secured dial-up access to the ESP ; and implementation of strong technical controls at access points to the ESP to ensure authenticity of users who enable external interactive access into the ESP. Additionally, the Cyber Assets are protected by a firewall. SPP RE_URE2 also uses a network intrusion detection system to analyze network traffic at access points to the ESP for known and suspect malicious activity. Moreover, access to Cyber Assets located within the ESP is limited to only those individuals with authorized physical and/or electronic access rights. SPP RE_URE2 attested that there were no security alerts or cyber attacks during the violation duration. | when the Standard became mandatory and enforceable on SPP RE URE2 | Mitigation Plan completion | $74,500 (for SPP201100642, SPP201100643, SPP2011008244, SPP2011008247, SPP2011008248, SPP2011008249, SPP2011008250, SPP2011008252, SPP2011008253, SPP2011008254, SPP2011008255, and SPP2011008291) | Self-Report; Compliance Audit | To mitigate this violation, SPP RE_URE2: 1) revised its organizational processes and technical and procedural mechanisms documents to include all the requirements of R2, including: (i) an electronic access control process for documenting and approving open ports and services for each device used for operations and monitoring of Cyber Assets located within the ESP ; (ii) authentication method in its documented authentication methods ; and (iii) a review process for authorization rights in accordance with CIP-004 R4; 2) conducted a review of its open ports and services and compared them to its documented ports and services baseline to ensure that only ports and services required for operations and monitoring Cyber Assets within the ESP were enabled ; 3) where technically feasible, implemented its documented appropriate use banners on all electronic access control system devices; and 4) submitted a Technical Feasible Exception for electronic access control system devices that are incapable of displaying the appropriate use banner. | 2013-06-17 | 2013-08-28 | Neither Admits nor Denies | SPP RE reviewed SPP RE_URE2's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination.
Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPP RE_URE2) | NCRXXXXX | SPP2011008249 | Settlement Agreement | During a Compliance Audit SPP RE determined that SPP RE_URE2 was in violation of CIP-005-1 R3.2 because it did not monitor and log access at all access points to the Electronic Security Perimeter (ESP) 24 hours a day, seven days a week. Access logs were not captured during a three-week period when the logging server was out of service. Additionally, only approximately ten percent of the access logs were manually reviewed for attempts at or actual unauthorized access within 90 calendar days. | CIP-005-1 | R3.2 | Medium | Severe | This violation posed a moderate risk and not a serious or substantial risk to the reliability of the bulk power system (BPS). SPP RE determined that the violation posed a moderate risk because the failure to implement an electronic or manual process for monitoring and logging access at all access points to the ESP presented a risk of SPP RE_URE2 not being aware of unauthorized attempts and/or access into its ESP. Such vulnerabilities, if exploited, could have resulted in the loss of highly sensitive data, corruption of data, manipulation of applications or data, or complete system failure, thereby placing the reliability of the BPS at risk. SPP RE_URE2’s Critical Cyber Assets (CCAs) are protected by a firewall. SPP RE_URE2 also uses a network intrusion detection system to analyze network traffic at access points to the ESP for known and suspect malicious activity. Moreover, access to CCAs is limited to only those individuals with authorized physical and/or electronic access rights. SPP RE_URE2 attested that there were no cybersecurity incidents during the violation duration. | when the Standard became mandatory and enforceable on SPP RE URE2 | Mitigation Plan completion | $74,500 (for SPP201100642, SPP201100643, SPP2011008244, SPP2011008247, SPP2011008248, SPP2011008249, SPP2011008250, SPP2011008252, SPP2011008253, SPP2011008254, SPP2011008255, and SPP2011008291) | Compliance Audit | To mitigate this violation, SPP RE_URE2: 1) purchased, installed, and configured a new server with software that now monitors and logs access at all access points to the ESP 24 hours a day, seven days a week; the server will alert designated response personnel of unauthorized attempts and/or access to the ESP, prompting an immediate investigation; and 2) revised its monitoring procedure to reflect the new logging and monitoring server and updated its log retention requirement. | 2013-07-29 | 2013-08-22 | Neither Admits nor Denies | SPP RE reviewed SPP RE_URE2's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination.
Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPP RE_URE2) | NCRXXXXX | SPP2011008250 | Settlement Agreement | During a Compliance Audit SPP RE determined that SPP RE_URE2 was in violation of CIP-005-1 R4.3 because it did not perform the necessary steps to ensure that it discovered all access points to its Electronic Security Perimeter (ESP). SPP RE_URE2’s Cyber Vulnerability Assessment (CVA) included an electronic scanning of only the networks inside the ESP. While this identifies the Cyber Assets connected to a network segment within the ESP, this scan alone does not identify Cyber Assets also connected to one or more network segments outside of the ESP. There is no evidence that each Cyber Asset was interrogated, or that a manual tracing of cables or a scan of every network occurred, and there was not any other process documented to determine if there are any Cyber Assets with direct network connectivity both inside and outside of the ESP. | CIP-005-1 | R4.3 | Medium | Severe | This violation posed a moderate risk and not a serious or substantial risk to the reliability of the bulk power system (BPS). SPP RE determined that the violation posed a moderate risk because a violation of CIP-005-1 R4 presented a risk of unauthorized access and exploitable vulnerabilities to Critical Cyber Assets (CCAs) and/or other Cyber Assets located within SPP RE_URE2’s ESP without its knowledge. Such access and vulnerabilities, if exploited, could result in loss of sensitive data, corruption of data, manipulation of applications or data, or complete system failure, thereby placing the reliability of the BPS at risk. However, the risk to the BPS was reduced because SPP RE_URE2’s CCAs were behind a firewall, and SPP RE_URE2 was utilizing a network intrusion detection system to analyze network traffic for known and suspect malicious activity. SPP RE_URE2 attested that there were no security alerts or incidents during the violation duration. | when the Standard became mandatory and enforceable on SPP RE URE2 | Mitigation Plan completion | $74,500 (for SPP201100642, SPP201100643, SPP2011008244, SPP2011008247, SPP2011008248, SPP2011008249, SPP2011008250, SPP2011008252, SPP2011008253, SPP2011008254, SPP2011008255, and SPP2011008291) | Compliance Audit | To mitigate this violation, SPP RE_URE2: 1) amended its annual CVA procedures to include a manual inspection of cables to identify possible additional access points; 2) installed new software on each Cyber Asset within the ESP to continually monitor for configuration changes; and 3) conducted a new CVA pursuant to its new procedures to ensure all access points the ESP were identified. | 2013-05-31 | 2013-07-15 | Neither Admits nor Denies | SPP RE reviewed SPP RE_URE2's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination.
Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPP RE_URE2) | NCRXXXXX | SPP2011008252 | Settlement Agreement | During a Compliance Audit SPP RE determined that SPP RE_URE2 was in violation of CIP-006-1 R3 because it failed to monitor physical access to the Physical Security Perimeter (PSP) 24 hours a day, seven days a week. Access logs were reviewed for unauthorized access attempts once a day on business days, which did not meet the R3 requirement to review and respond to unauthorized access attempts immediately. Though SPP RE_URE2 maintained that it performed human observation of access points via video camera in accordance with R3.2, the use of system dispatchers to perform this function as a secondary responsibility in lieu of alarm systems was not effective 24 hours a day and thus did not satisfy the requirement for monitoring physical access at all access points to the PSP 24 hours a day, seven days a week. | CIP-006-1 | R3 | Medium | Severe | This violation posed a moderate risk and not a serious or substantial risk to the reliability of the bulk power system (BPS). SPP RE determined that the violation posed a moderate risk because failure to monitor physical access to the PSP presented a risk of SPP RE_URE2 not being aware of unauthorized attempts and/or access into its PSP. Such vulnerabilities, if exploited, could have resulted in the loss of highly sensitive data, corruption of data, manipulation of applications or data, or complete system failure, thereby placing the reliability of the BPS at risk. Once daily review of access logs did not allow the entity to be alerted to or respond to unauthorized access attempts immediately . Although SPP RE_URE2 observed access points as a secondary responsibility, this did not allow for 24 hours a day, seven days a week access monitoring. There were no instances of attempted or actual unauthorized access during the violation duration. | when the Standard became mandatory and enforceable on SPP RE URE2 | Mitigation Plan completion | $74,500 (for SPP201100642, SPP201100643, SPP2011008244, SPP2011008247, SPP2011008248, SPP2011008249, SPP2011008250, SPP2011008252, SPP2011008253, SPP2011008254, SPP2011008255, and SPP2011008291) | Compliance Audit | To mitigate this violation, SPP RE_URE2: 1) configured audible and visual alarms to alert personnel 24 hours a day, seven days a week, of unauthorized access attempts to the PSP; 2) revised its monitoring and logging physical access procedure to require personnel to investigate alarms immediately; and 3) trained all affected personnel on the new procedures. | 2013-04-06 | 2012-10-03 | Neither Admits nor Denies | SPP RE reviewed SPP RE_URE2's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination.
Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPP RE_URE2) | NCRXXXXX | SPP2011008253 | Settlement Agreement | During a Compliance Audit SPP RE determined that SPP RE_URE2 was in violation of CIP-006-1 R6 because it did not have a documented maintenance and testing program to ensure its physical security systems functioned properly. Because SPP RE_URE2 did not have a documented maintenance and testing plan as required by R6, it failed to adhere to the testing and maintenance and retention requirements as prescribed in R6.1 through R6.3. | CIP-006-1 | R6; R6.1; R6.2; R6.3 | Medium | Severe | This violation posed a moderate risk and not a serious or substantial risk to the reliability of the bulk power system bulk power system (BPS). SPP RE determined that the violation posed a moderate risk because even though the SPP RE_URE2 attested that it was conducting all maintenance and testing to ensure its physical security systems were functioning properly it could not support the attestation with documentation. Although SPP RE_URE2 did not have a documented program for testing and maintaining its physical security systems, SPP RE_URE2 attested that it did perform such testing and maintenance. It further attested that there were no incidents attributable to a failure of the physical security systems during the violation duration. | when the Standard became mandatory and enforceable on SPP RE URE2 | Mitigation Plan completion | $74,500 (for SPP201100642, SPP201100643, SPP2011008244, SPP2011008247, SPP2011008248, SPP2011008249, SPP2011008250, SPP2011008252, SPP2011008253, SPP2011008254, SPP2011008255, and SPP2011008291) | Compliance Audit | To mitigate this violation, SPP RE_URE2: 1) developed and implemented a physical security system maintenance and testing plan to meet the requirements of CIP-006; 2) trained all affected personnel on the new program; and 3) tested all physical security systems pursuant to the program. | 2013-05-07 | 2013-06-26 | Neither Admits nor Denies | SPP RE reviewed SPP RE_URE2's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination.
Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPP RE_URE2) | NCRXXXXX | SPP2011008254 | Settlement Agreement | SPP RE_URE2 submitted a Self-Report stating that it was in violation of CIP-007-1 R5.1 and R5.3. Regarding R5.1, SPP RE_URE2’s account management policy did not include procedural controls to ensure that individual and shared system accounts and authorized access permissions are consistent with the concept of “need to know” with respect to work functions performed. Additionally, while SPP RE_URE2 maintained a list of approved user accounts, the list did not include the user’s specific electronic access rights, and a central log of account requests and approvals was not maintained. Therefore, SPP RE_URE2 was neither able to ensure that user accounts were implemented as approved by designated personnel per R5.1.1 nor generate logs of sufficient detail to create historical audit trails of individual user account access activity for a minimum of 90 days per R5.1.2. Further, SPP RE_URE2 was unable to demonstrate that it had conducted annual reviews of its user accounts to verify access privileges were in accordance with Standard CIP-003 Requirement R5 and Standard CIP-004 Requirement R4 as required by R5.1.3. Regarding R5.2, SPP RE_URE2’s policy did not address the management of scope and acceptable use of administrator, shared, and default accounts. Also, SPP RE_URE2 did not maintain a list of individuals with access to shared accounts as required by R5.2.2. Moreover, SPP RE_URE2’s policy did not include management of shared user accounts per R5.2.3. During an ensuing Compliance Audit, SPP RE determined that SPP RE_URE2 was also in violation of R5.3 because one account password did not contain the required alpha, numeric, and special characters, and two account passwords remained unchanged for 1,024 days. | CIP-007-1 | R5; R5.1; R5.1.1; R5.1.2; R5.1.3; R5.2; R5.2.2; R5.2.3; R5.3.2; R5.3.3 | Medium | Severe | This violation posed a moderate risk and not a serious or substantial risk to the reliability of the bulk power system (BPS). SPP RE determined that the violation posed a moderate risk because failing to maintain a compliant Account Management program presented a risk of unauthorized access to and the introduction of exploitable vulnerabilities in SPP RE_URE2’s Cyber Assets without its knowledge. Such vulnerabilities, if exploited, could result in loss of sensitive data, corruption of data, manipulation of applications or data, or complete system failure, thereby placing the reliability of the BPS at risk. SPP RE_URE2 did maintain a list of approved users, all of whom had cleared background checks. Additionally, SPP RE_URE2’s Cyber Assets are protected by a firewall. SPP RE_URE2 also uses a network intrusion detection system to analyze network traffic at access points to the ESP for known and suspect malicious activity. Moreover, access to Critical Cyber Assets is limited to only those individuals with authorized physical and/or electronic access rights. SPP RE_URE2 attested that there were no cyber security incidents during the violation duration. | when the Standard became mandatory and enforceable on SPP RE URE2 | when the user access list was revised | $74,500 (for SPP201100642, SPP201100643, SPP2011008244, SPP2011008247, SPP2011008248, SPP2011008249, SPP2011008250, SPP2011008252, SPP2011008253, SPP2011008254, SPP2011008255, and SPP2011008291) | Self-Report; Compliance Audit | To mitigate this violation, SPP RE_URE2: 1) changed the passwords of the accounts to adhere to the requirements of R5.3 and R5.3.2; 2) revised its Account Management policy to: (i) include procedural controls to ensure that individual and shared system accounts and authorized access permissions are consistent with the concept of “need to know” with respect to work functions performed; (ii) provide adequate reviews of all user accounts to ensure they were implemented as approved by designated personnel; (iii) ensure that annual reviews of its user accounts are conducted to verify access privileges are in accordance with Standard CIP-003 Requirement R5 and Standard CIP-004 Requirement 4 as required by R5.1.3; and (iv) address management of shared, administrator, and default accounts; 3) added specific electronic rights to its list of approved user accounts; 4) added shared user accounts to its electronic access list; 5) generates and maintains logs with sufficient detail to create historical audit trails of all user accounts access activity for a minimum of 90 days; and 6) trained all affected personnel on newly implemented procedures. | 2013-11-13 | 2013-11-13 | Neither Admits nor Denies | SPP RE reviewed SPP RE_URE2's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination.
Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPP RE_URE2) | NCRXXXXX | SPP2011008255 | Settlement Agreement | During a Compliance Audit SPP RE determined that SPP RE_URE2 was in violation of CIP-007-1 R6. Specifically, SPP RE_URE2 did not document the organizational processes and technical and procedural mechanisms for monitoring security events on all Cyber Assets within the Electronic Security Perimeter (ESP) as required by requirement R6.1. In addition, while SPP RE_URE2 utilizes a manual log review process, most available logs were not being reviewed. Moreover, most logs were not retained for at least 90 days per R6.4. Therefore, because the majority of logs were neither retained nor reviewed, SPP RE_URE2 was unable to ensure that it was capable of detecting all Cyber Security Incidents and alerting such incidents to appropriate personnel as required by R6.2. | CIP-007-1 | R6 | Medium | Severe | This violation posed a moderate risk and not a serious or substantial risk to the reliability of the bulk power system (BPS). SPP RE determined that the violation posed a moderate risk because failing to properly monitor and alert for Cyber Security Incidents presented a risk of the introduction of exploitable vulnerabilities in SPP RE_URE2’s Cyber Assets without its knowledge. Such vulnerabilities, if exploited, could result in loss of sensitive data, corruption of data, manipulation of applications or data, or complete system failure, thereby placing the reliability of the BPS at risk. SPP RE_URE2’s Cyber Assets are protected by a firewall. SPP RE_URE2 also uses a network intrusion detection system to analyze network traffic at access points to the ESP for known and suspect malicious activity. Moreover, access to Cyber Assets within the ESP is limited to only those individuals with authorized physical and/or electronic access rights. SPP RE_URE2 attested that there were no cybersecurity incidents during the violation duration. | when the Standard became mandatory and enforceable on SPP RE URE2 | present | $74,500 (for SPP201100642, SPP201100643, SPP2011008244, SPP2011008247, SPP2011008248, SPP2011008249, SPP2011008250, SPP2011008252, SPP2011008253, SPP2011008254, SPP2011008255, and SPP2011008291) | Compliance Audit | To mitigate this violation, SPP RE_URE2 will: 1) purchase and install logging and alerting software that will retain logs for at least 90 calendar days; and 2) implement documented organization processes and technical and procedural mechanisms for monitoring for security events on all Cyber Assets within the ESP. | 2/13/2014 (the accepted proposed completion date) | TBD | Neither Admits nor Denies | SPP RE reviewed SPP RE_URE2's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination.
Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPP RE_URE2) | NCRXXXXX | SPP2011008291 | Settlement Agreement | SPP RE_URE2 submitted a Self-Report stating that it was in violation of CIP-006-1 R1 because of deficiencies in its physical security plan. The plan did not include procedures for the appropriate use of physical access control as required by R1.4 and for updating the plan within 90 calendar days of a physical security system redesign or reconfiguration as required by R1.7. During an ensuing Compliance Audit SPP RE determined that SPP RE_URE2 failed to have its physical security plan approved by its senior manager or delegate(s) and protect Cyber Assets used in the access control and monitoring of the Physical Security Perimeter (PSP) with the protective measures specified in R1.8. | CIP-006-1 R1 | R1; R1.4; R1.8 | Medium | Severe | This violation posed a minimal risk and not a serious or substantial risk to the reliability of the bulk power system. . SPP RE_URE2 had a documented physical security plan, albeit deficient. Although senior management failed to formally approve the plan, the senior manager regularly attends the CIP compliance team meetings and was aware of the plan. The failure to provide the devices the required protective measures pursuant to CIP-006-1 R1.8 may have led to unauthorized physical access to Critical Cyber Assets, but no such unauthorized access occurred during the violation period. The PACS devices were located within the designated PSP. | when the Standard became mandatory and enforceable on SPP RE URE2 | Mitigation Plan completion | $74,500 (for SPP201100642, SPP201100643, SPP2011008244, SPP2011008247, SPP2011008248, SPP2011008249, SPP2011008250, SPP2011008252, SPP2011008253, SPP2011008254, SPP2011008255, and SPP2011008291) | Self-Report; Compliance Audit | To mitigate this violation, SPP RE_URE2: 1) revised its physical security plan to include: (i) annual review and approval process controls; (ii) the appropriate use of physical access controls; (iii) a requirement to update the plan within 30 calendar days of the completion of any physical security system redesign or reconfiguration; (iv) devices involved in the violation and how they are protected; and (v) senior management approval. | 2013-08-30 | 2013-08-30 | Neither Admits nor Denies | SPP RE reviewed SPP RE_URE2's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination.
Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 3 (SPP RE_URE3) | NCR00658 | SPP2012010286 | Settlement Agreement | During a Compliance Audit, SPP RE determined that SPP RE_URE3 was in violation of CIP-006-1 R1.8. SPP RE_URE3 failed to afford all the protective measures specified in CIP-005-1 R2, R2.2, R3.2, and CIP-007-1 R4.2 for some Cyber Assets used in the access control and monitoring of SPP RE_URE3 Physical Security Perimeter (PSP). SPP RE_URE3 failed to fully implement CIP-005-2 R2. SPP RE_URE3 did not include two devices located on its network, which are used for controlling physical access to identified PSPs, in its documented processes and mechanisms. SPP RE_URE3 failed to afford the protective measures specified in CIP-005-2 R2.2. SPP RE_URE3's ports and services baseline did not identify ephemeral port ranges required for operations and monitoring of Cyber Assets within an Electronic Security Perimeter (ESP). Without such port ranges, SPP RE_URE3 was unable to identify all ports that could be associated with normal and emergency operations and monitoring of Cyber Assets within the ESP. As a result, SPP RE_URE3 was unable to ensure that each enabled port associated with a particular enabled service for normal and emergency operations and monitoring of Cyber Assets within the ESP was the required port to run the associated service. SPP RE_URE3 failed to fully implement CIP-005-1 R3. SPP RE_URE3 did not include two devices located on the corporate network in its documented processes. SPP RE_URE3 failed to fully implement CIP-007-1 R4.2. SPP RE_URE3 was unable to provide evidence of testing of antivirus signature files before installing them onto the devices. | CIP-006-1 | R1; R1.8 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to provide the protective measures specified in CIP-006-1 R1.8 presented a risk of the introduction of exploitable vulnerabilities in SPP RE_URE3’s system without its knowledge. Such vulnerabilities, if exploited, could have resulted in the loss of sensitive data, corruption of data, manipulation of applications or data, or complete system failure, thereby placing the reliability of the BPS at risk. The devices, however, resided within a PSP and thus were afforded CIP-006 physical security protective measures. The security measures included physical access controls, monitoring and logging of physical access, and maintenance and testing programs to ensure physical security systems function properly. In addition, physical and electronic access to the devices and Cyber Assets residing within the PSP was limited to only those individuals with authorized physical and/or electronic access rights. SPP RE_URE3 attested that there were no security alerts or cyber attacks during the violation duration. | when the Standard became mandatory and enforceable on SPP RE_URE3 | Mitigation Plan completion | 5000 | Compliance Audit | To mitigate this violation, SPP RE_URE3: 1) developed and implemented a ports and services program, which provided guidance to affected staff in managing and complying with the ports and services requirements in the NERC CIP Standard CIP-005 R2.2 and CIP-007 R2; R2, R2.2, R3.2, and CIP-007-1 R4.2; 2) performed a port scan on the devices to identify all ports that could enable all associated services for operations and monitoring of Cyber Assets and within SPP RE_URE3's ESP, and updated its ports and services baseline document; 3) relocated the devices behind two new firewalls; and 4) revised its document to detail the process of testing antivirus signatures. | 2012-09-13 | 2012-11-13 | Neither Admits nor Denies | SPP RE reviewed SPP RE_URE3 internal compliance program (ICP) and considered it, as well as its cooperation throughout the settlement process, to be a mitigating factors in the penalty determination.
Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE) | NCRXXXXX | WECC2012009123 | Settlement Agreement | WECC_URE1 submitted a Self-Certification to WECC stating that it was in violation of CIP-007-3 R7. Upon learning the device was damaged, WECC_URE1 returned the device to the manufacturer for replacement under warranty. However, WECC_URE1 did not document the return. Because the device involved in this violation was used in WECC_URE1's access control and monitoring of one of its Electronic Security Perimeters (ESPs), WECC determined that WECC_URE1 was in violation of CIP-005-3 R1, not CIP-007-3 R7, and referred the matter to WECC Enforcement. WECC Enforcement determined that WECC_URE1 is in violation of CIP-005-3 R1 for failing to afford its device used in the access control and monitoring of one of its ESPs the protections in CIP-007-3 R7.3. | CIP-005-3a | R1 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The device in scope is devoid of any markings that would alert a hypothetical bad actor that the device contains information that was used as part of a system belonging to the entity. In addition, the entity stated the information stored on the device alone may not be sufficient for causing damage to ESP since this information is specific to entity's internal network. As compensating measures, the device was returned safely to the manufacturer which has in place rigorous policies for handling such devices, including deleting files from the device's memory, if any. | when WECC_URE1 disposed of the device | Mitigation Plan completion | $7,000 (for WECC2012009123 and WECC2012009124) | Self-Certification | To mitigate this violation, WECC_URE1 counseled its management on the importance of following WECC_URE1's disposing and redeploying of Cyber Asset procedure, as well as to evaluate the methods and processes for interacting with equipment vendors to determine the most appropriate approaches for disposing and redeploying Cyber Assets under warranty. | 2012-05-31 | 2012-07-27 | Admits | WECC reviewed WECC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE) | NCRXXXXX | WECC2012009124 | Settlement Agreement | WECC_URE2 submitted a Self-Report to WECC stating that it was in violation of CIP-004-3 R4. WECC dismissed WECC_URE2's potential violation of CIP-004-3 R4, and determined that the scope of the violation was related to CIP-006-3c R1.4, and all activity would be addressed under NERC tracking number WECC2012009124. Because the employee was granted access to WECC_URE2's CCAs erroneously, WECC concluded that these facts and circumstances constitute a violation of CIP-006-3c R1.4, not CIP-004-3 R4. | CIP-006-3c | R1 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. As compensating measures, WECC_URE2 stated that the employee had a PRA and cybersecurity training prior to getting the access, and had been cleared to access a different PSP. In addition, the CCA in scope is located in a locked cabinet that had monitoring and logging measures to detect any unauthorized activity. | when the employee was given access to WECC_URE2's CCAs | when the employee's access was revoked | $7,000 (for WECC2012009123 and WECC2012009124) | Self-Report | To mitigate this violation, WECC_URE2: 1) revoked the employee's physical access to WECC_URE2's PSPs; 2) developed an improved process workflow, with additional steps, for system administrators granting physical access to NERC restricted sites; 3) communicated the improved process workflow to all system administrators to ensure the additional steps are followed; and 4) met with the system administrators to describe and reinforce the revised access provisioning process. | 2012-02-15 | 2012-06-07 | Admits | WECC reviewed WECC_URE2's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. WECC considered compliance history as an aggravating factor in penalty determination.
Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2013012043 | Notice of Confirmed Violation | WECC_URE3 submitted a Self-Certification stating that it was in violation of CIP-007-3a R6. Specifically, WECC_URE3 reported that it failed to implement automated tools or organizational process controls to monitor system events that are related to cybersecurity for Cyber Assets within Electronic Security Perimeters (ESPs). WECC determined that WECC_URE3 was in violation of CIP-007-3a R6 for failing to activate and implement security status monitoring (logging) on the devices after the upgrade. | CIP-007-3a | R6 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The violation posed a moderate risk because, for over one year, WECC_URE3's failure to ensure that automated tools or organizational process controls were in place to monitor system events related to cybersecurity exposed Cyber Assets to possible unauthorized access attempts. The risk to the reliability of the BPS was mitigated by the following mitigating factors. All the affected devices were located within an identified ESP and Physical Security Perimeter where access is restricted to only authorized individuals. | when WECC_URE3 performed the upgrade | Mitigation Plan completion | 35000 | Self-Certification | To mitigate this violation, WECC_URE3: 1) revised the security test plan form; 2) revised the IT NERC CIP implementation checklist; and 3) revised its process for logging test evidence. | 2013-09-11 | TBD | Does Not Contest | WECC reviewed WECC_URE3's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. WECC determined that WECC_URE3’s compliance history to be an aggravating factor in the penalty determination