## PUBLIC_CIP Violations
Region | Registered Entity | NCR_ID | NERC Violation ID # | Notice of Confirmed Violation or Settlement Agreement | Description of the Violation | Reliability Standard | Req. | Violation Risk Factor | Violation Severity Level | Risk Assessment | Violation Start Date | Violation End Date | Total Penalty or Sanction ($) | Method of Discovery | Description of Mitigation Activity | Mitigation Completion Date | Date Regional Entity Verified Completion of Mitigation | "Admits," "Agrees/Stipulates," "Neither Admits nor Denies," or "Does Not Contest" | Other Factors Affecting the Penalty Determination, including Compliance History, Internal Compliance Program and Compliance Culture
ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2014013427 | Settlement Agreement | RFC_URE1 submitted a Self-Report to ReliabilityFirst stating that it was in violation of CIP-002-1 R3. RFC_URE1 reported that during an internal compliance review, it discovered at a RFC_URE1 Critical Asset substation two Ethernet cables connecting two managed Ethernet switches to a Ethernet switch. The switch was connected via fiber to an internet protocol (IP) ring that connected several non-critical substations. Other Cyber Assets were connected to the managed Ethernet switches. None of the Cyber Assets at the Critical Asset substation were classified as Critical Cyber Assets (CCAs) despite the use of routable protocol by the two managed Ethernet switches. In addition, during the Compliance Audit, ReliabilityFirst discovered two storage devices that were not declared as CCAs. RFC_URE1 later reported in its Mitigation Plan for CIP-002-1 R3 that it had identified a physical Ethernet cable connection from these two external storage devices to servers that run a database. The assets were initially classified as protected Cyber Assets, but not NERC CCAs. After confirming the function of the storage devices, RFC_URE1 assessed them using its CCA identification process and classified them as CCAs. RFC_URE1 determined that, in part, the root cause of the violation is that its annual assessments did not include a separate step to identify the use of routable protocol. RFC_URE1 made a strategic decision prior to CIP mandatory enforcement to remove routable protocol from Critical Asset substations. Based on this earlier decision, RFC_URE1’s annual assessments did not include a separate step to identify routable protocol as it assumed that no routable protocol was being used in Critical Asset facilities. As a result, isolated devices, which used routable protocol, were not identified as CCAs. Further, RFC_URE1 also determined that a procedure utilized in the CCA identification process included a form that was pre-populated and relied on historical answers, which increased the possibility of misclassifying an asset. Finally, RFC_URE1 determined that the evaluation of Cyber Assets needed someone that has IT experience and would have an adequate understanding of how the Cyber Assets are connected to the network equipment and relevant configurations and protocols being used. | CIP-002-1 | R3 | High | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Although RFC_URE1 disconnected the relevant Ethernet cables and the external storage devices are located within a Physical Security Perimeter, assets not protected by the full suite of CIP-007 security controls may have been vulnerable to misuse or compromise. The long duration of the violation – over four years – also increased the risk to the BPS. In addition, although RFC_URE1 conducted annual assessments those reviews assumed that routable protocol had been removed from all substations and therefore the RFC_URE1 reviewer, who also did not have information technology expertise, did not recognize assets that were subject to CCA classification. As a result, the internal controls in place prior to mitigation of this violation were not fully effective. The risk to the BPS was mitigated for the following reasons. The external network connection is a RFC_URE1 private network behind a firewall, which is not part of the Electronic Security Perimeter (ESP), and is not exposed to the internet. | when the Standard became mandatory and enforceable on RFC_URE1 | Mitigation Plan completion | $0 (for RFC2014013427 and RFC2014013705) | Self-Report | To mitigate this violation, RFC_URE1: 1) unplugged the network connection at the Critical Asset substation; 2) investigated and assessed all Cyber Assets in all Critical Asset substations; 3) developed, updated and supplemented documentation to any existing processes and procedures to address non-BPS Cyber Assets at Critical Asset substations, including new asset identification templates, configuration guides, ESP diagrams, and recovery plans; 4) conducted an investigation to determine the root cause, extent of condition, and corrective actions; 5) submitted technical feasibility exceptions for controls that were not technically feasible to apply; 6) included personnel with the technical expertise needed to complete an effective annual assessment; and 7) applied protective measures of the CIP Standards to the newly-identified CCAs. | 9/30/2014 | TBD | Neither Admits nor Denies | RFC reviewed RFC_URE1's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination. Although the risk determinations for the violations were not minimal, RFC_URE1 has been cooperative through the enforcement process and has voluntarily and timely mitigated the violations. ReliabilityFirst determined that a monetary penalty is not warranted for the violations. This is in part based on RFC_URE1’s clear commitment to strengthening its internal controls and preventing recurrence of noncompliance. ReliabilityFirst is committed to using the enforcement process to incent strong compliance programs and encourage the development of robust internal controls. RFC_URE1’s response to the audit findings is behavior that ReliabilityFirst seeks to encourage, as these are positive, proactive steps to prevent recurrence of noncompliance. In light of this response, ReliabilityFirst determined that a monetary penalty was not necessary or appropriate, as it would neither incent desired behavior nor improve BPS reliability. ReliabilityFirst also considered that the violations were not indicative of systemic issues in RFC_URE1’s compliance program, or resulting from a significant lack of internal controls. Although both violations are classified as “moderate” risk issues, these assessments were based solely on the risk inherent in violations of those particular Standards, and were not related to the implementation of RFC_URE1’s compliance program. Furthermore, the root causes of the violations are not likely to be repeated; the CIP-002-1 R3 violation was an incomplete effort prior to the mandatory compliance date that led to an assumption of the status of the affected devices, and the CIP-009-1 R4 issue involved RFC_URE1’s faulty interpretation of the Standard made in good faith and quickly corrected upon notice of ReliabilityFirst’s interpretation. RFC_URE1 did not receive mitigating credit for self-reporting because the Self-Report was submitted after receiving notice of an upcoming Compliance Audit.
ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2014013705 | Settlement Agreement | During the Compliance Audit, ReliabilityFirst determined that RFC_URE1 was in violation of CIP-009-1 R4. RFC_URE1 failed to provide evidence of backup of information required to successfully restore Critical Cyber Assets for network-attached storage (NAS) servers. Instead, RFC_URE1 stated that it uses mirroring, which is real-time replication of data on a backup system, as a backup method. However, mirroring is insufficient for CIP-009-1 R4 compliance because it does not provide a reliable method of recovery under all circumstances. For example, accidentally modified or deleted files, corrupted files, and malicious code would be replicated to the backup source, leaving no recovery files in such events. RFC_URE1 determined that, in part, the root cause of the violation is that RFC_URE1 failed to recognize that its chosen method for backup was insufficient for recovery. | CIP-009-1 | R4 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). RFC_URE1 allowed a risk to the BPS to exist over a period of more than four years by not developing a functional backup and recovery plan for the NAS servers. This lack of recovery planning meant that these servers were vulnerable to a wide array of potential harm including accidental and intentional data manipulation and corruption. The risk to the BPS was mitigated for the following reasons. The NAS servers were classified as CCAs and are afforded the protections required in CIP-002-3 through CIP-009-3 standards. Additionally, the NAS servers reside within Physical Security Perimeters and a segregated Electronic Security Perimeter (ESP). Finally, elevated authorized electronic access is required to access the NAS servers. | when the Standard became mandatory and enforceable on RFC_URE1 | Mitigation Plan completion | $0 (for RFC2014013705 and RFC2014013427). | Compliance Audit | To mitigate this violation, RFC_URE1: 1) established a procedure for backing up and recovering the NAS servers; 2) performed the backup of the NAS server system configuration; 3) updated the training and reference material document regarding the backup and restoration procedures for CCAs within the Electronic Security Perimeter to ensure it included instructions for backing up and restoring the NAS server configuration; and 4) conducted training for relevant personnel, including how to achieve compliance with the standard and provide example of good compliance evidence. | 2014-11-24 | TBD | Neither Admits nor Denies | RFC reviewed RFC_URE1's internal compliance program (ICP) and considered it to be a neutral factor in the penalty determination. Although the risk determinations for the violations were not minimal, RFC_URE1 has been cooperative through the enforcement process and has voluntarily and timely mitigated the violations. ReliabilityFirst determined that a monetary penalty is not warranted for the violations. This is in part based on RFC_URE1’s clear commitment to strengthening its internal controls and preventing recurrence of noncompliance. ReliabilityFirst is committed to using the enforcement process to incent strong compliance programs and encourage the development of robust internal controls. RFC_URE1’s response to the audit findings is behavior that ReliabilityFirst seeks to encourage, as these are positive, proactive steps to prevent recurrence of noncompliance. In light of this response, ReliabilityFirst determined that a monetary penalty was not necessary or appropriate, as it would neither incent desired behavior nor improve BPS reliability. ReliabilityFirst also considered that the violations were not indicative of systemic issues in RFC_URE1’s compliance program, or resulting from a significant lack of internal controls. Although both violations are classified as “moderate” risk issues, these assessments were based solely on the risk inherent in violations of those particular Standards, and were not related to the implementation of RFC_URE1’s compliance program. Furthermore, the root causes of the violations are not likely to be repeated; the CIP-002-1 R3 violation was an incomplete effort prior to the mandatory compliance date that led to an assumption of the status of the affected devices, and the CIP-009-1 R4 issue involved RFC_URE1’s faulty interpretation of the Standard made in good faith and quickly corrected upon notice of ReliabilityFirst’s interpretation.
Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity (SPP_URE1) | NCRXXXX | SPP2012010644 | Settlement Agreement | SPP_URE1 submitted a Self-Report stating that it was in violation of CIP-007-1 R3. Specifically, SPP_URE1 had not included a Cyber Asset in its patch management program and was unable to provide evidence that patches were assessed for another Cyber Asset, per R3.1. Accordingly, no compensating measures were applied to these Cyber Assets to mitigate risk per R3.2. With regard to SPP_URE1's failure to include the server in its patch management program, the root cause was that during its installation, SPP_URE1's configuration management policy for ensuring that new devices are fully documented with procedures covering applicable security controls, including patching, was not followed. Due to employee oversight, patches were not assessed for the device. | CIP-007-1 | R3; R3.1; R3.2 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The lack of patch assessment and installation, and the failure to apply compensating measures, where appropriate, creates the risk that SPP_URE1's Cyber Assets would be susceptible to vulnerabilities that would have otherwise been prevented by patching. The risk posed by this violation was mitigated by SPP_URE1's policy to deny access to devices that attempt to communicate with its Cyber Assets from outside its Electronic Security Perimeter (ESP), and no Cyber Assets or Critical Cyber Assets within SPP_URE1's ESPs have internet access. Therefore, the probability of unauthorized access to SPP_URE1's Cyber Assets within its ESPs is remote. SPP_URE1 has installed an antivirus application on its Cyber Assets and its ESP networks are continuously monitored by a network intrusion detection system. These activities increase the likelihood that SPP_URE1 would detect unauthorized access of its ESPs. | when the Standard became mandatory and enforceable | Mitigation Plan completion | None | Self-Report | To mitigate this violation, SPP_URE1: 1) moved the functions performed by both Cyber Assets to an existing Cyber Asset that is patched according to SPP_URE1's security patch management program; and 2) decommissioned both Cyber Assets. | 2013-01-02 | 2013-06-12 | Neither Admits nor Denies | SPP RE reviewed SPP_URE1's internal compliance program (ICP) and considered it to be a mitigating factor. SPP RE considered SPP_URE1's compliance history and determined there were no relevant instances of noncompliance.
Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity (SPP_URE1) | NCRXXXX | SPP2012010645 | Settlement Agreement | SPP_URE1 submitted a Self-Report stating that it was in violation of CIP-006-1 R1.8. Two of SPP_URE1's Physical Access Control System (PACS) Cyber Assets used for physical security monitoring were not afforded the protective measures required by CIP-003 R1, R6; CIP-005 R2, R3; CIP-007 R2, R3, R4, R5.1.2, R5.2.3, R5.3.2, R5.3.3, R6; and CIP-009 R1. SPP_URE1 failed to include two PACS Cyber Assets in the Cyber Asset security policy, it failed to apply a change control process to the PACS Cyber Assets, it failed to capture system event logs for the PACS Cyber Assets and review the logs every 90 days. SPP_URE also failed to submit Technical Feasibility Exceptions (TFEs) for the PACS Cyber Asset that could not meet patching requirements, and for the PACS Cyber Assets that could not meet password complexity nor password change requirements. The root cause of the violation was that the SPP_URE1 employees supporting these assets were not originally within the IT Department and were not aware of the specific NERC requirements. | CIP-006-1 | R1.8 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The failure to afford all the protective measures of CIP-006-1 R1.8 to the two PACS Cyber Assets presented the risk that if the assets were compromised, SPP_URE1's incident response may not have been alerted of an unauthorized attempt to access SPP_URE1's Physical Security Perimeter (PSP). During the period of noncompliance, SPP_URE1 had several security controls in place which mitigated the risk posed by this violation. Both PACS Cyber Assets reside within a PSP and an Electronic Security Perimeter (ESP). All personnel who interacted with the PACS Cyber Assets were authorized for unescorted physical and/or electronic access to Critical Cyber Assets. SPP_URE1 utilizes a Network Intrusion Detection System (NIDS) to monitor and alarm for unauthorized access, and to detect malware. SPP_URE1's NIDS is monitored during office hours by qualified personnel and is configured to send alerts to authorized personnel on a 24 x 7 basis. | when the Standard became mandatory and enforceable | Mitigation Plan completion | None | Self-Report | To mitigate this violation, SPP_URE1: 1) performed a compliance status assessment for the two PACS Cyber Assets to determine the required mitigating activities in order to meet compliance with CIP-006-3 R2.2/CIP-006-1 R1; 2) added the Cyber Assets to SPP_URE1's Cyber Security Policy; 3) included the Cyber Assets in SPP_URE1's Change Control Process 4) included the Cyber Assets in SPP_URE1's mitigation for dial-up devices; 5) began capturing the Cyber Assets logs on SPP_URE1's logging server, and included the logs in its 90-day review process; 6) established, documented, and implemented a process to ensure that only ports and services required for normal and emergency operations were enabled; 7) applied SPP_URE1's security patch management process to one of the Cyber Assets, and submitted a Technical Feasibility Exception (TFE) for the other Cyber Asset that cannot meet patching requirements ; 8) updated the anti-virus and malware signature files on the Cyber Assets; 9) for one of the Cyber Assets, established a log to track shared account use; 10) set up account logging for the shared account; 11) submitted TFEs for the Cyber Asset that cannot meet password complexity nor password-change requirements; 12) performed log reviews for the two PACS Cyber Assets; and 13) included the two PACS Cyber Assets in SPP_URE1's recovery plan. | 2013-10-30 | 2014-04-29 | Neither Admits nor Denies | SPP RE reviewed SPP_URE1's internal compliance program (ICP) and considered it to be a mitigating factor. SPP RE considered SPP_URE1's compliance history and determined there were no relevant instances of noncompliance.
Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity (SPP_URE1) | NCRXXXX | SPP2012011085 | Settlement Agreement | SPP_URE1 submitted a Self-Report stating that it was in violation of CIP-005-1 R1. SPP_URE1 failed to identify a Remote Terminal Unit (RTU) test server as an Electronic Access Point (EAP). The test server, which resides inside an Electronic Security Perimeter (ESP), was directly connected to RTU test equipment residing outside the SPP_URE1 ESP, but no electronic access point was identified between the server and the test equipment. The root cause of the violation was that this configuration existed prior to the mandatory compliance date. | CIP-005-1 | R1 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The failure to identify the RTU test server as an access point meant SPP_URE1 failed to institute appropriate access controls to prevent unauthorized access to the SPP_URE1 ESP. The risk posed by the violation was mitigated by SPP_URE1's implementation of a Network Intrusion Detection System (NIDS) to monitor and alarm for unauthorized access within its network. SPP_URE1's NIDS is monitored during office hours by qualified personnel, and is configured to send alerts to authorized personnel on a 24x7 basis. Technicians who work with the test server and RTUs have authorized physical access to the SPP_URE1 Physical Security Perimeters and hold current Personnel Risk Assessments. Applicable patches have been applied to the test server; anti-virus is installed; and security logs are reviewed. | when SPP_URE1 failed to identify an EAP | Mitigation Plan completion | None | Self-Report | To mitigate this violation, SPP_URE1: 1) added a firewall between the test server and the test RTU equipment located outside the ESP to create an access-controlled EAP between the two locations; and 2) improved its annual vulnerability assessment process to include a physical walk-through and cable trace to identify all access points to the ESP. | 2012-10-12 | 2013-07-12 | Neither Admits nor Denies | SPP RE reviewed SPP_URE1's internal compliance program (ICP) and considered it to be a mitigating factor. SPP RE determined that SPP_URE1's compliance history should not serve as a basis for aggravating the penalty.
Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity (SPP_URE1) | NCRXXXX | SPP2012011410 | Settlement Agreement | SPP RE determined that SPP_URE1 was in violation of CIP-007-2a R1. Specifically, SPP_URE1 was unable to provide evidence showing that cyber security testing was performed prior to installation of several Cyber Assets. SPP_URE1 did not maintain sufficient documentation to demonstrate that testing occurred on newly built workstations and a virtual environment host server. Adequate evidence was not maintained to demonstrate that the associated security controls were properly configured prior to placing the Cyber Assets into production. Subsequent to the audit and during mitigation of the aforementioned noncompliance, SPP_URE1 identified an additional instance of non-compliance. A set of firewalls were added to the outer boundary of two servers bringing the servers into the SPP_URE1 Electronic Security Perimeters (ESPs), but SPP_URE1 could not demonstrate that CIP-007-3 R1 testing was conducted on the two servers prior to introduction into SPP_URE1 ESPs. SPP_URE1 also discovered that a third-party software upgrade was performed on a Cyber Asset without properly testing security controls and documenting the results. The instances described resulted from a lack of staff training with regard to configuration management and change control. | CIP-007-2a | R1 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The failure to test the introduction of new Cyber Assets, or significant changes to Cyber Assets in the ESP creates a risk that SPP_URE1's security controls may have been weakened due to the modification, thereby exposing the SPP_URE1 ESP and its associated network to malicious attack. The risk posed by this violation is mitigated because the implicated devices were afforded the CIP required protections (including security patching and anti-malware). The security controls of the Cyber Assets in scope of this violation were checked during SPP_URE1's annual Cyber Vulnerability Assessments and whenever significant changes were implemented to these Cyber Assets. Additionally, SPP_URE1's access control and monitoring devices are configured to deny all access attempts originating from outside its ESPs, thereby significantly limiting the risk that actual unauthorized access could occur. SPP_URE1's ESP networks are continuously monitored by a network intrusion detection system, which provides a redundant detection mechanism in the event that SPP_URE1 failed to identify an unintended change in its security controls. | when new workstations and/or a new server were installed | Mitigation Plan completion | None | Compliance Audit | To mitigate the violation, SPP_URE1: 1) replaced the two servers in 2013 to bring them into compliance; 2) performed a comparison scan of the third party software upgrade to the asset's baseline to review and assess security controls; 3) provided refresher training to IT staff on NERC requirements for Cyber Assets; 4) provided training to IT staff on use of the testing templates, and added the templates to the Configuration Management Plan for easy access; and 5) added an additional review step to its change control process. | 2013-08-02 | 2013-09-11 | Neither Admits nor Denies | SPP RE reviewed SPP_URE1's internal compliance program (ICP) and considered it to be a mitigating factor. SPP RE considered SPP_URE1's compliance history and determined there were no relevant instances of noncompliance.
Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity (SPP_URE1) | NCRXXXX | SPP2012011415 | Settlement Agreement | SPP RE determined that SPP_URE1 was in violation of CIP-007-1 R5 (5.1.2, 5.1.3, 5.2.3, 5.3.3). SPP_URE1 was unable to provide evidence to demonstrate that historical audit trails of individual user account access activity for Windows systems was adequately logged as required by R5.1.2. While login failures were logged, successful logins were not. After the audit, SPP_URE1 found that three network switches and two routers were not logging all individual account access activity as required by R5.1.2. Access failures and successes were not being logged as a result of the lack of staff training with regard to configuration management. SPP_URE1 did not review all user accounts at least annually to verify access privileges are in accordance with CIP-003 R5, and CIP-004 R4 as required by CIP-007 R5.1.3. Specifically, the audit team discovered that although SPP_URE1 was reviewing shared user accounts, access privileges for individual user accounts were not reviewed. The noncompliance was due to employee oversight during the annual review of account access. SPP_URE1 was unable to provide evidence of an audit trail of shared account use as required by R5.2.3. Specifically, the audit team discovered that all Supervisory Control and Data Acquisition (SCADA) and Energy Management System (EMS) operators and the system/network administrator used the same shared user account, but a log was not maintained to identify the individual who was accessing the shared account at any particular time. The noncompliance resulted from employee oversight. SPP RE found that SPP_RE failed to change the domain password for a SCADA service account annually as required by R5.3.3. SPP_RE had not changed the password because doing so would have resulted in a system error. Although the password change was technically infeasible, SPP_RE had not requested a Technical Feasibility Exception (TFE) nor documented compensating measures. | CIP-007-1 | R5; R5.1.2, R5.1.3, R5.2.3, R5.3.3 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The failure to adequately track the use of the accounts in question (individual windows accounts, shared operator accounts, and switch/router accounts) creates a risk that an unauthorized person could have accessed the SPP_URE1 Electronic Security Perimeter (ESP). Such unauthorized access could have negatively impacted SPP_URE1's network, its operator workstations, and its EMS devices. Additionally, the failure to adequately review access potentially increases the risk of an insider attack because the scope of individuals with access to critical systems may have included more individuals than was required. During the period of noncompliance, SPP_URE1 had several security controls in place which mitigated the risk of this violation. Individuals with access to the Physical Security Perimeter (PSP) and ESP have completed physical and cyber security training as well as Personnel Risk Assessments. SPP_URE1 maintains policies to remove access when personnel leave or transfer to other departments. Information Technology staff utilize an electronic work order system for work assignment and activity tracking (which could be cross referenced against access times to narrow potential abuse of account privilege); and the SPP_URE1 ESP is continuously monitored by an intrusion detection system, which increases the likelihood that potentially malicious activity in the environment would be detected. | when the Standard became mandatory and enforceable | Mitigation Plan completion | None | Compliance Audit | To mitigate the violation, SPP_URE1: 1) revised its logging policy to include login and logoff successes and failures, and updated its log management document to include the new account logging policy; 2) created a spreadsheet of accounts to include individual user accounts. The spreadsheet is utilized as a template to identify accounts requiring review during SPP_URE1's annual accounts audit; 3) implemented an electronic log in order to maintain a record of shared user account access in which shared account users log their account use time; 4) filed a TFE with SPP RE to address the inability to change the service account password; and 5) migrated the functionality of the Windows cluster to a virtual server and disabled the service account password. | 2014-09-15 | 2014-10-08 | Neither Admits nor Denies | SPP RE reviewed SPP_URE1's internal compliance program (ICP) and considered it to be a mitigating factor. SPP RE considered SPP_URE1's compliance history and determined there were no relevant instances of noncompliance.
Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity (SPP_URE1) | NCRXXXX | SPP2012011416 | Settlement Agreement | SPP RE determined that SPP_URE1 was in violation of CIP-007-1 R6. Specifically, SPP_URE1 did not implement automated tools or organizational process controls to monitor specific system events related to cyber security for certain Supervisory Control and Data Acquisition (SCADA) system accounts, and no compensating measures were applied to mitigate risk. The root cause of the non-compliance was that SPP_URE1 did not log specific events for certain SCADA system accounts because the frequency of these logged events degraded server functionality. | CIP-007-1 | R6 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The failure to ensure that sufficient logging was enabled reduced SPP_URE1's awareness of system cyber security events within its Electronic Security Perimeters (ESP). However, SPP_URE1 utilizes a Network Intrusion Detection System (NIDS) to monitor and alarm for unauthorized access. SPP_URE1's NIDS is monitored during office hours by qualified personnel, and is configured to send all network traffic alerts to authorized personnel on a 24x7 basis, which increases the likelihood that SPP_URE1 would detect unauthorized access attempts into the SPP_URE1 ESPs. SPP_URE1 denies access to devices that attempt to communicate to its ESPs from outside the ESP, thereby limiting the risk that unauthorized access could occur. In addition, no devices within SPP_URE1's ESPs have internet access. These SCADA Cyber Assets reside within SPP_URE1's defined ESPs and Physical Security Perimeters (PSPs), with access limited to only authorized personnel. | when the Standard became mandatory and enforceable | Mitigation Plan completion | None | Compliance Audit | To mitigate this violation, SPP_URE1: 1) developed a script to allow for collating of security events; the collated list is reviewed quarterly, as required by CIP-007-3 R6; 2) submitted a Technical Feasibility Exception for security event logging of certain system accounts; and 3) updated its Log Management document to address security event logging for the applications related to this violation. | 2014-01-02 | 2014-06-06 | Neither Admits nor Denies | SPP RE reviewed SPP_URE1's internal compliance program (ICP) and considered it to be a mitigating factor. SPP RE considered SPP_URE1's compliance history and determined there were no relevant instances of noncompliance.
Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity (SPP_URE1) | NCRXXXX | SPP2012010987 | Settlement Agreement | SPP_URE1 was in violation of CIP-005-1 R2.1, R2.2, and R2.4. SPP_URE1 failed to document and implement organizational processes and technical and procedural mechanisms for control of electronic access at all electronic access points to its Electronic Security Perimeter(s) (ESP). Specifically, two switches, one at the Primary Control Center (PCC) and one at the Backup Control Center (BCC), were not capable of being configured to explicitly permit authorized data traffic into the ESP and deny other traffic by default as required by CIP-005-1 R2.1. The switches could not be configured such that only the ports and services required for operations and monitoring Cyber Assets within the ESP were enabled as required by CIP-005-1 R2.2. Furthermore, the switches were not capable of supporting strong technical controls at the access points to ensure authenticity of the accessing party as required by CIP-005-1 R2.4, and SPP_URE1 had not sought a Technical Feasibility Exception. The root cause of the violation was SPP_URE1's oversight that the devices were not technically capable of being configured to meet the requirement. | CIP-005-1 | R2; R2.1; R2.2; R2.4 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Because the switches lacked the specified configuration and technical controls, there was the risk that unauthorized electronic access into SPP_URE1's ESP might occur. However, SPP_URE1 had procedural, organizational, and technical mechanisms in place for control of electronic access via the switches. SPP_URE1's access control and monitoring devices are configured to deny all access attempts originating from outside the ESP, thereby limiting the risk that unauthorized access could occur. SPP_URE1's ESP network is continuously monitored by a network intrusion detection system, which increases the likelihood that SPP_URE1 would detect unauthorized access attempts into the SPP_URE1 ESPs. Network traffic between the two switches flows over a communications path owned and controlled by SPP_URE1. The switches are located within Physical Security Perimeters (PSPs) and physical access is restricted to authorized personnel with cyber security training and Personnel Risk Assessments. | when the Standard became mandatory and enforceable | Mitigation Plan completion | None | Compliance Investigation | To mitigate this violation and prevent recurrence, SPP_URE1 installed two pairs of stacked firewalls as ESP access point devices between its PCC and BCCs. The firewalls are configured to explicitly permit authorized data traffic into the ESP, deny unauthorized data traffic by default, are configured such that only required ports and services are enabled, and support strong technical controls. | 2014-06-06 | 2014-09-23 | Neither Admits nor Denies | SPP RE reviewed SPP_URE1's internal compliance program (ICP) and considered it to be a mitigating factor. SPP RE considered SPP_URE1's compliance history and determined there were no relevant instances of noncompliance.