## PUBLIC_CIP Violations
Region | Registered Entity | NCR_ID | NERC Violation ID # | Notice of Confirmed Violation or Settlement Agreement | Description of the Violation | Reliability Standard | Req. | Violation Risk Factor | Violation Severity Level | Risk Assessment | Violation Start Date | Violation End Date | Total Penalty or Sanction ($) | Method of Discovery | Description of Mitigation Activity | Mitigation Completion Date | Date Regional Entity Verified Completion of Mitigation | "Admits," "Agrees/Stipulates," "Neither Admits nor Denies," or "Does Not Contest" | Other Factors Affecting the Penalty Determination, including Compliance History, Internal Compliance Program and Compliance Culture
Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2013012654 | Settlement Agreement | WECC_URE1 submitted a Self-Report stating that it was in violation of CIP-004-3a R2. WECC_URE1 issued temporary access badges to three employees so the employees could build a kitchen within a Physical Security Perimeter (PSP) where Critical Cyber Assets (CCA) were located. WECC_URE1's authorizing employee mistakenly believed that the three employees had received CCA training during the previous calendar year. However, the three employees last received CCA training two years prior. The three employees had physical access to eleven CCAs and one non-critical Cyber Asset at WECC_URE1's control center. As a result, WECC_URE1 was in violation of CIP-004-3a R2.1 for failing to ensure the three employees were trained prior to being granted access to the CCAs. The root cause of this violation was human error when WECC_URE1 verified the training dates for the three employees. | CIP-004-3a | R2 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE1 failed to ensure that three employees received training prior to being granted physical access to eleven CCAs and one non-CCA at WECC_URE1's control center. WECC_URE1's failure to train its employees on the proper use of Critical Assets increased the opportunity for the employees to improperly use the CCAs. Although WECC_URE1 granted access to the three employees, WECC_URE1 implemented preventive and detective controls. Specifically, WECC_URE1 implemented live video monitoring of the PSP 24 hours a day seven days a week. Additionally, each of the personnel involved in the violation had received prior CCA training. Furthermore, in this instance, the employees involved only had access to the PSP on a limited basis after receiving temporary access badges. Moreover, the PSP had a minimum of eight authorized, trained personnel inside at all times. The personnel and cameras minimized or prevented physical access to the CCAs and therefore would have prevented any unauthorized access to the supervisory control and data acquisition system. | when the three employees were granted access to the CCAs | when the three employees no longer had access to the CCAs | $65,000 (for WECC2013012654, WECC2014013374, WECC2014013375, and WECC2014013373) | Self-Report | To mitigate this violation, WECC_URE1: 1) started documenting the actual date of last CIP training in the Temporary Access Badge Log; 2) distributed a Bulk Operation Guide to all responsible senior load dispatchers responsible for issuing temporary badges and managing the Temporary Access Badge Log; 3) revised its Energy Control Centers (ECC) instructions for issuing temporary ECC badges that instructs entry of last CIP training date in the Temporary Access Badge Log; and 4) updated its training program for the load dispatcher with revised procedure related to issuing temporary ID badges for access to restricted areas of the ECC. | 2013-08-16 | 12/20/2013 | Neither Admits nor Denies | WECC reviewed WECC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. WECC considered WECC_URE1's CIP-004 R2 compliance history to be an aggravating factor in the penalty determination.
Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2014013374 | Settlement Agreement | WECC determined that WECC_URE1 was in violation of CIP-005-3a R2. WECC_URE1 performed troubleshooting that affected a router identified as an access point. During the troubleshooting, WECC_URE1 personnel issued a command that negated WECC_URE1's configured access list leaving the router without CIP-005 R2 controls. As a result, WECC_URE1 failed to use an access control model that denies access by default, such that explicit permissions were specified on the access point. WECC_URE1 also failed to enable only ports and services required for operations and for monitoring Cyber Assets within the Electronic Security Perimeter (ESP) at one access point. The scope of this violation includes one access point and one ESP. The root cause of this violation was lack of training when conducting work on access points and by a lack of appropriately configured firewall that inherently denies access by default. | CIP-005-3a | R2 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. For three years, one WECC_URE1 access point lacked the protections required by CIP-005-3a R2.1 and R2.2. This exposed WECC_URE1 to the potential risk of unauthorized individuals using the unprotected access point to gain access to WECC_URE1's other devices and networks. Although one of WECC_URE1's access points lacked the protections required by CIP-005-3a R2.1 and R2.2, WECC_URE1 did implement and document organizational processes and technical and procedural mechanisms for control of electronic access at all electronic access points to the ESP. Additionally, WECC_URE1 implemented a defense-in-depth architecture of physical and logical cyber security controls, including physical security mechanisms, special locks, and closed circuit television. WECC_URE1 also implemented internal cyber security controls including firewalls, vulnerability scanning tools, and a Security Information Events Management system. | when WECC_URE1 issued the command | when WECC_URE1 activated the Access Control List (ACL) on the router in scope | $65,000 (for WECC2013012654, WECC2014013374, WECC2014013375, and WECC2014013373) | Compliance Audit | To mitigate this violation, WECC_URE1: 1) activated the ACL on the router; 2) retrained its technical personnel on the proper procedure to follow when conducting work at non-firewall access point devices and to ensure that ACLs are reapplied once work is completed; 3) checked all Access Points for instances where non-firewall devices are used as access points and ensured that the device denies access by default; and 4) implemented a firewall that inherently denies access by default. | 5/9/2014 | 11/21/2014 | Neither Admits nor Denies | WECC reviewed WECC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2014013375 | Settlement Agreement | WECC determined that WECC_URE1 was in violation of CIP-006-3a R2. WECC_URE1 failed to identify fourteen Cyber Assets that authorize and log access to the Physical Security Perimeter and afford them CIP protection outlined in Standard CIP-006-3a R2. WECC_URE1 has eleven Physical Access Control System (PACS) panels capable of providing access, monitoring, and logging independent of WECC_URE1's PACS servers. The control panels in scope are capable of controlling access to all fourteen of WECC_URE1's Physical Security Perimeters (PSPs). WECC_URE1 also has three workstations capable of provisioning access to all of WECC_URE1's PSPs. WECC_URE1 did not provide the eleven panels and three workstations all of the protections identified in CIP-006-3a R2. The root cause of this violation was WECC_URE1's misunderstanding of whether the devices in scope were subject to the Reliability Standards. | CIP-006-3a | R2 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE1 did not provide three workstations and eleven panels with all of the protections identified in CIP-006-3a R2 potentially exposing WECC_URE1's Critical Cyber Assets to access by unauthorized individuals. However, the panels in scope were protected by the inherent protections of the PACS network through WECC_URE1's PACS servers. WECC_URE1 installed the panels in either a PSP or a location protected from unauthorized physical access. WECC_URE1 also installed the workstations in either a PSP or located protected from unauthorized physical access, such as WECC_URE1 Central Monitoring Station or Badging Office. Furthermore, the 14 devices in scope were provided some of the protections identified in CIP-006-3a R2.2. Specifically, the panels and workstations were afforded the protections required by CIP-003 R1-R5, CIP-004, CIP-006 R4-R5, CIP-007 R7, and CIP-008. | when the Standard became mandatory and enforceable | Mitigation Plan completion | $65,000 (for WECC2013012654, WECC2014013374, WECC2014013375, and WECC2014013373) | Compliance Audit | To mitigate this violation, WECC_URE1: 1) completed the change management form to include PACS workstations as devices afforded the protections of CIP-006 requirements (where applicable) and other requirements denoted in CIP-006 R2; 2) modified the change control management procedure and form to better detail when PACS devices must be added to the CIP Cyber Asset inventory; 3) reviewed the list of PACS devices to be afforded the protections of CIP-006 requirements (where applicable) and other requirements denoted in CIP-006 R2, verified the counts are correct and determined if Technical Feasibility Exceptions (TFEs) are required; 4) submitted TFEs (if required) to WECC; 5) developed an implementation schedule for bringing the PACS devices into compliance; 6) trained affected personnel on the modifications to the change control procedure; and 7) completed and signed off on change management forms demonstrating completion of implementation schedule for the PACS devices in scope. | 11/12/2014 | TBD | Neither Admits nor Denies | WECC reviewed WECC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2014013373 | Settlement Agreement | WECC determined that WECC_URE1 was in violation of CIP-007-3a R8. Specifically, WECC_URE1 did not perform a Cyber Vulnerability Assessment (CVA) on each Cyber Asset in 2011 and 2012. Instead, WECC_URE1 used a representative system model to perform CVAs of representative devices. As a result, WECC_URE1 omitted 13 Cyber Assets from the 2012 CVA. Ten of the devices were Critical Cyber Assets (CCAs), two were non-critical Cyber Assets, and one was an Electronic Control and Monitoring device. WECC_URE1 also omitted 11 Cyber Assets from the 2011 CVA. Eight of the devices were CCAs, two of the devices were non-Critical Cyber Assets, and one of the devices was a Physical Access Control System device. The root cause of this violation was WECC_URE1's reliance on a representative system model to perform CVAs. | CIP-007-3a | R8 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE1 did not perform CVAs on all Cyber Assets in 2011 and 2012. This could have exposed WECC_URE1 to successful cyber-attacks against WECC_URE1's Cyber Assets. However, WECC_URE1 implemented compensating measures to decrease the risk associated with only performing CVAs on representative devices. Specifically, WECC_URE1 implemented a defense-in-depth architecture of physical and logical cyber security controls. This defense-in-depth architecture includes physical security mechanisms with guards, special locks, closed circuit television, and logical perimeter controls. WECC_URE1 also implemented internal cyber security controls including firewalls, vulnerability scanning tools, and a Security Information Events Management system. WECC_URE1 Tripwire reports also confirmed that the baselines of the devices in scope matched those of the representative devices. | when WECC_URE1 used the representative system model during the 2011 CVA | when WECC_URE1 performed the CVA on all required Cyber Assets | $65,000 (for WECC2013012654, WECC2014013374, WECC2014013375, and WECC2014013373) | Compliance Audit | To mitigate this violation, WECC_URE1: 1) assessed devices currently with Tripwire to assure that baselines of devices omitted from the CVA have no applicable deviation from the devices used as the representative sample when performing the CVA; 2) developed the WECC_URE1 plan for CVA requiring the individual testing of all devices and ensured all required activities were performed; 3) trained appropriate personnel on the new CVA plan; 4) implemented the new CVA plan against all required Cyber Assets; and 5) performed a quality assurance review for the implementation of the CVA Plan. | 12/15/2014 | TBD | Neither Admits nor Denies | WECC reviewed WECC_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.
Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2014013750 | Settlement Agreement | WECC_URE2 submitted a Self-Certification stating that it was in violation of CIP-003-3 R6. WECC_URE2 reported that its CIP-003-3 R6 procedure required the creation of a security control checkout form for every significant change. The security control checkout form documents a breakdown of how a significant change affects all applicable CIP-002 through CIP-009 requirements and ensures that all applicable CIP controls are applied prior to the change being put into production. WECC_URE2 reported there is no evidence of the form being created and filled out for the 23.85% change tickets that occurred in the year. WECC determined WECC_URE2 failed to follow its change control and configuration management process for 23.85% changes. WECC determined these changes affected 116 devices, and that the changes made by WECC_URE2 were patches and upgrades to servers, workstations, and other networking equipment. The root cause of the violation was WECC_URE2's failure to follow established procedures. Specifically, WECC_URE2 had inadequate oversight due to a lack of peer review or management review of change controls. WECC_URE2 did not have a dedicated quality assurance employee to verify results of change control. There was also a lack of training because some individuals did not know the change control and configuration management process. | CIP-003-3 | R6 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). WECC_URE2's failure to follow its change control and configuration management process could allow for adding or modifying hardware and software changes that could compromise WECC_URE2's reliable operation of it transmission lines. Although WECC_URE2 failed to follow its change control and configuration management process, it did implement preventive controls. WECC_URE2 ensured that all CIP applicable devices resided within Electronic Security Perimeters (ESPs). WECC_URE2's devices were configured with tightly restricted ingress Access Control Lists and ports and services. WECC_URE2 disabled all dial-up access to assets within the ESP and required two-factor authentication for all external interactive access. WECC_URE2 also implemented detective controls. WECC_URE2 implemented Tripwire file integrity checker to verify no unauthorized functional changes occurred. Tripwire was configured to issue pop-up alerts to responsible personnel when a detected unauthorized change occurred. WECC_URE2 also conducted annual Cyber Vulnerability Assessments on all of its devices residing within an ESP. WECC_URE2's Cyber Vulnerability Assessment did not find any unaccounted ports and services or any default user accounts on the systems in scope. WECC_URE2 reviewed the security logs for these controls per CIP-007 R6 and it was determined that no malicious software was detected. Further, all personnel with access to Cyber Assets in the 23.85% change management tickets had CIP training and had current personnel risk assessments. | when WECC_URE2 failed to follow its change control process | Mitigation Plan completion | $85,000 (for WECC2014013750, WECC2014013890, WECC2014013503, WECC2014013504, WECC2014013751, WECC2014013505, and WECC2014013897) | Self-Certification | To mitigate this violation, WECC_URE2: 1) created a security control checkout form training plan for the applicable group and delivered that training plan to the applicable group's quality assurance manager; 2) completed security checkout form documentation and training for the applicable group; and 3) completed security checkout form training for the applicable operations team. The training covered proper usage for the security checkout form as it relates to the NERC CIP-003-3 R6 process. | 8/29/2014 | TBD | Agrees/Stipulates | WECC reviewed WECC_URE2's internal compliance program and considered it to be a mitigating factor in the penalty determination. WECC considered WECC_URE2's CIP-003 compliance history to be an aggravating factor in the penalty determination.
Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2014013890 | Settlement Agreement | During a Compliance Audit, WECC determined that WECC_URE2 was in violation of CIP-004-3a R4. WECC determined that on two occasions WECC_URE2 failed to revoke access to Critical Cyber Assets (CCAs) within seven calendar days for personnel who no longer require access to CCAs. In the first instance, a contractor no longer required access to WECC_URE2's CCAs. WECC_URE2 revoked access 28 days later. In the second instance, a WECC_URE2 employee verbally resigned. WECC_URE2 revoked access 14 days later. After the audit, WECC_URE2 reported a third instance of noncompliance. In that instance, a WECC_URE2 employee verbally resigned. WECC_URE2 revoked access 11 days later. The root cause of this violation was due to improper communication with vendors when a contractor has left employment and lack of management training and awareness regarding effect of certain human resources policies as applied to the voluntary separation of employees having access to a CIP environment. | CIP-004-3a | R4; R4.2 | Lower | Moderate | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failure to revoke access to CCAs in a timely manner could allow unauthorized individuals to have malicious physical access to WECC_URE2's CCAs. Although WECC_URE2 failed to revoke access to CCAs within seven calendar days, this violation was limited to three occasions that involved three individuals, none of whom were terminated for cause. WECC_URE2 verified the individuals did not attempt access after their separation. Additionally, the periods for these three occasions were of short duration, lasting 28 days, 14 days, and 11 days respectively. No harm is known to have occurred. | eight calendar days after the contractor in the first instance of noncompliance no longer required access | when WECC_URE2 terminated the employee's access in the third instance of noncompliance | $85,000 (for WECC2014013750, WECC2014013890, WECC2014013503, WECC2014013504, WECC2014013751, WECC2014013505, and WECC2014013897) | Compliance Audit | To mitigate this violation, WECC_URE2: 1) revised the separation and exit policy and procedures, along with accompanying supervisor's exit checklist, to provide emphasis on entering termination transactions early and adding language specific to NERC CIP areas; 2) incorporated the policy, including termination transactions and retirements, into periodic reminders sent to supervisors; 3) updated vendor contract language to comply with NERC Standards; and 4) reviewed master agreements and Individual Task Assignments for inclusion of the new language once the agreements expired. | 2015-02-16 | TBD | Agrees/Stipulates | WECC reviewed WECC_URE2's internal compliance program and considered it to be a mitigating factor in the penalty determination. WECC considered WECC_URE2's CIP-004 compliance history to be an aggravating factor in the penalty determination.
Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2014013503 | Settlement Agreement | WECC_URE2 submitted a Self-Certification stating that it was in violation of CIP-005-3a R5. WECC_URE2 made 13 changes to its networks or controls. The changes included adding and removing devices and updating firewalls. All 13 devices in scope are classified as Electronic Access Control and Monitoring devices responsible for protecting devices essential to a WECC_URE2 control center department. WECC_URE2 failed to update four pieces of documentation within 90 calendar days of the change. The root cause of this violation was WECC_URE2's failure to follow established procedures. Specifically, WECC_URE2 used a change control checklist, but the checklist did not include an explicit step to update relevant documentation as a result WECC_URE2 staff involved did not update relevant documentation. | CIP-005-3a | R5; R5.2 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE2's failure to update relevant documentation after the 13 changes were made could have led to inaccurate documents that contain information regarding the CIP-005 protections of the Electronic Security Perimeters inside which the Critical Cyber Assets reside. Although WECC_URE2 failed to update the documentation, WECC_URE2 did implement preventive controls. WECC_URE2 followed all security related change controls when modifying, adding, or removing devices. As a result, devices were tested and approved prior to implementation of the change. No harm is known to have occurred. | 91 calendar days after WECC_URE2 made changes to its network or controls | Mitigation Plan completion | $85,000 (for WECC2014013750, WECC2014013890, WECC2014013503, WECC2014013504, WECC2014013751, WECC2014013505, and WECC2014013897) | Self-Certification | To mitigate this violation, WECC_URE2: 1) updated the four pieces of documentation; and 2) updated the checklist to include steps for updating documentation. | 1/9/2014 | 10/20/2014 | Agrees/Stipulates | WECC reviewed WECC_URE2's internal compliance program and considered it to be a mitigating factor in the penalty determination. WECC considered WECC_URE2's compliance history and determined there were no relevant instances of noncompliance.
Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2014013504 | Settlement Agreement | WECC_URE2 submitted a Self-Certification stating that it was in violation of CIP-006-1 R1. WECC_URE2 failed to conduct Cyber Vulnerability Assessments (CVAs) on 13 controls panels. WECC_URE2 never conducted full CVAs on three control panels. WECC_URE2 attempted to scan the three control panels, but the scan caused the control panels to crash. WECC_URE2's 16 control panels were not afforded the protective measures specified in Standards CIP-007-3 and CIP-009-3. WECC_URE2 also failed to verify that no default accounts resided on the panels on an annual basis. Additionally, two unauthorized personnel were left unescorted in an area containing WECC_URE2's Physical Access Control and Monitoring (PACM) server for the generating station's Physical Security Perimeters (PSPs) and a control panel. WECC also determined that WECC_URE2 failed to ensure that Cyber Assets that authorize or log access to the PSPs were protected from unauthorized physical access as required by CIP-006-3c R2.1. The root cause of this violation was equipment failure, lack of process and training issues as some of the WECC_URE2 personnel were not adequately trained on WECC_URE2's escorting procedures. | CIP-006-1 | R1; R1.8 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE2 uses the PACM devices in scope to implement physical controls required to protect WECC_URE2's devices. Unauthorized physical access to WECC_URE2's control panels could allow for physical compromise of the devices controlling all of WECC_URE2's transmission and generating systems which would affect WECC_URE2's peak load and generation. Although WECC_URE2 failed to ensure the 16 control panels classified as PACM devices were afforded the protective measures specified in CIP-006-3c R2, WECC_URE2 did implement preventive and detective controls. WECC_URE2 personnel responsible for recovering the devices were knowledgeable of the devices and had the vendors' contact information in the event the devices needed to be recovered. The control panels' functionality was limited by design which restricted malicious opportunities. Every year WECC_URE2 verified that no default accounts were enabled on the devices. WECC_URE2's PACM devices were all located in restricted facilities staffed 24 hours a day, seven days a week by personnel who only allowed access to authorized individuals. The two individuals left unescorted were discovered by staff who noticed the unescorted individuals and immediately notified WECC_URE2 management. WECC_URE2 confirmed that no harm occurred to the devices the unescorted individuals had access. | when the Standard became mandatory and enforceable on WECC_URE2 | Mitigation Plan completion | $85,000 (for WECC2014013750, WECC2014013890, WECC2014013503, WECC2014013504, WECC2014013751, WECC2014013505, and WECC2014013897) | Self-Certification | To mitigate this violation, WECC_URE2: 1) met with the escort employee who did not follow procedures and retrained him on PSP escorting procedures; 2) revised the Emergency Situations section of the CIP Cyber Security Policy to ensure that the situation in question is adequately covered for future occurrences; 3) updated and installed new signage at the generating station data center PSP; 4) updated the process and/or any other processes deemed necessary to ensure that if an information security emergency occurs in a CIP-protected area, the CIP Cyber Security Policy's emergency must be followed; 5) updated the CIP Cyber Security Training course; 6) developed procedures for performing a CVA on the PACS field panels; 7) performed and documented the results of a CVA on the PACS field panels; 8) updated the Recovery Plan procedures to include the PACS field panels; and 9) conducted the annual Recovery Plan exercise to include PACS field panels, documented the results of the exercise, and reviewed meeting minutes. | 8/30/2014 | TBD | Agrees/Stipulates | WECC reviewed WECC_URE2's internal compliance program and considered it to be a mitigating factor in the penalty determination. WECC considered WECC_URE2's CIP-006-3c compliance history to be an aggravating factor in the penalty determination.
Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2014013751 | Settlement Agreement | WECC_URE2 submitted a Self-Certification stating that it was in violation of CIP-007-3a R1. WECC_URE2 failed to implement the proper test procedures described in CIP-007-3a R1 for 31 change management tickets. The CIP-007 procedure states that a security control checkout form document is to be created for every significant change as this form helps ensures that all applicable CIP controls are applied, prior to the change being put into production. The security control checkout form was not filled out for the 31 significant change tickets. Further, WECC determined that WECC_URE2 were unable to confirm that testing was performed per the CIP-007 test procedure prior to the 31 significant changes being placed into production. These changes made by WECC_URE2 included patches and upgrades to servers, workstations, and other networking equipment that impacted 116 devices. The root cause of this violation was WECC_URE2's failure to follow established procedures. Specifically, WECC_URE2 had inadequate oversight due to a lack of peer review or management review of change controls. WECC_URE2 did not have a dedicated quality assurance employee to verify results of change control. There was also a lack of training because some individuals did not know the change control and configuration management process. | CIP-007-3a | R1 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE2's failure to complete its security check out form could have allowed for the adding or modifying hardware and software changes that are harmful to Critical Cyber Assets essential to the operation of the BPS. Although WECC_URE2 failed to complete its security check out form, WECC_URE2 did implement preventive controls. WECC_URE2 ensured that all CIP applicable devices resided within Electronic Security Perimeters (ESPs). WECC_URE2's devices were configured with tightly restricted ingress Access Control Lists and ports and services. WECC_URE2 also disabled all dial-up access to assets within the ESP and required two-factor authentication for all external interactive access. WECC_URE2 also implemented detective controls. WECC_URE2 implemented Tripwire File Integrity Checker to verify no unauthorized changes occurred. Tripwire File Integrity Checker was configured to issue pop-up alerts to responsible personnel when a detected unauthorized change occurred. WECC_URE2 also conducted annual Cyber Vulnerability Assessments (CVA) on all its devices residing within an ESP. WECC_URE2's CVA did not detect any unaccounted ports and services or any default user accounts on the systems in scope. WECC_URE2 reviewed the security logs for these controls per CIP-007 R6 and it was determined that no malicious software was detected. Further, all personnel with access to Cyber Assets in the 31 change management tickets had CIP training and had current personnel risk assessments. | when WECC_URE2 first failed to follow proper test procedures | Mitigation Plan completion | $85,000 (for WECC2014013750, WECC2014013890, WECC2014013503, WECC2014013504, WECC2014013751, WECC2014013505, and WECC2014013897) | Self-Certification | To mitigate this violation, WECC_URE2: 1) configured Tripwire Enterprise System to show all applicable security controls have been tested and passed to prevent occurrence of similar future issues; 2) created security control checkout form training plan for the applicable group and delivered it to the applicable group's manager; 3) completed security control checkout form documentation and training for the applicable group; and 4) completed security control checkout form training for the operations team. | 8/29/2014 | TBD | Agrees/Stipulates | WECC reviewed WECC_URE2's internal compliance program and considered it to be a mitigating factor in the penalty determination. WECC considered WECC_URE2's CIP-007 compliance history to be an aggravating factor in the penalty determination.
Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2014013505 | Settlement Agreement | WECC_URE2 submitted a Self-Certification stating that it was in violation of CIP-007-3a R3. WECC_URE2's procedures required WECC_URE2 to review security patches within 30 days of their release and apply security patches within 90 days of their evaluation if the security patches are determined to be applicable. A Java patch was released and WECC_URE2 determined it was applicable and should be applied. Specifically, WECC_URE2 attempted to install the patch, but due to technical limitations the patch failed. Specifically, WECC_URE2 applied the patch to the workstation, but the update broke the Oracle Forms software. To fix this problem WECC_URE2 needed to install an update to the Oracle Forms on the backend server. The Oracle Forms update would not work until WECC_URE2 installed additional RAM on the backend server. WECC_URE2 did not install the Java patch until approximately three months after the patch should have been applied. The root cause of the violation was failure to include in its procedure a process to deal with software issues. WECC_URE2 had an established procedure, but waited too long to find a solution for the software issue so that it could follow its procedures within the 90 day time period. | CIP-007-3a | R3 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE2's failure to install the patch impacted one workstation used by the operators to control WECC_URE2's energy management system (EMS). This failure could have allowed vulnerabilities on the workstation to remain unnoticed and unchecked for a longer duration. Although WECC_URE2 failed to install the patch within 90 days, WECC_URE2 did implement compensating controls. WECC_URE2 was aware of the patch and the associated vulnerabilities addressed by the patch. WECC_URE2 did install the patch as soon as technically feasible. The Electronic Security Perimeter (ESP) for the EMS is protected behind a Physical Security Perimeter with adequate controls, monitoring, and logging in accordance with CIP-006 R4, R5, and R6. All Cyber Assets within the ESP are protected with antivirus and anti-malware controls. WECC_URE2 reviewed the security logs for these controls per CIP-007 R6 and it was determined that no malicious software was detected. Finally, all personnel with access to the Windows workstation had CIP training and had current personnel risk assessments. | 91 days after WECC_URE2 determined the Java patch was applicable | when WECC_URE2 installed the Java patch | $85,000 (for WECC2014013750, WECC2014013890, WECC2014013503, WECC2014013504, WECC2014013751, WECC2014013505, and WECC2014013897) | Self-Certification | To mitigate this violation, WECC_URE2: 1) upgraded server memory to allow for successful back-end application updates; 2) upgraded Oracle Forms and performed Java updates; 3) documented the update in the CIP-007-3 R3 patch tracking spreadsheet; 4) updated the Technical Feasibility Exception (TFE) template to reflect different TFE options; and 5) trained operations IT subject matter experts on the new procedure. | 6/26/2014 | 11/24/2014 | Agrees/Stipulates | WECC reviewed WECC_URE2's internal compliance program and considered it to be a mitigating factor in the penalty determination. WECC considered WECC_URE2's CIP-007 compliance history to be an aggravating factor in the penalty determination.
Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2014013897 | Settlement Agreement | During a Compliance Audit, WECC determined that WECC_URE2 was in violation of CIP-007-3a R8. WECC_URE2 failed to annually perform a Cyber Vulnerability Assessment (CVA) on all Cyber Assets in the Electronic Security Perimeters (ESPs) and failed to perform a complete CVA because not all ports and services on all Cyber Assets were assessed. WECC_URE2 used ports and services information gathered from one Cyber Asset as a representative sample to satisfy the vulnerability for 38 other Cyber Assets. WECC_URE2 only scanned one device to collect current ports and services information and the information was gathered from a test system and not from the actual Cyber Assets in question. WECC_URE2 also failed to gather current ports and services information from an additional 23 Cyber Assets. This led to a violation that included 21 Critical Cyber Assets (CCAs) and 41 non-critical Cyber Assets. The root cause of the violation was a process deficiency. Specifically, the technical team involved was not able to perform the CVA scan due to device and system outage limitations and felt that a scan on a representative sample would be sufficient. | CIP-007-3a | R8; R8.2; R8.3 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Specifically, WECC_URE2's failure to conduct CVAs on 21 CCAs and 41 non-critical Cyber Assets led to a situation where WECC_URE2 put the 62 Cyber Assets at risk of compromise and unauthorized manipulation. Although WECC_URE2 failed to conduct the CVAs, WECC_URE2 did implement compensating measures. WECC_URE2 implemented a defense-in-depth strategy including physical and logical cyber security controls such as physical security mechanisms with guards and closed-circuit television. WECC_URE2 also implemented logical perimeter and other cyber security controls including firewalls, intrusion detection systems, and least-privilege account management practices. | the day after WECC_URE2 completed its Mitigation Plan for a prior violation of this Standard | present | $85,000 (for WECC2014013750, WECC2014013890, WECC2014013503, WECC2014013504, WECC2014013751, WECC2014013505, and WECC2014013897) | Compliance Audit | To mitigate this violation, WECC_URE2 will: 1) begin to transition to compliance with some or all of the CIP V5 Standards; 2) split the entire network to where all in-scope systems will be on two separate networks, two in each network; and 3) declare all Cyber Assets and systems at the generating facility to be part of one or more low impact Bulk Electric System cyber systems (LIBCS), as a result the LIBCS at the facility will no longer be in scope for any requirements pertaining to the execution of a CVA. | 11/5/2014 | TBD | Neither Admits nor Denies | WECC reviewed WECC_URE2's internal compliance program and considered it to be a mitigating factor in the penalty determination. WECC considered WECC_URE2's CIP-007 compliance history to be an aggravating factor in the penalty determination.
Western Electricity Coordinating Council (WECC) | WECC_URE3 | NCRXXXXX | WECC2014014001 | Settlement Agreement | WECC_URE3 submitted a Self-Report stating that it was in violation of CIP-007-3a R6. WECC_URE3 reported that it failed to ensure that all Cyber Assets within the Electronic Security Perimeter (ESP) implemented automated tools or organizational process controls to monitor system events that are related to cyber security, as required by CIP-007-3a R6. Specifically, WECC_URE3 failed to properly maintain and review logs for three Supervisory Control and Data Acquisition (SCADA) switches and to retain logs for 90 days for two Energy Management System (EMS) servers. As a result, WECC_URE3 reported that it had a violation of CIP-007-3a R6. WECC determined that WECC_URE3 failed to ensure that all Cyber Assets within the ESP implemented automated tools or organizational process controls to monitor system events that are related to cyber security, as required by CIP-007-3a R6. The root cause involving the three switches was human error in that one employee did not add the devices to the Security Incident and Event Management (SIEM) for monitoring. The root cause for the servers not retaining 90 days worth of logs was due to technical errors as a result of a mis-configuration after a re-installation on a client after testing was performed. | CIP-007-3a | R6; R6.4; R6.5 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE3 failed to implement automated tools or organizational process controls to monitor system events that are related to cyber security. Specifically, WECC_URE3 failed to maintain and review logs for three SCADA switches which provide internal communication between SCADA workstations and SCADA servers. WECC_URE3 also failed to retain logs for 90 days for two EMS servers. Failing to implement, maintain, and review a logging system and failing to retain logs for 90 days could lead to undetected security incidents. A malicious person could scan these devices to discover vulnerable ports and services and launch an attack against any discovered vulnerabilities. WECC_URE3 implemented strong preventative controls to prevent undetected security incidents from occurring. Specifically, WECC_URE3 configured the operating system on these switches to limit which ports and services are allowed to open and start prior to adding them to the ESP. In other words, this configuration restricts any unauthorized ports and services outside of their current configuration, reducing the likelihood of an unauthorized user from leveraging a vulnerable port or service and gaining remote access to the SCADA switches. WECC_URE3 also implemented strong detective controls to detect any security incidents. Specifically, WECC_URE3 implemented a SIEM device that is used to monitor the logs of the SCADA devices. If someone were to gain control of the switches and attempt to then gain control of other SCADA devices, the security information and event management (SIEM) could detect that attempt. Since the SIEM monitors the SCADA devices 24 hours per day, seven days a week, an email would have been sent to security personnel alerting them about an unauthorized access attempt. The security personnel on-call would likely investigate, review the logs, and determine the unauthorized ports and services to shut them down. This would stop the network connection of the unauthorized personnel by shutting down the unauthorized ports and services, preventing unauthorized access to the SCADA devices. As further compensation, WECC_URE3 implemented strong compensating controls. Specifically, WECC_URE3 implemented a Cisco operating system (IOS) configuration to prevent unknown Media Access Control (MAC) addresses from connecting to the network. This MAC address restriction would likely prevent remote logging into the SCADA switches and attempt to access other SCADA devices. WECC_URE3 implemented additional strong compensating controls. Specifically, WECC_URE3 implemented locks on cabinets that contain these switches which would likely prevent a malicious person from physically damaging the three switches in scope. The locked cabinets prevent employees from getting physical access to the switches and not be able to access the switches via a serial cable and its console port. WECC_URE3 also added a firewall to restrict network access within the ESP and provide access point protections. | the date that WECC_URE3 put the switches into production without the appropriate monitoring tools | Mitigation Plan completion | 15000 | Self-Report | To mitigate this violation, WECC_URE3: 1) WECC_URE3 submitted evidence of the new switches being added as data sources within its SIEM and its log collection occurring; and 2) WECC_URE3 configured the alarm/notification to notify WECC_URE3 personnel when a “data source” client has stopped forwarding logs. | 2014-08-01 | 2014-11-14 | Does Not Contest | WECC reviewed WECC_URE3's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination.