## Public CIP SNOP Posting
Region | Registered EntityName | NCR | NERC Violation ID | Notice of Confirmed Violation or Settlement Agreement | Description of the Violation | Reliability Standard | Req. | Violation Risk Factor | Violation Severity Level | Risk Assessment | Violation Start Date | Violation End Date | Total Penalty or Sanction ($) | Method of Discovery | Description of Mitigation Activity | Mitigation Completion Date | Date Regional Entity Verified Completion of Mitigation | "Admits," "Agrees/Stipulates," "Neither Admits nor Denies," or "Does Not Contest" | Other Factors Affecting the Penalty Determination, including Compliance History, Internal Compliance Program and Compliance Culture
Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2014013713 | Settlement Agreement | MRO_URE1 submitted a Self-Certification stating that it was in violation of CIP-003-3 R5, R5.1, R5.2, and R5.3. Following its annual CIP Information Protection assessment, MRO_URE1 identified two locations where CIP-protected information classified as confidential and/or confidential-restricted did not meet the requirements of CIP-003-3 R5.1, R5.2, and R5.3. In the first instance of noncompliance, the location used to store the CIP Log manager configuration documents for MRO_URE1 was not identified as a CIP information repository, resulting in noncompliance with R5, R5.1, R5.2, and R5.3. As a result, the owner of the repository did not have documented access control procedures per R5, did not perform annual user access and permissions reviews per R5.2, and did not assess and document at least annually the processes for controlling access privileges to protect information per R5.3. Additionally, the designated approvers were not identified on the logical designated approver personnel list as required by R5.1. Because the CIP information protection program and CIP Access Control Program failed to include this location, the associated access control requirements (R5.1-R5.3) were not met. In the second instance of noncompliance, a document management application used to store and maintain CIP documents had a shared privileged account which was not covered by an access control procedure, resulting in noncompliance with R5, R5.1, R5.2, and R5.3. As a result, the shared privileged account was not identified on the designated approver personnel list per R5.1, and annual user access and permission and process reviews had not been conducted per R5.2 and R5.3, respectively. The account owner mistakenly thought that the required access control procedure and designated approver were covered by the application access control procedures. The root cause of the first instance of noncompliance was an oversight in the process that led to the failure to identify a CIP information repository in the MRO_URE1 CIP information protection program and CIP Access Control Program. The root cause of the second instance of noncompliance was the result of inadequate procedures, as this repository failed to have a clearly applicable written access control procedure. | CIP-003-3 | R5: R5.1; R5.2; R5.3 | Lower | Severe | MRO determined that this violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). A violation of CIP-003-3 R5 has the potential to affect the reliable operation of the BPS by permitting unauthorized access to Critical Cyber Assets (CCAs), thus allowing potential compromise of confidential information. In the first instance, the data that was not stored in an identified CIP information repository was limited to the configuration files for the device, as opposed to the actual log data that tracked events for the CCAs. Additionally, the available evidence demonstrated that only non-CCAs were affected by this noncompliance. In the second instance, the data associated with the document management application was limited to the shared user account as opposed to each of the individual accounts. No improper access was discovered during mitigating activities, and the data identified for these instances of noncompliance could not be used to access CCAs. MRO_URE1 stated that access to Cyber Assets within the Electronic Security Perimeter (ESP) was limited to only those individuals with authorized physical and/or electronic access rights. The servers that house the applications are located in a data center with physical access restricted to authorized personnel. | When the standard became mandatory and enforceable on MRO_URE1 | When access control procedures and associated processes were implemented | $152,000 (for MRO2014013713, MRO2013013155, MRO2013012800, MRO2013012366, MRO2014014472, MRO2014013361, MRO2013013116, MRO2013011986, MRO2013012126, MRO2013013054, and MRO2013012127) | Self-Certification | To mitigate this violation, MRO_URE1: 1. created and implemented access control procedures and associated processes; 2. completed a gap assessment for the shared folders with CIP information; 3. remediated the compliance gaps by updating multiple existing procedures and creating one new procedure; and 4. trained any newly affected staff on CIP access controls. | 2014-08-06 | 2015-04-22 | Does Not Contest | MRO applied mitigating credit to the penalty amount for the following considerations: 1. MRO_URE1 has demonstrated the ability to self-assess and identify violations related to CIP Standards. It has undertaken a comprehensive review of its CIP Compliance Program and has continuously self-reported noncompliance; 2. MRO_URE1 demonstrated its commitment to reliability and security of its system through a comprehensive review of its CIP compliance program and a concerted effort to focus resources and improve management practices around CIP compliance efforts; 3. MRO_URE1 cooperated in an exemplary manner throughout the course of the investigation, risk determination, and mitigation phases of these violations; 4. MRO_URE1 invested in a design review, verification, and validation to assess MRO_URE1's security posture following implementation of an EMS replacement project; and 5. MRO gave significant credit to MRO_URE1 for its commitment to the development, implementation, and continuous improvement of its internal compliance program (ICP). MRO_URE1's prior noncompliance with CIP-003 R5 was not considered an aggravating factor.
Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2013013155 | Settlement Agreement | MRO_URE1 submitted Self-Reports stating that it was in violation of CIP-003-3 R6. The Self-Reports identified four instances of noncompliance with CIP-003-3 R6. 1. The change control process was not completed for work related to adding a devices and a control system. The work was completed properly, but the corresponding CIP-related documentation was not updated to reflect those changes within 90 days as required by MRO_URE1's procedures. The documentation was updated almost three weeks late. 2. An unsecured routable connection was discovered at an MRO_URE1 facility. 3. Serial communication changes were made when MRO_URE1 removed multiple communication connections to multiple MRO_URE1 substation devices. These changes did not have proper change control documentation completed within 90 days as required by MRO_URE1's change control and configuration management procedure. The documentation was updated approximately two months late. 4. A project which involved updating firmware at a MRO_URE1 substation did not have the necessary change control documentation submitted within 90 days as required by MRO_URE1's procedures. The documentation was updated almost two weeks late. The root cause of the violation was a failure to follow established procedures. | CIP-003-3 | R6 | Lower | Severe | MRO determined that this violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). A violation of CIP-003-3 R6 has the potential to affect the reliable operation of the BPS by providing the opportunity to exploit vulnerable Critical Cyber Assets (CCAs) after a Responsible Entity applies undocumented change control or configuration management activities to those CCAs. While the first, third, and fourth instances were limited to documentation, and posed a minimal potential risk to the BPS, the second instance resulted in extending the ESP unintentionally to a distribution control house for nearly two years. The potential risk posed by the fourth instance was reduced because it did not involve a control center, was limited to a single substation, and was self-identified during MRO_URE1's annual substation inventory. | When MRO_URE1 first failed to follow its change management control procedures, resulting in an unsecured routable connection | When MRO_URE1 properly updated the documentation according to its change management and configuration procedure | $152,000 (for MRO2014013713, MRO2013013155, MRO2013012800, MRO2013012366, MRO2014014472, MRO2014013361, MRO2013013116, MRO2013011986, MRO2013012126, MRO2013013054, and MRO2013012127) | Self-Report | To mitigate this violation, MRO_URE1 : 1. updated the CIP documentation for the instances where change control paperwork was completed but missed the 90-day timeline; 2. redesigned and implemented the substation network to address the non-compliant routable connection; 3. completed change controls forms for communication connections to a few MRO_URE1 substation devices that were disconnected; 4. evaluated and added additional program controls and monitoring practices to increase focus on change control processes; 5. completed change control forms for the firmware update project at one MRO_URE1 substation that had missed the 90-day timeline; and 6. added biweekly change control meetings to identify and review all change control activities occurring at Critical Asset substations. | 2014-03-05 | 2015-04-22 | Does Not Contest | MRO applied mitigating credit to the penalty amount for the following considerations: 1. MRO_URE1 has demonstrated the ability to self-assess and identify violations related to CIP Standards. It has undertaken a comprehensive review of its CIP Compliance Program and has continuously self-reported noncompliance; 2. MRO_URE1 demonstrated its commitment to reliability and security of its system through a comprehensive review of its CIP compliance program and a concerted effort to focus resources and improve management practices around CIP compliance efforts; 3. MRO_URE1 cooperated in an exemplary manner throughout the course of the investigation, risk determination, and mitigation phases of these violations; 4. MRO_URE1 invested in a design review, verification, and validation to assess MRO_URE1's security posture following implementation of an EMS replacement project; and 5. MRO gave significant credit to MRO_URE1 for its commitment to the development, implementation, and continuous improvement of its internal compliance program (ICP). MRO considered MRO_URE1's compliance history to be an aggravating factor in the penalty determination.
Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2013012800 | Settlement Agreement | MRO_URE1 submitted a Self-Report stating that it was in violation of CIP-004-3a R4.1 and R4.2. During a subsequent internal review, MRO_URE1 identified additional instances where the access list was not updated in the timeframe required by CIP-004-3a R4. MRO_URE1 self-identified seven instances of noncompliance with R4.1 and R4.2. In all seven instances of noncompliance, an employee or contractor retired, transferred, or resigned, thereby no longer requiring Physical Security Perimeter (PSP) access, but physical access was not removed from the access provisioning system in the required timeframe. The duration of the instances were: two days (three instances); three days (one instance); four days (one instance); seven days (one instance); and 11 days (one instance). The root cause of six instances was MRO_URE1 personnel's and contractors' failing to follow access policies, and the failure to execute access removal procedures. These instances were typically the result of the late submission of a personnel form. Instance number seven was caused by human error due to improper implementation of the revocation schedule by the administrator of the provisioning system. | CIP-004-3a | R4: R4.1; R4.2 | Lower | Severe | MRO determined that this violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). A violation of CIP-004-3a R4 has the potential to affect the reliable operation of the BPS by providing the opportunity for unauthorized personnel to access Critical Cyber Assets (CCAs), which could result in harm to the integrity of the CCAs. The overall number of errors was small (approximately half of a percent) in relation to the large number of access changes MRO_URE1 performs. Furthermore, none of the instances of noncompliance involved an individual who had been terminated, and MRO_URE1 had strong detective controls in place that limited the duration of the instances of noncompliance to less than two weeks. | When the first identified failure to revoke physical access occurred | When access was revoked and the access list was updated to accurately list physical access rights | $152,000 (for MRO2014013713, MRO2013013155, MRO2013012800, MRO2013012366, MRO2014014472, MRO2014013361, MRO2013013116, MRO2013011986, MRO2013012126, MRO2013013054, and MRO2013012127) | Self-Report | To mitigate this violation, MRO_URE1: 1. contacted vendors that have CIP access and reiterated the current requirements for timely access removal; 2. updated the agreement for vendors to specifically identify responsibilities relating to CIP access; 3. updated all user access control documentation with any changes due to the new agreements; 4. provided coaching and counseling to responsible personnel; 5. revoked access for the retired employees and contractors; 6. created a joint access agreement entity distribution email list; 7. revised and distributed the access removal template; 8. reminded the joint access agreement entity to use the removal template for all access removal requests, to use the distribution email list, and to copy MRO_URE1 on that request; and 9. developed a monthly communication process for emailing each entity to share information on pending retirements. | 2014-10-16 | 2015-02-27 | Does Not Contest | MRO applied mitigating credit to the penalty amount for the following considerations: 1. MRO_URE1 has demonstrated the ability to self-assess and identify violations related to CIP Standards. It has undertaken a comprehensive review of its CIP Compliance Program and has continuously self-reported noncompliance; 2. MRO_URE1 demonstrated its commitment to reliability and security of its system through a comprehensive review of its CIP compliance program and a concerted effort to focus resources and improve management practices around CIP compliance efforts; 3. MRO_URE1 cooperated in an exemplary manner throughout the course of the investigation, risk determination, and mitigation phases of these violations; 4. MRO_URE1 invested in a design review, verification, and validation to assess MRO_URE1's security posture following implementation of an EMS replacement project; and 5. MRO gave significant credit to MRO_URE1 for its commitment to the development, implementation, and continuous improvement of its internal compliance program (ICP). MRO_URE1's prior noncompliance with CIP-004 R4 was not considered an aggravating factor.
Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2013012366 | Settlement Agreement | MRO_URE1 submitted a Self-Certification stating that it was in violation of CIP-005-1 R1.5. MRO_URE1 subsequently discovered and reported 13 additional instances of noncompliance with CIP-005-1 R1.3 and R1.5. The identified instances include: 1. A security patch for an Access Point was not assessed within 30 days from its availability as required by CIP-007-1 R3.1. The duration of the instance was 12 days. 2. An Access Control Point at one substation was not configured to automatically alert for detected Cyber Security Incidents as required by CIP-007-1 R6.2. The duration of the instance was approximately three-and-a-half years. 3. Two shared passwords on servers used for authentication purposes were not changed within 90 days as required by MRO_URE1's policy. CIP-007-1 R5.3.3 requires that passwords be changed annually, or more frequently based on risk. The duration of the instance was approximately six months. 4. A failed hard drive used in the logging of dialup access was returned to the vendor without being erased as required by CIP-007-1 R7. The duration of the instance was approximately six months. 5. A dialup Access Point local default password was not changed as required by CIP-007-1 R5.2.1. The duration of the instance was approximately four-and-a-half years. 6. Alerts being generated by substation access points had not been consistently investigated according to MRO_URE1's documented procedures as required by CIP-007-1 R6. The duration of the instance was approximately four-and-a-half years. 7. The application that was provisioning control to substations was configured to use the corporate active directory servers but was not identified as a CIP-controlled Electronic Access Control or Monitoring System (EACMS) as required by R1.5. The duration of the instance was approximately one year. 8. MRO_URE1 failed to perform the scheduled evaluations for some security patches within 30 days as required by CIP-007-1 R3.1. The duration of the instance was approximately 14 months. 9. An undocumented Access Point was inadvertently established at a Critical Asset substation when a network connection was implemented in error in violation of R1.3. The duration of the instance was approximately seven months. 10. MRO_URE1 discovered additional instance where alerts being generated by substation access points were not consistently investigated according to MRO_URE1's documented procedures as required by CIP-007-1 R6. The duration of the instance was approximately four and a half years. 11. A logging device was not properly identified as an EACMS device and requirements associated with access control were not properly implemented as required by CIP-003-1 R5 and CIP-004-1 R4. The duration of the instance was approximately two-and-a-half years. 12. A system was not configured to alert on access or unauthorized login attempts as required by CIP-005-1 R3.2. Although the device was alerting for the devices it was monitoring, it was not monitoring itself or alerting for internal issues related to the system. The duration of the instance was approximately two and a half years. 13. A system did not implement documented processes for CIP significant changes as required by CIP-007-1 R1. Specifically, MRO_URE1 did not have any evidence of testing nor associated results. The duration of the instance was approximately ten months. 14. A system did not implement monitoring tools to monitor cyber security events as required by CIP-005-1 R3. The duration of the instance was approximately two-and-a-half years. 15. MRO_URE1 reported that a significant security patch was released but was not assessed until approximately five months later, which exceeded the 30 days allowed by CIP-007-1 R3.1. 16. MRO_URE1 reported that logging and alerting at ESP access points had become inactive at several substations after a firmware update was installed. This occurred even though the patch was tested in a lab environment prior to field implementation. The duration of the instance was approximately one month. The root cause of these instances was lack of sufficient processes. | CIP-005-1 | R1: R1.3; R1.5 | Medium | Severe | MRO determined that this violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). A violation of CIP-005-1 R1 has the potential to affect the reliable operation of the BPS by providing the opportunity for cyber intrusions to occur on Critical Cyber Assets (CCAs) located outside an established ESP. All but two of the issues (numbers four and eight) were limited to substations and not control centers. Two of the issues (numbers three and seven) were related to the implementation of a solution to provide an “Intermediate System” level of protection, which is a CIP V5 concept and exceeds the CIP V1 and V3 requirements. Finally, MRO_URE1 self-identified these issues, which is a strong indication of effective internal controls. | When the standard became mandatory and enforceable on MRO_URE1 | Mitigation Plan completion | $152,000 (for MRO2014013713, MRO2013013155, MRO2013012800, MRO2013012366, MRO2014014472, MRO2014013361, MRO2013013116, MRO2013011986, MRO2013012126, MRO2013013054, and MRO2013012127) | Self-Certification | To mitigate this violation, MRO_URE1: 1. developed security patch management, multiple failed authentication, firewall trafficking, and alarm tracking sheets; 2. created awareness of password checking and alarm verification through lists and bi-monthly meetings; 3. updated procedures and conducted testing to identify improvement opportunities for the patch management processes, change control processes; 4. disabled or removed some undocumented OS accounts, and other undocumented OS accounts were added to the current list of shared accounts; 5. configured a device to send user access attempts, including failed attempts, in the form of email alerts to the device's administrator; 6. formed a cross-functional team to review cross-departmental procedures used when a project involves remote connectivity; 7. reviewed and updated alert rules and cyber security protection documentation for the device; 8. completed physical security perimeter tasks; 9. applied CIP-005 R1.5 controls to the director, and implemented an application to new system; 10. setup and configured active directory in the EMS DMZ environment; 11. performed regular validation of the patch management process on a sampling of patches to determine that notifications and evaluations are being performed in a timely manner; and 12. incorporated a degaussing device, and maintained disk degaussing records to verify process compliance. | 2015-08-27 | 2015-12-28 | Does Not Contest | MRO applied mitigating credit to the penalty amount for the following considerations: 1. MRO_URE1 has demonstrated the ability to self-assess and identify violations related to CIP Standards. It has undertaken a comprehensive review of its CIP Compliance Program and has continuously self-reported noncompliance; 2. MRO_URE1 demonstrated its commitment to reliability and security of its system through a comprehensive review of its CIP compliance program and a concerted effort to focus resources and improve management practices around CIP compliance efforts; 3. MRO_URE1 cooperated in an exemplary manner throughout the course of the investigation, risk determination, and mitigation phases of these violations; 4. MRO_URE1 invested in a design review, verification, and validation to assess MRO_URE1's security posture following implementation of an EMS replacement project; and 5. MRO gave significant credit to MRO_URE1 for its commitment to the development, implementation, and continuous improvement of its internal compliance program (ICP). MRO_URE1's prior noncompliance with CIP-005 R1 was not considered an aggravating factor.
Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2014014472 | Settlement Agreement | MRO_URE1 submitted a Self-Report stating that it was in violation of CIP-005-1 R3. In preparation for an upcoming audit, MRO_URE1 discovered the firewalls protecting the communication between the Electronic Security Perimeters (ESPs) for the primary and backup control centers were not sending the required logs to the centralized syslog environment. Upon conducting an investigation, MRO_URE1 determined that the firewalls were not properly configured to log events and send all the logs to the centralized EMS Syslog environment. MRO_URE1's review revealed that the devices were not logging because the configuration was set to detect only a limited amount of specific information across the logging environment for alarming and notification, such as unauthorized access attempts. The primary cause of the findings was a combination of the initial lack of focused adherence to CIP requirements and a lack of internal controls that would have confirmed and verified compliance that the firewall was logging the relevant information. | CIP-005-1 | R3: R3.2 | Medium | Severe | MRO determined that this violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to log activity for an access point to the ESP at a control center represents a significant potential risk. Additionally, the violation existed for over five years, which increases the risk associated with the violation. In this case, the risk of this violation was reduced because the violation was limited to traffic between the primary and backup control centers. This communication path did not allow for interactive access from outside the ESP (i.e., the internet). All interactive access from outside the ESP was required to pass through the firewall at the primary control center. MRO did not detect any noncompliance associated with the firewall at the primary control center in the subsequent Compliance Audit. Additionally, the risk is limited because logging is a detective control to alert a registered entity of security events that have already occurred and is not intended to provide active security controls that prevent an adversary from obtaining access. | When the Standard became mandatory and enforceable on MRO_URE1 | When the firewalls were properly configured to send the required logs to the centralized syslog environment | $152,000 (for MRO2014013713, MRO2013013155, MRO2013012800, MRO2013012366, MRO2014014472, MRO2014013361, MRO2013013116, MRO2013011986, MRO2013012126, MRO2013013054, and MRO2013012127) | Self-Report | To mitigate this violation, MRO_URE1: 1. configured the Firewall Logging environment on the applicable Electronic Access Point (EAP); 2. verified that logs were being correctly captured and sent to the appropriate location; 3. reviewed CIP-005-1 with EMS personnel to reinforce the criticality of following NERC Reliability Standards; 4. reviewed the process for all EMS CIP Cyber Assets and identified improvement opportunities; and 5. updated EMS process and documentation. | 2015-05-05 | 2016-01-04 | Does Not Contest | MRO applied mitigating credit to the penalty amount for the following considerations: 1. MRO_URE1 has demonstrated the ability to self-assess and identify violations related to CIP Standards. It has undertaken a comprehensive review of its CIP Compliance Program and has continuously self-reported noncompliance; 2. MRO_URE1 demonstrated its commitment to reliability and security of its system through a comprehensive review of its CIP compliance program and a concerted effort to focus resources and improve management practices around CIP compliance efforts; 3. MRO_URE1 cooperated in an exemplary manner throughout the course of the investigation, risk determination, and mitigation phases of these violations; 4. MRO_URE1 invested in a design review, verification, and validation to assess MRO_URE1's security posture following implementation of an EMS replacement project; and 5. MRO gave significant credit to MRO_URE1 for its commitment to the development, implementation, and continuous improvement of its internal compliance program (ICP). MRO considered MRO_URE1's compliance history and determined there were no relevant instances of noncompliance.
Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2014013361 | Settlement Agreement | MRO_URE1 submitted a Self-Report stating that it was in violation of CIP-006-3c R2.2. For the first instance of noncompliance, MRO_URE1 reported that a shared administrator password was not updated within 90 days per MRO_URE1's password security policy and as required by CIP-007-3 R5.3.3. The account owner who manages this account receives one password change email notification every 90 days from a password vault tool, which includes all passwords that need to be changed and the due date. The account owner overlooked this email notification and upon realizing it, changed the password. The duration of the instance was approximately one month. In the second instance of noncompliance, MRO_URE1 did not perform scheduled evaluations for the security patches within 30 days of availability for an access provisioning system as required by CIP-007-3 R3.1. The duration of the instance was approximately four months. In the third instance of noncompliance, MRO_URE1 identified a CIP-006-3c R2.2 issue related to CIP-007-3 R5.3.3. During the process of approving and creating a new badge administrator account, MRO_URE1 discovered that one temporary contractor badge administrator had shared his application login credentials with another temporary contractor badge administrator, who used the account to log into an application. Badge administrators are the personnel who issue staff and contract personnel badges for MRO_URE1 facilities. The badge administrators have access to the application but can only create and print badges. They do not have the ability to modify access privileges, to manipulate PSPs, or to log into servers. The duration of the instance was less than one week. The root cause was insufficient process, inadequate coordination, and a lack of preventive controls. | CIP-006-3c | R2: R2.2 | Medium | Severe | MRO determined that this violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). A violation of CIP-006-3c R2 has the potential to affect the reliable operation of the BPS, providing the opportunity for undetected compromise of Critical Cyber Assets (CCAs) to occur without the Responsible Entity’s knowledge. Notwithstanding, except for CIP-007 R3.1 and R5.3.3, all the other protective measures specified in CIP-006-3c R2.2 had been afforded. The risk associated with instance one was minimal because MRO_URE1's policy to change the password every 90 days is aggressive and well within the 365-day discretionary minimum allowed by CIP-007-1 R5.3.3, the duration was relatively brief, and MRO_URE1 timely detected and self-reported the noncompliance. However, MRO determined the overall combined risk of this violation was moderate. Failure to assess security patches (instance two) represents a significant two-fold potential risk. For instance, the device may have a vulnerability, which is the purpose of the patch, and by the nature of the release of the patch, the vulnerability is well-known to those who may have a malicious intent to exploit the vulnerability. For instance three, the sharing of personal passwords is an indicator of weakness in the effectiveness of a training program, and the issue increases the potential for unauthorized physical access to control centers. This violation would typically pose a serious risk, but the risk was mitigated because it was timely discovered and was self-reported, and the noncompliance was limited to a few days, which is an indication of strong secondary controls. Further, the contractor in question only had physical access, and did not have logical or interactive access. Finally, MRO_URE1 promptly terminated the contractor who shared the password and reassigned the contractor who used the shared password, which displays a commitment to ensuring security of its facilities and the BPS. | When the shared administrator password was due to be reset | When the badge administrator accounts were disabled | $152,000 (for MRO2014013713, MRO2013013155, MRO2013012800, MRO2013012366, MRO2014014472, MRO2014013361, MRO2013013116, MRO2013011986, MRO2013012126, MRO2013013054, and MRO2013012127) | Self-Report | To mitigate this violation, MRO_URE1: 1. performed a CIP V3 and V5 assessment to determine what devices, if any, would be considered CIP Electronic Access Control Monitoring Systems (EACMS) or information repositories; 2. redesigned and procured needed hardware and software; 3. redesigned architecture to accommodate the Energy Management System environment; 4. installed systems and configured the environment; and 5. tested the functions of the specific system tool. | 2015-08-27 | 2016-01-03 | Does Not Contest | MRO applied mitigating credit to the penalty amount for the following considerations: 1. MRO_URE1 has demonstrated the ability to self-assess and identify violations related to CIP Standards. It has undertaken a comprehensive review of its CIP Compliance Program and has continuously self-reported noncompliance; 2. MRO_URE1 demonstrated its commitment to reliability and security of its system through a comprehensive review of its CIP compliance program and a concerted effort to focus resources and improve management practices around CIP compliance efforts; 3. MRO_URE1 cooperated in an exemplary manner throughout the course of the investigation, risk determination, and mitigation phases of these violations; 4. MRO_URE1 invested in a design review, verification, and validation to assess MRO_URE1's security posture following implementation of an EMS replacement project; and 5. MRO gave significant credit to MRO_URE1 for its commitment to the development, implementation, and continuous improvement of its internal compliance program (ICP). MRO_URE1's prior noncompliance with CIP-006 R2 was not considered an aggravating factor.
Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2013011986 | Settlement Agreement | MRO_URE1 submitted a Self-Certification stating that it was in violation of CIP-007-1 R3.1. There were four instances of noncompliance: 1. MRO_URE1 reported that a security patch was released , but was not assessed for applicability for almost two months, which exceeded the 30 days allowed by R3.1. The duration of the instance was approximately 24 days. 2. MRO_URE1 reported that a significant security patch was released but was not assessed for over five months, which exceeded the 30 days allowed by R3.1. The duration of the instance was approximately 100 days. 3. MRO_URE1 reported that it was not receiving security patch notifications for a certain operating system The duration of the instance was approximately 5 years. 4. MRO_URE1 reported that a review of its Security Patch Management controls identified a security patch that had not been assessed within 30 days of availability as required by R3.1. The duration of the instance was approximately one day. The root cause for failing to assess the security patches for instances one and three was miscommunication regarding the lack of notification of released patches. The root cause for instances two and four was ineffective internal controls to ensure adherence to MRO_URE1's Security Patch Management Program. | CIP-007-1 | R3: R3.1 | Lower | Severe | MRO determined that this violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). A violation of CIP-007-1 R3 has the potential to affect the reliable operation of the BPS by providing the opportunity for infiltration of unauthorized network traffic into the Electronic Security Perimeter (ESP) when security patches and upgrades are not installed on Cyber Assets within the ESP. Notwithstanding, all the issues were self-identified and self-reported, evidencing strong detective controls. Additionally, the noncompliance involving instances one and two were only applicable to substations, had a duration of less than 100 days, and were promptly mitigated. Further, instance three was merely a documentation error, and was mitigated by the submission of a Technical Feasibility Exception (TFE). Further, instance four had a duration of only one day. Additionally, MRO_URE1 states that the Critical Cyber Assets (CCAs) were protected by multiple layers of firewalls configured to only allow traffic using specific protocols to enter the network, which prevented unsolicited traffic from passing into the ESP. Access to Cyber Assets within the ESP was limited to only those individuals with authorized physical and/or electronic access rights. | When the first security patch for the full operating system was not updated | When MRO_URE1 submitted a TFE for certain patches | $152,000 (for MRO2014013713, MRO2013013155, MRO2013012800, MRO2013012366, MRO2014014472, MRO2014013361, MRO2013013116, MRO2013011986, MRO2013012126, MRO2013013054, and MRO2013012127) | Self-Certification | To mitigate this violation, MRO_URE1: 1. conducted initial training and awareness regarding compliance instances to affected employees; 2. implemented an action tracking tool to assign due dates and completion dates; 3. evaluated use of a third party for notification to monitor alerts; 4. reviewed, enhanced, and communicated security patch management program and developed a security patch management tracking sheet; 5. evaluated the possibility of a TFE submission for SEL human-machine interface devices; 6. reviewed CIP-007 R3 Security Patch Management with Energy Management System (EMS) personnel to ensure they understand the criticality of Security Patch Management; 7. reviewed Security Patch Management process for all EMS team-controlled CIP Cyber Assets to ensure proper steps are fully documented; 8. identified and applied opportunities for improvement in the Security Patch Management process; 9. reviewed, trained, and reinforced new processes and evidence with MRO_URE1 staff in order to meet CIP requirements; and 10. performed regular Security Patch Management improvement validation on a sampling of patches to determine that evaluations are being performed in a timely manner. | 2014-05-28 | 2015-04-22 | Does Not Contest | MRO applied mitigating credit to the penalty amount for the following considerations: 1. MRO_URE1 has demonstrated the ability to self-assess and identify violations related to CIP Standards. It has undertaken a comprehensive review of its CIP Compliance Program and has continuously self-reported noncompliance; 2. MRO_URE1 demonstrated its commitment to reliability and security of its system through a comprehensive review of its CIP compliance program and a concerted effort to focus resources and improve management practices around CIP compliance efforts; 3. MRO_URE1 cooperated in an exemplary manner throughout the course of the investigation, risk determination, and mitigation phases of these violations; 4. MRO_URE1 invested in a design review, verification, and validation to assess MRO_URE1's security posture following implementation of an EMS replacement project; and 5. MRO gave significant credit to MRO_URE1 for its commitment to the development, implementation, and continuous improvement of its internal compliance program (ICP). MRO_URE1's prior noncompliance with CIP-007 R3 was not considered an aggravating factor.
Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2013012126 | Settlement Agreement | MRO_URE1 submitted a Self-Report stating that it had an issue of CIP-007-3a R4.2 because it failed to implement its process for the update of anti-virus and malware prevention signatures for certain Critical Cyber Assets (CCAs) within the Electronic Security Perimeter (ESP). MRO_URE1 replaced its antivirus software, but failed to include all of the operating regions in the implementation. As a result, MRO_URE1 stopped receiving the automatic signature updates for certain CCAs. Signature updates of certain CCAs within the MRO_URE1 control center were not implemented, as required by R4.2. The duration of the instance was approximately 15 months. This violation occurred when MRO_URE1 stopped receiving automatic updates for the antivirus product and MRO_URE1 staff mistakenly believed that the first antivirus product was replaced company-wide by the second antivirus product. The root cause of the violation was lack of project oversight to ensure that the anti-virus product had been implemented on certain Cyber Assets within the ESP at MRO_URE1's primary and backup control centers. | CIP-007-3a | R4: R4.2 | Medium | Severe | MRO determined that this violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). A violation of CIP-007-3a R4 has the potential to affect the reliable operation of the BPS by providing the opportunity for the introduction, exposure, and propagation of malware on Cyber Assets within the ESP. The failure to update the anti-virus signatures for a large control center for over one year is a significant oversight and demonstrates a lack of attention to procedures. Notwithstanding, the violation was self-identified and self-reported, which is evidence of strong detective controls. Additionally, the anti-virus and malware prevention software was still running, albeit with outdated signatures. Further, MRO_URE1 installed an intrusion detection system (IDS) which was configured to detect the presence of viruses and malware at the access point to the ESP. IDS was not required at the time of the violation and is typically considered sufficient to meet the anti-malware requirements for CIP version 5. Finally, MRO_URE1 provided evidence that it provides training on the risks of removable media, which is the most common method for malware to infect control systems. This type of training is not required under CIP version 3. Additionally, MRO_URE1 stated that its CCAs and non-CCAs within the ESP were protected by pairs of firewalls running in an active/standby configuration, and configured to only allow traffic using specific protocols to enter the network, which prevented unsolicited traffic from passing into the ESP. MRO_URE1 deployed intrusion prevention/detection systems on the outside of the ESP firewalls, which provided real-time log analysis, event alerting, and blocking of both internal and external malicious transmissions to the control system ESP. MRO_URE1 implemented additional protective measures to protect Cyber Assets inside the ESP and access points to the ESP, including controlling access to network resources based on job functions, host-based anti-malware systems, where technically feasible; password and lockout policies; and personnel physical and cyber access reviews and control processes. In addition, MRO_URE1's control system network had no direct Internet connectivity, no access to e-mail servers or clients, and auto-run/auto-play functions were disabled on certain devices. Finally, access to MRO_URE1's Cyber Assets within the ESP was limited to only those individuals with authorized physical and/or electronic access rights. | When MRO_URE1 failed to run the necessary antivirus signatures | When the signature updates were performed for certain CCAs in MRO_URE1's primary and backup control centers | $152,000 (for MRO2014013713, MRO2013013155, MRO2013012800, MRO2013012366, MRO2014014472, MRO2014013361, MRO2013013116, MRO2013011986, MRO2013012126, MRO2013013054, and MRO2013012127) | Self-Report | To mitigate this violation, MRO_URE1: 1. installed anti-virus software, along with the most current anti-virus signature updates, on the MRO_URE1 EMS ESP Cyber Assets; 2. provided additional training to MRO_URE1 staff with security responsibilities; and 3. updated change management procedures to provide additional management oversight of anti-virus updates to ensure signatures remain current. | 2013-08-28 | 2014-10-31 | Does Not Contest | MRO applied mitigating credit to the penalty amount for the following considerations: 1. MRO_URE1 has demonstrated the ability to self-assess and identify violations related to CIP Standards. It has undertaken a comprehensive review of its CIP Compliance Program and has continuously self-reported noncompliance; 2. MRO_URE1 demonstrated its commitment to reliability and security of its system through a comprehensive review of its CIP compliance program and a concerted effort to focus resources and improve management practices around CIP compliance efforts; 3. MRO_URE1 cooperated in an exemplary manner throughout the course of the investigation, risk determination, and mitigation phases of these violations; 4. MRO_URE1 invested in a design review, verification, and validation to assess MRO_URE1's security posture following implementation of an EMS replacement project; and 5. MRO gave significant credit to MRO_URE1 for its commitment to the development, implementation, and continuous improvement of its internal compliance program (ICP). MRO_URE1's prior noncompliance with CIP-007 R4 was not considered an aggravating factor.
Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2013013054 | Settlement Agreement | MRO_URE1 submitted a Self-Report stating that it was in violation of CIP-007-3a R5. During its annual Substation Cyber Vulnerability Assessment (CVA), MRO_URE1 identified the following issues: 1. Approximately 40 percent of MRO_URE1's Critical Asset substations were found to have at least one protective relay with a default password that had not been changed since installation. The duration of the instance was approximately three-and-a-half years. 2. Approximately eight percent of MRO_URE1's Critical Asset substations were found to have a “backdoor” default password on six Remote Terminal Units (RTUs) (that were designated as Critical Cyber Assets (CCAs)) that had not been changed since installation. The duration of the instance was over four years. 3. Approximately 18 percent of MRO_URE1's Critical Asset substations were found to have a “super-user” default password on the legacy tone communication equipment which was not capable of being changed as required. If this issue had been documented, it would not have been a violation under CIP V5. The duration of the instance was over one month. 4. Approximately 28 percent of MRO_URE1's CCAs had a default password that had not been changed. The duration of the instance was approximately three years. 5. During an internal MRO_URE1 review of account management, sufficient evidence was not available to assure that a thorough review of access privileges had been performed on time, as required by R5.1. Available evidence did not consistently list the authorized shared account users, the authorized shared account users that had no activity for that quarter, or that all authorized shared account users were reviewed to determine whether they had a continued business need to maintain their access, as required by R5.2.2, R5.2.3, and R5.1, respectively. The review revealed that the documentation provided as evidence of the shared account activity annual review did not match the dated attestation provided by the personnel who performed the review. The review also identified eight shared accounts which did not have an audit trail of account use, as required by R5.1.2. The duration of the instance was approximately five years. The primary cause of the findings was a lack of sufficient processes regarding adherence to CIP requirements. MRO_URE1 made aggressive changes to its internal substation policies and procedures, and has since aggressively looked for areas of noncompliance. These findings are a result of that effort. | CIP-007-1 | R5: R5.1; R5.1.2; R5.2; R5.2.2; R5.2.3; R5.3; R5.3.3 | Medium | Severe | MRO determined that this violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The need to change default passwords on CCAs is fundamental. The accounts with default passwords present the most risk because they are typically “super-user” accounts that have broad capability to configure and/or operate the Cyber Assets. The risk is significant for these accounts with default passwords because the password can be easily obtained. However, for parts one through four of this violation, regarding the default password issues, the risk related to unchanged default passwords was reduced for the following reasons: 1. The issues were self-identified by MRO_URE1 and promptly mitigated. Additionally, MRO_URE1 initiated a comprehensive mitigation plan to ensure that all default passwords were discovered; 2. The issues were limited to substations and did not impact control centers; and 3. MRO_URE1 was conservative during the determination as to what substations constituted Critical Assets in its Risk-Based Assessment Methodology (RBAM). This is evidenced by the reduction in Version 3 Critical Asset substations compared to Version 5 Medium Impact substations after applying the bright-line impact rating criteria. The comprehensive review of access and approval is critical in ensuring the access approval and termination process is complete and accurate. For part number five of this violation, regarding the account management issue, the potential effectiveness of this critical management practice was reduced in the event that an adversary was utilizing a shared account. The potential risk was reduced by the following factors: 1. This issue was self-identified during an internal review which was not mandated by the requirements; 2. The review of shared accounts is performed quarterly as opposed to yearly, which is the maximum duration allowed by the Standard; and 3. The lack of an audit trail, which was identified during the review, is mitigated by the corporate policy of requiring two-factor authentication for remote access into an ESP. This was not mandated until Version 5 of the requirements. | When MRO_URE1 was required to be compliant with CIP-007-1 R5 | When the Mitigation Plan was completed | $152,000 (for MRO2014013713, MRO2013013155, MRO2013012800, MRO2013012366, MRO2014014472, MRO2014013361, MRO2013013116, MRO2013011986, MRO2013012126, MRO2013013054, and MRO2013012127) | Self-Report | To mitigate this violation, MRO_URE1: 1. changed the default passwords on protective relay devices that were identified during the Cyber Vulnerability Assessment (CVA); 2. developed a list of devices that are known to have default passwords; 3. developed a Substation CVA procedure; 4. enhanced CVA process procedure and templates relating to default password and network community string checks; 5. changed the default passwords on RTU devices and disconnected devices with super-user passwords; 6. performed Quarterly Activity Report (QAR) validations; 7. reviewed manufacturer technical manuals to identify factory default accounts or passwords; and 8. developed a plan to change any newly identified default accounts and passwords. | 2016-03-25 | 2016-09-26 | Does Not Contest | MRO applied mitigating credit to the penalty amount for the following considerations: 1. MRO_URE1 has demonstrated the ability to self-assess and identify violations related to CIP Standards. It has undertaken a comprehensive review of its CIP Compliance Program and has continuously self-reported noncompliance; 2. MRO_URE1 demonstrated its commitment to reliability and security of its system through a comprehensive review of its CIP compliance program and a concerted effort to focus resources and improve management practices around CIP compliance efforts; 3. MRO_URE1 cooperated in an exemplary manner throughout the course of the investigation, risk determination, and mitigation phases of these violations; 4. MRO_URE1 invested in a design review, verification, and validation to assess MRO_URE1's security posture following implementation of an EMS replacement project; and 5. MRO gave significant credit to MRO_URE1 for its commitment to the development, implementation, and continuous improvement of its internal compliance program (ICP). MRO_URE1's prior noncompliance with CIP-007 R5 was not considered an aggravating factor.
Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2013012127 | Settlement Agreement | MRO_URE1 submitted a Self-Report stating that it was in violation of CIP-007-1 R6. MRO_URE1 failed to implement security status monitoring for certain assets within the Electronic Security Perimeter (ESP). An application was installed to monitor an operating system, but did not adequately address the requirements of R6 for the certain assets. This noncompliance was uncovered during an internal Energy Management System (EMS) review of the software inventory list for all operating regions. Many assets were affected by this noncompliance, including multiple control centers and numerous Critical Cyber Assets (CCAs). The root cause was insufficient processes. | CIP-007-1 | R6: R6.1; R6.2; R6.3; R6.4; R6.5 | Medium | Severe | MRO determined that this violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to monitor the security status of multiple large control centers is a significant oversight and can potentially cause significant risk in the system. A violation of CIP-007-1 R6 has the potential to affect the reliable operation of the BPS by providing the opportunity for undetected compromise of CCAs and other system events that are related to cyber security to occur without the Responsible Entity’s knowledge. Notwithstanding, the requirement for logging and the associated monitoring of logs is a detective control, as opposed to a preventive control. The requirement for the reporting of security status events can help limit the effect of attacks, but does not prevent them from occurring. Further, MRO_URE1 utilized an intrusion detection system (IDS), which was configured to detect the presence of viruses and malware at the access point to the ESP. IDS was not required at the time of the violation and is typically considered sufficient to meet the anti-malware requirements for CIP version 5. Moreover, MRO_URE1 provided evidence that it provides training on the risks of removable media, which is the most common method for malware to infect control systems. Additionally, this type of training is not under version 3 requirements of the standard. Further, the violation was self-identified, evidencing effective internal controls. MRO_URE1 also stated that its CCAs and non-CCAs within the ESP were protected by pairs of firewalls running in an active/standby configuration, and configured to only allow traffic using specific protocols to enter the network, which prevented unsolicited traffic from passing into the ESP. MRO_URE1 deployed intrusion prevention/detection systems on the outside of the ESP firewalls, which provided real-time log analysis, event alerting, and blocking of both internal and external malicious transmissions to the control system ESP. MRO_URE1 implemented additional protective measures to protect Cyber Assets inside the ESP and access points to the ESP, including controlling access to network resources based on job functions, host-based anti-malware systems, where technically feasible; password and lockout policies; and personnel physical and cyber access reviews and control processes. In addition, MRO_URE1's control system network had no direct Internet connectivity, no access to e-mail servers or clients, and auto-run/auto-play functions were disabled on all Windows devices. Finally, access to MRO_URE1's Cyber Assets within the ESP was limited to only those individuals with authorized physical and/or electronic access rights. | When the Standard became mandatory and enforceable on MRO_URE1 | When MRO_URE1 completed the process of configuring and testing to ensure that all Cyber Assets within its ESPs were properly logging, monitoring, and alerting for events | $152,000 (for MRO2014013713, MRO2013013155, MRO2013012800, MRO2013012366, MRO2014014472, MRO2014013361, MRO2013013116, MRO2013011986, MRO2013012126, MRO2013013054, and MRO2013012127) | Self-Report | To mitigate this violation, MRO_URE1: 1. reviewed monitoring and event alerting implementation plan and architecture; 2. implemented monitoring and event alerting on certain devices; 3. reviewed monitoring and event alerting of Cyber Assets in ESPs; and 4. updated Cyber Asset configuration documentation and validated that all Cyber Assets were properly configured. | 2013-10-29 | 2014-10-31 | Does Not Contest | MRO applied mitigating credit to the penalty amount for the following considerations: 1. MRO_URE1 has demonstrated the ability to self-assess and identify violations related to CIP Standards. It has undertaken a comprehensive review of its CIP Compliance Program and has continuously self-reported noncompliance; 2. MRO_URE1 demonstrated its commitment to reliability and security of its system through a comprehensive review of its CIP compliance program and a concerted effort to focus resources and improve management practices around CIP compliance efforts; 3. MRO_URE1 cooperated in an exemplary manner throughout the course of the investigation, risk determination, and mitigation phases of these violations; 4. MRO_URE1 invested in a design review, verification, and validation to assess MRO_URE1's security posture following implementation of an EMS replacement project; and 5. MRO gave significant credit to MRO_URE1 for its commitment to the development, implementation, and continuous improvement of its internal compliance program (ICP). MRO considered MRO_URE1's compliance history and determined there were no relevant instances of noncompliance.
Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2013013116 | Settlement Agreement | MRO_URE1 submitted a Self-Report stating that it was in violation of CIP-006-3c R6. While reviewing access logs and camera footage for the MRO_URE1 control center, MRO_URE1 identified that a cleaning contractor (contractor one) had entered the control center but did not sign in using the manual log. Contractor one was granted access by a second cleaning contractor (contractor two) who had badge access but also did not sign in using the manual log. MRO_URE1 further discovered that contractor two provided access to contractor one daily for approximately eight days. In each instance, contractor one was in the control center for up to thirty minutes performing cleaning duties. Personnel for the cleaning contractor had received training in CIP access requirements. Upon learning of the issue, MRO_URE1 promptly issued written and telephone notice to the contract vendor to take corrective action. The root cause of the violation was the contractor’s failure to fully understand MRO_URE1's escorted visitor policy. | CIP-006-3c | R6 | Lower | Severe | MRO determined that this violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). A violation of CIP-006-3c R6 has the potential to affect the reliable operation of the BPS by providing the opportunity for undetected compromise of Cyber Assets to occur without the Responsible Entity’s knowledge. Notwithstanding, the unauthorized visitor (contractor one) was properly escorted by the authorized contractor (contractor two). Additionally, the issue occurred at a manned distribution control center with limited BPS Critical Assets. Finally, the issue was self-identified and promptly mitigated, which is an indication of strong internal controls. | When contractor one first accessed the MRO_URE1 control center without following the access policy | When contractor one last accessed the MRO_URE1 control center without following the access policy | $152,000 (for MRO2014013713, MRO2013013155, MRO2013012800, MRO2013012366, MRO2014014472, MRO2014013361, MRO2013013116, MRO2013011986, MRO2013012126, MRO2013013054, and MRO2013012127) | Self-Report | To mitigate this violation, MRO_URE1: 1. allowed only CIP-certified contract cleaners to enter the MRO_URE1 CIP-restricted areas, as MRO_URE1 no longer permits escorting of non-certified CIP personnel; 2. provided CIP certification training to contract cleaners whose job duties require CIP access, including building supervisor, primary cleaner, and one alternate, in their primary language; 3. reinforced the policy that only CIP-certified cleaners may clean the CIP spaces, and that if there are no CIP-certified cleaners available, the spaces should not be cleaned; and 4. requires quarterly CIP re-training for all contract cleaners with CIP access. Records will be kept in each individual's personnel folder, available upon request. | 2013-10-11 | 2015-04-22 | Does Not Contest | MRO applied mitigating credit to the penalty amount for the following considerations: 1. MRO_URE1 has demonstrated the ability to self-assess and identify violations related to CIP Standards. It has undertaken a comprehensive review of its CIP Compliance Program and has continuously self-reported noncompliance; 2. MRO_URE1 demonstrated its commitment to reliability and security of its system through a comprehensive review of its CIP compliance program and a concerted effort to focus resources and improve management practices around CIP compliance efforts; 3. MRO_URE1 cooperated in an exemplary manner throughout the course of the investigation, risk determination, and mitigation phases of these violations; 4. MRO_URE1 invested in a design review, verification, and validation to assess MRO_URE1's security posture following implementation of an EMS replacement project; and 5. MRO gave significant credit to MRO_URE1 for its commitment to the development, implementation, and continuous improvement of its internal compliance program (ICP). MRO_URE1's prior noncompliance with CIP-006 R6 was not considered an aggravating factor.
ReliabilityFirst Corporation (ReliabilityFirst or RFC) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2015014836 | Settlement Agreement | RFC_URE1 submitted a Self-Report to ReliabilityFirst reporting it was in violation of CIP-004-3a R4. RFC_URE1 discovered that although it conducted reviews during the second and fourth quarters of a certain year of all lists of personnel who had authorized cyber access to Critical Cyber Assets (CCAs), it failed to include a particular segment of personnel in both cases. Additionally, RFC_URE1 also discovered that it failed to conduct the requisite review of personnel with authorized unescorted physical access to CCAs. The root cause of this violation was that RFC_URE1 relied on a manual process to conduct its personnel list reviews. This major contributing factor relates to the management practice area of workforce management, which focuses on, inter alia, developing a program to manage employee permissions and access to assets. | CIP-004-3a | R4 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the quarterly review process is a redundancy and not the primary mechanism RFC_URE1 utilizes to identify personnel who no longer require access. RFC_URE1 primarily uses a personnel status change and access revocation procedure and software application to initiate the removal of an individual’s cyber or physical access when it is no longer required. This procedure requires RFC_URE1 supervisors and contractor sponsors to submit a personnel status change and access revocation ticket whenever access is no longer required. Second, RFC_URE1 properly followed the personnel status change and access revocation procedure in this case and identified and removed cyber access for one individual despite the fact that the individual remained on the access list, which RFC_URE1 failed to review on a quarterly basis. | the beginning of the third quarter | when RFC_URE1 completed all of the requisite reviews | $0 (for RFC2015014836, RFC2015014973, RFC2015014832, RFC2015014714, RFC2015014834, RFC2015014775, RFC2015015022, RFC2015014833, and RFC2015014837) | Self-Report | To mitigate this violation, RFC_URE1: 1) removed from the list the one individual identified who no longer required authorized cyber access to CCAs; 2) entered quarterly reviews into an electronic system that will automatically notify by email the responsible departments. These notifications will be initiated at the beginning of each quarter and will continue weekly for 60 days and then daily until the electronic task is completed; 3) assigned responsibility to an IT compliance team to update and maintain the electronic system used to track the required quarterly reviews. This team will develop a procedure that will ensure independent monitoring of the quarterly review process, including a scheduled monthly meeting to review the status of all pending quarterly reviews; and 4) configured the electronic system used to track the required quarterly reviews to automatically provide daily email notifications to management and compliance personnel whenever the quarterly reviews are not completed 30 days prior to the end of the quarter. This escalation process is designed to ensure that the proper attention and resources are focused on completing the quarterly reviews. | 4/30/2015 | TBD | Agrees/Stipulates | In most instances, a Regional Entity could appropriately treat such noncompliance without any penalty or negotiation of a Settlement Agreement through the Compliance Exception (CE) or Find, Fix, Track, and Report (FFT) programs. ReliabilityFirst observed that RFC_URE1 accelerated its self-monitoring efforts based on the impending implementation of the CIP Version 5 Reliability Standards. ReliabilityFirst focused additional resources on RFC_URE1's Self-Reports because RFC_URE1 was awaiting regulatory actions, such as new Reliability Standards or an approaching Compliance Audit, to assess its security and compliance. ReliabilityFirst chose to treat these violations in a Settlement Agreement instead of as CEs or FFTs in order to discourage RFC_URE1 and other registered entities from relying solely on such outside activities as the impetus for self-evaluations. ReliabilityFirst reviewed RFC_URE1's internal compliance program and considered it to be a partial mitigating factor in the penalty determination. Effective oversight of the reliability of the BES depends on robust and timely self-reporting by registered entities. RFC_URE1 identified and reported the Alleged Violations at issue in this Agreement due to the execution of its compliance program and its comprehensive review of its entire CIP compliance program. As a result, ReliabilityFirst seeks to encourage this type of self-reporting, characterized by timely detection and correction unrelated to a pending regional compliance monitoring action, by awarding mitigating credit. RFC_URE1 has been highly cooperative throughout the entire enforcement process. Throughout the enforcement process, RFC_URE1 has voluntarily provided ReliabilityFirst with an abundance of information regarding the Alleged Violations in a manner that was detailed, thorough, thoughtful, organized, and timely. RFC_URE1 has been open with ReliabilityFirst regarding its Alleged Violations, processes, systems, and organization and this insight has allowed ReliabilityFirst to better analyze the Alleged Violations and assist RFC_URE1 with resolving the same. As stated above, RFC_URE1's response to the Alleged Violations was efficient and effective, and ReliabilityFirst awarded mitigating credit to encourage this sort of response by other registered entities in the future. RFC_URE1 has taken actions that exceed what is required to mitigate each of the Alleged Violations, and which ReliabilityFirst therefore considers worthy of credit as Above and Beyond action items. The Above and Beyond activities described below enhance the reliability of the BES beyond mere baseline compliance with the Reliability Standards, and therefore ReliabilityFirst viewed them favorably when determining the appropriate penalty. RFC_URE1 has made significant operational upgrades to its CIP program and cyber security activities. These upgrades and improvements include purchasing and implementing technology to automate several processes and procedures to further strengthen RFC_URE1's compliance objectives as the company transitions to CIP v5. ReliabilityFirst and RFC_URE1 also agreed to several non-monetary sanctions including: (1) moving RFC_URE1's CIP v5 audit up to the second quarter of its designated year; (2) increasing RFC_URE1's audit frequency from every six years to every three years; and (3) requiring RFC_URE1's CEO to execute the Settlement Agreement. ReliabilityFirst did not consider RFC_URE1's CIP-004 R4 compliance history to be an aggravating factor in the penalty determination.
ReliabilityFirst Corporation (ReliabilityFirst or RFC) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2015014973 | Settlement Agreement | RFC_URE1 submitted a Self-Report to ReliabilityFirst reporting it was in violation of CIP-004-3a R4. RFC_URE1's internal control designed to monitor personnel status changes within the payroll system detected that ten days prior a RFC_URE1 employee with Critical Cyber Asset (CCA) access started a new job at a different facility and no longer required unescorted physical access to CCAs. Upon discovery, RFC_URE1 immediately removed authorized unescorted physical access to CCAs for this employee. The root cause of this first instance of the violation was the fact that the employee’s supervisor did not enter a ticket in the personnel status change and access revocation system to revoke access. The supervisor’s oversight was the result of the fact that he had been recently promoted to the position and had not received the annually provided training on using the personnel status change and access revocation system and the importance of entering tickets in the system. This major contributing factor relates to the management practice area of workforce management, which focuses on, inter alia, delivering training, education, and awareness to employees. During the course of mitigating this particular instance, RFC_URE1 discovered two additional instances involving access revocation for a college intern who planned to work when school was not in session. The intern did not require access to CCAs for a period of approximately three and a half months, and for a separate period of approximately one and a half months. However, the intern’s supervisor did not submit a formal request to remove the intern’s access via RFC_URE1's personnel status change and access revocation. Consequently, the intern’s name remained on the list of personnel with authorized cyber or authorized unescorted physical access to CCAs. Notably, prior to the intern’s departure on both occasions, the intern was required to surrender his access badge and electronic authentication device to his supervisor. Therefore, the intern did not have access during these periods of time. The root cause of this second instance of the violation was that RFC_URE1 had not made extensive use of interns in recent years and its personnel status change and access revocation policy did not specifically address interns who frequently return to the company to work every few months. Therefore, the intern’s supervisor was not aware of his responsibility to initiate a request via the personnel status change and access revocation system in order to have the intern’s name removed from the access list. This major contributing factor relates to the management practice area of workforce management, which focuses on, inter alia, developing a program to manage employee permissions and access to assets. | CIP-004-3a | R4 | Lower | Moderate | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. With respect to the first instance, RFC_URE1's internal controls quickly and effectively detected the issue and alerted the appropriate personnel to investigate and correct it. Although the employee no longer required access to CCAs, the employee remained properly qualified per the RFC_URE1 cyber security policy and remained a RFC_URE1 employee in good standing following the position change. With respect to the second instance, as stated earlier, the access list is a redundancy, and despite the fact that the intern’s supervisor did not follow RFC_URE1's personnel status change and access revocation policy, the supervisor collected the intern’s physical access badge and electronic authentication device. Moreover, the intern remained properly qualified per RFC_URE1's cyber security policy for access, meaning that he had undergone a current background check and annual training. | when the first employee should have had access revoked | when the employee should have had access again | $0 (for RFC2015014836, RFC2015014973, RFC2015014832, RFC2015014714, RFC2015014834, RFC2015014775, RFC2015015022, RFC2015014833, and RFC2015014837) | Self-Report | To mitigate this violation, RFC_URE1: With respect to the first instance: 1) revoked authorized unescorted physical access to CCAs for the employee involved; 2) provided training, both verbal and written, to the supervisor related to the personnel status change and access revocation process; 3) established a process to provide electronic training materials to newly hired or promoted supervisors and new sponsors concerning the personnel status change and access revocation procedure within 30 days of their assuming the position. The new supervisors and sponsors will confirm electronically that they have reviewed the training materials and understand the process; 4) implemented a quarterly awareness process that will remind supervisors and sponsors of the personnel status change and access revocation procedure and their obligation to submit a ticket whenever there is a personnel change. The awareness process will utilize various communication methods including, but not limited to, emails, newsletters, bulletin boards, RFC_URE1 intranet, and corporate video communication screens; and 5) conducted the annual personnel status change and access revocation procedure interactive training earlier in the year to communicate the new expectations for training new supervisors and sponsors, and the quarterly awareness program. With respect to the second instance: 1) modified the language of the personnel status change and access revocation and the associated training material to further define the term “Personnel” to include interns; and 2) communicated to supervisors and sponsors via an awareness email the recent change made to the personnel status change and access revocation policy that the definition of “Personnel” has been clarified to include interns. | 6/30/15 | TBD | Agrees/Stipulates | In most instances, a Regional Entity could appropriately treat such noncompliance without any penalty or negotiation of a Settlement Agreement through the Compliance Exception (CE) or Find, Fix, Track, and Report (FFT) programs. ReliabilityFirst observed that RFC_URE1 accelerated its self-monitoring efforts based on the impending implementation of the CIP Version 5 Reliability Standards. ReliabilityFirst focused additional resources on RFC_URE1's Self-Reports because RFC_URE1 was awaiting regulatory actions, such as new Reliability Standards or an approaching Compliance Audit, to assess its security and compliance. ReliabilityFirst chose to treat these violations in a Settlement Agreement instead of as CEs or FFTs in order to discourage RFC_URE1 and other registered entities from relying solely on such outside activities as the impetus for self-evaluations. ReliabilityFirst reviewed RFC_URE1's internal compliance program and considered it to be a partial mitigating factor in the penalty determination. Effective oversight of the reliability of the BES depends on robust and timely self-reporting by registered entities. RFC_URE1 identified and reported the Alleged Violations at issue in this Agreement due to the effective execution of its compliance program and its comprehensive review of its entire CIP compliance program. As a result, ReliabilityFirst seeks to encourage this type of self-reporting, characterized by timely detection and correction unrelated to a pending regional compliance monitoring action, by awarding mitigating credit. RFC_URE1 has been highly cooperative throughout the entire enforcement process. Throughout the enforcement process, RFC_URE1 has voluntarily provided ReliabilityFirst with an abundance of information regarding the Alleged Violations in a manner that was detailed, thorough, thoughtful, organized, and timely. RFC_URE1 has been open with ReliabilityFirst regarding its Alleged Violations, processes, systems, and organization and this insight has allowed ReliabilityFirst to better analyze the Alleged Violations and assist RFC_URE1 with resolving the same. As stated above, RFC_URE1's response to the Alleged Violations was efficient and effective, and ReliabilityFirst awarded mitigating credit to encourage this sort of response by other registered entities in the future. RFC_URE1 has taken actions that exceed what is required to mitigate each of the Alleged Violations, and which ReliabilityFirst therefore considers worthy of credit as Above and Beyond action items. The Above and Beyond activities described below enhance the reliability of the BES beyond mere baseline compliance with the Reliability Standards, and therefore ReliabilityFirst viewed them favorably when determining the appropriate penalty. RFC_URE1 has made significant operational upgrades to its CIP program and cyber security activities. These upgrades and improvements include purchasing and implementing technology to automate several processes and procedures to further strengthen RFC_URE1's compliance objectives as the company transitions to CIP v5. ReliabilityFirst and RFC_URE1 also agreed to several non-monetary sanctions including: (1) moving RFC_URE1's CIP v5 audit up to the second quarter of its designated year; (2) increasing RFC_URE1's audit frequency from every six years to every three years; and (3) requiring RFC_URE1's CEO to execute the Settlement Agreement. ReliabilityFirst did not consider RFC_URE1's CIP-004 R4 compliance history to be an aggravating factor in the penalty determination.
ReliabilityFirst Corporation (ReliabilityFirst or RFC) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2015014832 | Settlement Agreement | RFC_URE1 submitted a Self-Report to ReliabilityFirst reporting it was in violation of CIP-005-3a R1. During its annual Cyber Vulnerability Assessment, RFC_URE1 discovered that an Electronic Access Control and Monitoring (EACM) device (i.e., a firewall), which was used for access control of an Electronic Security Perimeter, had a default Simple Network Management Protocol (SNMP) community string. (An SNMP is like a password and allows or denies access to a device. Most network vendors ship their equipment with a “default community string,” which is like a default password.) Upon further investigation, RFC_URE1 discovered that the SNMP default community string on this EACM device had been in use since the device was placed into service approximately three years earlier. This circumstance was scheduled to be corrected during the year being audited, along with a second redundant EACM device, when they were being upgraded to a newer SNMP version. However, during the scheduled work, the SNMP version upgrade was first applied to the secondary device, which resulted in the SNMP failing. The SNMP upgrade was backed out per the change control procedure, and a ticket was opened with the vendor to assist in the resolution of the issue. The RFC_URE1 subject matter expert performing the change did not upgrade the primary device until the issue with the SNMP upgrade on the secondary device had been resolved. However, because the issue had not been resolved, the primary EACM device was never removed from service to perform the SNMP upgrade and the default community string remained. The root cause of this violation was the fact that the device configuration checklist for this particular device type did not contain detailed instructions for configuration of SNMP. This major contributing factor relates to the management practice areas of asset and configuration management, which focuses on, inter alia, controlling changes to assets, and implementation, which focuses on, inter alia, identifying technical processes or technical areas associated with deployment of new designs or revisions to existing design critical to grid reliability. | CIP-005-3a | R1 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the firewall at issue was locked down and did not allow remote access such that only RFC_URE1's network team could access it by physically being present. Second, the information at risk was limited to information about the hardware itself (e.g., manufacturer, date of production, etc.) and not about the network. Third, the SNMP default community string only applied to this one specific device (primary and secondary). Therefore, an attacker could not use this information to glean any additional information from other servers. Fourth, the EACM device was protected behind corporate firewalls restricting access from networks external to RFC_URE1. | when RFC_URE1 put the primary EACM device into service | when RFC_URE1 changed the SNMP default community string on the EACM device | $0 (for RFC2015014836, RFC2015014973, RFC2015014832, RFC2015014714, RFC2015014834, RFC2015014775, RFC2015015022, RFC2015014833, and RFC2015014837) | Self-Report | To mitigate this violation, RFC_URE1: 1) changed the SNMP default community string on the EACM device in addition to completing the SNMP version upgrade; 2) reviewed and strengthened all EACM configuration checklist documents to include the review and modification of the default SNMP community strings; and 3) changed the system used to monitor the health of cyber assets to deny access for connected cyber assets that have default SNMP community strings. This change will provide an additional control when new devices are placed into service. | 4/15/2015 | TBD | Agrees/Stipulates | In most instances, a Regional Entity could appropriately treat such noncompliance without any penalty or negotiation of a Settlement Agreement through the Compliance Exception (CE) or Find, Fix, Track, and Report (FFT) programs. ReliabilityFirst observed that RFC_URE1 accelerated its self-monitoring efforts based on the impending implementation of the CIP Version 5 Reliability Standards. ReliabilityFirst focused additional resources on RFC_URE1's Self-Reports because RFC_URE1 was awaiting regulatory actions, such as new Reliability Standards or an approaching Compliance Audit, to assess its security and compliance. ReliabilityFirst chose to treat these violations in a Settlement Agreement instead of as CEs or FFTs in order to discourage RFC_URE1 and other registered entities from relying solely on such outside activities as the impetus for self-evaluations. ReliabilityFirst reviewed RFC_URE1's internal compliance program and considered it to be a partial mitigating factor in the penalty determination. Effective oversight of the reliability of the BES depends on robust and timely self-reporting by registered entities. RFC_URE1 identified and reported the Alleged Violations at issue in this Agreement due to the execution of its compliance program and its comprehensive review of its entire CIP compliance program. As a result, ReliabilityFirst seeks to encourage this type of self-reporting, characterized by timely detection and correction unrelated to a pending regional compliance monitoring action, by awarding mitigating credit. RFC_URE1 has been highly cooperative throughout the entire enforcement process. Throughout the enforcement process, RFC_URE1 has voluntarily provided ReliabilityFirst with an abundance of information regarding the Alleged Violations in a manner that was detailed, thorough, thoughtful, organized, and timely. RFC_URE1 has been open with ReliabilityFirst regarding its Alleged Violations, processes, systems, and organization and this insight has allowed ReliabilityFirst to better analyze the Alleged Violations and assist RFC_URE1 with resolving the same. As stated above, RFC_URE1's response to the Alleged Violations was efficient and effective, and ReliabilityFirst awarded mitigating credit to encourage this sort of response by other registered entities in the future. RFC_URE1 has taken actions that exceed what is required to mitigate each of the Alleged Violations, and which ReliabilityFirst therefore considers worthy of credit as Above and Beyond action items. The Above and Beyond activities described below enhance the reliability of the BES beyond mere baseline compliance with the Reliability Standards, and therefore ReliabilityFirst viewed them favorably when determining the appropriate penalty. RFC_URE1 has made significant operational upgrades to its CIP program and cyber security activities. These upgrades and improvements include purchasing and implementing technology to automate several processes and procedures to further strengthen RFC_URE1's compliance objectives as the company transitions to CIP v5. ReliabilityFirst and RFC_URE1 also agreed to several non-monetary sanctions including: (1) moving RFC_URE1's CIP v5 audit up to the second quarter of its designated year; (2) increasing RFC_URE1's audit frequency from every six years to every three years; and (3) requiring RFC_URE1's CEO to execute the Settlement Agreement. ReliabilityFirst did not consider RFC_URE1's CIP-005 R1 compliance history to be an aggravating factor in the penalty determination.
ReliabilityFirst Corporation (ReliabilityFirst or RFC) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2015014714 | Settlement Agreement | RFC_URE1 submitted a Self-Report to ReliabilityFirst reporting it was in violation of CIP-006-1 R1. During planned monthly periodic testing of RFC_URE1's Physical Access Control System (PACS), RFC_URE1 discovered that access to a single Physical Security Perimeter (PSP) was not restricted to personnel who had been granted unescorted physical access. Security personnel were able to gain access to the PSP using a special “test” ID Card, which had been configured without unescorted physical access credentials. RFC_URE1 investigated the incident and discovered that the PACS Network Controller located within the PSP had failed to properly reboot following a configuration change initiated via a communication network from a centrally located PACS workstation. This configuration change was inadvertently attempted on this Controller five days earlier by a RFC_URE1 CIP-qualified contractor conducting maintenance on the PACS. The contractor failed to notify RFC_URE1 personnel that the Controller configuration change attempt had occurred, which resulted in RFC_URE1 personnel not performing the required Controller testing following a configuration change. This failed reboot left the Controller in an abnormal state, resulting in access to the specific PSP being granted to personnel with any RFC_URE1 ID Card, regardless of the individual’s specific access credentials. Additionally, the Controller failed to either internally or externally log access to the PSP during the five-day period. Upon further investigation, RFC_URE1 also discovered that although the PACS Controllers are part of the overall PACS, RFC_URE1 had not afforded the PACS Controllers the protective measures as required by CIP-006-3c R2. RFC_URE1 personnel did not initially believe that the PACS Controllers were within the scope of this Standard/Requirement because RFC_URE1 believed that they did not overtly perform the functions of granting or logging access. Rather, RFC_URE1 stated that these Controllers serve as intermediary devices that convert and communicate programmed instructions from centralized PACS servers to the physical security access devices as part of the authentication process necessary to gain access to PSPs. During normal operations, RFC_URE1 does not use these Controllers to independently authorize or log access to PSPs. The root cause of this violation was human error. With respect to the specific issue with the improper configuration of the PACS Controller, RFC_URE1 did not include the PACS Controllers in the same change control process used for PACS workstations and servers. This omission contributed to the miscommunication between the contractor performing the work and the responsible RFC_URE1 personnel. This major contributing factor relates to the management practice area of asset and configuration management, which focuses on, inter alia, controlling changes to assets. With respect to the broader issue of including PACS Controllers under CIP-006 R2, RFC_URE1 personnel misinterpreted the Standard/Requirement, which resulted in a multi-year duration. (ReliabilityFirst notes that the new CIP-006-5 R3 Part 3.1 explicitly brings this type of equipment into scope to avoid this type of misinterpretation. Specifically, CIP-006-5 R3 Part 3.1 provides: “Maintenance and testing of each Physical Access Control System and locally mounted hardware or devices at the Physical Security Perimeter at least once every 24 calendar months to ensure they function properly.”) The issue related to this specific Network controller being left in an abnormal state began when the configuration change was inadvertently attempted, and ended five days later, when RFC_URE1 conducted the successful reboot which restored the Network Controller to its normal operating state. The broader issue related to affording these Controllers the protective measures as required by CIP-006-3c R2 started on the date RFC_URE1 was required to comply with CIP-006-1 R1 and ended approximately five and a half years later on the date RFC_URE1 completed its Mitigation Plan. | CIP-006-1 | R1 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, during the five-day window when the PACS Controllers were left in an abnormal state, RFC_URE1 was vulnerable to the risk of insider threats because any RFC_URE1 personnel with an ID badge could have gained access to the PSP. Furthermore, RFC_URE1 would not have been able to identify who accessed the PSP during this five-day window because the PACS Controllers were not logging access. Second, in addition to this five-day window of vulnerability, RFC_URE1 failed to afford its PACS Controllers the other protections required by CIP-006 R2 for over five years. The risk posed by the foregoing facts and circumstances was mitigated by the following factors. First, RFC_URE1 proactively identified this instance related to the abnormal state of the PACS Controllers through its internal detective controls. Specifically, RFC_URE1 security personnel discovered this abnormal condition during planned monthly PACS testing. However, ReliabilityFirst notes that RFC_URE1 should have identified this condition more promptly by conducting this planned monthly PACS testing more frequently. Second, the PACS Controllers were within PSPs or locations which are monitored 24 hours per day, 7 days per week by security personnel. In fact, before an unauthorized person would have been able to gain access to this particular site, he or she would have been required to pass two outer check points at the facility. Third, the PACS Controllers are located within locked cabinets with tamper alarms such that only RFC_URE1 CIP-qualified personnel had access to them. | when RFC_URE1 was required to comply with the Standard | Mitigation Plan completion | $0 (for RFC2015014836, RFC2015014973, RFC2015014832, RFC2015014714, RFC2015014834, RFC2015014775, RFC2015015022, RFC2015014833, and RFC2015014837) | Self-Report | To mitigate this violation, RFC_URE1: 1) conducted a forced reboot of the device using the proper configuration settings upon discovery of the abnormal Controller condition at the specific PSP location. After the Controller was rebooted, security personnel conducted a test using a special “test” ID Card to verify that the PACS was functioning properly and access to this specific PSP was not permitted for personnel not granted unescorted access. In addition, Security personnel verified that the remaining 14 PACS Controllers related to PSPs were functioning properly and in a normal state; 2) implemented new visual indicators and alarming on the PACS system displays to alert security personnel of Controllers in an abnormal operating condition; 3) revised the configuration of all 15 PACS Controllers related to PSPs to include a new, more secure default setting. This setting change will ensure that if a Controller enters an abnormal state for any reason, it will deny access for all access attempts. This new configuration will ensure access to a PSP is controlled and prompt an immediate investigation; 4) tested all 15 PACS Controllers related to PSPs, after implementation of the new Controller configuration described in Item 3 above, in an abnormal state to verify that the new setting denies access to the PSP as expected; 5) included the Controllers in the same change control process used for PACS workstations and servers in order to ensure that the configuration of all 15 PACS Controllers related to PSPs are properly maintained following required changes. Changes to Controllers could include but are not limited to: replacement, operating system upgrades, application revisions, patching, configuration changes, etc.; 6) reviewed and approved the personnel with authorized individual or shared account access to the Controllers, by the designated individual responsible for authorizing such access, to ensure their “need to know” with respect to work functions performed; 7) designated a person for the Controllers to be included on the RFC_URE1 list of designated personnel who are responsible for authorizing logical or physical access to protected information; 8) added the Controllers to the RFC_URE1 Asset Database that is used to track cyber assets within the scope of the RFC_URE1 CIP Cyber Security Policy. Inclusion of the devices in this database will ensure they are included in the RFC_URE1 change and configuration management program as well as covered by all associated RFC_URE1 Cyber Security Policy procedures and processes (i.e. cyber vulnerability assessments, incident response plans, etc); 9) developed and implemented a formal change and configuration management procedure that includes the Controllers; 10) verified and/or developed (where required) test procedures that outline testing security controls when significant changes are made to the Controllers; 11) established, documented, and implemented a security patch management program for tracking, evaluating, testing, and installing applicable cyber security patches for the Controllers; 12) developed a policy for managing the Controller shared account that limits access to only those with authorization, an audit trail of the account use, and steps for securing the account in the event of personnel changes; 13) established and implemented formal procedures for the disposal or redeployment of Controllers; 14) created recovery plans for the Controllers that will be reviewed at least annually; 15) documented and implemented the processes and procedures for managing ports and services associated with the Controllers to include documenting those ports and services enabled for operations and for monitoring the Controllers. A Technical Feasibility Exception (TFE) will be submitted for approval for the Controllers with respect to the unused ports and services that cannot be disabled due to technical limitations. In support of the TFE, RFC_URE1 is going to implement an additional layer of firewall protections as a mitigating measure due to the open Controller ports that are not required for operations and cannot be disabled. These firewalls will be configured to disable external access to all ports not needed for operation of the Controllers; 16) submitted a TFE for approval for the Controllers with respect to anti-virus software and malware prevention tools because it is not technically feasible for the Controllers to use anti-virus software and other malware prevention tools; 17) submitted a TFE for approval for the Controllers with respect to the inability to enforce required password complexity for the shared account. Although it is technically feasible for the Controller shared account passwords to consist of a minimum of six characters, and a combination of alpha, numeric and special characters which can be changed annually or more frequently, the Controller cannot enforce use of such password complexity; 18) submitted a TFE for approval for the Controllers with respect to monitoring system events because it is not technically feasible for the Controllers to implement automated tools or organizational process controls to monitor system events related to cyber security; 19) documented the organizational processes and technical and procedural mechanisms for control of electronic access at all electronic access points to the Controller protected network; and 20) included the devices (Controllers in the RFC_URE1 Asset Database (see Mitigation Action #8 above)) in the scope of all future Cyber Vulnerability Assessments (CVAs) conducted at least annually. However, in order to assess the vulnerability of the Controllers after completing the Mitigation Actions included in this Mitigation Plan, RFC_URE1 will conduct a limited scope CVA for the Controllers. | 2015-08-31 | 2016-01-28 | Agrees/Stipulates | In most instances, a Regional Entity could appropriately treat such noncompliance without any penalty or negotiation of a Settlement Agreement through the Compliance Exception (CE) or Find, Fix, Track, and Report (FFT) programs. ReliabilityFirst observed that RFC_URE1 accelerated its self-monitoring efforts based on the impending implementation of the CIP Version 5 Reliability Standards. ReliabilityFirst focused additional resources on RFC_URE1's Self-Reports because RFC_URE1 was awaiting regulatory actions, such as new Reliability Standards or an approaching Compliance Audit, to assess its security and compliance. ReliabilityFirst chose to treat these violations in a Settlement Agreement instead of as CEs or FFTs in order to discourage RFC_URE1 and other registered entities from relying solely on such outside activities as the impetus for self-evaluations. ReliabilityFirst reviewed RFC_URE1's internal compliance program and considered it to be a partial mitigating factor in the penalty determination. Effective oversight of the reliability of the BES depends on robust and timely self-reporting by registered entities. RFC_URE1 identified and reported the Alleged Violations at issue in this Agreement due to the execution of its compliance program and its comprehensive review of its entire CIP compliance program. As a result, ReliabilityFirst seeks to encourage this type of self-reporting, characterized by timely detection and correction unrelated to a pending regional compliance monitoring action, by awarding mitigating credit. RFC_URE1 has been highly cooperative throughout the entire enforcement process. Throughout the enforcement process, RFC_URE1 has voluntarily provided ReliabilityFirst with an abundance of information regarding the Alleged Violations in a manner that was detailed, thorough, thoughtful, organized, and timely. RFC_URE1 has been open with ReliabilityFirst regarding its Alleged Violations, processes, systems, and organization and this insight has allowed ReliabilityFirst to better analyze the Alleged Violations and assist RFC_URE1 with resolving the same. As stated above, RFC_URE1's response to the Alleged Violations was efficient and effective, and ReliabilityFirst awarded mitigating credit to encourage this sort of response by other registered entities in the future. RFC_URE1 has taken actions that exceed what is required to mitigate each of the Alleged Violations, and which ReliabilityFirst therefore considers worthy of credit as Above and Beyond action items. The Above and Beyond activities described below enhance the reliability of the BES beyond mere baseline compliance with the Reliability Standards, and therefore ReliabilityFirst viewed them favorably when determining the appropriate penalty. RFC_URE1 has made significant operational upgrades to its CIP program and cyber security activities. These upgrades and improvements include purchasing and implementing technology to automate several processes and procedures to further strengthen RFC_URE1's compliance objectives as the company transitions to CIP v5. ReliabilityFirst and RFC_URE1 also agreed to several non-monetary sanctions including: (1) moving RFC_URE1's CIP v5 audit up to the second quarter of its designated year; (2) increasing RFC_URE1's audit frequency from every six years to every three years; and (3) requiring RFC_URE1's CEO to execute the Settlement Agreement. ReliabilityFirst did not consider RFC_URE1's CIP-006 R1 compliance history to be an aggravating factor in the penalty determination.
ReliabilityFirst Corporation (ReliabilityFirst or RFC) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2015014834 | Settlement Agreement | RFC_URE1 submitted a Self-Report to ReliabilityFirst reporting it was in violation of CIP-007-3a R1. During an internal review of CIP-007 R1.3, RFC_URE1 discovered that documented test results could not be located from test procedures used to verify that certain patches did not adversely affect existing cyber security controls for Cyber Assets within the Electronic Security Perimeter. The missing test result documentation included five months of operating system patching, and an upgrade to the reporting tool for the enterprise storage device. RFC_URE1 Subject Matter Experts investigated the occurrence and determined that the requisite test procedures were completed, however the documented results were not available. The root cause of this violation was the fact that RFC_URE1: (a) relied on a manual process for collecting test results as the test procedures were being performed; and (b) lacked a coordinated tracking process. This major contributing factor relates to the management practice area of asset and configuration management, which focuses on, inter alia, verifying the integrity of assets and configuration items by establishing and maintaining change records. | CIP-007-3a | R1 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, RFC_URE1 initially tests patches in its Quality Assurance Program test environment, during which any problems with the patches would have been noted or flagged by the cyber security controls when the device was put into production. Second, this violation is a documentation issue. As explained earlier, RFC_URE1 had performed the requisite testing, but did not collect the test result documentation. | when RFC_URE1 was required to comply with the Standard | Mitigation Plan completion | $0 (for RFC2015014836, RFC2015014973, RFC2015014832, RFC2015014714, RFC2015014834, RFC2015014775, RFC2015015022, RFC2015014833, and RFC2015014837) | Self-Report | To mitigate this violation, RFC_URE1: 1) implemented a change to internal practices to track cyber testing progress and test result documentation; and 2) revised Cyber Security Test procedure to include notification when each phase of testing is completed. | 2015-05-06 | 2016-01-28 | Agrees/Stipulates | In most instances, a Regional Entity could appropriately treat such noncompliance without any penalty or negotiation of a Settlement Agreement through the Compliance Exception (CE) or Find, Fix, Track, and Report (FFT) programs. ReliabilityFirst observed that RFC_URE1 accelerated its self-monitoring efforts based on the impending implementation of the CIP Version 5 Reliability Standards. ReliabilityFirst focused additional resources on RFC_URE1's Self-Reports because RFC_URE1 was awaiting regulatory actions, such as new Reliability Standards or an approaching Compliance Audit, to assess its security and compliance. ReliabilityFirst chose to treat these violations in a Settlement Agreement instead of as CEs or FFTs in order to discourage RFC_URE1 and other registered entities from relying solely on such outside activities as the impetus for self-evaluations. ReliabilityFirst reviewed RFC_URE1's internal compliance program and considered it to be a partial mitigating factor in the penalty determination. Effective oversight of the reliability of the BES depends on robust and timely self-reporting by registered entities. RFC_URE1 identified and reported the Alleged Violations at issue in this Agreement due to the execution of its compliance program and its comprehensive review of its entire CIP compliance program. As a result, ReliabilityFirst seeks to encourage this type of self-reporting, characterized by timely detection and correction unrelated to a pending regional compliance monitoring action, by awarding mitigating credit. RFC_URE1 has been highly cooperative throughout the entire enforcement process. Throughout the enforcement process, RFC_URE1 has voluntarily provided ReliabilityFirst with an abundance of information regarding the Alleged Violations in a manner that was detailed, thorough, thoughtful, organized, and timely. RFC_URE1 has been open with ReliabilityFirst regarding its Alleged Violations, processes, systems, and organization and this insight has allowed ReliabilityFirst to better analyze the Alleged Violations and assist RFC_URE1 with resolving the same. As stated above, RFC_URE1's response to the Alleged Violations was efficient and effective, and ReliabilityFirst awarded mitigating credit to encourage this sort of response by other registered entities in the future. RFC_URE1 has taken actions that exceed what is required to mitigate each of the Alleged Violations, and which ReliabilityFirst therefore considers worthy of credit as Above and Beyond action items. The Above and Beyond activities described below enhance the reliability of the BES beyond mere baseline compliance with the Reliability Standards, and therefore ReliabilityFirst viewed them favorably when determining the appropriate penalty. RFC_URE1 has made significant operational upgrades to its CIP program and cyber security activities. These upgrades and improvements include purchasing and implementing technology to automate several processes and procedures to further strengthen RFC_URE1's compliance objectives as the company transitions to CIP v5. ReliabilityFirst and RFC_URE1 also agreed to several non-monetary sanctions including: (1) moving RFC_URE1's CIP v5 audit up to the second quarter of its designated year; (2) increasing RFC_URE1's audit frequency from every six years to every three years; and (3) requiring RFC_URE1's CEO to execute the Settlement Agreement. ReliabilityFirst did not consider RFC_URE1's CIP-007 R1 compliance history to be an aggravating factor in the penalty determination.
ReliabilityFirst Corporation (ReliabilityFirst or RFC) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2015014775 | Settlement Agreement | RFC_URE1 submitted a Self-Report to ReliabilityFirst reporting it was in violation of CIP-007-1 R2. Following its audit, RFC_URE1 brought in a consultant to help with CIP compliance. However, RFC_URE1 later discovered that it had a misunderstanding of what was required under the standard as a result of this engagement and therefore was not monitoring its UDP ports and services at the appropriate frequency per the Standard. RFC_URE1 had been performing periodic scans of its UDP ports and services. RFC_URE1 determined that it should have been monitoring these ports and services in real time to capture all relevant justifications in its baselines. The root cause of this violation was RFC_URE1's interaction with the contractor, the result of which was RFC_URE1's failure to monitor its UDP ports and services at the required frequency. This major contributing factor relates to the management practice area of asset and configuration management, which focuses on, inter alia, establishing inventory and configuration baselines. | CIP-007-1 | R2 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. Incomplete or improper baselines make change control and configuration management difficult to perform properly because without proper baselines it is more difficult for an entity to detect and respond to malicious changes. The risk posed by the foregoing facts and circumstances was mitigated by the following factors. First, RFC_URE1 was performing periodic scans of its UDP ports and services. Therefore, RFC_URE1 could, at any given time, have produced reports of all open UDP ports and services. Second, RFC_URE1 was protecting the cyber assets that use UDP ports behind corporate firewalls and EACM devices restricting access from the RFC_URE1 corporate network and networks external to RFC_URE1. Additionally, the devices were protected by antivirus and malware prevention software. | when RFC_URE1 was required to comply with the Standard | Mitigation Plan completion | $0 (for RFC2015014836, RFC2015014973, RFC2015014832, RFC2015014714, RFC2015014834, RFC2015014775, RFC2015015022, RFC2015014833, and RFC2015014837) | Self-Report | To mitigate this violation, RFC_URE1: 1) prepared a documented baseline, prior to placing the rebuilt Cyber Assets in-service, for each asset that included the following: (a) Inventory of all Applications required for normal and emergency operations of the Cyber Asset, including the RFC_URE1 group assigned ownership of the Application, version and patching status, and supporting justification for the Application; and (b) Identification of all ports and services required for normal and emergency operation of the Cyber Asset, including supporting justification for the ports and services; 2) rebuilt and configured the Cyber Assets in scope by installing only those Applications that are identified and justified in the baseline documentation. The Applications will be installed at the most current applicable version and patch level; 3) developed, documented, and implemented, in support of the rebuilt Cyber Assets and in conjunction with RFC_URE1's CIPv5 implementation project, new processes and procedures concerning change control, configuration, and patch management. These new processes and procedures will ensure that the Cyber Assets (after being placed in service) continue to have only those Applications installed and ports and services enabled that are justified for normal and emergency operations; 4) enabled host-based firewalls on each of the Cyber Assets in scope to deny access to all ports and services that are not documented as required for normal and emergency operations of the Applications on the Cyber Asset. The host-based firewalls will be in addition to the existing perimeter-based firewalls that deny access to unjustified ports and services by default; and 5) tested each Cyber Asset to ensure that only it enables only those ports and services that are identified and justified in the baseline documentation. After each of the newly rebuilt Cyber Assets are tested, they will be placed in service in the new network environment. | 2016-03-18 | 2016-05-02 | Agrees/Stipulates | In most instances, a Regional Entity could appropriately treat such noncompliance without any penalty or negotiation of a Settlement Agreement through the Compliance Exception (CE) or Find, Fix, Track, and Report (FFT) programs. ReliabilityFirst observed that RFC_URE1 accelerated its self-monitoring efforts based on the impending implementation of the CIP Version 5 Reliability Standards. ReliabilityFirst focused additional resources on RFC_URE1's Self-Reports because RFC_URE1 was awaiting regulatory actions, such as new Reliability Standards or an approaching Compliance Audit, to assess its security and compliance. ReliabilityFirst chose to treat these violations in a Settlement Agreement instead of as CEs or FFTs in order to discourage RFC_URE1 and other registered entities from relying solely on such outside activities as the impetus for self-evaluations. ReliabilityFirst reviewed RFC_URE1's internal compliance program and considered it to be a partial mitigating factor in the penalty determination. Effective oversight of the reliability of the BES depends on robust and timely self-reporting by registered entities. RFC_URE1 identified and reported the Alleged Violations at issue in this Agreement due to the execution of its compliance program and its comprehensive review of its entire CIP compliance program. As a result, ReliabilityFirst seeks to encourage this type of self-reporting, characterized by timely detection and correction unrelated to a pending regional compliance monitoring action, by awarding mitigating credit. RFC_URE1 has been highly cooperative throughout the entire enforcement process. Throughout the enforcement process, RFC_URE1 has voluntarily provided ReliabilityFirst with an abundance of information regarding the Alleged Violations in a manner that was detailed, thorough, thoughtful, organized, and timely. RFC_URE1 has been open with ReliabilityFirst regarding its Alleged Violations, processes, systems, and organization and this insight has allowed ReliabilityFirst to better analyze the Alleged Violations and assist RFC_URE1 with resolving the same. As stated above, RFC_URE1's response to the Alleged Violations was efficient and effective, and ReliabilityFirst awarded mitigating credit to encourage this sort of response by other registered entities in the future. RFC_URE1 has taken actions that exceed what is required to mitigate each of the Alleged Violations, and which ReliabilityFirst therefore considers worthy of credit as Above and Beyond action items. The Above and Beyond activities described below enhance the reliability of the BES beyond mere baseline compliance with the Reliability Standards, and therefore ReliabilityFirst viewed them favorably when determining the appropriate penalty. RFC_URE1 has made significant operational upgrades to its CIP program and cyber security activities. These upgrades and improvements include purchasing and implementing technology to automate several processes and procedures to further strengthen RFC_URE1's compliance objectives as the company transitions to CIP v5. ReliabilityFirst and RFC_URE1 also agreed to several non-monetary sanctions including: (1) moving RFC_URE1's CIP v5 audit up to the second quarter of its designated year; (2) increasing RFC_URE1's audit frequency from every six years to every three years; and (3) requiring RFC_URE1's CEO to execute the Settlement Agreement. ReliabilityFirst did not consider RFC_URE1's CIP-007 R2 compliance history to be an aggravating factor in the penalty determination.
ReliabilityFirst Corporation (ReliabilityFirst or RFC) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2015015022 | Settlement Agreement | RFC_URE1 submitted a Self-Report to ReliabilityFirst reporting it was in violation of CIP-007-1 R3. RFC_URE1 conducted an investigation of recent industry threat intelligence and discovered that certain third-party applications installed on Cyber Assets within the Electronic Security Perimeter (ESP) did not have appropriate patches applied. These third-party applications did not include the operating systems or primary applications (such as the SCADA system, state estimator, etc.) on the Cyber Assets within the ESP. Additionally, while performing the mitigating actions, RFC_URE1 utilized a patch monitoring system to monitor operating systems for applications that require patching. This system leveraged a tool to assist in identifying missing patches and potential vulnerabilities. RFC_URE1 assessed the tool's reports daily as part of its normal process and analyzed them through its existing risk assessment process, which considers: (a) how the vulnerability is exploited; (b) if the vulnerability has an active exploit; (c) if the vulnerability can be exploited with the other controls in place; and (d) what the vulnerability might affect. Through this process, no new vulnerability was ranked as “critical” to the environment during this time period. However, the evaluation of each patch was not individually documented during this period, as the formalized process for patch management for third-party applications was not in place until required under the mitigation plan. The root cause of this violation was the fact that RFC_URE1 had not established, documented, or implemented a security patch management program for tracking, evaluating, testing, and installing applicable cyber security software patches for these third-party applications. This major contributing factor relates to the management practice area of asset and configuration management, which focuses on, inter alia, establishing inventory and configuration baselines. | CIP-007-1 | R3 | Lower | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the fact that patching is a baseline compliance and security activity. The failure to install patches can result in computers and servers crashing, creating a reliability issue. This risk was mitigated by the following factors. First, the applications affected did not include the operating systems or primary applications (such as SCADA). Second, the Cyber Assets at issue were protected behind ESP Electronic Access Control and Monitoring devices and did not have access to the RFC_URE1 corporate network or the internet. Furthermore, these Cyber Assets were not used for corporate functions like email or internet access. | when RFC_URE1 was required to comply with the Standard | Mitigation Plan completion | $0 (for RFC2015014836, RFC2015014973, RFC2015014832, RFC2015014714, RFC2015014834, RFC2015014775, RFC2015015022, RFC2015014833, and RFC2015014837) | Self-Report | To mitigate this violation, RFC_URE1: 1) prepared a documented baseline, prior to placing the rebuilt Cyber Assets in service, for each asset that will include the following: (a) Inventory of all Applications required for normal and emergency operations of the Cyber Asset, including the RFC_URE1 group assigned ownership of the Application, version and patching status, and supporting justification for the Application; and (b) Identification of all ports and services required for normal and emergency operation of the Cyber Asset, including supporting justification for the ports and services; 2) rebuilt and configured the Cyber Assets in scope by installing only those Applications that are identified and justified in the baseline documentation. The Applications will be installed at the most current applicable version and patch level; 3) developed, documented, and implemented, in support of the rebuilt Cyber Assets and in conjunction with RFC_URE1's CIPv5 implementation project, new processes and procedures concerning change control, configuration, and patch management. These new processes and procedures will ensure that the Cyber Assets (after being placed in service) continue to have only those Applications installed and ports and services enabled that are justified for normal and emergency operations; 4) enabled, as an above and beyond measure, host-based firewalls on each of the Cyber Assets in scope to deny access to all ports and services that are not documented as required for normal and emergency operations of the Applications on the Cyber Asset. The host-based firewalls will be in addition to the existing perimeter-based firewalls that deny access to unjustified ports and services by default; and 5) tested each Cyber Asset to ensure that it enabled only those ports and services that are identified and justified in the baseline documentation. After each of the newly rebuilt Cyber Assets are tested, they will be placed in service in the new network environment. | 2016-03-18 | 2016-04-29 | Agrees/Stipulates | In most instances, a Regional Entity could appropriately treat such noncompliance without any penalty or negotiation of a Settlement Agreement through the Compliance Exception (CE) or Find, Fix, Track, and Report (FFT) programs. ReliabilityFirst observed that RFC_URE1 accelerated its self-monitoring efforts based on the impending implementation of the CIP Version 5 Reliability Standards. ReliabilityFirst focused additional resources on RFC_URE1's Self-Reports because RFC_URE1 was awaiting regulatory actions, such as new Reliability Standards or an approaching Compliance Audit, to assess its security and compliance. ReliabilityFirst chose to treat these violations in a Settlement Agreement instead of as CEs or FFTs in order to discourage RFC_URE1 and other registered entities from relying solely on such outside activities as the impetus for self-evaluations. ReliabilityFirst reviewed RFC_URE1's internal compliance program and considered it to be a partial mitigating factor in the penalty determination. Effective oversight of the reliability of the BES depends on robust and timely self-reporting by registered entities. RFC_URE1 identified and reported the Alleged Violations at issue in this Agreement due to the execution of its compliance program and its comprehensive review of its entire CIP compliance program. As a result, ReliabilityFirst seeks to encourage this type of self-reporting, characterized by timely detection and correction unrelated to a pending regional compliance monitoring action, by awarding mitigating credit. RFC_URE1 has been highly cooperative throughout the entire enforcement process. Throughout the enforcement process, RFC_URE1 has voluntarily provided ReliabilityFirst with an abundance of information regarding the Alleged Violations in a manner that was detailed, thorough, thoughtful, organized, and timely. RFC_URE1 has been open with ReliabilityFirst regarding its Alleged Violations, processes, systems, and organization and this insight has allowed ReliabilityFirst to better analyze the Alleged Violations and assist RFC_URE1 with resolving the same. As stated above, RFC_URE1’s response to the Alleged Violations was efficient and effective, and ReliabilityFirst awarded mitigating credit to encourage this sort of response by other registered entities in the future. RFC_URE1 has taken actions that exceed what is required to mitigate each of the Alleged Violations, and which ReliabilityFirst therefore considers worthy of credit as Above and Beyond action items. The Above and Beyond activities described below enhance the reliability of the BES beyond mere baseline compliance with the Reliability Standards, and therefore ReliabilityFirst viewed them favorably when determining the appropriate penalty. RFC_URE1 has made significant operational upgrades to its CIP program and cyber security activities. These upgrades and improvements include purchasing and implementing technology to automate several processes and procedures to further strengthen RFC_URE1's compliance objectives as the company transitions to CIP v5. ReliabilityFirst and RFC_URE1 also agreed to several non-monetary sanctions including: (1) moving RFC_URE1's CIP v5 audit up to the second quarter of its designated year; (2) increasing RFC_URE1's audit frequency from every six years to every three years; and (3) requiring RFC_URE1's CEO to execute the Settlement Agreement. ReliabilityFirst considered RFC_URE1’s CIP-007 R3 compliance history to be an aggravating factor in the penalty determination.
ReliabilityFirst Corporation (ReliabilityFirst or RFC) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2015014833 | Settlement Agreement | RFC_URE1 submitted a Self-Report to ReliabilityFirst reporting it was in violation of CIP-007-3a R5. During its annual Cyber Vulnerability Assessment, RFC_URE1 discovered that four Critical Cyber Assets and one non-critical Cyber Asset within the Electronic Security Perimeter had a default Simple Network Management Protocol (SNMP) community string. RFC_URE1 investigated and determined that the SNMP default community strings on these servers had been in use since the devices were placed into service. The root cause of this violation was the fact that the device configuration checklist for these devices did not contain detailed instructions for configuration of SNMP. This major contributing factor relates to the management practice areas of asset and configuration management, which focuses on, inter alia, controlling changes to assets, and implementation, which focuses on, inter alia, identifying technical processes or technical areas associated with deployment of new designs or revisions to existing design critical to grid reliability. | CIP-007-3a | R5 | Lower | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the information at risk was limited to information about the hardware itself (e.g., manufacturer, date of production, etc.). Second, each SNMP default community string only applied to the one specific device. Therefore, an attacker could not use this information to glean any additional information from other servers. Third, these devices were protected behind corporate firewalls restricting access from networks external to RFC_URE1. Furthermore, these devices are located within controlled access facilities, which include protection against unauthorized physical access with multiple layers of electronic and physical access controls, such as guards, account management, and access controls. | when RFC_URE1 placed the devices into service | Mitigating Activities completion | $0 (for RFC2015014836, RFC2015014973, RFC2015014832, RFC2015014714, RFC2015014834, RFC2015014775, RFC2015015022, RFC2015014833, and RFC2015014837) | Self-Report | To mitigate this violation, RFC_URE1: 1) changed the SNMP default community strings on the five servers; 2) reviewed all server configuration checklist documents and strengthen the SNMP configuration section by including the review and modification of the default SNMP community strings; and 3) changed the system used to monitor the health of cyber assets to deny access for connected cyber assets that have default SNMP community strings. This change will provide an additional control when new devices are placed into service. | 4/15/2015 | TBD | Agrees/Stipulates | In most instances, a Regional Entity could appropriately treat such noncompliance without any penalty or negotiation of a Settlement Agreement through the Compliance Exception (CE) or Find, Fix, Track, and Report (FFT) programs. ReliabilityFirst observed that RFC_URE1 accelerated its self-monitoring efforts based on the impending implementation of the CIP Version 5 Reliability Standards. ReliabilityFirst focused additional resources on RFC_URE1's Self-Reports because RFC_URE1 was awaiting regulatory actions, such as new Reliability Standards or an approaching Compliance Audit, to assess its security and compliance. ReliabilityFirst chose to treat these violations in a Settlement Agreement instead of as CEs or FFTs in order to discourage RFC_URE1 and other registered entities from relying solely on such outside activities as the impetus for self-evaluations. ReliabilityFirst reviewed RFC_URE1's internal compliance program and considered it to be a partial mitigating factor in the penalty determination. Effective oversight of the reliability of the BES depends on robust and timely self-reporting by registered entities. RFC_URE1 identified and reported the Alleged Violations at issue in this Agreement due to the execution of its compliance program and its comprehensive review of its entire CIP compliance program. As a result, ReliabilityFirst seeks to encourage this type of self-reporting, characterized by timely detection and correction unrelated to a pending regional compliance monitoring action, by awarding mitigating credit. RFC_URE1 has been highly cooperative throughout the entire enforcement process. Throughout the enforcement process, RFC_URE1 has voluntarily provided ReliabilityFirst with an abundance of information regarding the Alleged Violations in a manner that was detailed, thorough, thoughtful, organized, and timely. RFC_URE1 has been open with ReliabilityFirst regarding its Alleged Violations, processes, systems, and organization and this insight has allowed ReliabilityFirst to better analyze the Alleged Violations and assist RFC_URE1 with resolving the same. As stated above, RFC_URE1's response to the Alleged Violations was efficient and effective, and ReliabilityFirst awarded mitigating credit to encourage this sort of response by other registered entities in the future. RFC_URE1 has taken actions that exceed what is required to mitigate each of the Alleged Violations, and which ReliabilityFirst therefore considers worthy of credit as Above and Beyond action items. The Above and Beyond activities described below enhance the reliability of the BES beyond mere baseline compliance with the Reliability Standards, and therefore ReliabilityFirst viewed them favorably when determining the appropriate penalty. RFC_URE1 has made significant operational upgrades to its CIP program and cyber security activities. These upgrades and improvements include purchasing and implementing technology to automate several processes and procedures to further strengthen RFC_URE1's compliance objectives as the company transitions to CIP v5. ReliabilityFirst and RFC_URE1 also agreed to several non-monetary sanctions including: (1) moving RFC_URE1's CIP v5 audit up to the second quarter of its designated year; (2) increasing RFC_URE1's audit frequency from every six years to every three years; and (3) requiring RFC_URE1's CEO to execute the Settlement Agreement. ReliabilityFirst did not consider RFC_URE1's CIP-007 R5 compliance history to be an aggravating factor in the penalty determination.
ReliabilityFirst Corporation (ReliabilityFirst or RFC) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2015014837 | Settlement Agreement | RFC_URE1 submitted a Self-Report to ReliabilityFirst reporting it was in violation of CIP-007-1 R5. During its comprehensive internal review of its processes and procedures, RFC_URE1 discovered that it had not tracked shared database accounts until it determined that individual users had access to these shared accounts. Upon further investigation, RFC_URE1 also discovered that, although technical and procedural controls were in place to manage shared accounts, including limiting access to those with authorization and logging usage of shared accounts, RFC_URE1 failed to maintain an audit trail that associated the authorized user’s identity with each individual use of the shared account. Additionally, while performing the mitigating actions, RFC_URE1 discovered that it failed to include integrated access cards in its review of all shared accounts. Integrated access cards are remote access cards that provide administrators with the ability to remotely access physical servers in order to troubleshoot issues when a physical server is no longer responding. RFC_URE1 reviewed the use of these shared accounts and added them to the procedure controls put in place as part of the mitigating actions. The root cause of this violation was the fact that RFC_URE1 did not believe these particular accounts were covered by the Standard/Requirement because these accounts cannot provide interactive access to Cyber Assets. With respect to the audit trail issue, RFC_URE1 did not believe that it was required to track shared account usage down to the individual authorized user at the time of each use. | CIP-007-1 | R5 | Lower | High | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, RFC_URE1 had processes and procedures in place to know who had access to the shared accounts and, where technically feasible, had maintained logs of shared account use. Second, access to all shared accounts associated with Critical Cyber Assets and non-critical Cyber Assets within the Electronic Security Perimeter required users to have either authorized cyber access or unescorted physical access, which included current background checks and annual training. | when RFC_URE1 was required to comply with the Standard | Mitigation Plan completion | $0 (for RFC2015014836, RFC2015014973, RFC2015014832, RFC2015014714, RFC2015014834, RFC2015014775, RFC2015015022, RFC2015014833, and RFC2015014837) | Self-Report | To mitigate this violation, RFC_URE1: 1) implemented a manual audit trail process to track the individual user when the shared account is used for the following shared accounts: administrative, system, application, and generic accounts which allow for interactive logons (excluding field devices). The manual process requires the individual user to send an email to a designated email account that includes the following information: (a) Shared Account Name; (b) Individual user of the shared account; and (c) Date and Time when access was required; 2) reviewed all shared database accounts to identify the owner and to create a list of authorized individual users of the accounts. An audit trail of when the shared database accounts are used and the individual authorized user will be retained by using the manual methods described in Mitigation Action #1 above; 3) configured the RFC_URE1 work management system with new device-specific work orders for field devices that are accessed via a shared account. When work activities are completed on these devices using the new work order, the user is forced to respond as to whether a shared account was used to access the device. The responses will be saved in the work management system, and a report will be produced to create an audit trail of the date the shared account was used and the individual authorized user; 4) formalized the manual audit trail process by including the procedure in the RFC_URE1 IT Technology Standards document. In addition, the account type definitions have been established and also inserted into the IT Technology Standards; 5) disabled, where possible, through verified testing, the interactive logon for the accounts identified in Mitigation Action #1 above, by enabling the following user rights assignments via Group Policy: Deny Logon Locally and Deny Logon Thru Terminal Services. This will remove the ability for an individual to use the account for interactive access; and 6) replaced, where possible, the accounts identified in mitigation action #1 (above) with individual accounts, which will then be tracked to the SMEs assigned to manage the identified devices. After testing, the account will be first disabled and then deleted. | 2015-07-30 | 2016-01-28 | Agrees/Stipulates | In most instances, a Regional Entity could appropriately treat such noncompliance without any penalty or negotiation of a Settlement Agreement through the Compliance Exception (CE) or Find, Fix, Track, and Report (FFT) programs. ReliabilityFirst observed that RFC_URE1 accelerated its self-monitoring efforts based on the impending implementation of the CIP Version 5 Reliability Standards. ReliabilityFirst focused additional resources on RFC_URE1's Self-Reports because RFC_URE1 was awaiting regulatory actions, such as new Reliability Standards or an approaching Compliance Audit, to assess its security and compliance. ReliabilityFirst chose to treat these violations in a Settlement Agreement instead of as CEs or FFTs in order to discourage RFC_URE1 and other registered entities from relying solely on such outside activities as the impetus for self-evaluations. ReliabilityFirst reviewed RFC_URE1's internal compliance program and considered it to be a partial mitigating factor in the penalty determination. Effective oversight of the reliability of the BES depends on robust and timely self-reporting by registered entities. RFC_URE1 identified and reported the Alleged Violations at issue in this Agreement due to the execution of its compliance program and its comprehensive review of its entire CIP compliance program. As a result, ReliabilityFirst seeks to encourage this type of self-reporting, characterized by timely detection and correction unrelated to a pending regional compliance monitoring action, by awarding mitigating credit. RFC_URE1 has been highly cooperative throughout the entire enforcement process. Throughout the enforcement process, RFC_URE1 has voluntarily provided ReliabilityFirst with an abundance of information regarding the Alleged Violations in a manner that was detailed, thorough, thoughtful, organized, and timely. RFC_URE1 has been open with ReliabilityFirst regarding its Alleged Violations, processes, systems, and organization and this insight has allowed ReliabilityFirst to better analyze the Alleged Violations and assist RFC_URE1 with resolving the same. As stated above, RFC_URE1's response to the Alleged Violations was efficient and effective, and ReliabilityFirst awarded mitigating credit to encourage this sort of response by other registered entities in the future. RFC_URE1 has taken actions that exceed what is required to mitigate each of the Alleged Violations, and which ReliabilityFirst therefore considers worthy of credit as Above and Beyond action items. The Above and Beyond activities described below enhance the reliability of the BES beyond mere baseline compliance with the Reliability Standards, and therefore ReliabilityFirst viewed them favorably when determining the appropriate penalty. RFC_URE1 has made significant operational upgrades to its CIP program and cyber security activities. These upgrades and improvements include purchasing and implementing technology to automate several processes and procedures to further strengthen RFC_URE1's compliance objectives as the company transitions to CIP v5. ReliabilityFirst and RFC_URE1 also agreed to several non-monetary sanctions including: (1) moving RFC_URE1's CIP v5 audit up to the second quarter of its designated year; (2) increasing RFC_URE1's audit frequency from every six years to every three years; and (3) requiring RFC_URE1's CEO to execute the Settlement Agreement. ReliabilityFirst considered RFC_URE1's CIP-007 R5 compliance history to be an aggravating factor in the penalty determination.
Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2016015861 | Settlement Agreement | WECC_URE1 submitted a Self-Report stating that it was in violation of CIP-006-3c R2.2. WECC_URE1 reported that it inadvertently approved electronic access to one of its servers (Server A), which was a Physical Access Control System (PACS) server, to nine off-shore contractor personnel. WECC_URE1's Information Technology department (IT) engaged a contractor to obtain technical support for WECC_URE1's IT assets. To receive the technical support needed, an Active Directory group was created, so contractor personnel could electronically access a non-CIP document library, which resided in the same WECC_URE1 admin network as WECC_URE1's upgraded server (Server B). At the time, the upgraded server, Server B, was not a CIP Cyber Asset; however, WECC_URE1 was in the process of upgrading its PACS from one Server A to Server B, making the upgraded Server B a PACS. Upon learning that the contractors could access the upgraded server, Server B, the WECC_URE1 Domain Administrator immediately conducted an investigation of Server A, revealing the same misconfiguration. Once WECC_URE1 discovered this issue, it immediately revoked the electronic access for the nine contractors and promptly corrected the misconfiguration. The root cause was a failure to ensure the individual responsible for creating the Active Directory was aware of CIP standards during the onboarding of the contractors, resulting in a misconfiguration of permissions for a group on a PACS server. | CIP-006-3c | R2; R2.2 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Specifically, WECC_URE1 failed to protect a PACS server from unauthorized electronic access as required by CIP-006-3c R2.2. Such failure could potentially result in fraudulent or errant activity on the CIP Cyber Asset by the parties given access. Depending on the access privileges granted, the potential harm could be significant in that this unauthorized electronic access could lead to access to a Physical Security Perimeter (PSP) which could affect operations, thus impacting the reliability of the bulk power system (BPS). WECC_URE1 had implemented controls to prevent the unauthorized access. The PACS server was actively monitored 24 hours a day, seven days a week; WECC_URE1's PSPs have alarms and alerting for unauthorized physical access. The nine contractors had only local administrative access privileges, which restricted their access to the PACS server software and, therefore, they were unable to change physical access rights; unlock doors to the PSPs; update any panels; or authorize local administrative rights to the server. During the issue, there were no alerts of unsuccessful, and/or failed, attempts to electronically access the Server A servers. Further, there were no configuration changes to the servers and/or attempts to shut down the servers. Finally, none of the nine contractors accessed the servers. | when WECC_URE1 misconfigured a PACS server permission group and provisioned unauthorized electronic access to PACS servers for nine off-shore contractors | Mitigation Plan completion | 26000 | Self-Report | To mitigate this violation, WECC_URE1: 1) revoked the electronic access of the nine contractors; 2) reconfigured the group permissions on the PACS server; 3) created a separate NERC CIP domain for the access control and security management software system; 4) implemented multi-factor authentication to the new NERC CIP domain; and 5) required new access control and security management software IT Administrators be NERC CIP-certified. | 2015-01-22 | 2017-01-06 | Agrees/Stipulates | Credit was not given for WECC_URE1's internal compliance program (ICP). Although WECC_URE1 has a documented ICP that has been provided to WECC; WECC determined that WECC_URE1 did not implement its ICP with effective internal controls in place to identify this issue Credit was not given for self-reporting because the Self-Report was submitted 525 days after WECC_URE1 discovered this issue.
Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2015014903 | Settlement Agreement | WECC_URE2 submitted a Self-Report stating that it was in violation of CIP-005-3a R2. WECC_URE2 reported that it did not maintain technical mechanisms for control of electronic access at 40 Electronic Access Points (EAPs) to the Electronic Security Perimeters (ESPs) as required by CIP-005-3a R2.1. Specifically, during troubleshooting to resolve Energy Management System (EMS) application communication interruptions, WECC_URE2 disabled its Access Control Lists (ACLs) which specified which users or system processes were granted access to 40 EAP devices at several substations and control centers. WECC_URE2's control center reported a large number of red-border statuses on EMS workstations installed at several WECC_URE2 substations. The EMS issues a red-border status when there is a communication interruption between the workstation and the EMS server. The severity of these problems resulted in several EMS workstations becoming unusable. These red-border events happened intermittently, each interruption lasting between 4 to 10 seconds and did not happen daily. At its peak, WECC_URE2 estimated an operator probably experienced a red-border event approximately three times in an hour. WECC_URE2's priority was to stabilize the environment promptly and get workstations running properly. Initial troubleshooting efforts pointed to firewall or network-related issues. WECC_URE2's first attempt was to resolve network port mismatches, and second, WECC_URE2 sought to reduce switch ACL logging. These attempts did not resolve the red-border issues. WECC_URE2 then disabled ACLs on the switches between several substations and control centers to further eliminate variables. Disabling the switch ACLs appeared to reduce, but not eliminate, the number of red-border statuses. WECC_URE2 had previously transitioned operating systems. WECC_URE2, therefore, assessed the associated workstations, to determine whether any of the changes implemented during this transition contributed to the red-border issues. One of the changes implemented during the transition was a reduction of a specific Remote Procedure Call (RPC) dynamic port range. Once WECC_URE2 returned the RPC port range back to its original, pre-transition setting, the operational environment stabilized. WECC_URE2 performed security testing pursuant to CIP-007 as part of the upgrade; however, this issue was not identified during that testing. WECC determined the root cause of this violation to be WECC_URE2 failing to follow its documented processes for emergency deviations from compliance pursuant to CIP-003-3a R1.1, as described in NERC Violation ID WECC2016016705. | CIP-005-3a | R2; R2.1; R2.2 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Specifically, in this instance, WECC_URE2 failed to maintain ACLs on 40 EAPs at several substations and control centers, increasing the risk of a range of cyber security attacks, which could have resulted in system disruption or disablement, data loss or data theft, and/or remote seizure of WECC_URE2's computer systems. Such cyber security attacks could have directly affected WECC_URE2's ability to effectively control system load on its transmission system, which could be categorized as a potential for causing harm to the BPS, thereby potentially affecting the reliability of the BPS. However, in an effort to mitigate risk, WECC_URE2 maintained all other cyber security controls on its networks, and employed its automation system manager system to monitor for cyber security events on and through the affected EAPs. WECC_URE2 stated that a review of network traffic logs did not reveal any security related anomalies. Additionally, each switching center had multiple EMS workstations that could be used in place of those workstations that experienced red-border issues. As a standard practice, WECC_URE2's switching centers can share their Areas of Responsibility (AORs) with other WECC_URE2 switching centers. If needed, the control center could pass control of an AOR to another switching center without the risk or disruption of control, maintaining continuity of service. While these efforts did help to minimize risk, they were predominately cyber security monitoring actions, and thus could not effectively replace the preventive controls afforded by the ACLs on the EAPs. | when WECC_URE2 disabled the ACLs on the devices in scope | when WECC_URE2 re-enabled the last of the ACLs on the devices in scope | $87,000 (for WECC2015014903 and WECC2016016705) | Self-Report | To remediate and mitigate this violation, WECC_URE2: 1) returned the RPC port range back to its original pre-transition setting; 2) re-enabled the ACLs on 40 EAPs devices, which was coordinated with the staff; and 3) created a new procedure for subject matter experts to follow when a similar issue occurs that gives guidance on proper handling of CIP devices during an outage, and communicated this guidance to all applicable staff. | 7/14/2015 | 11/23/2015 | Admits | Credit was not given for WECC_URE2's internal compliance program (ICP). Although WECC_URE2 has a documented ICP that has been provided to WECC, it is WECC's belief that had the ICP been implemented properly, WECC_URE2 would have been able to identify, assess, and correct this violation in a timely manner. WECC_URE2 submitted its Mitigation Plan 145 days after self-reporting; therefore, WECC considered the tardiness of the Mitigation Plan as an aggravating factor. WECC_URE2 self-reported 457 days after discovery. Therefore, WECC did not apply self-reporting credit to the penalty amount.
Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2016016705 | Settlement Agreement | WECC_URE2 submitted a Self-Report stating that it was in violation of CIP-003-3 R1.1. WECC_URE2 had a temporary deviation from compliance, in accordance with its cyber security policy, when it disabled 40 Access Control Lists (ACLs) in order to troubleshoot an Energy Management System (EMS) application communication interruption. Per WECC_URE2's CIP-003-3 R1 cyber security policy, prior to the deviation or immediately after the issue was resolved, WECC_URE2 was to obtain approval to deviate from compliance from the NERC CIP Senior Manager or delegate(s), which it did not. It was determined that WECC_URE2 did properly vet the change to disable the ACLs, it just failed to obtain the appropriate signature per its cyber security policy. The root cause of this violation was management policy guidance or expectations were not well-defined, understood, or enforced. | CIP-003-3 | R1; R1.1 | Medium | Severe | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). WECC_URE2 failed to implement its CIP cyber security policy. Specifically, failure to obtain NERC CIP Senior Manager approval on an emergency change could have resulted in implementing a change that had not been adequately planned or vetted. The change, which involved disabling 40 Electronic Access Point (EAP) devices, created the potential for a range of cyber security attacks that could have resulted in system disruption; disablement; data loss or data theft; and/or remote seizure of computer systems. Such cyber security attacks could have directly affected WECC_URE2's ability to effectively control system load, which could have had the potential for causing harm to the BPS. However, the likelihood of these situations occurring is low since this is an administrative control and the presence of the NERC CIP Senior Manager's signature does not directly reduce the likelihood of the above occurring. WECC_URE2 implemented controls that reduced the risk utilizing an automation system manager that detects changes to configurations and monitors for cyber security events on its EAPs. In addition, WECC_URE2 utilized physical access controls including, a defense-in-depth strategy, which would lower the likelihood that bad actors could physically access systems. | when WECC_URE2 failed to obtain NERC CIP Senior Manager or delegate(s) approval prior to or immediately after resolution of a temporary compliance deviation per its CIP-003-3 R1 cyber security policy | Mitigation Plan completion | $87,000 (for WECC2015014903 and WECC2016016705) | Self-Report | To remediate and mitigate this violation, WECC_URE2 sent an email to its IT managers instructing them to remind staff and reinforce the importance of following the directives outlined in WECC_URE2's NERC CIP cyber security policy relating to temporary compliance deviations, which indicates should a similar reliability/emergency event occur, a temporary deviation request will be submitted to the IT manager who will in turn communicate it to the WECC_URE2 NERC CIP Senior Manager or delegate for approval. | 2015-07-14 | 2017-01-13 | Admits | Credit was not given for WECC_URE2's internal compliance program (ICP). Although WECC_URE2 has a documented ICP that has been provided to WECC, it is WECC's belief that had the ICP been implemented properly, WECC_URE2 would have been able to identify, assess, and correct this violation in a timely manner. WECC_URE2 submitted its Mitigation Plan 145 days after self-reporting; therefore, WECC considered the tardiness of the Mitigation Plan as an aggravating factor. WECC_URE2 self-reported 457 days after discovery. Therefore, WECC did not apply self-reporting credit to the penalty amount.