## Public CIP SNOP Posting
Region | Registered EntityName | NCR | NERC Violation ID | Notice of Confirmed Violation or Settlement Agreement | Description of the Violation | Reliability Standard | Req. | Violation Risk Factor | Violation Severity Level | Risk Assessment | Violation Start Date | Violation End Date | Total Penalty or Sanction ($) | Method of Discovery | Description of Mitigation Activity | Mitigation Completion Date | Date Regional Entity Verified Completion of Mitigation | "Admits," "Agrees/Stipulates," "Neither Admits nor Denies," or "Does Not Contest" | Other Factors Affecting the Penalty Determination, including Compliance History, Internal Compliance Program and Compliance Culture
Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201002165 | Settlement Agreement | WECC_URE1 submitted a Self-Certification stating that it had a possible issue of noncompliance of CIP-006-1 R1. A WECC SME reviewed the supplemental data and conducted telephone interviews with WECC_URE1's compliance personnel. Based on the interviews with WECC_URE1, the WECC SME confirmed WECC_URE1 failed to create and maintain a Physical Security Plan, approved by a senior manager or delegate. Based on the investigation and available information, the SME determined WECC_URE1 was in possible violation of CIP-006-1 R1. The SME forwarded the findings to WECC Enforcement. WECC Enforcement reviewed the information submitted by WECC_URE1 and the SME’s findings, and determined WECC_URE1 was in violation of CIP-006-1 R1, due to WECC_URE1's failure to create and maintain a Physical Security Plan, approved by a senior manager or delegate. Additionally, WECC_URE1 submitted a Self-Report for CIP-004-3 R4. In this instance, a security guard clicked the wrong checkbox in the physical access management system and gave the contractor in scope inadvertent access to a Physical Security Perimeter (PSP). When the security guard updated WECC_URE1's CIP-004-3 R4 access list, they realized and corrected the error. A WECC SME discussed the violation with WECC_URE1 and determined that the instance of noncompliance was actually a violation of CIP-006-3 R1.4, instead of a CIP-004-3 R4 violation. WECC added this instance of noncompliance to the scope of the above open enforcement action. The duration of this violation was approximately 81 months. | CIP-006-1 | R1 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). WECC_URE1 failed to create and maintain a Physical Security Plan to ensure that all Cyber Assets in an identified Electronic Security Perimeter (ESP) are also located within a PSP. Failing to create and maintain a Physical Security Plan could allow Cyber Assets within that PSP to go unprotected, unmonitored, or unchecked. This could allow unauthorized physical access to Critical Cyber Assets (CCAs) within that PSP, which could be used to affect the operation of the BPS. As compensating measures, WECC_URE1 had security in place several years prior to the beginning of this violation at all WECC_URE1 projects. All security plans included significant attention to securing the powerhouses. Further, WECC_URE1 had standard operating procedures and processes that were compliant with other regulations at the time of the violation. For these reasons, WECC determined that this violation posed a moderate risk to the reliability of the BPS. | When the Standard became mandatory and enforceable on WECC_URE1 | When WECC_URE1 finished transitioning to CIP Version 5 | No Penalty | Self-Certification | To mitigate this violation, WECC_URE1: 1) updated its Physical Security Plan to include: i. defined operational or procedural controls to restrict physical access; ii. utilization of multiple different physical access controls to collectively allow unescorted physical access into PSPs to only those individuals who have authorized unescorted physical access; iii. monitoring for unauthorized access through a physical access point into a PSP; iv. an alarm or alert in response to detected unauthorized access through a physical access point into a PSP to the personnel identified in the Bulk Electric System (BES) Cyber Security Incident response plan within 15 minutes of detection; v. monitoring of each Physical Access Control Systems (PACS) for unauthorized physical access; vi. an alarm or alert in response to detected unauthorized physical access to a PACS to the personnel identified in the BES Cyber Security Incident response plan within 15 minutes of the detection; vii. logged entries of each individual with authorized unescorted physical access into each PSP, with information to identify the individual and date and time of entry; viii. retaining of physical access logs of entry of individuals with authorized unescorted physical access into each PSP for at least 90 calendar days; and ix. restricted physical access to nonprogrammable communication components used for connection between applicable Cyber Assets within the same Electronic Security Perimeter (ESP) in those instances when such nonprogrammable communication components are located outside of a PSP; 2) implemented extensive modifications to the existing security systems at all of its Critical Assets; 3) updated the current Physical Security Plan documentation or created documents, where only informal procedures were in place; and 4) procured and developed a PACS test bench to evaluate new software and hardware and to test new components to the system. | 2016-07-01 | 2016-10-07 | Does Not Contest | WECC considered WECC_URE1's compliance history and determined there were no relevant instances of noncompliance.
Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2014014941 | Settlement Agreement | WECC_URE2 submitted a Self-Report stating that it was in violation of CIP-005-3a R1.5. Specifically, WECC_URE2 failed to test backup media to ensure information essential to recovery is available, as specified in CIP-009-3 R5, and required by CIP-005-3 R1.5 for Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeter (ESP). This issue affected 12 Cyber Assets. The cause of this issue was a lack of proper settings and procedures for the affected routers and switches. The data to successfully recover the affected assets was stored on a server that had been decommissioned and whose data was stored in a format that was irretrievable. WECC determined that this violation began when a server was decommissioned and the data to successfully recover the affected assets was no longer readily available, and ended when WECC_URE2 implemented changes to its settings so that configurations are written to a remote server when the configuration is altered, and performed manual backups on firewalls to servers, which are themselves backed up, for a total of 1,371 days of noncompliance. | CIP-005-3a | R1 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Specifically, WECC_URE2 failed to provide evidence of testing back up media for network equipment. Failure to annually test backup media for Cyber Assets used in the access control and/or monitoring of the ESP could lead to recovery plans that are ineffective. Alternatively, WECC_URE2 may be forced to restore outdated information from a known good backup image in order to resume normal operations. However, WECC_URE2 had several controls in place to prevent and detect irrecoverable CCAs and their potential effect to the BPS. These controls include that there are redundant hardware and configurations in production and the Quality Assurance environment, so the proper configuration could be taken from the Quality Assurance environment, and Cyber Vulnerability Assessments were performed annually on the configuration. | When the server was decommissioned and the data to successfully recover the affected assets was no longer readily available | When WECC_URE2 implemented changes to its settings so that configurations are written to a remote server when the configuration is altered, and performed manual backups on firewalls to servers, which are themselves backed up | No Penalty | Self-Report | To mitigate this violation, WECC_URE2: 1) implemented an archive command on switches and routers, so configurations are written to a remote server when the configuration is altered, and performed manual backups on firewalls to server, which are themselves backed up; 2) ensured backup/configuration/compliance information is stored in a generic format that can be recovered without special software; and 3) revised backup processes to ensure backups are done consistently, so media testing can take place. | 6/9/2016 | 12/15/2016 | Does Not Contest | WECC did not give credit for WECC_URE2’s Internal Compliance Program (ICP). Although WECC_URE2 does have a documented ICP that has been provided to WECC, WECC determined that, due to the length of the violation, WECC_URE2’s ICP failed, in this instance, to adequately detect the violation in a timely manner.
Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2015014926 | Settlement Agreement | WECC_URE2 submitted a Self-Report stating that it was in violation of CIP-006-3c R2.2. Specifically, WECC_URE2 failed to implement the protective measures specified in CIP-007-3 R5 and R6, needed to prevent unauthorized physical access to one Physical Security Perimeter (PSP). WECC_URE2 discovered that an employee, who was not authorized to grant access, was granting unauthorized personnel physical access to a PSP using other users’ Physical Access Control System (PACS) credentials to make the change. WECC_URE2 investigated the incident and determined that the accounts were not properly managed and that the monitoring was insufficient to timely discover the unauthorized activity. The cause of this issue was that the field controllers were not identified as being a PACS elements so they were not captured under the CIP management functions. Staff turnover and unclear roles and responsibilities between the maintenance, physical security, and IT groups led to this misidentification. Additionally, there was insufficient monitoring to discover the unauthorized activity due to inadequate procedures. The PACS application audit log for users was available, but not reviewed until a problem was discovered via direct observation. WECC determined that this violation began when WECC_URE2 first failed to implement various protective measures, required by CIP-006 R2.2, and ended when WECC_URE2 completed its mitigating activities for a total of 1,400 days of noncompliance. | CIP-006-3c | R2 | Medium | Severe | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Specifically, WECC_URE2 control measures needed to prevent unauthorized physical access to a PSP. Failure to control access to restricted areas, such as a PSP, could result in unauthorized access by adversaries, who could ultimately gain access to protected BPS Cyber Assets. However, WECC_URE2 had several controls in place to prevent and detect the unauthorized access to the BES Cyber Assets, including, monitoring of the PSP; regular maintenance and testing of the field controllers; Personnel Risk Assessments were completed for all people involved in the incident; the PACS monitoring was functioning; WECC_URE2’s access control process indicated the unauthorized access; PACS audit logs were functioning and upon review captured all unauthorized actions; appropriate patching was taking place for server/operating system and applications; and server/operating system user reviews were performed. | When WECC_URE2 first failed to implement various protective measures, required by CIP-006 R2.2 | Mitigation Plan completion | No penalty | Self-Report | To mitigate this violation, WECC_URE2: 1) either deleted the non-approved access or provided approval for access, depending on need; 2) implemented proper user account controls, according to CIP version 5; 3) clarified and documented roles and responsibilities for all parts of PACS management, including ensuring PACS roles and responsibilities were clear and communicated; 4) ensured user account controls are addressed in CIP version 5 transition; and 5) completed an administrative action for the employee who improperly granted access. | 7/1/2016 | 2016-12-09 | Does Not Contest | WECC did not give credit for WECC_URE2's Internal Compliance Program (ICP). Although WECC_URE2 does have a documented ICP that has been provided to WECC, WECC determined that, due to the length of the violation, WECC_URE2’s ICP failed, in this instance, to adequately detect the violation in a timely manner.