## Sheet1
The Searchable FFT Informational Spreadsheet is based on remediated issues that were submitted for informational purposes only. In the event of a conflict between information on the Searchable FFT spreadsheet and posted FFTs, the posted FFTs govern.
Filing | Region | Registered Entity Name | NCR | NERC Violation ID | Standard | Req. | Description of Remediated Issue | Description of the Risk Assessment | Description and Status of Mitigation Activity
2017-09-28 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2017017451 | CIP-005-5 | R2 | MRO_URE1 stated that Cyber Assets deployed on the corporate network and some EACMS devices had Interactive Remote Access (IRA) into the Backup Control Center's (BCC) Electronic Security Perimeters (ESP) through the firewall without utilizing an Intermediate System. These direct connections were allowed through use of firewall rules under CIP v3, but after CIP v5, these connections were required to go through an Intermediate System. This issue was discovered during MRO_URE1's vulnerability assessment. The cause of the noncompliance was that MRO_URE1 failed to consider all direct connections into the ESPs when re-routing direct connections through its newly implemented Intermediate System. The duration of the noncompliance was approximately five months. | This issue posed a moderate risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System. Specifically, the risk was not minimal because inadequate safeguards regarding IRA can allow unauthorized access to a registered entity's network with potentially significant consequences. Additionally, the direct access was enabled for four months and the direct access for the corporate Cyber Assets was utilized on two occasions. However, the risk was not serious or substantial because the direct connections initiated by the corporate Cyber Assets, which were allowed prior to CIP V5, were only initiated twice; within two months of the enforcement date, indicating that the active use of the direct connections was limited. Further, the EACMS devices with IRA into the BCC ESPs are required to have the same protections as Intermediate Systems. MRO determined that the issue was appropriate for FFT treatment because of MRO_URE1's compliance history, and that the issue was self-reported that is an indication of functioning detective controls. No harm is known to have occurred. MRO_URE1 has no relevant history of noncompliance. | To mitigate this issue, MRO_URE1 modified Electronic Access Point rules to require the utilization of an Intermediate System to access devices within the BCC ESP. MRO verified that mitigating activities were complete as of November 1, 2016.
2017-09-28 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE2017016868 | CIP-005-5 | R1; P1.3 | During a Compliance Audit, Texas RE determined that TRE_URE1 had an issue with CIP-005-5 R1. In particular, TRE_URE1 did not require inbound and outbound access permissions, including the reason for granting access, and deny all other access by default as required by CIP-005-5 R1, Part 1.3. Two TRE_URE1 servers associated with TRE_URE1’s state estimator function became subject to CIP compliance under the newly applicable CIP version 5 Standards. During an access privilege review for the various state estimators on its system TRE_URE1 determined that the two servers at issue remained located within Electronic Security Perimeters (ESPs) that did not possess the requisite inbound and outbound access permissions on their applicable Electronic Access Points (EAPs). As a result, individuals could access these systems using Interactive Remote Access without first going through an Intermediate System. Subsequently TRE_URE1 completed the logical transfer of these two servers to ESPs with appropriate inbound and outbound access permissions, ending the issue. The root cause of TRE_URE1’s noncompliance was an inadequate process to ensure that all BES Cyber Systems were located inside ESPs with the appropriate access management controls, including required inbound and outbound access permissions. In particular, TRE_URE1 did not have a process to inventory its BES Cyber Assets, including assets newly subject to CIP version 5 compliance, and compare that inventory with ESP access permissions to ensure that all BES Cyber Assets were located within the proper ESP. The duration of the noncompliance was approximately 14 days. | This issue posed a moderate risk and did not pose a serious or substantial risk to the bulk power system (BPS). The two servers at issue are used to monitor TRE_URE1’s Transmission system and provide an estimate of its state at a given point in time using data from the telemetered points to process and compute the voltage magnitude and angles. Not having the correct inbound and outbound access permissions for the EAPs at issue increased the risk that these servers could be compromised and either rendered inoperable or used for unauthorized interactive access with other TRE_URE1 systems. However, the risk to the reliability of the BPS was reduced because of the following five factors. First, the duration of this issue was short, lasting only 14 days. Second, while the servers at issue are needed for system planning purposes, an intruder could not directly operate or control TRE_URE1 equipment through those servers. Third, TRE_URE1 possessed backup systems that could be utilized to manually assess its system state if the two servers at issue were rendered inoperable. Fourth, TRE_URE1 had additional protections in place for the two servers at issue, including security event logging, periodic patching procedures, malicious code prevention, multiple physical security and access controls. These additional protections both reduced the likelihood the servers could be compromised and the impact of a potential compromise on other TRE_URE1 BES Cyber Systems. Finally, TRE_URE1 personnel who had access to servers all had current Personnel Risk Assessments and had successfully completed CIP Cyber Security awareness training. No harm is known to have occurred. Texas RE considered TRE_URE1’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, TRE_URE1: 1) logically transferred the two servers at issue to ESPs with the appropriate access inbound and outbound access permissions for the applicable EAPs; 2) implemented a process that compares daily ESP scans to the inventory of BES Cyber Assets in order to ensure that all applicable Cyber Assets are within the appropriate ESPs; and 3) developed a new procedure to review all Cyber Assets during changes to the CIP requirements to ensure proper controls are in place under any revised NERC Reliability Standards. Texas RE has verified the completion of all mitigation activity.
2017-09-28 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE2017016869 | CIP-005-5 | R2; P2.1; P2.2; P2.3 | During a Compliance Audit, Texas RE determined that TRE_URE1 had an issue with CIP-005-5 R2, Parts 2.1, 2.2, and 2.3. In particular, TRE_URE1 allowed Interactive Remote Access to BES Cyber Systems without using an Intermediate System, utilizing encryption that terminates at an Intermediate System, and requiring multi-factor authentication for all Interactive Remote Access sessions. Two TRE_URE1 servers associated with TRE_URE1’s state estimator function became subject to CIP compliance under the newly applicable CIP version 5 Standards. During an access privilege review for the various state estimators on its system, TRE_URE1 determined that the two servers at issue remained located within Electronic Security Perimeters (ESPs), allowing Interactive Remote Access to the servers without first going through an Intermediate System. As a result, TRE_URE1 likewise neither required multi-factor authentication for Interactive Remote Access sessions with the two servers nor utilized encryption terminating at an Intermediate System. TRE_URE1 subsequently completed the logical transfer of these two servers to ESPs with appropriate Interactive Remote Access permissions and controls, ending the issue. The root cause of TRE_URE1’s noncompliance was an inadequate process to ensure that all BES Cyber Systems were located inside ESPs with the appropriate access management controls. In particular, TRE_URE1 did not have a process to inventory its BES Cyber Assets, including assets newly subject to CIP version 5 compliance, and compare that inventory with ESP access permissions to ensure that all BES Cyber Assets were located within the proper ESP. The duration of the noncompliance was approximately 14 days. | This issue posed a moderate risk and did not pose a serious or substantial risk to the bulk power system (BPS). The two servers at issue are used to monitor TRE_URE1’s Transmission system and provide an estimate of its state at a given point in time using data from the telemetered points to process and compute the voltage magnitude and angles. Not requiring Interactive Remote Access through an Intermediate System increased the risk that these servers could be compromised and either rendered inoperable or used for unauthorized interactive access with other TRE_URE1 systems. In addition, because the servers’ data traffic was not encrypted, there could have been unauthorized interception or manipulation of system state information. Finally, single factor authentication is less secure than multi-factor authentication, creating an increased risk compromised passwords. However, the risk to the reliability of the BPS was reduced because of the following five factors. First, the duration of this issue was short, lasting only 14 days. Second, while the servers at issue are needed for system planning purposes, an intruder could not directly operate or control TRE_URE1 equipment through those servers. Third, TRE_URE1 possessed backup systems that could be utilized to manually assess its system state if the two servers at issue were rendered inoperable. Fourth, TRE_URE1 had additional protections in place for the two servers at issue, including security event logging, periodic patching procedures, malicious code prevention, multiple physical security and access controls. These additional protections both reduced the likelihood the servers could be compromised and the impact of a potential compromise on other TRE_URE1 BES Cyber Systems. Finally, TRE_URE1 personnel who had access to servers all had current Personnel Risk Assessments and had successfully completed CIP Cyber Security awareness training. No harm is known to have occurred. Texas RE considered TRE_URE1’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, TRE_URE1: 1) logically transferred the two servers at issue to ESPs with the appropriate Interactive Remote Access permissions and controls; 2) implemented a process that compares daily ESP scans to the inventory of BES Cyber Assets in order to ensure that all applicable Cyber Assets are within the appropriate ESPs; and 3) developed a new procedure to review all Cyber Assets during changes to the CIP requirements to ensure proper controls are in place under any revised NERC Reliability Standards. Texas RE has verified the completion of all mitigation activity.
2017-09-28 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 2 (TRE_URE2) | NCRXXXXX | TRE2016016391 | CIP-005-5 | R1; P1.3 | TRE_URE2 submitted a Self-Report stating that it had an issue with CIP-005-5 R1. In particular, TRE_URE2 did not require inbound and outbound access permissions, including the reason for granting access, and deny all other access by default as required by CIP-005-5 R1, Part 1.3. Two TRE_URE2 servers associated with TRE_URE2’s state estimator function became subject to CIP compliance under the newly applicable CIP version 5 Standards. During an access privilege review for the various state estimators on its system, TRE_URE2 determined that the two servers at issue remained located within Electronic Security Perimeters (ESPs) that did not possess the requisite inbound and outbound access permissions on their applicable Electronic Access Points (EAPs). As a result, individuals could access these systems using Interactive Remote Access without first going through an Intermediate System. Subsequently, TRE_URE2 completed the logical transfer of these two servers to ESPs with appropriate inbound and outbound access permissions, ending the issue. The root cause of TRE_URE2’s noncompliance was an inadequate process to ensure that all BES Cyber Systems were located inside ESPs with the appropriate access management controls, including required inbound and outbound access permissions. In particular, TRE_URE2 did not have a process to inventory its BES Cyber Assets, including assets newly subject to CIP version 5 compliance, and compare that inventory with ESP access permissions to ensure that all BES Cyber Assets were located within the proper ESP. The duration of the noncompliance was approximately 14 days. | This issue posed a moderate risk and did not pose a serious or substantial risk to the bulk power system (BPS). The two servers at issue are used to monitor TRE_URE2’s Transmission system and provide an estimate of its state at a given point in time using data from the telemetered points to process and compute the voltage magnitude and angles. Not having the correct inbound and outbound access permissions for the EAPs at issue increased the risk that these servers could be compromised and either rendered inoperable or used for unauthorized interactive access with other TRE_URE2 systems. However, the risk to the reliability of the BPS was reduced because of the following five factors. First, the duration of this issue was short, lasting only 14 days. Second, while the servers at issue are needed for system planning purposes, an intruder could not directly operate or control TRE_URE2 equipment through those servers. Third, TRE_URE2 possessed backup systems that could be utilized to manually assess its system state if the two servers at issue were rendered inoperable. Fourth, TRE_URE2 had additional protections in place for the two servers at issue, including security event logging, periodic patching procedures, malicious code prevention, multiple physical security and access controls. These additional protections both reduced the likelihood the servers could be compromised and the impact of a potential compromise on other BES Cyber Systems. Finally, personnel who had access to servers all had current Personnel Risk Assessments and had successfully completed CIP Cyber Security awareness training. No harm is known to have occurred. Texas RE considered TRE_URE2’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, TRE_URE2: 1) logically transferred the two servers at issue to ESPs with the appropriate access inbound and outbound access permissions for the applicable EAPs; 2) implemented a process that compares daily ESP scans to the inventory of BES Cyber Assets in order to ensure that all applicable Cyber Assets are within the appropriate ESPs; and 3) developed a new procedure to review all Cyber Assets during changes to the CIP requirements to ensure proper controls are in place under any revised NERC Reliability Standards. Texas RE has verified the completion of all mitigation activity.
2017-09-28 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 2 (TRE_URE2) | NCRXXXXX | TRE2017018345 | CIP-005-5 | R2; P2.1; P2.2; P2.3 | TRE_URE2 submitted a Self-Report stating that it had an issue with CIP-005-5 R1 relating to its failure to require inbound and outbound access permissions, including the reason for granting access, and deny all other access by default as required by CIP-005-5 R1, Part 1.3. Subsequently, Texas RE determined that the issue described in TRE_URE2's CIP-005-5 R1 Self-Report was also a noncompliance of CIP-005-5 R2, Parts 2.1, 2.2, and 2.3. In particular, TRE_URE2 allowed Interactive Remote Access to BES Cyber Systems without using an Intermediate System, utilizing encryption that terminates at an Intermediate System, and requiring multi-factor authentication for all Interactive Remote Access sessions. Two servers associated with TRE_URE2’s state estimator function became subject to CIP compliance under the newly applicable CIP version 5 Standards. During an access privilege review for the various state estimators on its system, TRE_URE2 determined that the two servers at issue remained located within Electronic Security Perimeters (ESPs), allowing Interactive Remote Access to the servers without first going through an Intermediate System. As a result, TRE_URE2 likewise neither required multi-factor authentication for Interactive Remote Access sessions with the two servers nor utilized encryption terminating at an Intermediate System. Subsequently, TRE_URE2 completed the logical transfer of these two servers to ESPs with appropriate Interactive Remote Access permissions and controls, ending the issue. The root cause of TRE_URE2’s noncompliance was an inadequate process to ensure that all BES Cyber Systems were located inside ESPs with the appropriate access management controls. In particular, TRE_URE2 did not have a process to inventory its BES Cyber Assets, including assets newly subject to CIP version 5 compliance, and compare that inventory with ESP access permissions to ensure that all BES Cyber Assets were located within the proper ESP. The duration of the noncompliance was approximately 14 days. | This issue posed a moderate risk and did not pose a serious or substantial risk to the bulk power system (BPS). The two servers at issue are used to monitor TRE_URE2’s Transmission system and provide an estimate of its state at a given point in time using data from the telemetered points to process and compute the voltage magnitude and angles. Not requiring Interactive Remote Access through an Intermediate System increased the risk that these servers could be compromised and either rendered inoperable or used for unauthorized interactive access with other TRE_URE2 systems. In addition, because the servers’ data traffic was not encrypted, there could have been unauthorized interception or manipulation of system state information. Finally, single factor authentication is less secure than multi-factor authentication, creating an increased risk compromised passwords. However, the risk to the reliability of the BPS was reduced because of the following five factors. First, the duration of this issue was short, lasting only 14 days. Second, while the servers at issue are needed for system planning purposes, an intruder could not directly operate or control TRE_URE2 equipment through those servers. Third, TRE_URE2 possessed backup systems that could be utilized to manually assess its system state if the two servers at issue were rendered inoperable. Fourth, TRE_URE2 had additional protections in place for the two servers at issue, including security event logging, periodic patching procedures, malicious code prevention, multiple physical security and access controls. These additional protections both reduced the likelihood the servers could be compromised and the impact of a potential compromise on other TRE_URE2 BES Cyber Systems. Finally, TRE_URE2 personnel who had access to servers all had current Personnel Risk Assessments and had successfully completed CIP Cyber Security awareness training. No harm is known to have occurred. Texas RE considered TRE_URE2’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, TRE_URE2: 1) logically transferred the two servers at issue to ESPs with the appropriate Interactive Remote Access permissions and controls; 2) implemented a process that compares daily ESP scans to the inventory of BES Cyber Assets in order to ensure that all applicable Cyber Assets are within the appropriate ESPs; and 3) developed a new procedure to review all Cyber Assets during changes to the CIP requirements to ensure proper controls are in place under any revised NERC Reliability Standards. Texas RE has verified the completion of all mitigation activity.
2017-08-31 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2016016366 | CIP-007-6 | R4. | NPCC_URE1 submitted a Self-Report stating that it had an issue of CIP-007-6 R4. NPCC_URE1's system problem report workflow tool generates a task to review captured logs every 15 days. NPCC_URE1 failed to execute the review of logged events every 15 calendar days for its two of its systems. There was a failure to execute the task when it was generated in the workflow tool due to conflicting priorities and changes to the task assignee's roles and responsibilities. The issue started when the logs should have been reviewed and ended when the logs were reviewed in both systems. Additionally, NPCC_URE1 did not configure its systems' automatic alerting function to detect failure of event logging per R4.2.2. The cause of the noncompliance was a lack of understanding of the standard requirement regarding the scope of detection on failures and the associated logging. The systems were retaining logs and providing email alerts for predetermined events such as failed access/login attempts but did not provide alerts when devices failed to log. The duration of the noncompliance started on the enforceable date of the standard and ended when both systems were configured correctly . | The issue posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. NPCC_URE1 discovered that they did not review system one logs for 61 days and system two logs for 67 days. The review of logs indicated there were no security events during the duration that the logs were not reviewed. NPCC_URE1 did not identify any devices that failed to log during the duration that the alerting function was not configured correctly. Alerting was functional for predetermined events such as failed access/login attempts. Both systems are behind firewalls that are monitored and separate from the corporate environment and the internet. Both systems deploy intrusion detection appliances to monitor inbound and outbound traffic. Remote access is controlled via two factor authentication from any outside source. Communications between discreet Electronic Security Perimeter/Physical Security Perimeters is controlled by firewalls and communication between Electronic Security Perimeters is encrypted. No harm is known to have occurred | To mitigate this issue, NPCC_URE1: 1) disciplined the individual who failed to complete the task; 2) performed reviews back to the enforceable date of the standard; 3) provided training and overview of responsibilities to subject matter experts. A formal review of open task items will be done and escalated moving forward; 4) implemented a suite of tools for system two which has the ability to create alerts based on thresholds configured for each asset type that requires logging. The alert is sent to an internal distribution list and details which system has failed to log. A redundant server has been put into place in the event the server itself is unavailable to perform the alerting function. Alerts are reviewed on a daily basis; and 5) implemented a tool for system one which allows assets to report syslog events. The tool provides a daily report which shows devices that did not communicate successfully. The report is sent to the responsible subject matter experts for its review. An additional report of the top reporting devices is also emailed and compared to the inactive devices report. Reviews of the reports are recorded in an email and within a ticketing tracking database to indicate the time of the review and any anomalies that occurred. In the event that an asset is no longer reporting, an subject matter expert will be deployed to investigate the issue.
2017-08-31 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 2 (NPCC_URE2) | NCRXXXXX | NPCC2016016364 | CIP-007-6 | R4. | NPCC_URE2 submitted a Self-Report stating that it had an issue of CIP-007-6 R4. NPCC_URE2's system problem report workflow tool generates a task to review captured logs every 15 days. NPCC_URE2 failed to execute the review of logged events every 15 calendar days for its two of its systems. There was a failure to execute the task when it was generated in the workflow tool due to conflicting priorities and changes to the task assignee's roles and responsibilities. The issue started when the logs should have been reviewed and ended when the logs were reviewed both systems. Additionally, NPCC_URE2 did not configure its systems' automatic alerting function to detect failure of event logging per R4.2.2. The cause of the noncompliance was a lack of understanding of the standard requirement regarding the scope of detection on failures and the associated logging. The systems were retaining logs and providing email alerts for predetermined events such as failed access/login attempts but did not provide alerts when devices failed to log. The duration of the noncompliance started on the enforceable date of the standard and ended when both systems were configured correctly . | The issue posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. NPCC_URE2 discovered that they did not review system one logs for 61 days and system two logs for 67 days. The review of logs indicated there were no security events during the duration that the logs were not reviewed. NPCC_URE2 did not identify any devices that failed to log during the duration that the alerting function was not configured correctly. Alerting was functional for predetermined events such as failed access/login attempts. Both systems are behind firewalls that are monitored and separate from the corporate environment and the internet. Both systems deploy intrusion detection appliances to monitor inbound and outbound traffic. Remote access is controlled via two factor authentication from any outside source. Communications between discreet Electronic Security Perimeter/Physical Security Perimeters is controlled by firewalls and communication between Electronic Security Perimeters is encrypted. No harm is known to have occurred | To mitigate this issue, NPCC_URE2: 1) disciplined the individual who failed to complete the task; 2) performed reviews back to the enforceable date of the standard; 3) provided training and overview of responsibilities to subject matter experts. A formal review of open task items will be done and escalated moving forward; 4) implemented a suite of tools for system two which has the ability to create alerts based on thresholds configured for each asset type that requires logging. The alert is sent to an internal distribution list and details which system has failed to log. A redundant server has been put into place in the event the server itself is unavailable to perform the alerting function. Alerts are reviewed on a daily basis; and 5) implemented a tool for system one which allows assets to report syslog events. The tool provides a daily report which shows devices that did not communicate successfully. The report is sent to the responsible subject matter experts for its review. An additional report of the top reporting devices is also emailed and compared to the inactive devices report. Reviews of the reports are recorded in an email and within a ticketing tracking database to indicate the time of the review and any anomalies that occurred. In the event that an asset is no longer reporting, an subject matter expert will be deployed to investigate the issue.
2017-08-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2017016743 | CIP-010-2 | R1 | RFC_URE1 submitted a Self-Report to ReliabilityFirst stating that it had an issue with CIP-010-2 R1. RFC_URE1 discovered that three in-scope Cyber Assets (Electronic Access Control or Monitoring Systems (EACMS) devices) did not have sufficient baselines established under CIP-010-2 R1.1. Specifically, these EACMS devices did not have sufficient documentation of their operating system, installed software, logical network accessible ports, and security patches. CIP-010-2 R1.1 permits RFC_URE1 to maintain baseline configurations for groups of one or more Cyber Assets. RFC_URE1 documents its baseline configurations by groups of one or more Cyber Assets and uses Devices Roles to represent groups of like Cyber Assets that share common baseline configuration items (operating system, installed software, logical network accessible ports and security patches). In this case, these three EACMS devices were assigned to a specific Device Role. These three EACMS devices, however, did not share a common profile of operating system, installed software, logical network accessible ports or security patches with the other Cyber Assets in their shared Device Role. The three EACMS devices should have had their own Device Role and when RFC_URE1 performed baseline data collections for these three devices, the data collections were inadvertently not compared or checked against the inventory of Cyber Assets. Following from this mistake, baselines for the three EACMS devices were not created. RFC_URE1 maintains self-monitoring internal controls to detect errors or irregularities with respect to its newly implemented CIP v5 compliance program. For this issue, RFC_URE1 performed a compliance review of its compliance with CIP-010-2 R1 after the July 1, 2016 implementation date for the creation of configuration baselines for Cyber Assets. (RFC_URE1 has one Medium Impact Bulk Electric System (BES) Cyber System and the in-scope Cyber Assets reviewed in this review included the Medium Impact BES Cyber System and its associated EACMS, Physical Access Control Systems and Protected Cyber Assets.) That review discovered this issue. This noncompliance involves the management practice of asset and configuration management because RFC_URE1 did not have an effective process in place to ensure that baseline configurations were established for all relevant Cyber Assets. This lack of a process and an inability to create baselines for these three EACMS devices is a root cause of this noncompliance. The duration of the noncompliance was approximately five months. | This issue posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by this issue is that failing to establish baselines for these three EACMS devices could result in RFC_URE1 failing to detect and track both authorized and unauthorized changes to these devices. This includes changes that could adversely affect system security. Another factor elevating the risk is RFC_URE1’s two other recent CIP-007 Self-Reports both showed struggles with asset and configuration management. Those other two Self-Reports having similar contributing causes and that contributed to the moderate risk determination. The risk is moderated because these devices are not BES Cyber Assets meaning the devices do not directly impact the reliable operation of the BES which reduces the impact that an unauthorized change could have on the devices at issue. Lastly, for the duration of the issue, the devices did not undergo any changes that required the use of proper change management and the devices were functioning normally. ReliabilityFirst determined that this issue was appropriate for FFT treatment because it posed a moderate risk as RFC_URE1 did not establish baselines for three EACMS devices for approximately five months and failing to establish baselines for these three EACMS devices could result in RFC_URE1 failing to detect and track both authorized and unauthorized changes to these devices. Another factor elevating the risk is the fact that RFC_URE1’s two other recent CIP-007 Self-Reports both showed struggles with asset and configuration management. No harm is known to have occurred. While evaluating RFC_URE1, ReliabilityFirst identified weaknesses in RFC_URE1’s asset and configuration management. Following from those weaknesses, ReliabilityFirst will focus on how RFC_URE1 handles asset and configuration management. | To mitigate this issue, the RFC_URE1: 1) completed a review of its Cyber Asset Inventory to determine if other devices were missed; 2) reviewed and revised Device Role names to be more descriptive in its Cyber Asset Inventory and to include the platform of the device as necessary for additional clarification. A Cyber Asset may be assigned to a Device Role when it shares in common with other Cyber Assets in the Device Role each of the following: (1) Same platform; (2) Same function; (3) Same installed software; and (4) Same data collection method; 3) expanded Authoritative Inventory to track additional attributes for each Cyber Asset. The Inventory now identifies the Data Collection Method(s) for each Cyber Asset that is subject to CIP. When data collections are performed each month, they are checked against the Cyber Asset Inventory to ensure that data from all Cyber Assets subject to NERC CIP has been collected and this will help prevent recurrence. The new procedures were demonstrated and discussed with all subject matter experts responsible for CIP compliance activities. Documented procedures were revised and improved; 4) created baseline documentation for the missing devices; and 5) updated the monthly patching process to check against the Cyber Asset Inventory to ensure that data from all Cyber Assets subject to NERC CIP has been collected and this will help prevent recurrence. ReliabilityFirst has verified the completion of all mitigation activity.
2017-06-29 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2017016762 | CIP-006-6 | R1. | FRCC_URE1 submitted a Self-Report stating that it had an issue of CIP-006-6 R1. For 42 days, a control center card key panel failed to record all access types and thus retain those log records. Therefore, FRCC_URE1 failed to log and retain for at least 90 days successful log entries of each individual with authorized unescorted physical access into one Physical Security Perimeter as required by Parts 1.8 and 1.9. An administrator ran a report and noticed not all accesses were being recorded for a control center. A physical security coordinator was dispatched to the site to further investigate. The coordinator again tested for all events and confirmed that all events except one were logged. As an isolated event with no indication of malicious activity, this initial assessment of the issue did not warrant a need to initiate a full incident response. To correct the issue, the coordinator rebooted the card key panel and tested the panel again to confirm that all event types were logging. The vendor was contacted for assistance in recovering the historical logs. The vendor informed FRCC_URE1 that any events stored locally on the device were deleted when the cardkey panel was rebooted. Therefore, FRCC_URE1 is unable to retrieve the logs during the period in question. The root cause for this violation was unable to be identified with certainty. Because the reboot of the cardkey panel erases the cardkey panel’s memory, the vendor was unable to diagnose the panel to determine a definitive root cause. Though the vendor had not observed this specific issue elsewhere, the vendor believed the likely root cause was a firmware issue and suggested that the defect could be corrected with a recent firmware update. | This issue posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. A compromise of the cardkey panel could have allowed undetected physical access to the computing equipment. This risk, however, was reduced as all access to the requires two-factor authentication and is monitored by the security team using security cameras 24/7 as an additional internal control. No actual physical security breach was observed during the 42 days that the logs were not created and retained. FRCC determined that the issue was appropriate for FFT treatment because all other event types were properly logged during the 42 days. Additionally, this event is isolated with no indication of malicious activity. No harm is known to have occurred. | To mitigate this violation, FRCC_URE1: 1) rebooted the cardkey panel to correct the logging issue 2) reviewed the logs of other NERC cardkey panels to determine extent of condition 3) created a cardkey panel procedure for rebooting that requires retrieving, if possible, locally stored event logs and other pertinent diagnostic data before rebooting 4) Upgraded all NERC cardkey panels to the latest firmware and replaced the cardkey panel in question 5) Created a new detective control to alarm when a cardkey panel is storing logs locally and not sending them to the server
2017-06-29 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2017017657 | CIP-005-5 | R2 | MRO determined that MRO_URE1 had an issue of CIP-005-5 R2, Parts 2.1-2.3. Specifically, MRO_URE1 had a firewall misconfiguration that allowed Interactive Remote Access into the Electronic Security Perimeter (ESP) to two servers located in the ESP without first going through an intermediate system. This occurred when changes were made to the firewall that allowed direct FTP, SSH, HTTP and HTTPS communications to and from these servers. The cause of this noncompliance was a vendor configuration change that was not detected by MRO_URE1 when it transitioned to CIP Version 5. When the change was made, MRO_URE1 did not have any Critical Cyber Assets, and, therefore did not have to follow a CIP-mandated change management Reliability Standard such as CIP-003-3 R6. During MRO_URE1's transition to CIP Version 5, it did not detect this pre-existing issue and was not aware that these two servers could communicate without first going through an intermediate system. The duration of the noncompliance was approximately 2 months. | This issue posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The risk was not minimal because SSH, FTP, HTTP, and HTTPS are widely known ports that are typically targeted by skilled adversaries. An adversary could attack the servers directly through methods such as Distributed Denial of Service (DDOS) or Brute Force Password Crack type attacks. However, the risk was not serious or substantial because MRO_URE1 stated that logging was enabled. The two servers were behind a firewall and access for those devices was limited to four specific ports. No harm is known to have occurred. MRO_URE1 has no relevant history of noncompliance with CIP-005-5. | To mitigate this issue, MRO_URE1: 1) closed the connections to the servers; 2) implemented the change management requirements of CIP-010-2; and 3) took over the management of its Access Control Lists, and no longer relies upon a vendor, which has elevated its knowledge and familiarity with these issues.
2017-06-29 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2016016580 | CIP-006-6 | R1. | NPCC_URE1 submitted a Self-Report stating that it had an issue of CIP-006-6 R1. During a scheduled delivery to the lower level operations area, a visitor was able to gain access to a NERC CIP designated area. When the delivery person arrived at the lower level operations area, he was met by the receptionist at a mantrap. A mantrap is a small space with two sets of doors, such that the first set of doors must close before the second set opens. It protects access to the non-NERC CIP area which borders the NERC CIP area. He was granted access through the mantrap and signed the non-NERC CIP visitor log book. He was told by the receptionist where to deliver and that she would be back shortly to escort him out. Having completed his delivery, he looked for assistance to exit through the mantrap and in trying the nearest door, gained unauthorized access to a NERC CIP designated area which is staffed 24/7. An employee immediately observed the individual and questioned him as to how he gained access. The individual stated that he had pushed on the door and it opened. The individual was immediately escorted out of the CIP designated area, back to the non-NERC CIP area and through the mantrap by the employee. The employee checked the door in question and found it secure. The employee took action to notify the responsible individual identified in the BES Cyber Security Incident Response Plan of detection of the unauthorized access. After assessing the situation, the employee notified personnel of the unauthorized access into the CIP designated area and that the situation was under control. Further review of this incident confirmed that the unauthorized access triggered a correct “Forced Door Alarm” which was received by the Security Command Center. A root cause investigation of this incident found that the door in question had malfunctioned. This door was recently modified to change the door controls for exiting from motion sensor controlled to smart handles. In the instant case, a “Forced Door Alarm” was triggered when the magnetic connection (which indicates the door status –open/closed) was separated when the door was pushed open without the door being fully closed and locked. After extensive tries of opening and closing the door the malfunction condition was able to be duplicated, but not consistently. This testing determined that the latch was intermittently getting hung up on the strike plate, so the door indicated closed but was not actually fully closed and locked. | This issue posed a moderate risk and not pose a serious or substantial risk to the BPS. The noncompliance resulted in an unauthorized individual having the ability to access a CIP designated area. The individual was scheduled for the visit and was IDed when given access through the man-trap into the non-NERC CIP area. The individual was immediately escorted out by an employee. Any unauthorized entry would be detected as employees question all individuals, not part of the area as to the purpose of their visit and their credentials. Action was also taken to notify the responsible individual identified in the BES Cyber Security Incident Response Plan of detection of the unauthorized access within 15 minutes of the event. No harm is known to have occurred. | To mitigate this issue, NPCC_URE1: 1) adjusted door hardware to prevent re-occurrence and tested door for proper operation; 2) took disciplinary action against the security command center employee for not responding to a forced door alarm; 3) confirmed that the individual that gained unauthorized access was on official business and scheduled to make the delivery; 4) developed guideline documents as "lessons learned" to prevent recurrence of SCC operator failure. All alarm notification and response procedures were updated as necessary and reviewed with the operators; 5) communicated informal and formal awareness messages highlighting this incident to operations personnel addressing visitors and PSP access points to the lower level operations non-CIP and NERC CIP areas; 6) posted additional signage on all NERC CIP doors emphasizing the message that access is for "Authorized Personnel Only." 7) replaced CIP designated wooden doors with Steel doors; and 8) evaluated the existing PSP configuration to reduce the risk of unauthorized access. NPCC has verified the completion of all mitigation activity.
2017-06-29 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2016016424 | CIP-003-3 | R6 | RFC_URE1 submitted a Self-Report to ReliabilityFirst stating that it had an issue with CIP-003-3 R6. This noncompliance involves three separate instances. In the first instance, an Information Technology (IT) team supporting RFC_URE1’s Commercial Operations knew that another team planned to install software on certain workstations, including 29 workstations used to dispatch RFC_URE1’s generation fleet. Prior to the software deployment, the IT team requested the dispatcher workstations be excluded from the software deployment. However, despite this request, the software was installed on the dispatcher workstations without going through IT’s process for managing changes. IT discovered the software on the workstations and RFC_URE1 immediately removed the software from all workstations. RFC_URE1 conducted an assessment and determined that existing security controls were not adversely affected. Regarding the root cause, RFC_URE1 determined that the software uses “scopes” to define which assets may receive a software “push.” In this case, the IT team correctly created a scope to exclude dispatcher workstations from the push, but, the same team was unaware that their membership in a corporate domain group with administrative authority to the server would override the newly-created scope and push the software to all workstations. This involves the management practice of asset and configuration management because RFC_URE1 did not control changes to its configuration items. Regarding the second incident, a system administrator discovered that a software client was installed on 29 CIP workstations in error and without the required change management activities. The system administrator identified the error when he attempted to restart one of the affected workstations. The administrator immediately contacted the administrator to ask him to stop the installations. He then uninstalled the software from the devices on which it had already been installed and conducted an assessment and confirmed that no ports were opened or user IDs created by this unplanned installation. After correcting the immediate problem, system administrators investigated the cause and determined that the query the software uses to define the devices in the scope was inadvertently changed. RFC_URE1 determined that the cause was the upgrade of the software server as part of the move to the new data center. When the server was upgraded and placed in service in the data center, system administrators copied settings and queries from the old server to the new server, but changed one qualifier in a query from “and” to “or,” which caused the query to return the workstations at issue for inclusion for the software push. There were no records of post-implementation testing of the scope queries. This root cause involves the management practice of verification, which includes controls to confirm that a process was completed as intended. Here, there should have been a post-implementation test of the scope queries to verify that the queries were entered correctly. Regarding the third incident, a daily review of baseline exceptions from a detective tool alerted RFC_URE1 that new, unauthorized software had been installed on 4 BES Cyber Assets the day before. A contractor installed the software on recovery servers. The contractor had NERC/CIP clearance for unescorted cyber and physical access and had taken RFC_URE1’s NERC CIP training. Regarding the root cause, the contractor saw the software installed on the test server and thus incorrectly thought it would be permissible to install it in the production environment to assist with his work. This issue involves workforce management, which includes establishing strategic training and awareness needs for staff and contractors. The duration of this issue was approximately nine months. | This issue posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. Executing changes on CIP assets without properly executing test procedures could potentially introduce system instability or affect functionality. However, these risks were mitigated by the following factors. Regarding all three instances, RFC_URE1 quickly detected the issues (all within two days of occurrence) and thereafter quickly mitigated the issues. Additionally, regarding the first instance, the software was tested prior to deployment (although it did not go through IT’s formal change management process), thus making it less likely that the software would have adversely affected the assets at issue. Also, the workstations do not use printers, so the software was not functional on the workstations. Regarding the second instance, the software was approved for RFC_URE1 assets, thus making it less likely that the software would have adversely affected the assets at issue. Regarding the third instance, there were no known vulnerabilities for the version of the software that was installed, thus reducing the likelihood that the software would cause vulnerabilities in the system. Additionally, it should be noted that as part of Version 5 implementation, RFC_URE1 installed a tool that performs a daily review of baseline exceptions from the system. Accordingly, RFC_URE1 will now be able to timely detect these types of incidents through the tool and thus reduce the likelihood that they may cause a vulnerability in its system. ReliabilityFirst determined that this issue was appropriate for FFT treatment because the issues posed only moderate risk to the BPS and RFC_URE1 quickly self-identified and mitigated the issues, then self-reported the issues. No harm is known to have occurred. | To mitigate this issue, RFC_URE1: 1) uninstalled the unauthorized software on all affected assets; 2) performed testing to ensure that CIP-005 and CIP-007 controls were not affected by the changes; 3) provided guidance to the contractor on the proper change management procedures; and 4) separated the software core for the domain (regarding the first two incidents), which isolated the assets and thus prevents unintended software pushes.
2017-06-29 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2016016431 | CIP-003-3 | R6 | RFC_URE2 submitted a Self-Report to ReliabilityFirst stating that it had an issue with CIP-003-3 R6. This noncompliance involves three separate instances. In the first instance, an Information Technology (IT) team supporting RFC_URE2’s Commercial Operations knew that another team planned to install software on certain workstations, including 29 workstations used to dispatch RFC_URE2’s generation fleet. Prior to the software deployment, the IT team requested the dispatcher workstations be excluded from the software deployment. However, despite this request, the software was installed on the dispatcher workstations without going through IT’s process for managing changes. IT discovered the software on the workstations and RFC_URE2 immediately removed the software from all workstations. RFC_URE2 conducted an assessment and determined that existing security controls were not adversely affected. Regarding the root cause, RFC_URE2 determined that the software uses “scopes” to define which assets may receive a software “push.” In this case, the IT team correctly created a scope to exclude dispatcher workstations from the push, but, the same team was unaware that their membership in a corporate domain group with administrative authority to the server would override the newly-created scope and push the software to all workstations. This involves the management practice of asset and configuration management because RFC_URE2 did not control changes to its configuration items. Regarding the second incident, a system administrator discovered that the software client was installed on 29 CIP workstations in error and without the required change management activities. The system administrator identified the error when he attempted to restart one of the affected workstations. The administrator immediately contacted the administrator to ask him to stop the installations. He then uninstalled the software from the devices on which it had already been installed and conducted an assessment and confirmed that no ports were opened or user IDs created by this unplanned installation. After correcting the immediate problem, system administrators investigated the cause and determined that the query the software uses to define the devices in the scope was inadvertently changed. RFC_URE2 determined that the cause was the upgrade of the software server as part of the move to the new data center. When the server was upgraded and placed in service in the data center, system administrators copied settings and queries from the old server to the new server, but changed one qualifier in a query from “and” to “or,” which caused the query to return the workstations at issue for inclusion for the software push. There were no records of post-implementation testing of the scope queries. This root cause involves the management practice of verification, which includes controls to confirm that a process was completed as intended. Here, there should have been a post-implementation test of the scope queries to verify that the queries were entered correctly. Regarding the third incident, a daily review of baseline exceptions from a detective tool alerted RFC_URE2 that new, unauthorized software had been installed on 4 BES Cyber Assets the day before. A contractor installed the software on recovery servers. The contractor had NERC/CIP clearance for unescorted cyber and physical access and had taken RFC_URE2’s NERC CIP training. Regarding the root cause, the contractor saw the software installed on the test server and thus incorrectly thought it would be permissible to install it in the production environment to assist with his work. This issue involves workforce management, which includes establishing strategic training and awareness needs for staff and contractors. The duration of this issue was approximately nine months. | This issue posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. Executing changes on CIP assets without properly executing test procedures could potentially introduce system instability or affect functionality. However, these risks were mitigated by the following factors. Regarding all three instances, RFC_URE2 quickly detected the issues (all within two days of occurrence) and thereafter quickly mitigated the issues. Additionally, regarding the first instance, the software was tested prior to deployment (although it did not go through IT’s formal change management process), thus making it less likely that the software would have adversely affected the assets at issue. Also, the workstations do not use printers, so the software was not functional on the workstations. Regarding the second instance, the software was approved for RFC_URE2 assets, thus making it less likely that the software would have adversely affected the assets at issue. Regarding the third instance, there were no known vulnerabilities for the version of the software that was installed, thus reducing the likelihood that the software would cause vulnerabilities in the system. Additionally, it should be noted that as part of Version 5 implementation, RFC_URE2 installed a tool that performs a daily review of baseline exceptions from the system. Accordingly, RFC_URE2 will now be able to timely detect these types of incidents through the tool and thus reduce the likelihood that they may cause a vulnerability in its system. ReliabilityFirst determined that this issue was appropriate for FFT treatment because the issues posed only moderate risk to the BPS and RFC_URE2 quickly self-identified and mitigated the issues, then self-reported the issues. No harm is known to have occurred. | To mitigate this issue, RFC_URE2: 1) uninstalled the unauthorized software on all affected assets; 2) performed testing to ensure that CIP-005 and CIP-007 controls were not affected by the changes; 3) provided guidance to the contractor on the proper change management procedures; and 4) separated the software core for the domain (regarding the first two incidents), which isolated the assets and thus prevents unintended software pushes.
2017-06-29 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC2016016582 | CIP-005-3a | R1 | RFC_URE3 submitted a Self-Report to ReliabilityFirst stating that it had an issue with CIP-005-3a R1. RFC_URE3 commissioned four devices as part of the Shared Infrastructure Remediation (SIR) project and CIP v5 transition efforts. The devices were appropriately brought into CIP scope as BES Cyber Assets (BCAs). Four out-of-band management interfaces for the devices were originally intended to be shut down and not used. As a result of RFC_URE3’s intent to not use these devices, RFC_URE3 did not include these four out-of-band management interfaces in the commissioning process for the four devices. These four out-of-band management interfaces became a compliance issue due to how the migration of the interfaces and network switches was conducted. Prior to the SIR project, some 7K network switches held both Electronic Security Perimeter (ESP) and non-ESP subnets. The purpose of the SIR project was to migrate physical network connections and ESP subnets off of 7K switches and to put all switches dedicated to RFC_URE3's critical infrastructure on 5K network switches. The four devices (and their four out-of-band management interfaces) were commissioned on an ESP subnet that lived on a 5K switch. However, while the four out-of-band management interfaces were routed through the 5K switch, their IP address was on a subnet that was not identified as an ESP and lived on a 7K switch. At the time, a temporary route was put in place between the critical infrastructure 5K switch and the 7K switch so the systems would continue to be connected to the network prior to completing the SIR project. More than seven months later, to complete the SIR project, the temporary links between 5K and 7K network switches needed to be severed so that only critical infrastructure traffic was routed through the 5K switches. As part of completing this severing task, the Networking & Telecommunications team was reviewing the VLAN configurations and discovered that the four out-of-band management interfaces for the devices were active and connected to the network through a 7K switch on a non-ESP subnet. The four out-of-band management interfaces were not supposed to be active nor connected to the network through a 7K switch on a non-ESP subnet. This noncompliance involves the management practice of information management. Information management is involved because RFC_URE3 did not have a control in place to verify that out-of-band management interfaces were inactive. This lack of a control is a root cause of this noncompliance. The duration of this issue was approximately seven months. | This issue posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by not properly commissioning the four out-of-band management interfaces is that they could have vulnerabilities that allow a bad actor to get inside an ESP and compromise BCAs. That risk is minimized because RFC_URE3 had multiple protections related to the out-of-band management interfaces in place throughout the noncompliance that minimized the risk: a. The out-of-band management interfaces are all in the Physical Security Perimeter (PSP) and are protected from physical and logical access. b. Access to the PSP is approved by authorized personnel. c. Personnel with authorized access have completed CIP training and Personnel Risk Assessments. d. The devices connected to the out-of-band management interfaces were all tested to ensure that they did not adversely impact existing cyber security controls prior to being placed in the production environment. e. All other assets within the ESP have anti-virus and antimalware tools installed. ReliabilityFirst determined that the issue was appropriate for FFT treatment because it posed a moderate risk and because of RFC_URE3’s relevant compliance history with CIP-005 R1. No harm is known to have occurred. | To mitigate this issue, RFC_URE3: 1) severed the link between a 5K and a 7K switch, causing the four out-of-band management interfaces to go offline and become unreachable over the network. RFC_URE3’s action to replace its shared infrastructure configuration will prevent this issue from reoccurring. Replacing RFC_URE3’s shared infrastructure configuration eliminates the current architectural configuration that placed the out-of-band management interfaces on a non-ESP network. The new architectural configuration eliminates shared infrastructure and ensures that the out-of-band management interfaces reside on an ESP, without connectivity to non-ESP networks; 2) completed a Shared Infrastructure Remediation (SIR) project to eliminate shared infrastructure between critical systems inside an ESP and non-critical systems outside of an ESP. This project has significantly reduced the likelihood of a similar issue. The assets at issue in this noncompliance were connected via a shared network and this will not be possible moving forward; 3) brought back online the four Cyber Assets impacted in a designated ESP subnet; and 4) updated the commission task language to direct System Administrators to verify that all logical interfaces have been identified, including out-of-band interfaces, and to validate that connected interfaces are on the appropriate network depending on the host classification. These controls will prevent recurrence. RFC_URE3 will complete the following mitigation activities: 1) develop training material for the IT division on RFC_URE3's scope management process that will include information regarding identification and classification of out-of-band management interfaces and the associated protections required; and 2) deliver training to the IT division on RFC_URE3's scope management process that will include information regarding identification and classification of out-of-band management interfaces and the associated protections required.
2017-06-29 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC2016016583 | CIP-005-3a | R2 | RFC_URE3 submitted a Self-Report to ReliabilityFirst stating that it had an issue with CIP-005-3a R1. RFC_URE3 commissioned four devices as part of the Shared Infrastructure Remediation (SIR) project and CIP v5 transition efforts. The devices were appropriately brought into CIP scope as BES Cyber Assets (BCAs). Four out-of-band management interfaces for the devices were originally intended to be shut down and not used. As a result of RFC_URE3’s intent to not use these devices, RFC_URE3 did not include these four out-of-band management interfaces in the commissioning process for the four devices. These four out-of-band management interfaces became a compliance issue due to how the migration of the interfaces and network switches was conducted. Prior to the SIR project, some 7K network switches held both Electronic Security Perimeter (ESP) and non-ESP subnets. The purpose of the SIR project was to migrate physical network connections and ESP subnets off of 7K switches and to put all switches dedicated to RFC_URE3's critical infrastructure on 5K network switches. The four devices (and their four out-of-band management interfaces) were commissioned on an ESP subnet that lived on a 5K switch. However, while the four out-of-band management interfaces were routed through the 5K switch, their IP address was on a subnet that was not identified as an ESP and lived on a 7K switch. At the time, a temporary route was put in place between the critical infrastructure 5K switch and the 7K switch so the systems would continue to be connected to the network prior to completing the SIR project. More than seven months later, to complete the SIR project, the temporary links between 5K and 7K network switches needed to be severed so that only critical infrastructure traffic was routed through the 5K switches. As part of completing this severing task, the Networking & Telecommunications team was reviewing the VLAN configurations and discovered that the four out-of-band management interfaces for the devices were active and connected to the network through a 7K switch on a non-ESP subnet. The four out-of-band management interfaces were not supposed to be active nor connected to the network through a 7K switch on a non-ESP subnet. This noncompliance involves the management practice of information management. Information management is involved because RFC_URE3 did not have a control in place to verify that out-of-band management interfaces were inactive. This lack of a control is a root cause of this noncompliance. The duration of this issue was approximately seven months. | This issue posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by not properly commissioning the four out-of-band management interfaces is that they could have vulnerabilities that allow a bad actor to get inside an ESP and compromise BCAs. That risk is minimized because RFC_URE3 had multiple protections related to the out-of-band management interfaces in place throughout the noncompliance that minimized the risk: a. The out-of-band management interfaces are all in the Physical Security Perimeter (PSP) and are protected from physical and logical access. b. Access to the PSP is approved by authorized personnel. c. Personnel with authorized access have completed CIP training and Personnel Risk Assessments. d. The devices connected to the out-of-band management interfaces were all tested to ensure that they did not adversely impact existing cyber security controls prior to being placed in the production environment. e. All other assets within the ESP have anti-virus and antimalware tools installed. ReliabilityFirst determined that the issue was appropriate for FFT treatment because it posed a moderate risk and because of RFC_URE3’s relevant compliance history with CIP-005 R1. No harm is known to have occurred. | To mitigate this issue, RFC_URE3: 1) severed the link between a 5K and a 7K switch, causing the four out-of-band management interfaces to go offline and become unreachable over the network. RFC_URE3’s action to replace its shared infrastructure configuration will prevent this issue from reoccurring. Replacing RFC_URE3’s shared infrastructure configuration eliminates the current architectural configuration that placed the out-of-band management interfaces on a non-ESP network. The new architectural configuration eliminates shared infrastructure and ensures that the out-of-band management interfaces reside on an ESP, without connectivity to non-ESP networks; 2) completed a Shared Infrastructure Remediation (SIR) project to eliminate shared infrastructure between critical systems inside an ESP and non-critical systems outside of an ESP. This project has significantly reduced the likelihood of a similar issue. The assets at issue in this noncompliance were connected via a shared network and this will not be possible moving forward; 3) brought back online the four Cyber Assets impacted in a designated ESP subnet; and 4) updated the commission task language to direct System Administrators to verify that all logical interfaces have been identified, including out-of-band interfaces, and to validate that connected interfaces are on the appropriate network depending on the host classification. These controls will prevent recurrence. RFC_URE3 will complete the following mitigation activities: 1) develop training material for the IT division on RFC_URE3's scope management process that will include information regarding identification and classification of out-of-band management interfaces and the associated protections required; and 2) deliver training to the IT division on RFC_URE3's scope management process that will include information regarding identification and classification of out-of-band management interfaces and the associated protections required.
2017-06-29 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC2016016584 | CIP-005-3a | R3 | RFC_URE3 submitted a Self-Report to ReliabilityFirst stating that it had an issue with CIP-005-3a R1. RFC_URE3 commissioned four devices as part of the Shared Infrastructure Remediation (SIR) project and CIP v5 transition efforts. The devices were appropriately brought into CIP scope as BES Cyber Assets (BCAs). Four out-of-band management interfaces for the devices were originally intended to be shut down and not used. As a result of RFC_URE3’s intent to not use these devices, RFC_URE3 did not include these four out-of-band management interfaces in the commissioning process for the four devices. These four out-of-band management interfaces became a compliance issue due to how the migration of the interfaces and network switches was conducted. Prior to the SIR project, some 7K network switches held both Electronic Security Perimeter (ESP) and non-ESP subnets. The purpose of the SIR project was to migrate physical network connections and ESP subnets off of 7K switches and to put all switches dedicated to RFC_URE3's critical infrastructure on 5K network switches. The four devices (and their four out-of-band management interfaces) were commissioned on an ESP subnet that lived on a 5K switch. However, while the four out-of-band management interfaces were routed through the 5K switch, their IP address was on a subnet that was not identified as an ESP and lived on a 7K switch. At the time, a temporary route was put in place between the critical infrastructure 5K switch and the 7K switch so the systems would continue to be connected to the network prior to completing the SIR project. More than seven months later, to complete the SIR project, the temporary links between 5K and 7K network switches needed to be severed so that only critical infrastructure traffic was routed through the 5K switches. As part of completing this severing task, the Networking & Telecommunications team was reviewing the VLAN configurations and discovered that the four out-of-band management interfaces for the devices were active and connected to the network through a 7K switch on a non-ESP subnet. The four out-of-band management interfaces were not supposed to be active nor connected to the network through a 7K switch on a non-ESP subnet. This noncompliance involves the management practice of information management. Information management is involved because RFC_URE3 did not have a control in place to verify that out-of-band management interfaces were inactive. This lack of a control is a root cause of this noncompliance. The duration of this issue was approximately seven months. | This issue posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The risk posed by not properly commissioning the four out-of-band management interfaces is that they could have vulnerabilities that allow a bad actor to get inside an ESP and compromise BCAs. That risk is minimized because RFC_URE3 had multiple protections related to the out-of-band management interfaces in place throughout the noncompliance that minimized the risk: a. The out-of-band management interfaces are all in the Physical Security Perimeter (PSP) and are protected from physical and logical access. b. Access to the PSP is approved by authorized personnel. c. Personnel with authorized access have completed CIP training and Personnel Risk Assessments. d. The devices connected to the out-of-band management interfaces were all tested to ensure that they did not adversely impact existing cyber security controls prior to being placed in the production environment. e. All other assets within the ESP have anti-virus and antimalware tools installed. ReliabilityFirst determined that the issue was appropriate for FFT treatment because it posed a moderate risk and because of RFC_URE3’s relevant compliance history with CIP-005 R1. No harm is known to have occurred. | To mitigate this issue, RFC_URE3: 1) severed the link between a 5K and a 7K switch, causing the four out-of-band management interfaces to go offline and become unreachable over the network. RFC_URE3’s action to replace its shared infrastructure configuration will prevent this issue from reoccurring. Replacing RFC_URE3’s shared infrastructure configuration eliminates the current architectural configuration that placed the out-of-band management interfaces on a non-ESP network. The new architectural configuration eliminates shared infrastructure and ensures that the out-of-band management interfaces reside on an ESP, without connectivity to non-ESP networks; 2) completed a Shared Infrastructure Remediation (SIR) project to eliminate shared infrastructure between critical systems inside an ESP and non-critical systems outside of an ESP. This project has significantly reduced the likelihood of a similar issue. The assets at issue in this noncompliance were connected via a shared network and this will not be possible moving forward; 3) brought back online the four Cyber Assets impacted in a designated ESP subnet; and 4) updated the commission task language to direct System Administrators to verify that all logical interfaces have been identified, including out-of-band interfaces, and to validate that connected interfaces are on the appropriate network depending on the host classification. These controls will prevent recurrence. RFC_URE3 will complete the following mitigation activities: 1) develop training material for the IT division on RFC_URE3's scope management process that will include information regarding identification and classification of out-of-band management interfaces and the associated protections required; and 2) deliver training to the IT division on RFC_URE3's scope management process that will include information regarding identification and classification of out-of-band management interfaces and the associated protections required.
2017-06-29 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2015014951 | CIP-005-3a | R4; R4.2, R4.4, R4.5 | During a Compliance Audit, SPP RE determined that SPPRE_URE1 had an issue of noncompliance with CIP-005-3a R4.2, R4.4, and R4.5. SPPRE_URE1 retained consultants to perform the required annual Cyber Vulnerability Assessment (CVA) in two consecutive years; however, the CVAs lacked sufficient detail to support that all required elements of the CVAs had been performed for all in-scope Cyber Assets per R4.2, R4.4, and R4.5. More specifically, the CVAs noted that certain steps were performed to satisfy R4.2, R4.4, and R4.5, but the CVAs did not identify which Cyber Assets were evaluated and they contained only summary statements that no issues were found. As a result, SPP RE requested the documentation SPPRE_URE1 provided the consultants to perform the CVAs to determine whether all in-scope Cyber Assets were evaluated and to corroborate the summary statements in the CVAs. Although SPPRE_URE1 attested that its consultants were provided the documentation required to perform the CVAs, per the consulting agreements, the consultants destroyed all documents used to conduct the CVAs upon completion of the CVAs, and SPPRE_URE1 failed to retain a copy of such documentation. As a result, SPP RE was unable to determine whether the CVAs addressed all required elements for all in-scope Cyber Assets per R4.2, R4.4, and R4.5. The duration of this instance of noncompliance was 738 days, beginning the day after the first insufficient CVA was required to address all of the requirements of CIP-005-3a R4, and ending the date SPPRE_URE1’s most recent CVA was completed, which addresses all of the requirements of CIP-005-3a R4. The root cause of this instance of noncompliance was a combination of lack of management oversight to ensure that the CVAs performed by SPPRE_URE1’s consultants contained sufficient detail to ensure full adherence to CIP-005-3a R4 and human error due to personnel not adhering to the evidence documentation retention requirement in SPPRE_URE1’s procedure. SPPRE_URE1 is no longer employing third parties to conduct CIP-related CVAs and therefore the working papers and related documentation are no longer covered under a data disposition agreement. Consequently, the data is retained by SPPRE_URE1 as working papers associated with the CVA as required by CIP-005-3a R5 requirements, which was not within the scope of the Compliance Audit, nor was a violation of said requirements identified herein. | This issue posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Noncompliance with CIP-005-3a R4 has the potential to affect the reliability of the BPS by presenting a risk of unauthorized access and exploitable vulnerabilities to Critical Cyber Assets and/or other Cyber Assets located within SPPRE_URE1’s Electronic Security Perimeter (ESP) without SPPRE_URE1’s knowledge. SPPRE_URE1 attested that its consultants were provided the documentation required to perform the CVAs; however, because the working papers and related documentation were not retained or made available to SPP RE, SPP RE was unable to verify that all required elements of the CVAs had been performed for all in-scope PACS Cyber Assets. Notwithstanding, SPPRE_URE1’s CVAs identified the vulnerability assessment process (R4.1) and all access points to the ESP (R4.3). SPPRE_URE1 attested that its consultants were provided the documentation required to perform the CVAs, and the CVAs indicated that certain steps were performed on Cyber Assets within the ESP per R4.2, R4.4, and R4.4, and that no issues were identified. Although SPP RE could not identify the specific Cyber Assets evaluated in the CVAs or corroborate the summary statements in the CVAs that no issues were identified, at a minimum, the CVAs demonstrate that multiple Cyber Assets had been evaluated. Additionally, SPPRE_URE1’s ESP was continuously monitored and protected by an intrusion prevention/detection system, which provided real-time log analysis, event alerting, and blocking of both internal and external malicious transmissions on Cyber Assets within the ESP. Cyber Assets with sensitive data were separated from the rest of the network to reduce the potential for unauthorized access of sensitive data. SPPRE_URE1 implemented additional protective measures to protect Cyber Assests inside the ESP and access points to the ESP, including permissions controlling access to network resources based on job functions, network and host based anti-malware systems, password and lockout policies, personnel physical and cyber access reviews and control processes. Access to Cyber Assets within the ESP was limited to only those individuals with authorized physical and/or electronic access rights. No harm is known to have occurred. | To mitigate this instance of noncompliance, SPPRE_URE1: 1) discontinued the use of third parties to conduct CIP-related CVAs, which eliminated working papers and related documentation associated with CVAs from being covered under a data disposition agreement with third parties; 2) internally performed a current CVA, which addresses all requirements of CIP-005-3a R4; and 3) retained documentation supporting the CVA as required by CIP-005-3a R5. SPP RE has verified the completion of all mitigation activity.
2017-06-29 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2015014952 | CIP-006-3c | R2; R2.2 | During a Compliance Audit, SPP RE determined that SPPRE_URE1 had an issue of noncompliance with CIP-006-3c R2.2 for not affording its Physical Access Control System (PACS) the protective measures specified in CIP-007-3a R8.2, R8.3, and R8.4. CIP-007-3a R8 (as made applicable by CIP-006-3c R2.2) requires SPPRE_URE1 to “perform a cyber vulnerability assessment (CVA) of all Cyber Assets within the Electronic Security Perimeter (ESP) at least annually,” which must include in part “a review to verify that only ports and services required for operation of the Cyber Assets within the ESP are enabled (R8.2); a review of controls for default accounts (R8.3); and documentation of the results of the assessment, and the execution status of that action plan (R8.4).” SPPRE_URE1 retained consultants to perform the required annual CVA in two consecutive years; however, the CVAs lacked sufficient detail to support that all required elements of the CVAs had been performed for all in-scope PACS Cyber Assets per CIP-007-3a R8.2, R8.3, and R8.4. More specifically, the CVAs noted that certain steps were performed to satisfy R8.2, R8.3, and R8.4, but the CVAs did not identify which Cyber Assets were evaluated and they contained only summary statements that no issues were found. As a result, SPP RE requested the documentation SPPRE_URE1 provided the consultants to perform the CVAs to determine whether all in-scope Cyber Assets were evaluated and to corroborate the summary statements in the CVAs. Although SPPRE_URE1 attested that its consultants were provided the documentation required to perform the CVAs, per the consulting agreements, the consultants destroyed all documents used to conduct the CVAs upon completion of the CVAs, and SPPRE_URE1 failed to retain a copy of such documentation. As a result, SPP RE was unable to determine whether the CVAs addressed all required elements for all in-scope PACS Cyber Assets per R8.2, R8.3, and R8.4. The duration of this instance of noncompliance was 738 days, beginning the day after the first insufficient CVA was required to address all of the protective requirements specified in CIP-006-3c R2.2, i.e., CIP-007-3a R8.2, R8.3, and R8.4, and ending the date SPPRE_URE1’s most recent CVA was completed, which addresses CIP-007-3a R8.2, R8.3, and R8.4. The root cause of this instance of noncompliance was a combination of lack of management oversight to ensure that the CVAs performed by SPPRE_URE1’s consultants contained sufficient detail to ensure full adherence to CIP-006-3c R2.2, i.e., CIP-007-a R8.2, R8.3, and R8.4, and human error due to personnel not adhering to the evidence documentation retention requirement in SPPRE_URE1’s procedure. SPPRE_URE1 is no longer employing third parties to conduct CIP related CVAs and therefore the working papers and related documentation are no longer covered under a data disposition agreement. Consequently, the data is retained by SPPRE_URE1 as working papers associated with the CVA as required by CIP-005-3a R5 requirements, which was not within the scope of the Compliance Audit, nor was a violation of said requirements identified herein. | This issue posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). A violation of CIP-006-3c R2.2 has the potential to affect the reliable operation of the BPS by providing the opportunity for undetected compromise of Critical Cyber Assets to occur. SPPRE_URE1 attested that its consultants were provided the documentation required to perform the CVAs; however, because the working papers and related documentation were not retained or made available to SPP RE, SPP RE was unable to verify that all required elements of the CVAs had been performed for all in-scope PACS Cyber Assets. Notwithstanding, SPPRE_URE1 protected its PACS from unauthorized physical access per CIP-006-3c R2.1. SPPRE_URE1 attested that its consultants were provided the documentation required to perform the CVAs, and the CVAs indicated that certain steps were performed on Cyber Assets within the ESP per CIP-007-3a R8.2, R8.3, and R8.4, and that no issues were identified. Although SPP RE could not identify the specific PACS Cyber Assets evaluated in the CVAs or corroborate the summary statements in the CVAs that no issues were identified, at a minimum, the CVAs demonstrate that multiple Cyber Assets had been evaluated. Additionally, SPPRE_URE1 implemented perimeter firewalls to the access points to the ESP. SPPRE_URE1’s ESP was continuously monitored and protected by an intrusion prevention/detection system, which provided real-time log analysis, event alerting, and blocking of both internal and external malicious transmissions on Cyber Assets within the ESP. Cyber Assets with sensitive data were separated from the rest of the network to reduce the potential for unauthorized access of sensitive data. SPPRE_URE1 implemented additional protective measures to protect Cyber Assests inside the ESP and access points to the ESP, including permissions controlling access to network resources based on job functions, network, and host based anti-malware systems, password and lockout policies, personnel physical and cyber access reviews and control processes. Access to Cyber Assets within the ESP was limited to only those individuals with authorized physical and/or electronic access rights. No harm is known to have occurred. | To mitigate this instance of noncompliance, SPPRE_URE1: 1) discontinued the use of third parties to conduct CIP-related CVAs, which eliminated working papers and related documentation associated with CVAs from being covered under a data disposition agreement with third parties; 2) internally performed a current CVA, which addresses all requirements of CIP-006-3c R2.2, i.e., CIP-007-3a R8; and 3) retained documentation supporting the CVA as required by CIP-005-3a R5. SPP RE has verified the completion of all mitigation activity.
2017-06-29 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2015014953 | CIP-007-3a | R8; R8.2, 8.3, 8.4 | During a Compliance Audit, SPP RE determined that SPPRE_URE1 had an issue of noncompliance with CIP-007-3a R8.2, R8.3, and R8.4. SPPRE_URE1 retained consultants to perform the required annual Cyber Vulnerability Assessment (CVA) in 2013 and 2014; however, the CVAs lacked sufficient detail to support that all required elements of the CVAs had been performed for all in-scope Cyber Assets per R8.2, R8.3, and R8.4. More specifically, the CVAs noted that certain steps were performed to satisfy R8.2, R8.3, and R8.4, but the CVAs did not identify which Cyber Assets were evaluated and they contained only summary statements that no issues were found. As a result, SPP RE requested the documentation SPPRE_URE1 provided the consultants to perform the CVAs to determine whether all in-scope Cyber Assets were evaluated and to corroborate the summary statements in the CVAs. Although SPPRE_URE1 attested that its consultants were provided the documentation required to perform the CVAs, per the consulting agreements, the consultants destroyed all documents used to conduct the CVAs upon completion of the CVAs, and SPPRE_URE1 failed to retain a copy of such documentation. As a result, SPP RE was unable to determine whether the CVAs addressed all required elements for all in-scope Cyber Assets per R8.2, R8.3, and R8.4. The duration of this instance of noncompliance was 738 days, beginning the day after the first insufficient CVA was required to address all of the requirements of CIP-007-3a R8, and ending the date SPPRE_URE1’s most recent CVA was completed, which addresses all of the requirements of CIP-007-3a R8. The root cause of this instance of noncompliance was a combination of lack of management oversight to ensure that the CVAs performed by SPPRE_URE1’s consultants contained sufficient detail to ensure full adherence to CIP-007-3a R8 and human error due to personnel not adhering to the evidence documentation retention requirement in SPPRE_URE1’s procedure. SPPRE_URE1 is no longer employing third parties to conduct CIP related CVAs and therefore the working papers and related documentation are no longer covered under a data disposition agreement. Consequently, the data is retained by SPPRE_URE1 as working papers associated with the CVA as required by CIP-005-3a R5 requirements, which was not within the scope of the Compliance Audit, nor was a violation of said requirements identified herein. | This issue posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Noncompliance with CIP-007-3a R8 has the potential to affect the reliability of the BPS by presenting a risk of unauthorized access and exploitable vulnerabilities to Critical Cyber Assets and/or other Cyber Assets located within SPPRE_URE1’s Electronic Security Perimeter (ESP) without SPPRE_URE1’s knowledge. SPPRE_URE1 attested that its consultants were provided the documentation required to perform the CVAs; however, because the working papers and related documentation were not retained or made available to SPP RE, SPP RE was unable to verify that all required elements of the CVAs had been performed for all in-scope PACS Cyber Assets. Notwithstanding, SPPRE_URE1’s CVAs identified the vulnerability assessment process (R8.1). SPPRE_URE1 attested that its consultants were provided the documentation required to perform the CVAs, and the CVAs indicated that certain steps were performed on Cyber Assets within the ESP per R8.2, R8.3, and R8.4, and that no issues were identified. Although SPP RE could not identify the specific Cyber Assets evaluated in the CVAs or corroborate the summary statements in the CVAs that no issues were identified, at a minimum, the CVAs demonstrate that multiple Cyber Assets had been evaluated. Additionally, SPPRE_URE1’s ESP was continuously monitored and protected by an intrusion prevention/detection system, which provided real-time log analysis, event alerting, and blocking of both internal and external malicious transmissions on Cyber Assets within the ESP. Cyber Assets with sensitive data were separated from the rest of the network to reduce the potential for unauthorized access of sensitive data. SPPRE_URE1 implemented additional protective measures to protect Cyber Assests inside the ESP and access points to the ESP, including permissions controlling access to network resources based on job functions, network and host based anti-malware systems, password and lockout policies, personnel physical and cyber access reviews and control processes. Access to Cyber Assets within the ESP was limited to only those individuals with authorized physical and/or electronic access rights. No harm is known to have occurred. | To mitigate this instance of noncompliance, SPPRE_URE1: 1) discontinued the use of third parties to conduct CIP-related CVAs, which eliminated working papers and related documentation associated with CVAs from being covered under a data disposition agreement with third parties; 2) internally performed a current CVA, which addresses all requirements of CIP-007-3a R8; and 3) retained documentation supporting the CVA as required by CIP-005-3a R5. SPP RE has verified the completion of all mitigation activity.
2017-05-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2016016291 | CIP-002-5.1 | R1 | RFC_URE1 submitted a Self-Report to ReliabilityFirst stating that as a it had an issue with CIP-002-5.1 R1. This noncompliance involves four assets, two of which were not on RFC_URE1’s Cyber Asset List, but were otherwise protected pursuant to the CIP Standards, and two of which were not on the Cyber Asset List and were not within a defined Electronic Security Perimeter (ESP). In preparation for CIP Version 5, RFC_URE1 began a project to implement two new servers for use as backup servers to route Inter-Control Center Communications Protocol (ICCP) data for generation setpoint control. For its primary ICCP, RFC_URE1 leased three lines, and the new servers were intended to act as backup in case all three leased lines became unavailable. RFC_URE1 learned that delivery of the new servers was delayed, so as a temporary alternative, RFC_URE1 used two existing non-CIP servers as backup. Although these servers were otherwise compliant with the CIP Standards (e.g., vulnerability scanning, patching, and password protections), they were not located within an ESP. RFC_URE1 intended this solution to be temporary, and planned on implementing the new servers, which would have been within an ESP, before the Version 5 deadline. However, the new servers were not delivered until after the deadline, and RFC_URE1 continued to use the non-CIP servers as temporary backup, but failed to include the temporary servers on its Cyber Asset List and failed to place the servers within an ESP. RFC_URE1 identified the noncompliance through a detective control as part of its project management process. As part of its after-action review, RFC_URE1 conducted a review to verify that all CIP assets were on its Cyber Asset List and identified two additional servers that should have been, but were not, on its Cyber Asset List. These servers were otherwise compliant with all CIP Standards, including being located within an ESP. The root cause of the first instance involving the temporary backup servers was a combination of equipment delay and lack of clear process to verify that assets are NERC compliant as necessary throughout the duration of new projects. The root cause of the second instance, which was identified in the after-action review, was a misclassification during the creation of a new ESP, and lack of verification processes associated with the creation of the ESP. These causes involve the management practice of asset and configuration management, which includes change control processes to ensure that the entity understands and accounts for the effects of changes to its environment. The duration of the noncompliance was approximately four months. | This issue posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. Regarding the backup servers not within an ESP, the potential risk is that a bad actor would compromise the servers and send inaccurate generation setpoints to RFC_URE1, which could have a negative impact on the BPS. However, this risk was reduced based on the following factors. First, in order to use these backup servers, the configuration is such as that the operator must first enable the servers as backup. This only occurs in three instances, thus limiting the opportunity for a compromise: (1) the ICCP system fails, which is unlikely; (2) all three lines fail, which is unlikely; or (3) for the brief time period each month where the backup server is enabled during drills to ensure the system is operational. Additionally, the servers had other protections in place (e.g., vulnerability scanning, patching, and password protections) that reduced the likelihood of compromise. Regarding the servers identified during the after-action review, the risk of not including an asset on a Cyber Asset List is that RFC_URE1 will not implement the required protections. However, for the two servers at issue, this was merely a documentation type of noncompliance because the assets were afforded all of the protections required by the CIP Standards, including being within a defined ESP. Additionally, regarding all four servers, RFC_URE1 self-identified the issue through a detective control, which limited the duration of any risk to the BPS. No harm is known to have occurred. | To mitigate this issue, RFC_URE1: 1) verified that it included all assets within the ESP on the asset list; 2) migrated production control of ICCP function from the temporary servers to the new servers within the ESP and implemented all cyber security controls on the servers; 3) added all four servers to its asset list; 4) updated its project reviews process to monitor for and notify the compliance department of CIP-related projects; and 5) developed a checklist for adding and removing assets in a High Impact area and communicated the checklist to all applicable employees.
2017-05-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2016016351 | CIP-010-2 | R1 | RFC_URE2 submitted a Self-Report stating that it had an issue of CIP-010-2 R1. While conducting a routine evidence review, RFC_URE2’s IT team identified that RFC_URE2 did not establish a baseline for four new BES Cyber Assets (BCAs). The four BCAs were all work stations in RFC_URE2’s backup control center (a tertiary center) that primarily performed the function of serving as a backup control center that could be activated if the primary control center went offline or had other technical issues. RFC_URE2 did not establish a baseline for these four new BCAs because RFC_URE2 improperly executed its cyber asset commissioning process. RFC_URE2 discovered the following issues for the four BCAs. For those BCAs: a. RFC_URE2 did not establish and maintain a baseline; b. RFC_URE2 did not authorize subsequent changes to the baseline; c. RFC_URE2 did not monitor subsequent changes to the baseline; d. RFC_URE2 did not implement physical port protection; and e. RFC_URE2 installed two patches on these BCAs without performing the proper cyber security testing on those patches. After discovering the four BCAs at issue, RFC_URE2 performed a comprehensive review of all of its BCAs to determine if there were any other BCAs that did not have established baselines. RFC_URE2’s IT team identified an additional BCA, another workstation, during this comprehensive review that had similar issues to the prior four BCAs. For this additional BCA, RFC_URE2 did not authorize changes to the baseline and RFC_URE2 installed five patches on this BCA without performing the proper cyber security testing on those patches. This issue involves the management practices of asset and configuration management and implementation. A primary root cause for this issue is that RFC_URE2 did not have an effective process or control in place to ensure that baselines and all other necessary compliance conditions were met when RFC_URE2 installed these five new BCAs. RFC_URE2 also had a breakdown in implementation because RFC_URE2 personnel did not understand due to ineffective communication that baselines needed to be established for these five BCAs. This breakdown is shown by the fact that RFC_URE2’s IT team installed the new BCAs following its existing processes and the IT team did not recognize that baselines for these BCAs needed to be established by the CIP Version 5 enforceable date. Another contributing cause was ineffective training because the RFC_URE2 team member responsible for authorizing changes to the BCAs did not obtain authorization for any of the changes to the baseline because he believed that the BCAs were still in a pre-production environment. This duration of the noncompliance was approximately 2 months. | This issue posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. By placing the five BCAs into RFC_URE2’s production environment before fully executing their commissioning process and recovery plan process, RFC_URE2 opened vulnerabilities into their protected network for more than two months before the issue was properly mitigated. This moderate potential risk is mitigated by the following factors. The BCAs involved in this issue were all workstations located in the RFC_URE2 backup control center (a tertiary center) meaning the workstations were not in use during the noncompliance which reduces the risk. Additionally, the BCAs were protected by a Physical Security Perimeter (PSP) and an Electronic Security Perimeter (ESP). The BCAs resided in a separate ESP than the primary and backup operations center assets which reduces risk to other BCAs in use during the period of noncompliance because if the BCAs at issue were compromised, they were segmented away from the primary and backup operations center assets in a separate ESP. The initial four BCAs at issue were discovered during a routine evidence review which indicates that RFC_URE2’s detective controls are working effectively. The RFC_URE2 employees installing the new BCAs were all trusted employees with current Personnel Risk Assessments and NERC CIP training which reduces the risk that the employees installing the BCAs were bad actors that would attempt to compromise the BCAs or use the BCAs to compromise other parts of RFC_URE2’s system. Lastly, ReliabilityFirst notes that the backup center was not activated during the period of noncompliance, which further reduces the risk because the BCAs at issue were never activated during the period of noncompliance. No harm is known to have occurred. | To mitigate this issue, RFC_URE2: 1) conducted a one-on-one discussion with the individual who applied changes without appropriate change management in place and had an incorrect assumption about the production status of the workstations to ensure acknowledgement of the issue and commitment to correction and improvement going forward; 2) conducted a review session with the entire staff on NERC CIP Requirements and support activities of NERC CIP Assets managed by the work group; 3) reinforced the requirement to use a pre-production checklist for all new NERC CIP Assets, even when not part of an IT project; 4) revised its procedure to clarify and enhance roles and responsibilities and sequence of events in the baseline establishment process; and 5) updated annual cyber security training to include more detail on the process for commissioning new assets. ReliabilityFirst has verified the completion of all mitigation activity.
2017-04-27 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2016015895 | CIP-005-5 | R2 | RFC_URE1 submitted a Self-Report stating that it had an issue with CIP-005-5 R2. Throughout the course of RFC_URE1’s CIP Version 5 transition, RFC_URE1 had engaged in ongoing collaborative conversations with each of its Regions. During one such conversation with MRO, MRO disclosed that it had interpreted CIP-005-5 R2 to include IT management systems such as patch and backup management. RFC_URE1 then vetted this interpretation with ReliabilityFirst, who then discussed it with the other Regions. ReliabilityFirst then reported back to RFC_URE1 that all Regions were in agreement with this interpretation. Prior to this, RFC_URE1 interpreted the Standard and Requirement such that it believed users, who initiate access from their workstations to IT management systems that interact with Cyber Assets within the Electronic Security Perimeter (ESP), did not engage in Interactive Remote Access. After discussions with the Regions described above, RFC_URE1 determined that its interpretation was not in alignment with the Standard and Requirement. As a result of this misinterpretation, RFC_URE1 was unable to implement the protections required for these types of Interactive Remote Access sessions, specifically, encryption and multi-factor authentication. RFC_URE1 then performed a thorough analysis of its systems that align with the approved interpretation. RFC_URE1 originally identified IT management systems as Intermediate Systems and multiple cyber assets. However, during technical design planning, two of the previously identified systems were removed from scope because one system had already been moved in the ESP, and another system did not allow interactive remote access as previously believed. Due to the uniqueness of its systems, the volume of assets, and complex technical solutions required to implement dual-factor authentication requirements on each system, RFC_URE1 stated that it would not be compliant with CIP-005-5 R2 by the CIP Version 5 enforceable date. The root cause of this noncompliance was a misinterpretation of the Standard and Requirement by RFC_URE1. This major contributing factor involves the management practice of workforce management, which focuses on providing training, education, and awareness to employees. The duration of the noncompliance was approximately one year. | This issue posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The systems at issue are used to manage both critical and non-critical systems. Therefore, if they were compromised, they could be used for unauthorized interactive access with RFC_URE1’s systems. The failure to have these systems protected by encryption and multi-factor authentication increases the risk that they could be compromised. This moderate potential risk is mitigated by the following factors. First, RFC_URE1 identified this issue through its awareness of the new CIP v5 Standards. Well before the effective date of those Standards, RFC_URE1 began working with the Regions to develop an effective mitigation strategy, which reduced the risk of any potential harm occurring. Second, RFC_URE1 has additional protections in place for these systems such as periodic security patching, access control, physical security, training of authorized personnel and malicious code prevention. These additional protections reduce the likelihood that (a) a compromise could occur, and (b) any potential compromise could have a serious effect on RFC_URE1’s operations. No harm is known to have occurred. ReliabilityFirst determined that the issue was appropriate for FFT treatment because it posed a moderate risk to the reliability of the bulk power system. | To mitigate this issue, RFC_URE1: 1) assessed IT management systems against the new guidance and the list of qualifying systems was identified; 2) assessed qualifying IT management systems from a security perspective and prioritized; 3) check-in with ReliabilityFirst; 4) determined a technical solution for dual-factor authentication of these systems and completed technical design; 5) updated the NERC CIP Scope Management Procedure to reflect the new interpretation, and added a procedure for identifying intermediate systems; and 6) check-in with ReliabilityFirst; RFC_URE1 will also: 7) complete build-out and cutover of Management Systems; and 9) update ReliabilityFirst upon completion.
2017-04-27 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE2016016025 | CIP-004-3a | R3; R3.2 | TRE_URE1 submitted a Self-Report stating that it had identified three instances of noncompliance with CIP-004-3a R3.2. Specifically, TRE_URE1 failed to update personnel risk assessments (PRAs) at least every seven years after the initial PRA for three contractors who had authorized unescorted physical access rights to Critical Cyber Assets (CCAs). Under the version of the TRE_URE1 non-employee PRA review and renewal process in effect at the time of this issue, TRE_URE1 personnel were required to run a report in November or December of the preceding year to identify all non-TRE_URE1 employee PRAs that would expire in the upcoming year. However, the TRE_URE1 personnel responsible for running this report did not do so as required under the existing process. As a result, TRE_URE1 failed to identify the PRA expiration for a single contractor. Accordingly, this contractor continued to retain unescorted physical access to CCAs. At the end of the following year, TRE_URE1 personnel again failed to run the required PRA report for the upcoming year. As a result of this failure, TRE_URE1 did not identify two additional contractor PRA expirations. Therefore, these two additional contractors also continued to retain unescorted physical access to CCAs after their respective PRAs had expired. TRE_URE1 initially revoked unescorted access rights for two of the three contractors at issue during a general review of existing access privileges. Subsequently, TRE_URE1 discovered the PRA issue during a review of its contractor PRA reports as part of TRE_URE1’s preparations to transition to the CIP Version 5 Standards. TRE_URE1 then contacted the third contractor’s employer in an effort to renew the expired PRA. In doing so, however, TRE_URE1 still did not revoke unescorted physical access rights to the final contractor at issue. Finally, TRE_URE1 did revoke this third contractors access rights approximately four months after discovering the issue. The root cause of this issue was an inadequate process to ensure that TRE_URE1 personnel either updated PRAs for contractors within the required seven-year time frame or revoked unescorted access rights to CCAs. In particular, TRE_URE1’s process for identifying the need for PRA renewals for non-TRE_URE1 employees relied on TRE_URE1 personnel remembering to run a single annual report. Given the infrequent nature of non-TRE_URE1 employee PRA expirations, this represented a non-repetitive and infrequent task that was likely to be missed without sufficient reminders or other prompts to ensure the task’s performance. The duration of the noncompliance was approximately two years and two months. | This issue posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failure to conduct a timely PRA review and renewal could have allowed individuals with malicious intent to have access to CCAs and damage them, resulting in possible disruptions or load losses. Moreover, in the current circumstances, the duration of this issue was long, with the three contractors at issue retaining authorized unescorted physical access rights to CCAs for between 294 and 587 days after their respective PRAs had expired. Further, two of the three contractors at issue physically accessed areas that contained CCAs on multiple occasions during the extended period of noncompliance. Finally, TRE_URE1 did not remove access rights for one contractor until four months after it discovered the PRA renewal issue. Balanced against this is the fact that the three contractors at issue did pass their initial background checks and worked for trusted, long-term vendors with TRE_URE1. Second, following the issue, TRE_URE1 subsequently renewed the PRAs and restored unescorted physical access to CCAs for two of the contractors at issue. With regard to the third contractor, that individual was no longer on an active contract, so no PRA renewal was required. Third, the three contractors possessed only physical access rights to CCAs and did not have corresponding electronic access rights. TRE_URE1 security staff visually and electronically monitored its CCAs 24 hours a day, 7 days a week. As such, TRE_URE1 could have likely detected any malicious attempt to physically damage CCAs. Fourth, TRE_URE1 possesses redundant systems for managing reliable operations of the Bulk Electric System (BES), which would have immediately assumed operation of the grid if any CCAs had been physically damaged. Finally, TRE_URE1 had a large number of personnel with authorized unescorted physical access to CCAs during the duration of the issue and had no additional issues regarding expiring PRAs during that time. No harm is known to have occurred. | To mitigate this issue, TRE_URE1 suspended access to all applicable CCAs for the three contractors. Additionally, TRE_URE1 will complete the following mitigation activities: 1) implement a new process in which automatic email alerts will be issued beginning in October of each year to multiple staff requesting a report from the applicable system of the contractor PRAs that will expire during the upcoming calendar year; 2) implement a new process in which automatic email alerts will continue to be issued to multiple staff requesting the PRA update process be completed with either a refreshed PRA or access suspension until such task is completed; and 3) create a new quarterly report and reconciliation control to ensure no PRA issues exist for the upcoming calendar quarter.
2017-03-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2016015598 | CIP-007-3a | R5.3.3 | WECC_URE1 submitted a Self-Report stating that it had an issue of CIP-007-3a R5.3.3. WECC_URE1 did not change passwords for 11 administrative and generic accounts at least annually per CIP-007-3a R5.3.3, on 111 devices. This issue started when WECC_URE1 failed to annually change passwords on the administrative accounts in scope on 111 devices and ended when WECC_URE1 changed the passwords on all the administrative accounts in scope, for a total of 186 days of noncompliance. The root cause of this issue was lack of communication when transferring compliance responsibilities from one individual to another. | This issue posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Specifically, WECC_URE1 failed to ensure each password on the administrative accounts in scope were changed at least annually, or more frequently based on risk. Failure to perform annual password changes could potentially provide malicious actors sufficient time to compromise account password and utilize the passwords to gain access to Critical Cyber Assets and cause harm to the bulk power system (BPS). The devices with the administrative accounts that did not have password changes were located within a Physical Security Perimeter, where access was limited to authorized personnel only. The administrative accounts were used to process backups, copy files, and send emails, or shutdown/reboot dumb devices. Passwords for these accounts are changed every time a person privileged to know the password leaves the department. WECC_URE1 had no personnel changes from the last date the passwords were changed. No harm is known to have occurred. WECC_URE1 does not have previous violations of this Standard and Requirement | To mitigate this issue, WECC_URE1: 1) Implemented a checklist of tasks, along with an automated preventive control in the form of an email notification that assigns a task to the employee responsible for changing administrative and generic account passwords on applicable devices; 2) Required an acknowledgement of the task completion for each notification; 3) Escalated to a Supervisor if the notification is not acknowledged; and 4) Continued escalation to WECC_URE1’s Vice President of Transmission, who is the CIP Senior Manager.
2017-03-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2016015600 | CIP-007-3a | R5.3.3 | WECC_URE2 submitted a Self-Report stating that it had an issue of CIP-007-3a R5.3.3. WECC_URE2 did not change passwords for 11 administrative and generic accounts at least annually per CIP-007-3a R5.3.3, on 111 devices. This issue started when WECC_URE2 failed to annually change passwords on the administrative accounts in scope on 111 devices and ended when WECC_URE2 changed the passwords on all the administrative accounts in scope, for a total of 186 days of noncompliance. The root cause of this issue was lack of communication when transferring compliance responsibilities from one individual to another. | This issue posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Specifically, WECC_URE2 failed to ensure each password on the administrative accounts in scope were changed at least annually, or more frequently based on risk. Failure to perform annual password changes could potentially provide malicious actors sufficient time to compromise account password and utilize the passwords to gain access to Critical Cyber Assets and cause harm to the bulk power system (BPS). The devices with the administrative accounts that did not have password changes were located within a Physical Security Perimeter, where access was limited to authorized personnel only. The administrative accounts were used to process backups, copy files, and send emails, or shutdown/reboot dumb devices. Passwords for these accounts are changed every time a person privileged to know the password leaves the department. WECC_URE2 had no personnel changes from the last date the passwords were changed. No harm is known to have occurred. WECC_URE2 does not have previous violations of this Standard and Requirement | To mitigate this issue, WECC_URE2: 1) Implemented a checklist of tasks, along with an automated preventive control in the form of an email notification that assigns a task to the employee responsible for changing administrative and generic account passwords on applicable devices; 2) Required an acknowledgement of the task completion for each notification; 3) Escalated to a Supervisor if the notification is not acknowledged; and 4) Continued escalation to WECC_URE2’s Vice President of Transmission, who is the CIP Senior Manager.
2017-03-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2015014749 | CIP-006-3a | R5 | During a Compliance Audit, WECC determined that WECC_URE3 had an issue of noncompliance with CIP-006-3 R5. WECC found that WECC_URE3 failed to ensure that unauthorized access attempts, as defined by WECC_URE3’s physical security plan, were reviewed immediately due to the failure of its Physical Access Control System (PACS) to alert in certain situations. Specifically, during the site tour at the Control Center, WECC found that WECC_URE3 was not monitoring or reviewing all unauthorized physical access attempt logs, based on the definition of unauthorized access attempt found in the physical security plan, and that this configuration and definition had been in place since implementation. The site physical security plan stated five or more unauthorized access attempts, such as repeatedly scanning an access badge, in less than a minute is an unauthorized access attempt and should trigger an alert. In contrast to the physical security plan, there was not an alert when the audit team, with an employee that did not have access to the Physical Security Perimeter (PSP) door, made five unauthorized physical access attempts with an access badge in less than a minute. WECC_URE3 personnel verbally confirmed this would be the case. The PACS logs were also directly observed by WECC and showed the unauthorized physical access attempts. Upon further investigation, WECC_URE3 discovered that its PACS were unable to alert on five unauthorized physical access attempts with an access badge in less than a minute. The scope of the issue included one PSP protecting 16 Critical Cyber Assets (CCAs) and 20 non-CCA devices, all within a single Electronic Security Perimeter (ESP). The root cause of this issue was the inability of the PACS system to alert on five unauthorized physical access attempts with an access badge in less than a minute. The PACS were unable to meet the criteria specified in the physical security plan, based on the definition of an unauthorized access attempt found in that plan. WECC determined that this issue began when the Standard became mandatory and enforceable on WECC_URE3, and ended when WECC_URE3 completed its mitigating activities, for a total of 1,651 days of noncompliance. | This issue posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE3 failed to enable the PACS at the Control Center to alert for unauthorized access attempts, which prevented WECC_URE3 from reviewing such alerts immediately in accordance with the procedures specified in the site physical security plan. Failing to alert or alarm on unauthorized access attempts for physical access could allow unauthorized access to the PSP to go unnoticed and unchecked, thereby potentially allowing malicious access to cyber assets. However, WECC_URE3 has deployed a defense in depth strategy with layered and controlled security. Although the exterior of the access points are not monitored via closed circuit television (CCTV), there are cameras monitoring several access points on the interior of the Control Center. No harm is known to have occurred. WECC determined that the issue was appropriate for FFT treatment because it was a moderate risk issue without relevant compliance history. | To mitigate this issue, WECC_URE3 updated the physical security plan to reflect the fact that the PACS system does not have the technical capability to alert for five unauthorized physical access attempts with an access badge in less than a minute, and removed this language from the latest version of the physical security plan. Despite this change, WECC_URE3's program continued to state that, for PSPs, “Monitoring of all access points is satisfied by either human observation and/or alarm systems that alert key personnel upon activation.”
2017-03-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2015014750 | CIP-007-3a | R6 | During a Compliance Audit, WECC determined that WECC_URE3 had an issue of noncompliance with CIP-007-3a R6. WECC_URE3 failed to implement automated tools or organizational process controls to monitor system events for eight CCAs. Specifically, eight CCAs failed to produce logs, due to a configuration issue on the devices. The root caause was this configuration issue. WECC determined that this issue began on the last recorded log entry date for these devices and ended when WECC_URE3 configured, installed, and deployed the devices to log according to the requirements, for a total 170 days of noncompliance. | This issue posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE3 failed to implement automated tools or organizational process controls to monitor system events for eight CCAs. Failing to monitor the system events of CCAs could allow adversarial threats to compromise an organization’s operational infrastructure, affecting the reliability of the BPS. However, WECC_URE3 had compensating controls in place to reduce the risk to the BPS. Specifically, WECC_URE3 implemented a defense-in-depth architecture of physical security controls that restricts physical unauthorized access to the affected assets and perimeter logical security, in the form of filtered discretionary access control rules. No harm is known to have occurred. WECC determined that the issue was appropriate for FFT treatment because it was a moderate risk issue without relevant compliance history. | To mitigate this issue, WECC_URE3: 1) properly configured devices with appropriate settings to generate logs, maintain logs, and subsequently provide the ability to review logs that are generated and maintained according to the Reliability Standards; 2) trained authorizing personnel on the updated procedures; and 3) updated the installation procedures to include configuring logging settings for all devices within the Electronic Security Perimeter (ESP).
2017-03-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2015014751 | CIP-007-3a | R8 | During a Compliance Audit, WECC determined that WECC_URE3 had an issue of noncompliance with CIP-007-3a R8. Specifically, WECC_URE3 failed to perform a Cyber Vulnerability Assessment (CVA) for six Cyber Assets, including five CCAs and one Electronic Access Control and Monitoring (EACM) device. The root cause of this issue was WECC_URE3’s CVA Standard Operating Procedure (SOP), which did not have a mechanism to compare scans to devices from the inventory list. WECC determined that this issue began the date of the last recorded CVA for the devices in scope and ended when WECC_URE3 performed the CVA on the applicable devices, for a total 193 days of noncompliance. | This issue posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE3 failed to perform a CVA on six Cyber Assets. Failing to perform a CVA on CCAs and EACM devices could pose a significant risk to WECC_URE3’s operational environment, if no effort to identity and mitigate potential vulnerabilities to the infrastructure occurs. However, WECC_URE3 had compensating controls in place to reduce the risk to the BPS. Specifically, WECC_URE3 implemented a defense-in-depth architecture of physical security controls that restricts physical unauthorized access to the affected assets and perimeter logical security, in the form of filtered discretionary access control rules. No harm is known to have occurred. WECC determined that the issue was appropriate for FFT treatment because it was a moderate risk issue without relevant compliance history. | To mitigate this issue, WECC_URE3: 1) performed the CVA on the applicable devices; 2) reviewed and updated the CVA SOP to include steps for developing a list of devices from the inventory to use as a checklist against the scans and/or account checks during the CVA; 3) tested the new procedure steps of developing a list and checking it against the scans; and 4) reviewed the new procedure with the IT Security Personnel.
2017-03-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2015014759 | CIP-007-3a | R2 | During a Compliance Audit, WECC determined that WECC_URE3 had an issue of noncompliance with CIP-007-3a R2. Specifically, WECC_URE3 failed to establish, document, and implement a process to ensure that only those ports and services required for normal and emergency operations are enabled for four Cyber Assets. The root cause of this issue was that the less than adequate process for pre-deployment testing of the ports and services for devices. WECC determined that this issue began on the earliest date for these devices that only the ports and services required for normal and emergency operations were enabled, and ended when WECC_URE3 performed a ports and services scan to compare with the baseline, for a total 332 days of noncompliance. | This issue posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE3 failed to establish, document, and implement a process to ensure that only those ports and services required for normal and emergency operations are enabled for Cyber Assets. Failing to enable only ports and services required for normal and emergency operations could allow unauthorized individuals to gain unauthorized access to the devices in scope. However, WECC_URE3 had controls in place to reduce the risk to the BPS. Specifically, WECC_URE3 implemented an alarm that notifies administrators if these Cyber Assets go offline or if there is an outage of these Cyber Assets. No harm is known to have occurred. WECC determined that the issue was appropriate for FFT treatment because it was a moderate risk issue without relevant compliance history. | To mitigate this issue, WECC_URE3: 1) completed a review of the Testing Procedure to verify that the procedure incorporates the pre-deployment testing of the ports and services for devices; 2) trained personnel on reviewed procedure; and 3) performed ports and services scan to compare with the baseline.
2017-01-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2015014593 | CIP-003-1 | R5 | RFC_URE1 submitted a Self-Report to ReliabilityFirst stating that it was in violation of CIP-003-1 R5. While migrating two databases, which contained Critical Cyber Asset Information, from a storage location that was being retired by RFC_URE1, RFC_URE1 discovered that access to these two databases was not managed in accordance with RFC_URE1’s Information Protection Program. These two databases contained 18 documents that included CIP Sensitive or CIP Restricted Information. Specifically, these documents consisted of operational procedures for troubleshooting and/or administering the Energy Management System (“EMS”) or Generation Management System (“GMS”) and related equipment. RFC_URE1 determined that 218 personnel had access to this information. All of those people had current Personnel Risk Assessments (“PRAs”), and 210 of them had completed required CIP training. The root cause of this noncompliance was the fact that these databases, which had been in place prior to the NERC CIP Standards becoming enforceable, were not set up as CIP assets in RFC_URE1’s Database. This contributing factor involves the management practices of asset and configuration management, which includes establishing assets and configuration items inventory, information management, which includes managing information item confidentiality and privacy, and workforce management, which includes providing training, education, and awareness to employees. The duration of the noncompliance was approximately 4-1/2 years. | This issue posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the fact that the information at risk related to the administration of the EMS and GMS systems. Therefore, if an unauthorized person had accessed this information, the person could have affected these systems, which are essential to BPS reliability. The risk posed by this issue was mitigated by the following factors. First, although 218 people had access to this information, all of them had current PRAs and 210 of them had completed CIP training, reducing the risk that anyone with access to this information would use it nefariously. Second, the exposed documents did not contain any information that would assist an unauthorized person to access the EMS or GMS. Therefore, an unauthorized person would first be required to obtain individual security credentials before accessing the EMS or GMS to enact the procedures. No harm is known to have occurred. | To mitigate this issue, RFC_URE1: 1) completed the retirement of previous databases or moved necessary CIP-protected information and documents to an appropriately controlled CIP database; and 2) added the business area location and its associated electronic databases to the audit scope for the next annual CIP Information Protection Audit. ReliabilityFirst has verified the completion of all mitigation activity.
2017-01-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2015015124 | CIP-004-3a | R4 | RFC_URE1 submitted a Self-Report to ReliabilityFirst stating that it was in violation of CIP-004-3a R4. An employee of RFC_URE1 voluntarily left the company. During its annual review of CIP training, RFC_URE1 discovered that although it took steps to remove his authorized cyber and unescorted physical access to Critical Cyber Assets (CCAs) within seven calendar days of his departure, RFC_URE1 completed final revocation of his access privileges 16 days late. The root cause of this noncompliance was RFC_URE1’s lack of adequate internal controls surrounding its employee separation process. RFC_URE1 relied on a manual process pursuant to which the departing employee’s manager/supervisor would process the access removal requests, with no independent verification performed. This contributing factor involves the management practices of verification and reliability quality management, which includes maintaining a system for identifying and deploying internal controls for grid reliability. The duration of the noncompliance was approximately 15 days. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, RFC_URE1 took steps to remove the employee’s access to corporate facilities and networks within seven calendar days following his departure, rendering the remaining access privileges to certain Cyber Assets less likely to be exploited. Second, the employee had a valid Personnel Risk Assessment, reducing the risk that he would attempt to exploit any remaining access privileges. ReliabilityFirst also notes that through reviews of relevant access logs, RFC_URE1 determined that the employee did not access any Critical Cyber Assets after his departure date. No harm is known to have occurred. | To mitigate this issue, RFC_URE1: 1) removed the employee’s remaining access privileges to CCAs; 2) incorporated an internal control into the separation process for an independent group to ensure that responsible Managers (and/or clerical personnel) have processed the forms necessary to initiate the CIP access removal process for certain employees and Contractors, when required; and 3) ensured the new internal control is compatible with access processes and procedures RFC_URE1 is developing and implementing to comply with CIP-004 R4 and R5. ReliabilityFirst has verified the completion of all mitigation activity.
2017-01-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2015014594 | CIP-003-1 | R5 | RFC_URE2 submitted a Self-Report to ReliabilityFirst stating that it was in violation of CIP-003-1 R5. While migrating two databases, which contained Critical Cyber Asset Information, from a storage location that was being retired by RFC_URE2, RFC_URE2 discovered that access to these two databases was not managed in accordance with RFC_URE2’s Information Protection Program. These two databases contained 18 documents that included CIP Sensitive or CIP Restricted Information. Specifically, these documents consisted of operational procedures for troubleshooting and/or administering the Energy Management System (“EMS”) or Generation Management System (“GMS”) and related equipment. RFC_URE2 determined that 218 personnel had access to this information. All of those people had current Personnel Risk Assessments (“PRAs”), and 210 of them had completed required CIP training. The root cause of this noncompliance was the fact that these databases, which had been in place prior to the NERC CIP Standards becoming enforceable, were not set up as CIP assets in RFC_URE2’s Database. This contributing factor involves the management practices of asset and configuration management, which includes establishing assets and configuration items inventory, information management, which includes managing information item confidentiality and privacy, and workforce management, which includes providing training, education, and awareness to employees. The duration of the noncompliance was approximately 4-1/2 years. | This issue posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the fact that the information at risk related to the administration of the EMS and GMS systems. Therefore, if an unauthorized person had accessed this information, the person could have affected these systems, which are essential to BPS reliability. The risk posed by this issue was mitigated by the following factors. First, although 218 people had access to this information, all of them had current PRAs and 210 of them had completed CIP training, reducing the risk that anyone with access to this information would use it nefariously. Second, the exposed documents did not contain any information that would assist an unauthorized person to access the EMS or GMS. Therefore, an unauthorized person would first be required to obtain individual security credentials before accessing the EMS or GMS to enact the procedures. No harm is known to have occurred. | To mitigate this issue, RFC_URE2: 1) completed the retirement of previous databases or moved necessary CIP-protected information and documents to an appropriately controlled CIP database; and 2) added the business area location and its associated electronic databases to the audit scope for the next annual CIP Information Protection Audit. ReliabilityFirst has verified the completion of all mitigation activity.
2017-01-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2015015125 | CIP-004-3a | R4 | RFC_URE2 submitted a Self-Report to ReliabilityFirst stating that it was in violation of CIP-004-3a R4. During its annual review of CIP training, RFC_URE2 discovered that it had not removed all authorized cyber and unescorted physical access to Critical Cyber Assets granted to two employees and one contractor within seven calendar days following their voluntary departure from RFC_URE2. However, RFC_URE2 had taken steps to remove all three individuals’ access to corporate facilities and networks within seven calendar days following their departures. Employee #1, RFC_URE2 revoked the remaining access privileges 16 days late. Employee #2, RFC_URE2 revoked the remaining access privileges 22 days late. RFC_URE2 revoked the remaining access privileges for the contractor 44 days late. The root cause of this noncompliance was RFC_URE2’s lack of adequate internal controls surrounding its employee and contractor separation process. RFC_URE2 relied on a manual process pursuant to which the departing employee’s manager/supervisor would process the access removal requests, with no independent verification performed. This contributing factor involves the management practices of verification and reliability quality management, which includes maintaining a system for identifying and deploying internal controls for grid reliability. The duration of the noncompliance was approximately two months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, RFC_URE2 took steps to remove the employees’ and contractor’s access to corporate facilities and networks within seven calendar days following their departures, rendering the remaining access privileges to certain Cyber Assets less likely to be exploited. Second, the employees and the contractor each had a valid personnel risk assessment, reducing the risk that any of them would attempt to exploit any remaining access privileges. ReliabilityFirst also notes that through reviews of relevant access logs, RFC_URE2 determined that none of these individuals accessed any Critical Cyber Assets (CCAs) after their departure dates. No harm is known to have occurred. | To mitigate this issue, RFC_URE2: 1) removed remaining access privileges to CCAs; 2) incorporated an internal control into the separation process for an independent group to ensure that responsible Managers (and/or clerical personnel) have processed the forms necessary to initiate the CIP access removal process for certain RFC_URE2 employees and Contractors, when required. RFC_URE2 also ensured the new internal control is compatible with access processes and procedures RFC_URE2 is developing and implementing to comply with CIP-004 R4 and R5; 3) conducted a meeting with all Transmission personnel responsible for contractors to review the requirements and walk through the checklist to satisfy the documentation and the spirit of CIP Access Standard Requirements. The Director sent an e-mail to Transmission Personnel responsible for contractors to emphasize their responsibilities for ensuring contractors meet CIP access requirements. ReliabilityFirst has verified the completion of all mitigation activity.
2017-01-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2014014418 | CIP-006-3c | R1 | RFC_URE2 submitted a Self-Report to ReliabilityFirst stating that it was in violation of CIP-006-3c R1. Two contractors entered a substation Physical Security Perimeter (PSP) with the assistance of a crew working on-site at the substation, and RFC_URE2 did not log their access in accordance with the RFC_URE2 visitor control program. The contractors were intermittently escorted while they were in the PSP for approximately 45 minutes, when a supervisor entered the PSP and ascertained that the contractors did not have authorized access. The supervisor immediately escorted the contractors out of the PSP and notified his manager and the physical security department. The root cause of this noncompliance was the fact that the authorized employees incorrectly assumed that the contractors had access to the PSP and they did not ensure that every employee and contractor independently used the card reader to badge into the PSP as the group entered the relay house. This contributing factor involves the management practices of workforce management, which includes providing training, education, and awareness to employees, and external interdependencies, which includes managing risks due to external interdependencies. The duration of the noncompliance was approximately 45 minutes. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, although the contractors entered the PSP, they did not physically or logically access any Critical Cyber Assets at the substation. Second, the contractors were intermittently monitored while they were within the PSP. Third, the contractors all had valid personnel risk assessments (PRAs) in effect and were authorized to be working in the substation. Fourth, RFC_URE2 identified and corrected the problem in a relatively short period of time. No harm is known to have occurred. | To mitigate this issue, RFC_URE2: 1) promptly escorted the contractors from the PSP when the issue was identified; 2) counseled the substation contractors and employees assigned to the substation on the proper method of accessing a restricted area, proper use of keycards, and visitor access requirements; and 3) conducted a CIP access training during a contractor stand-down meeting for all contractors assigned to the site. ReliabilityFirst has verified the completion of all mitigation activity.
2017-01-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2015015110 | CIP-006-3c | R1 | RFC_URE2 submitted a Self-Report to ReliabilityFirst stating that it was in violation of CIP-006-3c R1. Two corporate security personnel identified six visitor trainees who were not continuously escorted while in a Physical Security Perimeter (PSP). The trainees were in a training room completing their CIP qualification and badging requirements, and the escort stood at the doorway, but failed to maintain continuous visual contact with them. Upon discovering the issue, the security personnel immediately escorted the trainees out of the PSP. The root cause of this noncompliance was the fact that the escort did not adequately understand the requirements for continually escorting visitors, which are contained in RFC_URE2’s Visitor Policy. This contributing factor involves the management practice of workforce management, which includes providing training, education, and awareness to employees. The duration of the noncompliance was approximately one day. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the trainees were present in the PSP to complete their CIP qualification and badging requirements. Second, all of the trainees were subsequently granted unescorted privileges. Third, the trainees were in a training environment, reducing the likelihood of any harm occurring. No harm is known to have occurred. | To mitigate this issue, RFC_URE2: 1) escorted six trainees out of the PSP; 2) reviewed the event and discussed the correct procedures for escorting visitors with the Training staff; 3) completed access process and all six trainees were granted unescorted access to the PSP; and 4) established an internal escort policy goal for escorting trainees who are not fully CIP qualified to assign one escort to each trainee. ReliabilityFirst has verified the completion of all mitigation activity.
2017-01-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2015015056 | CIP-007-3a | R2 | RFC_URE2 submitted a Self-Report to ReliabilityFirst stating that it was in violation of CIP-007-3a R2. During its annual cyber security vulnerability assessment, RFC_URE2 identified one open port on each of two Critical Cyber Assets (CCAs), which should have been disabled. RFC_URE2 also identified eight different CCAs with applicable Production Ports Service Baseline (PPSB) documents that were not adequately documented as required by RFC_URE2 procedures. The root cause of this noncompliance was the fact that, to improve the effectiveness and efficiency of the program, RFC_URE2 shifted the performance of most ports and services activities from corporate personnel to the asset owners at the specific business units. Due to the business unit personnel’s lack of understanding of the new procedures, the ports were not properly configured and the documentation was not properly updated. This contributing factor involves the management practice of workforce management, which includes providing training, education, and awareness to employees. The duration of the noncompliance was approximately ten months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. First, the devices at issue did not have the ability to impact any BPS assets. Second, the devices at issue were on a protected energy management system (EMS) demilitarized zone (DMZ) network. Accordingly, firewall rules prevented unauthorized access to the EMS DMZ network from either the RFC_URE2 corporate network or the other external networks. Third, RFC_URE2’s multi-layered security strategy for isolation of networks further mitigated the risk because the devices at issue were provided with (a) perimeter defenses; (b) network defenses; and (c) host defenses. Additionally, these devices were also physically located within a Physical Security Perimeter (PSP), which provides additional layers of security. No harm is known to have occurred. | To mitigate this issue, RFC_URE2: 1) completed a change control process to disable the two inappropriately open ports; 2) updated applicable PPSBs to properly document the eight ports (with inadequate documentation); 3) reviewed with the Network team the importance of verifying removal of configuration line items not necessary that result in closing unnecessary ports; 4) reviewed with the Server team the importance of verifying the PPSB; and 5) identified the CIP Cyber Assets per CIP Version 5 Standards and brought those CIP Cyber Assets into compliance with CIP Version 5 Standards in accordance with the NERC Implementation Plan. ReliabilityFirst has verified the completion of all mitigation activity.
2017-01-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC2015014726 | CIP-005-3a | R1 | RFC_URE3 submitted a Self-Report to ReliabilityFirst stating that it had an issue of CIP-005-3a R1. During a review of its network, an RFC_URE3 network analyst discovered that two servers, which were designated as Critical Cyber Assets, had their network switch ports incorrectly configured on a virtual local area network (VLAN), which was outside of the relevant Electronic Security Perimeter (ESP). (These two servers ran the Inter-Control Center Communications Protocol.) Originally, the VLAN on which these two servers were configured was within the ESP. However, during RFC_URE3’s transition to a new control center, routing for the VLAN that contained the two affected servers was moved outside the ESP. The root cause of this issue was the fact that RFC_URE3 completed the build documents for this project months prior to the completion of the work and lacked effective tools for identifying misconfigurations of its virtual networks. This major contributing factor involves the management practice of implementation, which focuses on ensuring that assets are implemented or modified in a manner that does not compromise grid security. The duration of the noncompliance was approximately 13 months. | This issue posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. This misconfiguration of the VLAN for these two servers created the possibility of unauthorized internal server-to-server communication. This risk was mitigated by the following factors. First, other than this VLAN misconfiguration, these two servers were afforded all other protections called for by the Reliability Standards because RFC_URE3 classified these servers as Critical Cyber Assets. Upon their commissioning, RFC_URE3 placed them into the ESP database and tracked them under its CIP compliance program. Moreover, RFC_URE3 has protected these servers through the completion of system information and event management logging, security scans, and an automated program for security and threat detection. Authorized changes on these two servers have also had proper CIP test plans and security controls testing. Second, the network access and virtual private network prevented unauthorized interactive remote access into these two servers. Third, these two servers sit behind four firewalls that are configured to restrict traffic through the deny-by-default functionality at the port granularity between RFC_URE3 and its members. No harm is known to have occurred. | To mitigate this issue, RFC_URE3: 1) moved these two servers within the ESP and confirmed that electronic access controls were working; 2) developed a new Policy Report that detects this type of misconfiguration in the future; 3) ran the Policy Report and confirm that this type of misconfiguration does not exist on other RFC_URE3 ESP subnetworks; 4) removed outside VLANs for all ESP subnetworks from the downstream layer 2 switches. This action reduces the risk of a system being assigned a VLAN outside the ESP by not having outside VLANs available on switches; 5) began a daily review of Policy Report as a misconfiguration detection method; and, 6) reduced complexity of firewall and switch network configurations thereby ensuring that ESP subnetwork ranges can only exist after all required protections are established.
2017-01-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC2015014803 | CIP-005-3a | R1 | RFC_URE3 submitted a Self-Report to ReliabilityFirst stating that it had an issue of CIP-005-3a R1. RFC_URE3 replaced its then-current central log repository and system of record with a new system which allows RFC_URE3 to centrally collect, analyze, alert, and archive log data from RFC_URE3 IT systems and infrastructure. At the time it implemented the new system, RFC_URE3 designated the Event Receivers as Cyber Assets used in the electronic access control and monitoring of the Electronic Security Perimeter(s) (EACMs) and afforded these devices with the required protective measures set forth in CIP-005-3 R1.5. However, during an annual review of the backup process, RFC_URE3 discovered that the backup and restoration plans associated with these devices were inadequate in that they did not provide adequate steps to recover and backup these devices. Moreover, RFC_URE3 believed that additional devices, originally not designated as Cyber Assets, met the definition of EACMs and should be afforded the corresponding protective measures. The root cause of this issue was the fact that RFC_URE3 did not tailor its backup and recovery plan for EACMs to account for the new devices. Additionally RFC_URE3 failed to timely assess whether these new devices were EACMs due to RFC_URE3’s phased implementation of the new system. This major contributing factor involves the management practice of implementation, which focuses on ensuring that a registered entity implements or modifies an asset in a manner that does not compromise grid reliability or resilience. The duration of the noncompliance was approximately two years. | This issue posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) based on the following factors. The risk posed by this issue is that if a security event occurred, RFC_URE3 would be at risk of not being able to quickly recover the associated logs to identify potential issues caused by the event. This risk was mitigated by the following factors. First, the devices at issue perform local backups daily, which RFC_URE3 saves monthly. Therefore, if the system needed to be recovered, RFC_URE3 could have utilized the monthly saved backups. Second, while these new devices are an important part of RFC_URE3’s security information and event management system (SIEM), they are not essential to running the BPS. Therefore, their loss would likely not cause a loss of generation, load, or energy management system visibility. Third, the only situation where the lack of an adequate restoration plan would have any impact would have been if an event had occurred and the RFC_URE3 personnel with institutional knowledge required to run the SIEM from local backups were not present. The low likelihood of this particular confluence of events occurring mitigates the potential risk of this issue. No harm is known to have occurred. | To mitigate this issue, RFC_URE3: 1) revised the existing Checkpoint Firewall Backup and Restoration plan to include instructions regarding SIEM, including all devices owned by the Cyber Security Department; 2) converted the updated restoration plan into controlled documents, which require an additional level of annual review that will aid in ensuring consistency and accuracy; 3) classified all remaining components of the new system as EACMs; and, 4) revised its Identification of Critical Cyber Asset Procedure to allow for on-demand identifications and designations of Cyber Assets rather than being limited to an annual identification process.
2016-12-29 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2016016356 | CIP-007-6 | R5 | FRCC_URE1 submitted a Self-Report stating that it was in violation of CIP-007-6 R5. FRCC_URE1 failed to technically or procedurally enforce password parameters for the required password length (R5.5.2), minimum password complexity (R5.5.2); or change known default passwords (R5.4) for accounts on relay and RTU BES Cyber Assets (BCAs). The BCAs came into scope on July 1, 2016 as newly identified medium impact BCAs under the new Standard. The process for on-boarding these devices as BCAs prior to the effective date of the Standard included changing all the default or existing passwords for all accounts on the devices to passwords that meet the version 5 requirements. FRCC_URE1 failed to properly identify the correct password configurations to be used when making the required changes or verify changes had been completed. FRCC_URE1 performed a root cause analysis and determined that the root causes for this potential noncompliance were the following: • The interim password standard was not completely V5 compliant. • The RTU devices were not included in the interim password standard – no written guidelines. • The process for changing passwords did not contain a verification step, which would have captured the identified deficiencies. • The implementation of the password changes was not thoroughly tracked, and if so, would have ensured that all steps in the process were completed for each device. | This issue posed a moderate risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). Failure to establish proper password parameters or change default passwords could result in the misuse and/or degradation of the RTUs. This could cause the loss of monitoring capability, the loss of the ability to remotely control equipment, and/or the miss-use of equipment at the substation. Additionally, the misuse and/or degradation of a relay BCAs could result in a loss of relay protection or a misoperation, which could potentially take a line out of service. The risk was reduced because physical security operational and procedural controls were in place to restrict physical access at all substations. Furthermore, there is no External Routable Connectivity to any of the substations and controls were in place to mitigate the ability to access the BCAs to a limited set of trusted team members who have completed NERC cyber security training, and have an active Personnel Risk Assessment (PRA). In addition, all the relay BCAs have primary and secondary level accounts. The primary accounts are read-only accounts with no operational functionality. The secondary accounts have operational functionality, but access cannot be achieved until first accessing the primary-level account. Both primary and secondary passwords are maintained in a password management solution which requires a separate two-factor authentication. Other than the small number of default account passwords, all other passwords had complexity and lengths that were close to the level of protection that would have been provided by version 5 compliant passwords. No harm is known to have occurred. | To mitigate this issue, FRCC_URE1: 1) added a field, as a preventive control, to substation’s asset management tool to track the implementation and use of the password management tool; and 2) changed identified non-compliant passwords to a compliant password configuration; and 3) reviewed and revised, as a preventive control, NERC CIP Desk Level Pprocedures (DLPs) for substation operation personnel and associated Cyber Security Controls Verification Checklist to ensure that account passwords meet the requirements of CIP-007 R5 consistent with device capability and that appropriate verification controls are in place. Communicated to and trained affected personnel on the revised DLP. To mitigate this issue, FRCC_URE1 will: 1) determine extent of condition by reviewing of all account passwords on medium impact substation devices to ensure that all account passwords are compliant with CIP-007 R5 requirements per device capability. Change all non-compliant passwords and report additional occurrences to FRCC; and 2) verify and ensure, as a preventative control, that all the passwords have been onboarded into the password management tool and that all the passwords have been changed via the password management tool per device capability for all account passwords on medium impact substation devices.
2016-12-29 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2014014109 | CIP-006-3c | R2 | MRO_URE1 stated that it had an issue of CIP-006-3c R2 because it had not provided the protections of CIP-003-3 R6, CIP-004-3a R4, CIP-006-3c R2, CIP-007-3 R2, CIP-007-3 R3, CIP-007-3 R5, and CIP-007-3 R6. MRO_URE1 stated that it had an issue of CIP-006-3c R2.1 because physical access control panels were located in a Physical Security Perimeter (PSP) that was behind a door that was not protected from unauthorized access as required. MRO_URE1 stated that it had not provided the protections of CIP-003-3 R6 because it did not follow the established Change Management process when it replaced the Physical Access Controls System (PACS) panel at its backup control center and two PACS door controllers at its primary control center. MRO_URE1 stated that it failed to provide the protections of CIP-004-3a R4 and CIP-007-3 R5 when it did not maintain an accurate and complete list of individuals with PACS system non-administrator level access during quarterly reviews (only reviewing accounts with admin level access). MRO_URE1 stated that it did not follow CIP-007-3 R2 because four PACS controllers each allowed two ports to remain open; this constituted noncompliance because MRO_URE1 had not obtained a TFE. MRO_URE1 stated that it had a CIP-007-3 R3 issue because it did not implement its security patch management program for a hypervisor that was missing a security patch. MRO_URE1 stated that it did not follow CIP-007-3 R5 because it did not manage a shared account access to the PACS using a "need-to-know" process. MRO_URE1 stated that it did not follow CIP-007-3 R6 because it did not review PACS SQL Server "logs of system events related to cyber security." While each of the issues had its own distinct cause, more generally, these issues were caused by a lack of training and formalized processes. The CIP-006-3c R2.1 issue was caused by a mechanical failure on one of the interior vault doors that caused the noncompliance for 14 days. The CIP-003-3 R6 issue was caused due to a lack of training and awareness in MRO_URE1's Security Department staff. The CIP-004-3a and CIP-007-3 R5 issue was caused by a failure to appreciate the differences in the PACS user access design between the old system and the new system. The CIP-007-3 R2 issue was caused due to a lack of awareness which led to MRO_URE1 not obtaining a TFE. The CIP-007-3 R3 issue was caused by a lack of internal procedures to fully integrate the hypervisor. The CIP-007-3 R5 issue was due to a lack of training that led to the System Administrator not knowing how to formally request, authorize, and document, shared account usage information. The CIP-007-3 R6 was caused by an incorrect assumption that the database server logs were automatically logging to the Operating System Event Log which does get reviewed. The noncompliance began when MRO_URE1 failed to review PACS database server logs, and ended when it patched the hypervisor. | This issue posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. While MRO_URE1 may have had multiple failures under CIP-006-3c R2, the scope of the noncompliance was narrow and each issue only involved a small number of accounts or devices. The CIP-003-3 R6 Change Management issue was a moderate risk issue, and was not minimal because the PACS system was excluded from the change process on more than one occasion, but the issue was not severe because the devices were behind an additional firewall that denies access to terminal controllers unless the access has been explicitly permitted and were located in a functioning PSP that would have presumably detected unauthorized access attempts. The CIP-007-3 R6 issue was a moderate risk issue, and was not a minimal risk issue because reviewing event logs from the PACS system helps identify when a system is under attack or malfunctioning, but the risk was not severe because reviewing the logs is a detective control and not a preventative control, the database Server is only accessible once a user has been authenticated to the CIP Domain, and compromising the server would not have allowed a user to gain access to MRO_URE1's Critical Cyber Assets (CCAs) because the server was outside the Electronic Security Perimeter (ESP) and because the database only applied to one factor of a two-factor authentication system. The CIP-006-3c R2.1 PSP door issue was minimal because MRO_URE1 had over-declared the number of PSPs it had, and this particular PSP did not have to be declared as one under CIP Version 3 or CIP Version 5. The CIP-007-3 R2 open port issue was also minimal because it is essentially a documentation issue that was mitigated with a TFE, and further these PACS devices were on a separate network that is protected by a firewall, and are not able to communicate to devices within MRO_URE1's ESP. The CIP-007-3 R3 issue was minimal because the hypervisor is protected by processes that would prevent or detect malicious activity, including security log reviews, account reviews, and that the device is located behind a corporate firewall. The CIP-007-3 R5 account management issue was minimal because the noncompliance was limited to a documentation issue. The CIP-004-3a R4 and the CIP-007-3 R5 issues were minimal because the PACS was outside the ESP and was inside its own DMZ, and there was only one non-admin user account enabled in the Active Directory. No harm is known to have occurred. MRO_URE1 does not have any relevant history of noncompliance. | To mitigate this issue, MRO_URE1 completed the following: 1) fixed the door that did not lock, added an alarm to the door, and Security Administration Staff implemented a peer review process to confirm all changes to the PACS; 2) filed a TFE for the open ports; 3) developed and implemented a training for all staff responsible for administering systems listed on MRO_URE1's Critical and Supporting Cyber Asset List; 4) configured the new terminal controller to match the established baseline; 5) documented the physical work involved in adding the two new terminal controllers; 6) removed the user account from the PACS Active Directory and updated its access review procedure to ensure all NERC CIP domain accounts are included in the reviews; 7) performed a review of the database Server logs and updated its log review procedure to include database Server logs; and 8) patched the hypervisor, performed a comprehensive review to determine the scope of the noncompliance, added the hypervisor as an asset to the ongoing assessment process, updated the Security Patch Management Policy to include virtual server hosts, and provided training to staff with access to the hypervisor. MRO_URE1 stated that mitigating activities were complete.
2016-12-29 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2016015744 | CIP-003-3 | R6 | RFC_URE1 submitted a Self-Report stating that it had an issue of CIP-003-3 R6. IT implemented a change request to replace the existing firewalls for the interface between the RFC_URE1 corporate environment and the RFC_URE1 plant CIP environment. The change request was submitted, reviewed, and approved. However, the change request did not mention the installation of a new network switch along with the new firewall installation. The new network switch was installed along with the new firewalls without having been approved as part of a change request thus violating CIP-003-3 R6. RFC_URE1 was installing the new network switch to connect the new CIP environment to the network. The environment had not yet been installed or connected at the time the employee submitted the change request for the firewalls so the employee incorrectly believed that the new network switch did not need to be declared as a CIP asset when the firewalls were being replaced. Additionally, the configuration details were not properly identified during the review of the change request. During the change request review, RFC_URE1 should have recognized that the new network switch was going to be routably connected to existing Critical Cyber Assets (CCAs) and Electronic Security Perimeter (ESP) access points. RFC_URE1 did not properly recognize during the change request review the impact of connecting the switch to the existing CIP environment and because of this failure did not include the installation of the new network switch in the firewall replacement change request. This noncompliance involved the management practices of work management and workforce management. Work management is implicated because RFC_URE1’s CIP V5 change management process did not clearly address how to process new CIP assets like the network switch. Workforce management is implicated because the employee inputting the change management request needs to be better trained to look out for these types of issues when he is putting in a change management request. The root cause was ineffective training. This issue started when RFC_URE1 installed the new network switch without an approved change management request and ended when RFC_URE1 discovered the issue during a post change evidence review and approved, after the fact, the installation of the new network switch. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The new network switch was fully configured for compliance with CIP V5 and analyzed in a secure state before it was installed. RFC_URE1 performed all necessary tests and followed all procedures for installing the new switch except for failing to specifically include the installation of the new switch in the change management request to replace the firewalls. The new network switch was connected to an authorized firewall, but nothing was connected to the new switch itself. RFC_URE1 properly documented the installation of the firewalls. RFC_URE1 also quickly identified, assessed, and corrected this noncompliance which shows that RFC_URE1’s internal controls are working effectively. Although this issue posed a minimal risk, ReliabilityFirst determined that the issue was appropriate for FFT treatment because RFC_URE1’s CIP V5 change management process did not clearly address how to process new CIP assets like the network switch and that weakness in the change management process makes this issue appropriate for FFT treatment. No harm is known to have occurred. | To mitigate this issue, RFC_URE1: 1) configured the new switch in a secure state and RFC_URE1’s post-change evidence review verified the proper configuration existed for installation of the new switch; 2) reviewed the CIP V5 change management process to determine if it could be streamlined or made more effective; 3) reviewed the importance of proper configuration management preparation and documentation with IT and CIP team members; 4) conducted periodic change review meetings to discuss outstanding, ongoing, and future change requests to ensure a complete understanding of the change, the devices affected, and the impacts; 5) required the change requestor to identify if a change in the ESP diagram is required when the change is originally submitted. RFC_URE1 ensured that the change management process effectively considers updating documentation following a change. Now that RFC_URE1 has completed its Mitigation Plan, particularly its first Milestone, RFC_URE1 will have an interactive discussion of each change request during weekly change review meetings, which adds another level of review to the change management process to supplement the work flow review and approval processes already in place. RFC_URE1 is further reinforcing proper change management behaviors and expectations to minimize the potential for making undocumented changes to its CIP environment. ReliabilityFirst has verified the completion of all mitigation activity.
2016-12-29 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2016015745 | CIP-007-3a | R4 | RFC_URE1 submitted a Self-Report stating that it had an issue of CIP-007-3a R4. This noncompliance contains two separate issues. First, an RFC_URE1 Network Engineer properly accessed a CIP firewall. While accessing that firewall, the Network Engineer gained access to an interface where he ran the “show version” command. Part of the output from running that command is the status of the Intrusion Prevention System (IPS). The status is either “running” or “not running.” The Network Engineer determined that the status was “not running” when he accessed the firewall. Upon further analysis, RFC_URE1 discovered that a change in status of the IPS was not set to log or generate an alert. Because there was no log and no alert, RFC_URE1 was unaware that the IPS was not running. RFC_URE1 violated CIP-007-3a R4 because it did not know if its IPS was running or not running. RFC_URE1’s use of this IPS mechanism on those firewalls serving as access points to the CIP environment at RFC_URE1 was documented in TFEs as a mitigating measure for the inability to install anti-virus tools on the corporate and firewalls, Switches, and the RTU. Second, RFC_URE1, while preparing for CIP V5 implementation, determined that the anti-virus tool on its Supervisory Control and Data Acquisition (SCADA) system had not been updated in approximately five years. Per SCADA system literature, the anti-virus tool is supposed to be updated monthly to obtain the latest threat protection, and as needed between monthly updates to address significant emergent threats. RFC_URE1 expected that its vendor for SCADA support, would provide notification to RFC_URE1 on antivirus signatures or anti-virus updates. RFC_URE1's vendor, however, never notified RFC_URE1 of any updates. This noncompliance involves the management practice of verification. RFC_URE1 did not verify that it had an alert in place to notify it when IPS was “not running” and did not verify that its vendor would notify RFC_URE1 of updates to its anti-virus software. RFC_URE1 did not have effective processes in place to verify these assumptions and the lack of effective verification processes was the root cause of this noncompliance. This issue started when RFC_URE1 first failed to update the anti-virus tool and ended when RFC_URE1 confirmed that it had updated to the latest version of the anti-virus tool and that it would need to replace the anti-virus tool because updates to that anti-virus tool are no longer available. | The first instance in the subject noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. RFC_URE1 confirmed that all other firewalls serving as electronic access points to the CIP environment had their IPS active during the time of the noncompliance. In addition, the main RFC_URE1 firewall had the same IPS module installed and it was also active at that time. Any threat would need to attach to a patch with specific permissions per the firewall access rules which minimizes the risk posed by this noncompliance because it makes it more difficult for a bad actor to take advantage of this one IPS not running. The second instance in the subject noncompliance posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. RFC_URE1 did not update its anti-virus tool on its SCADA system for five years and incorrectly believed that its vendor for SCADA support was updating the anti-virus tool for five years. This reveals RFC_URE1’s poor detective controls. The potential harm for this issue was high because a virus on the SCADA system could have led to a loss of visibility. The risk is mitigated by the following factors. RFC_URE1 ran a unique computer operating system. The anti-virus tool that was not updated was installed to protect Windows files stored on the unique system and RFC_URE1 did not have any Windows files stored on the unique system during the duration of the violation. Additionally, this unique system is difficult to attack and is rarely attacked with viruses. Lastly, RFC_URE1 had other redundant protections in place as part of a defense in depth strategy including multiple firewalls and a working IPS that would have made it extremely unlikely that any harm would have been realized from a network based attack. ReliabilityFirst determined that the issue was appropriate for FFT treatment because the second instance posed a moderate risk given its long duration and that RFC_URE1 did not verify that it had an alert in place to notify it when IPS was “not running” and did not verify that its vendor would notify RFC_URE1 of updates to its anti-virus software which shows that RFC_URE1 did not have effective processes in place to verify these assumptions. No harm is known to have occurred. | To mitigate this issue, RFC_URE1: 1) upgraded to the new Firewall with integrated IPS; 2) determined a way to log and issue an alert to CIP and IT network staff when the IPS changes status; 3) verified that the new Firewall IPS is configured to receive periodic updates to its signature/threat files; 4) documented the process to verify that the IPS is enabled and that signature/threat files are updated regularly; 5) reviewed and assigned responsibility, where needed, to support and maintain security controls on RFC_URE1 plant assets; 6) assigned clear responsibility to ensure IPS threat files are updated timely and effectively; 7) researched other anti-virus tools available for the SCADA system, since updates to the anti-virus tool are no longer available and determined a course of action to meet V5 obligations. RFC_URE1 plans to replace its SCADA system entirely in 2017 with a new system. RFC_URE1 also confirmed with its vendor for SCADA support, all of the vendor's and RFC_URE1’s responsibilities respectively; and 8) performed an extent of condition review on all anti-virus tools in the CIP program and developed and implemented appropriate remediation plans as needed. RFC_URE1 will complete the following mitigation activities by December 30, 2016: 1) provide enhanced compliance monitoring of documented anti-virus related processes. The process of determining if additional updates to the tool were available, coming up with an alternative to replace the tool, and performing an extent of condition review on all anti-virus tools in the CIP program and developing and implementing appropriate remediation plans as needed took an extended amount of time. Those Milestones needed to be completed before RFC_URE1 could provide enhanced compliance monitoring of documented anti-virus related processes which explains why the length of time for completion is required.
2016-12-29 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2016015603 | CIP-007-3a | R5 | WECC_URE1 submitted a Self-Report stating that it had a possible issue of noncompliance with CIP-007-3a R5.2. Specifically, WECC_URE1 reported that while implementing a new process to verify and review active accounts on Critical Cyber Assets (CCAs) for CIP Version 5 implementation, WECC_URE1 discovered a default user account named that had not been disabled on a single CCA when the device was put into production at WECC_URE1’s control center. WECC_URE1’s system administrators mistook the account for a well-known, similarly named windows service account. The account was actually a default account. The procedure document, in effect at the time the issue occurred, defined a default account as "Any account that is published in any vendor manual or exists on a Cyber Asset when it is received from a vendor." The default user account was created by a vendor contracted to setup the energy management system domain at WECC_URE1’s control center. WECC_URE1’s procedure states that default accounts of this nature should be disabled. This issue began when the default account on the CCA should have been disabled and ended when WECC_URE1 disabled the default account, for a total of 907 days of noncompliance. The root cause of this violation was a lack of understanding related to which accounts were necessary and thus should have been assessed. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System. In this instance, WECC_URE1 failed to disable a user account on one CCA. Failure to apply the applicable security control requirements to the user accounts specified within CIP-007-3a R5 could result in compromise to the associated Cyber Asset, which could be leveraged to negatively impact the availability or secure operation of the bulk electric system. However, the user account was enabled with minimal user privilege levels which minimized its threat level had it been compromised by intruders to the network. Additionally, access to the device was limited to individuals who had an approved Personnel Risk Assessment, had completed appropriate training, and were authorized to have such access. WECC_URE1 performed a security controls test on the default account which ensured that the device had not been inappropriately accessed and/or compromised. WECC_URE1 also reviewed the logs from the default account and confirmed the default account was never used. Based on this information and because no harm is known to have occurred, this issue posed minimal risk to the reliability of the BPS. WECC considered WECC_URE1 compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue WECC_URE1: 1) implemented both the review of CIP-004-5 R4 Parts 4.2 and 4.3 on a quarterly basis; and 2) updated procedures by asset to include a process to evaluate systems for default accounts and steps required to mitigate any issues identified; to include configuration analysis reports for each new asset and change event, resulting in lists of shared accounts and default accounts. WECC verfied completion of WECC_URE1's mitigating activities.
2016-11-30 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2016015464 | CIP-007-1 | R9 | MRO_URE1 submitted a Self-Report stating that, during its 2015 Cyber Vulnerability Assessment (CVA), MRO_URE1 discovered that it had open ports and services that were not included on the list of approved ports and services. Specifically, MRO_URE1 discovered that there were 36 devices that had open, but not approved ports on the baseline, and 12 servers that were missing baseline ports and services related to the Remote Access Card (RAC) server components. This was caused by MRO_URE1's failure to fully review or update its ports and services documentation. This issue lasted approximately seven years. | This issue posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The noncompliance can be categorized as documentation errors, as all open and undocumented ports were all deemed to be previously approved or necessary. Additionally, for the noncompliance related to the RAC device, the risk was further reduced because the RAC is not a stand alone asset, but a card with a network interface that is installed in a server to allow administrative support tasks. Finally, the risk was further reduced because the RAC interfaces were located on a separated VLAN within the Electronic Security Perimeter (ESP). No harm is known to have occurred. MRO_URE1 has no relevant history of noncompliance. | To mitigate this issue, MRO_URE1: 1) reviewed all undocumented ports, ensured they were necessary, then added them to the list of authorized ports; 2) captured the ports in the baselines; and 3) installed an intrusion detection system. MRO_URE1 stated that mitigating activities were complete.
2016-10-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2015015082 | CIP-003-3 | R6 | WECC_URE1 submitted a Self-Report stating that it had a possible issue of noncompliance with CIP-003-3 R6. Specifically, WECC_URE1 reported that it failed to follow its CIP change configuration management program prior to deploying a Critical Cyber Asset (CCA) into production. The CCA was an Energy Management System (EMS) workstation, which was being added for a new employee. At the time of deployment of the CCA, a change ticket had not been created, and WECC_URE1 CIP change configuration management program had not been followed. No one with authority to approve the deployment of the CCA was notified nor were they aware of the bypassing of the CIP change configuration management program prior to deployment. Subsequent to WECC_URE1 submittal of the above referenced Self-Report, WECC_URE1 discovered another possible issue of noncompliance with CIP-003-3 R6. Specifically, WECC_URE1 reported that another employee added software to a windows workstation classified as a CCA without following WECC_URE1’s CIP change configuration management program. The first issue began when the EMS workstation was deployed into production within the EMS without following WECC_URE1’s documented change control, and ended when WECC_URE1 completed a change ticket for the EMS workstation. The second issue began when unauthorized software was added to a windows workstation, and ended when that software was removed. The root cause of issue one was a lack of following documented processes and procedures for change management, and issue two was due to insufficient training relating to change management for CCAs. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). In this instance, WECC_URE1 failed to identify, control, and document a change to two CCAs in its production environment as required by CIP-003-3 R6. Failing to properly track changes to CCAs prior to deployment could lead to unauthorized changes being implemented. The workstation could have had an unapproved configuration, which could lead to vulnerabilities on the workstation that could be exploited, such as open ports and services that should not be enabled per the entity’s baseline, lack of anti-virus, software that is not up-to-date, etc. If vulnerabilities are discovered by a malicious party, through the use of network scanning tools, the person could attempt to exploit the vulnerability, which could allow the person to take control of the device. As the device was a CCA within the EMS Electronic Security Perimeter, the person could use control of the devices to perform EMS operations. Additionally, failure to implement change control and configuration management processes for software upgrades could potentially allow adding or modifying hardware and software changes that could be harmful to CCAs essential to the operation of Bulk Electric System (BES), thereby introducing or exposing potential security vulnerabilities to the CCAs. WECC_URE1 implemented strong preventive controls by utilizing an image from an existing CCA workstation to configure the new workstation. This image had approved ports and services, anti-virus, and current software, which could have prevented any vulnerabilities from existing on the new workstation. Additionally, WECC_URE1 implemented strong detective controls. Specifically, WECC_URE1 used additional software which monitored the network and could detect anomalous traffic from a malicious person, or vulnerabilities that may exist on devices as device baselines are stored in these network scanning tools, and alerts are generated when a device deviates from the baseline. These softwares also alert when new devices are put onto the production environment and an alert was issued within hours of the new workstation being put into production. For these reasons, and because no harm is known to have occurred, this issue posed minimal risk to the reliability of the Bulk Power System. WECC considered WECC_URE1 compliance history as a factor in its designation of these mitigated issues for FFT treatment. | To mitigate this issue(s) WECC_URE1: 1) completed its investigation by HR and made recommendations to management regarding corrective actions; 2) provided specific training related to CIP change management, and corporate emergency response personnel; 3) implemented robust CIP-010-2 R1 and R2 processes, to include a new CIP specific change management system; and 4) added additional software detective controls designed to quickly identify and alert for any unauthorized changes made to BES Cyber System, that will mitigate these issues from occurring in the future
2016-09-29 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2015015208 | CIP-005-3a | R2; R2.4 | During a Compliance Audit, SPP RE determined that SPPRE_URE1 had an issue of noncompliance with CIP-005-3a R2.4 because it did not afford strong technical controls for external interactive access to the Electronic Security Perimeter (ESP) to ensure authenticity of the accessing party. Forty-one individuals with authorized interactive access to SPPRE_URE1’s ESP were able to gain access to the ESP by remotely logging onto SPPRE_URE1’s jump host, i.e., virtual server, by utilizing their individual domain usernames and passwords. Although access to a target host, i.e., another device within the ESP, required an additional login with the user’s same individual domain username and password, the use of this single-factor authentication process to access the ESP via the jump host did not constitute strong technical controls to ensure authenticity of the accessing party. The duration of this issue was from the day after the previous Compliance Audit, through the date SPPRE_URE1 completed its Mitigation Plan. The root cause of this issue was a misunderstanding of the standard; specifically, SPPRE_URE1 believed that under version 3 of the standard, single-factor authentication for access to its ESP and other procedural controls was sufficient to constitute strong technical controls or procedural controls to ensure authentication of the accessing party. | This issue posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Noncompliance with CIP-005-3a R2.4 has the potential to affect the reliability of the BPS by providing the opportunity for unauthorized access to Cyber Assets inside the PSP. The risk was mitigated by SPPRE_URE1’s use of the jump host. The jump host (also referred to as an Intermediate system) is a computer that serves as a proxy between the Cyber Asset initiating the external communication, i.e., a remote user’s laptop, and the Cyber Assets within the ESP. Rather than allowing all the protocols the user might need for access to Cyber Assets inside the ESP, only the protocol required for remotely controlling the jump host is required. The use of a jump host also protects the Cyber Assets from vulnerabilities on the remote computer. If the remote computer is infected with malware, the use of a jump host, acting on behalf of the remote computer, prevents the malware from spreading to the Cyber Assets within the ESP. The implementation of a jump host for external interactive access into the Electronic Security Perimeter is mandatory in version 6 of the requirement. Additionally, all Cyber Assets within the ESP were protected by multiple layers of firewalls configured to allow only traffic using specific protocols to enter the network, which prevented unsolicited traffic from passing into the ESP. SPPRE_URE1’s ESP was continuously monitored and protected by an intrusion prevention/detection system, which provided real-time log analysis, event alerting, and blocking of both internal and external malicious transmissions on Cyber Assets within the ESP. Virtual Local Area Networks were being utilized to separate Cyber Assets with sensitive data from the rest of the network to reduce the potential for unauthorized access of sensitive data. SPPRE_URE1 implemented additional protective measures to protect Cyber Assests inside the ESP and access points to the ESP, including permissions controlling access to network resources based on job functions, network and host-based anti-malware systems, password and lockout policies, personnel physical and cyber access reviews, and control processes. Access to Cyber Assets within the ESP was limited to only those individuals with authorized physical and/or electronic access rights. No actual harm occurred as a result of the noncompliance. | To mitigate this minimal risk instance of noncompliance, SPPRE_URE1: 1) implemented multi-factor authentication for all external interactive access into its ESP; 2) revised its ESP Management Process to include multi-factor authentication for all external interactive access into its ESP; and 3) trained all affected personnel on the revisions to the ESP Management Process. SPP RE has verified the completion of all mitigation activity.
2016-08-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2014014461 | CIP-004-3 | R4 | RFC_URE1 submitted a Self-Report stating that it had an issue with CIP-004-3 R4. This issue involves RFC_URE1 not conducting quarterly reviews of lists of personnel who have access to Critical Cyber Assets (CCAs). First, RFC_URE1 failed to perform quarterly reviews on its access list because RFC_URE1’s Compliance Department responsible for conducting quarterly access reviews was unaware of the access type and thus did not know the access list existed such that it could review the list. The root causes of this issue were a miscommunication during the creation of the access type between the IT Support team, who manages the access, and the Compliance Department, who is tasked with conducting quarterly reviews of all access lists, and a lack of subsequent verification controls to identify the issue. Second, RFC_URE1’s Commercial Operations business unit implemented new software to which individuals were granted access. In order for RFC_URE1’s Compliance Department to perform quarterly access reviews, the software had to provide information regarding approved access to RFC_URE1’s Compliance Department. However, the output from the new software was not compatible with the Compliance Department’s software, and as a result, the Compliance Department did not have the necessary information to be able to conduct the quarterly reviews. Thus, RFC_URE1 did not conduct quarterly access reviews relating to access to the new software. RFC_URE1 was aware that the departments’ software was not compatible, but, due to an oversight and lack of subsequent verification controls to identify the issue, RFC_URE1 did not conduct quarterly access reviews, even manually. This issue started when the first quarterly review of access should have been completed and ended the day that the manual review of approved access rights was conducted. | This issue posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the access list was not reviewed for over two years. RFC_URE1’s failure to perform quarterly reviews of the list of personnel with authorized cyber and/or authorized unescorted physical access to CCAs could have allowed an unauthorized individual to gain access to critical systems leading to intentional misuse of the information or controls, potentially compromising the reliability of the BPS. However, the risk was mitigated because RFC_URE1 requires approvals within management and its IT Department to gain or revoke access to CCAs and, as a result, only trusted individuals are able to initially gain authorized access to CCAs, including the CCAs at issue here. Thus, because RFC_URE1 has thorough processes for granting and revoking access, it is less likely that individuals who should not have unauthorized access would incorrectly have access. Additionally, if an individual were terminated for cause, RFC_URE1’s access revocation system would have ensured the revocation of all of the individual’s access rights. ReliabilityFirst determined that the issue was appropriate for FFT treatment because the issue posed only moderate risk to the BPS and RFC_URE1 was highly cooperative throughout the enforcement process. No harm is known to have occurred. | To mitigate this issue, RFC_URE1: 1) completed a manual review by comparing actual access rights in the new software with the approved access rights stored in RFC_URE1's access tracking system, which ensured that the access tracking system data accurately reflected actual Control System (CS) accesses; 2) conducted a manual quarterly review of approved CS access rights by sending emails to the managers requesting review of direct report access rights. This review constituted the first quarterly access review for the new CS software; 3) installed Jump Stations within the Physical Security Perimeter (PSP) for use by “PI administrators” if they are not located within the PSP to add an additional layer of security; 4) to help prevent a recurrence, the business units at issue transferred daily access management and quarterly reviews of their NERC CIP assets to RFC_URE1’s access tracking system. Using RFC_URE1's access tracking system software helps to ensure that quarterly reviews are performed on schedule and with accurate data; 5) completed a quarterly review of CS and NERC CIP PI accesses using RFC_URE1's access tracking system to ensure the initial issue was corrected; and 6) created a set of controls in order to prevent this from recurring and to ensure that new CIP assets or modifications to existing assets for the business units at issue are reviewed, by CIP Standard, to ensure that all appropriate CIP procedures are performed as required for compliance. A checklist was created for use in business units that targets new or existing CIP assets and project managers are required to review and approve the completed checklists prior to implementation. Use of this checklist would have prevented the issues with the CS and NERC CIP PI access rights. ReliabilityFirst has verified the completion of all mitigation activity.
2016-08-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2014014462 | CIP-004-3a | R4 | RFC_URE2 submitted a Self-Report stating that it had an issue with CIP-004-3a R4. This issue involves RFC_URE2 not conducting quarterly reviews of lists of personnel who have access to Critical Cyber Assets (CCAs). First, RFC_URE2 failed to perform quarterly reviews on its access list because RFC_URE2’s Compliance Department responsible for conducting quarterly access reviews was unaware of the access type and thus did not know the access list existed such that it could review the list. The root causes of this issue were a miscommunication during the creation of the access type between the IT Support team, who manages the access, and the Compliance Department, who is tasked with conducting quarterly reviews of all access lists, and a lack of subsequent verification controls to identify the issue. Second, RFC_URE2’s Commercial Operations business unit implemented new software to which individuals were granted access. In order for RFC_URE2’s Compliance Department to perform quarterly access reviews, the software had to provide information regarding approved access to RFC_URE2’s Compliance Department. However, the output from the new software was not compatible with the Compliance Department’s software, and as a result, the Compliance Department did not have the necessary information to be able to conduct the quarterly reviews. Thus, RFC_URE2 did not conduct quarterly access reviews relating to access to the new software. RFC_URE2 was aware that the departments’ software was not compatible, but, due to an oversight and lack of subsequent verification controls to identify the issue, RFC_URE2 did not conduct quarterly access reviews, even manually. This issue started when RFC_URE2 was required to comply with CIP-004-3 R4, and ended the day that the manual review of approved access rights was conducted. | This issue posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the access list was not reviewed for over two years. RFC_URE2’s failure to perform quarterly reviews of the list of personnel with authorized cyber and/or authorized unescorted physical access to CCAs could have allowed an unauthorized individual to gain access to critical systems leading to intentional misuse of the information or controls, potentially compromising the reliability of the BPS. However, the risk was mitigated because RFC_URE2 requires approvals within management and its IT Department to gain or revoke access to CCAs and, as a result, only trusted individuals are able to initially gain authorized access to CCAs, including the CCAs at issue here. Thus, because RFC_URE2 has thorough processes for granting and revoking access, it is less likely that individuals who should not have unauthorized access would incorrectly have access. Additionally, if an individual were terminated for cause, RFC_URE2’s access revocation system would have ensured the revocation of all of the individual’s access rights. ReliabilityFirst determined that the issue was appropriate for FFT treatment because the issue posed only moderate risk to the BPS and RFC_URE2 was highly cooperative throughout the enforcement process. No harm is known to have occurred. | To mitigate this issue, RFC_URE2: 1) completed a manual review by comparing actual access rights in the new software with the approved access rights stored in RFC_URE2's access tracking system, which ensured that the access tracking system data accurately reflected actual Control System (CS) access rights; 2) conducted a manual quarterly review of approved CS access rights by sending emails to the managers requesting review of direct report access rights. This review constituted the first quarterly access review for the new CS software; 3) installed Jump Stations within the Physical Security Perimeter (PSP) for use by “PI administrators” if they are not located within the PSP to add an additional layer of security; 4) to help prevent a recurrence, the business units at issue transferred daily access management and quarterly reviews of their NERC CIP assets to RFC_URE2’s access tracking system. Using RFC_URE2's access tracking system software helps to ensure that quarterly reviews are performed on schedule and with accurate data; 5) completed a quarterly review of CS and accesses using RFC_URE2's access tracking system to ensure the initial issue was corrected; and 6) created a set of controls in order to prevent this from recurring and to ensure that new CIP assets or modifications to existing assets for the business units at issue are reviewed, by CIP Standard, to ensure that all appropriate CIP procedures are performed as required for compliance. A checklist was created for use in business units that targets new or existing CIP assets and project managers are required to review and approve the completed checklists prior to implementation. Use of this checklist would have prevented the issues with the CS and access rights. ReliabilityFirst has verified the completion of all mitigation activity.
2016-07-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2016015616 | CIP-004-3a | R4 | RFC_URE1 submitted a self-log to ReliabilityFirst stating that it had an issue of CIP-004-3a R4. This issue involved two separate instances. First, a project lead gave seven contractors passwords to Critical Cyber Assets (CCAs) while on-site at a project. Of the seven contractors, five had authorized unescorted physical access and none had authorized cyber access. The issue continued until it was discovered approximately six months later as a result of the project lead going on leave and his replacement immediately discovering the issue. Upon identification of the issue, RFC_URE1 immediately changed the passwords. Second, an authorized RFC_URE1 employee gave the password to the station Remote Terminal Unit (RTU) to a co-worker, also a RFC_URE1 employee, along with an email link for CIP passwords. The co-worker was unable to access the link because he did not have approved cyber access. The authorized employee assumed that because the co-worker had Physical Security Perimeter (PSP) access, he also had electronic access. At the time of the incident, the co-worker did not have an active request for electronic access. The employees immediately identified the issue and reported it to their local supervisor, who internally reported the incident that same day. The unauthorized employee obtained authorized cyber access eight days later. The root cause of this issue was a lack of oversight in information management in that RFC_URE1’s internal controls to prevent unauthorized access to CIP passwords were not effective. Another root cause was insufficient workforce management practices in that prior training on properly protecting CIP passwords was insufficient. The issue began when the project lead in the first instance gave CIP passwords to unauthorized contractors, and ended when RFC_URE1 discovered the first instance and changed the passwords. | This issue posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The potential risk from this issue, especially with the relatively long duration in the first instance, was that the individuals would use the passwords in a manner that would compromise the BPS. a. Regarding the first instance, the risk was mitigated by the following factors. First, the password was immediately changed upon discovery of the issue and the unauthorized contractors began the process of obtaining both physical and cyber access, as needed. Second, five of the seven contractors had physical access to that station at the time of the issue and all of the contractors ultimately obtained properly authorized physical and cyber access. Thus, the contractors were trusted resources who were not likely to compromise the BPS. Third, the contractors could not use the passwords at other stations because they did not have physical access to other stations. b. Regarding the second instance, the risk was mitigated by the following factors. First, the instance was reported that same day. The employees immediately informed their supervisor, who then reported the instance to the proper department. Second, the employee who received the passwords is a trusted individual with authorized access to the PSP, as well as CIP access to other stations, and the employee ultimately requested and was granted the access at issue here, thus reducing the likelihood that the employee would use the information in a way that would compromise the BPS. Third, the risk associated with an unauthorized individual possessing the RTU password would be limited to assets at that particular substation, and not the entire system, and the employee was unable to access the link because he did not have approved cyber access. ReliabilityFirst determined that the issue was appropriate for FFT treatment because the issue posed a moderate risk to the reliability of the BPS. Even with the mitigating factors, the risk was more than minimal, especially because of the long duration of the first instance in addition to the fact that this is a repeat issue. No harm is known to have occurred. | To mitigate this issue, RFC_URE1: 1) implemented a system, which stores passwords, and when a user logs on, that user is logged into the devices to which the user has authorized access. Under this system, no passwords are exchanged or shared by users, and the system conceals the password so that it cannot be replicated; 2) regarding the first instance, RFC_URE1 changed the passwords upon discovery of the instance; 3) at the time RFC_URE1 reported the first instance, five of the contractors had obtained properly authorized physical and cyber access and RFC_URE1 committed to process access requests for the remaining contractors; 4) the project lead, as well as the five contractors with access, took Cyber Security and Cyber Awareness training; and 5) regarding the second instance, the unauthorized co-worker obtained authorized cyber access. ReliabilityFirst has verified the completion of all mitigation activity.
2016-05-31 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2016015509 | CIP-006-3c | R1 | MRO_URE1 submitted a Self-Report stating that it had an issue of CIP-006-3c R1. MRO_URE1 reported that two contractors that were properly logged, were left unescorted several times in a back-up control center (BUCC), which is located within the Physical Security Perimeter (PSP). After submitting the Self-Report, MRO_URE1 discovered another instance of noncompliance. Shortly after the initial Self-Report, MRO_URE1 reported that three contractors that were properly logged, were left unescorted for up to 20 minutes in the control house of a generation facility. The cause of both instances of noncompliance was insufficient training regarding existing MRO_URE1 policies and a lack of adherence to those policies. This first instance of noncompliance began when the two contractors were not continuously escorted, and ended later that day, when the two contractors were again escorted; the second instance of noncompliance began when the three contractors were not continuously escorted, and ended later that same day, when the three contractors were again escorted. | MRO determined that this violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Proper escorting of visitors and contractors is a critical component of protecting the BPS critical infrastructure. In these instances, the risk was escalated due to the nature of the assets. However, the risk was mitigated by the following factors. The issues were self-reported and discovered promptly, which is a strong indication of secondary controls. Further, the unescorted contractors were properly logged and initially escorted. Finally, none of these issues exceeded two hours. MRO determined that MRO_URE1 has no aggravating compliance history. | To mitigate this issue, MRO_URE1: 1) provided continuous escorts to the contractors for the remainder of their time on-site; 2) provided additional training on MRO_URE1's visitor policies and distributed a training bulletin; 3) distributed a bulletin to generation personnel informing them that an unacceptable event (the second instance of noncompliance) occurred; and 4) has stated that it restricted the escort in the second instance of noncompliance from performing those duties until additional training was completed. MRO verified that mitigating activities were complete as of April 24, 2015.
2016-05-31 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE2016015473 | CIP-004-3a | R4; R4.2 | TRE_URE1 submitted a self-log stating that it had identified multiple instances of noncompliance with CIP-004-3a R4.2. Specifically, TRE_URE1 did not revoke access on three separate occasions to Critical Cyber Assets (CCAs) within 24 hours for personnel terminated for cause or within seven days for personnel no longer requiring such CCA access. After subsequent review, Texas RE determined that the instances of noncompliance posed a moderate risk to the reliability of the bulk power system. As a result, Texas RE removed this issue from TRE_URE1’s self-log. In the first instance, TRE_URE1 failed to revoke an employee’s unescorted physical access to CCAs within seven calendar days when the employee in question transferred job responsibilities. TRE_URE1 did not revoke the employee’s physical access rights until 52 days after the expiration of the 7-day access revocation window. In the second instance, TRE_URE1 failed to revoke an employee’s electronic CCA access within seven calendar days of that employee’s resignation. TRE_URE1 did not revoke that employee’s electronic access rights until after the expiration of the 7-day access revocation period. In the third instance, TRE_URE1 failed to revoke an employee’s electronic CCA access within 24 hours of that employee being terminated for cause. Specifically, TRE_URE1 did not complete the electronic access revocation process of the terminated employee until four days after the expiration of the required revocation period. The root cause of these instances pertained to the failure of TRE_URE1 personnel to fully implement TRE_URE1’s existing access revocation processes by either not requesting an access revocation or not acting to complete such a request in a timely fashion. Texas RE determined the issue duration to be for approximately six months, from the day after TRE_URE1 should have revoked the physical access rights of the employee in the first instance until the day TRE_URE1 revoked the third employee’s electronic access rights. | This issue posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. TRE_URE1’s failure to timely revoke CCA access on three separate occasions had the potential to affect the reliable operation of the bulk power system (BPS) by providing an opportunity for TRE_URE1 personnel who should not have had access to CCAs to potentially access such CCAs and damage them. In the third instance in particular, the TRE_URE1 employee in question was terminated for cause, increasing the risk that the employee or another individual might access CCAs located at critical facilities following the employee’s termination and harm their integrity. Finally, these three instances, combined with the five previous instances in which TRE_URE1 did not timely revoke CCA access, indicate a general weakness in TRE_URE1’s internal access revocation controls. Balanced against this is the fact that the first individual in question remained employed at TRE_URE1 and retained physical and electronic access to other CCAs as part of that employee’s new job function. Regarding the two additional instances, TRE_URE1 promptly revoked physical access upon discovering the issues for both the terminated employee and the employee resigning from the company. Additionally, these former employees could not remotely access CCAs because TRE_URE1 collected both of the former employees’ remote access tokens. Finally, TRE_URE1 uses a layered cyber defense approach to mitigate security risks, including a variety of physical and electronic controls to protect and continuously monitor CCAs within TRE_URE1’s Physical Security Perimeter (PSP). No harm is known to have occurred. Texas RE considered TRE_URE1’s compliance history in determining that this issue is appropriate for Find, Fix, and Track (FFT) treatment. TRE_URE1’s compliance history constituted an aggravating factor, increasing the risk determination and making this issue not appropriate for Compliance Exception treatment, even though it is a self-logged noncompliance. Texas RE determined that TRE_URE1’s compliance history should not serve as a basis for applying a penalty as TRE_URE1 has proposed and implemented mitigating activities to prevent future recurrence of these issues. | To mitigate this issue, TRE_URE1: 1) revoked authorized cyber and authorized unescorted physical access to CCAs for all three individuals; and 2) installed software that automatically revokes CCA access for employees on the designated date TRE_URE1 determines such CCA access is no longer required. Texas RE has verified the completion of all mitigation activity.
2016-05-31 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE2016015476 | CIP-004-3a | R4 | TRE_URE1 submitted a self-log stating that it had identified multiple instances of noncompliance with CIP-004-3a R4. Specifically, TRE_URE1 failed to maintain a list of personnel with cyber access rights to Critical Cyber Assets (CCAs), including specific electronic and physical access rights, as well as update the list within seven calendar days of any change in the access rights of such personnel. After subsequent review, Texas RE determined that the instances of noncompliance posed a moderate risk to the reliability of the bulk power system. As a result, Texas RE removed this issue from TRE_URE1’s self-log. A TRE_URE1 employee shared an intelligent electronic device (IED) password applicable to CCAs with seven contractors who did not have authorized electronic access rights. Because TRE_URE1 was unaware that the employee had shared the IED password with the seven contractors, TRE_URE1 failed to update its access lists to reflect this change within the required seven-day window. TRE_URE1 discovered the issue during its annual password review and changed the IED password, revoking all unauthorized electronic access rights. The root cause of the issue was that TRE_URE1 did not follow its process for granting new access rights to CCAs, along with maintaining the completeness and accuracy of access rights as required. In particular, the TRE_URE1 employee mistakenly assumed that all the contractors had electronic access rights because some of the contractors had authorized physical access. Texas RE determined the issue duration to be for approximately seven months, from the earliest date upon which TRE_URE1 should have updated its access lists to reflect the change in personnel access rights until the date TRE_URE1 changed the IED password, resulting in TRE_URE1’s access lists again accurately reflecting the access rights of the seven contractors. | This issue posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. TRE_URE1 failed to ensure accountability for all user activity and minimize the risk of unauthorized system access. The password provided electronic access to IEDs at TRE_URE1 CCAs. Further, at the time the seven contractors received unauthorized electronic access, five of the seven had not completed the requisite cyber security training and personnel risk assessment (PRA) to receive such access. The remaining two contractors had neither valid physical nor electronic access rights. Finally, all seven contractors retained such unauthorized electronic access rights for approximately seven months. Balanced against this risk was the fact that to use the IED password in question, an individual must be physically inside each CCA’s Physical Security Perimeter (PSP). Second, TRE_URE1 employs defense-in-depth to secure CCAs, including PSPs, Electronic Security Perimeters, firewalls and other protections. Finally, TRE_URE1 subsequently granted electronic access rights to five of the seven contractors, including access to the IED password and associated CCAs at issue here. No harm is known to have occurred. Texas RE considered TRE_URE1’s compliance history in determining that this issue is appropriate for Find, Fix, and Track (FFT) treatment. TRE_URE1’s compliance history constituted an aggravating factor, increasing the risk determination and making this issue not appropriate for Compliance Exception treatment, even though it is a self-logged noncompliance. Texas RE determined that TRE_URE1’s compliance history should not serve as a basis for applying a penalty as TRE_URE1 has proposed several measures to prevent future recurrence of these issues. In particular, TRE_URE1 plans to prevent future recurrence of this issue by using a technical solution that stores passwords in an intermediate system and requires two-factor authentication to access accounts. | To mitigate this issue, TRE_URE1 has completed the following actions: 1) changed the IED password; 2) granted access rights to the contractors in question and updated the access records to reflect this change; 3) verified that the electronic access records accurately reflect the electronic authorizations for the seven contractors in question; and 4) implemented an access system that stores passwords such that CCA passwords can no longer be shared or exchanged by users, and requires two-factor authentication for access. Texas RE has verified the completion of all mitigation activity.
2016-05-31 | TRE_URE1liability Entity (TRE_URE1) | Unidentified Registered Entity 2 (TRE_URE2) | NCRXXXXX | TRE2016015474 | CIP-004-3a | R4; R4.2 | TRE_URE2 submitted a self-log stating that it had identified multiple instances of noncompliance with CIP-004-3a R4.2. Specifically, TRE_URE2 did not revoke access on three separate occasions to Critical Cyber Assets (CCAs) within 24 hours for personnel terminated for cause or within seven days for personnel no longer requiring such CCA access. After subsequent review, TRE_URE1 determined that the instances of noncompliance posed a moderate risk to the reliability of the bulk power system. As a result, TRE_URE1 removed this issue from TRE_URE2’s self-log. In the first instance, TRE_URE2 failed to revoke an employee’s unescorted physical access to CCAs within seven calendar days when the employee in question transferred job responsibilities. TRE_URE2 did not revoke the employee’s physical access rights until 52 days after the expiration of the 7-day access revocation window. In the second instance, TRE_URE2 failed to revoke an employee’s electronic CCA access within seven calendar days of that employee’s resignation. TRE_URE2 did not revoke that employee’s electronic access rights until after the expiration of the 7-day access revocation period. In the third instance, TRE_URE2 failed to revoke an employee’s electronic CCA access within 24 hours of that employee being terminated for cause. Specifically, TRE_URE2 did not complete the electronic access revocation process of the terminated employee until four days after the expiration of the required revocation period. The root cause of these instances pertained to the failure of TRE_URE2 personnel to fully implement TRE_URE2’s existing access revocation processes by either not requesting an access revocation or not acting to complete such a request in a timely fashion. TRE_URE1 determined the issue duration to be for approximately six months, from the day after TRE_URE2 should have revoked the physical access rights of the employee in the first instance until the day TRE_URE2 revoked the third employee’s electronic access rights. | This issue posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. TRE_URE2’s failure to timely revoke CCA access on three separate occasions had the potential to affect the reliable operation of the bulk power system (BPS) by providing an opportunity for TRE_URE2 personnel who should not have had access to CCAs to potentially access such CCAs and damage them. In the third instance in particular, the TRE_URE2 employee in question was terminated for cause, increasing the risk that the employee or another individual might access CCAs located at critical facilities following the employee’s termination and harm their integrity. Finally, these three instances, combined with the five previous instances in which TRE_URE2 did not timely revoke CCA access, indicate a general weakness in TRE_URE2’s internal access revocation controls. Balanced against this is the fact that the first individual in question remained employed at TRE_URE2 and retained physical and electronic access to other CCAs as part of that employee’s new job function. Regarding the two additional instances, TRE_URE2 promptly revoked physical access upon discovering the issues for both the terminated employee and the employee resigning from the company. Additionally, these former employees could not remotely access CCAs because TRE_URE2 collected both of the former employees’ remote access tokens. Finally, TRE_URE2 uses a layered cyber defense approach to mitigate security risks, including a variety of physical and electronic controls to protect and continuously monitor CCAs within TRE_URE2’s Physical Security Perimeter (PSP). No harm is known to have occurred. TRE_URE1 considered TRE_URE2’s compliance history in determining that this issue is appropriate for Find, Fix, and Track (FFT) treatment. TRE_URE2’s compliance history constituted an aggravating factor, increasing the risk determination and making this issue not appropriate for Compliance Exception treatment, even though it is a self-logged noncompliance. TRE_URE1 determined that TRE_URE2’s compliance history should not serve as a basis for applying a penalty as TRE_URE2 has proposed and implemented mitigating activities to prevent future recurrence of these issues. | To mitigate this issue, TRE_URE2: 1) revoked authorized cyber and authorized unescorted physical access to CCAs for all three individuals; and 2) installed software that automatically revokes CCA access for employees on the designated date TRE_URE2 determines such CCA access is no longer required. TRE_URE1 has verified the completion of all mitigation activity.
2016-05-31 | TRE_URE1liability Entity (TRE_URE1) | Unidentified Registered Entity 2 (TRE_URE2) | NCRXXXXX | TRE2016015475 | CIP-004-3a | R4 | TRE_URE2 submitted a self-log stating that it had identified multiple instances of noncompliance with CIP-004-3a R4. Specifically, TRE_URE2 failed to maintain a list of personnel with cyber access rights to Critical Cyber Assets (CCAs), including specific electronic and physical access rights, as well as update the list within seven calendar days of any change in the access rights of such personnel. After subsequent review, TRE_URE1 determined that the instances of noncompliance posed a moderate risk to the reliability of the bulk power system. As a result, TRE_URE1 removed this issue from TRE_URE2’s self-log. A TRE_URE2 employee shared an intelligent electronic device (IED) password applicable to CCAs with seven contractors who did not have authorized electronic access rights. Because TRE_URE2 was unaware that the employee had shared the IED password with the seven contractors, TRE_URE2 failed to update its access lists to reflect this change within the required seven-day window. TRE_URE2 discovered the issue during its annual password review and changed the IED password, revoking all unauthorized electronic access rights. The root cause of the issue was that TRE_URE2 did not follow its process for granting new access rights to CCAs, along with maintaining the completeness and accuracy of access rights as required. In particular, the TRE_URE2 employee mistakenly assumed that all the contractors had electronic access rights because some of the contractors had authorized physical access. TRE_URE1 determined the issue duration to be for approximately seven months, from the earliest date upon which TRE_URE2 should have updated its access lists to reflect the change in personnel access rights until the date TRE_URE2 changed the IED password, resulting in TRE_URE2’s access lists again accurately reflecting the access rights of the seven contractors. | This issue posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. TRE_URE2 failed to ensure accountability for all user activity and minimize the risk of unauthorized system access. The password provided electronic access to IEDs at TRE_URE2 CCAs. Further, at the time the seven contractors received unauthorized electronic access, five of the seven had not completed the requisite cyber security training and personnel risk assessment (PRA) to receive such access. The remaining two contractors had neither valid physical nor electronic access rights. Finally, all seven contractors retained such unauthorized electronic access rights for approximately seven months. Balanced against this risk was the fact that to use the IED password in question, an individual must be physically inside each CCA’s Physical Security Perimeter (PSP). Second, TRE_URE2 employs defense-in-depth to secure CCAs, including PSPs, Electronic Security Perimeters, firewalls and other protections. Finally, TRE_URE2 subsequently granted electronic access rights to five of the seven contractors, including access to the IED password and associated CCAs at issue here. No harm is known to have occurred. TRE_URE1 considered TRE_URE2’s compliance history in determining that this issue is appropriate for Find, Fix, and Track (FFT) treatment. TRE_URE1’s compliance history constituted an aggravating factor, increasing the risk determination and making this issue not appropriate for Compliance Exception treatment, even though it is a self-logged noncompliance. TRE_URE1 determined that TRE_URE2’s compliance history should not serve as a basis for applying a penalty as TRE_URE2 has proposed several measures to prevent future recurrence of these issues. In particular, TRE_URE2 plans to prevent future recurrence of this issue by using a technical solution that stores passwords in an intermediate system and requires two-factor authentication to access accounts. | To mitigate this issue, TRE_URE2 has completed the following actions: 1) changed the IED password; 2) granted access rights to the contractors in question and updated the access records to reflect this change; 3) verified that the electronic access records accurately reflect the electronic authorizations for the seven contractors in question; and 4) implemented an access system that stores passwords such that CCA passwords can no longer be shared or exchanged by users, and requires two-factor authentication for access. TRE_URE1 has verified the completion of all mitigation activity.
2016-03-31 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2016015484 | CIP-006-3c | R1; R1.6 | NPCC_URE1 self-reported that it had a possible issue of CIP-006-3c R1.6 and R1.6.2. A supervisor employed by NPCC_URE1’s security vendor providing guard services to the control center was performing routine shift checks when he informed the security guard at the control center that he would assume the post while she went to the restroom. The security guard initially challenged the supervisor, as the supervisor was not on the list of personnel approved for access. However, when the supervisor further instructed the guard to take a break and use the restroom, the guard did not challenge the supervisor. The supervisor remained alone at the guard’s post in the control center lobby until the security guard returned from the restroom. The supervisor then proceeded unescorted into the control center to use the restroom as well. The supervisor remained unescorted within the control center for a period of 15-20 minutes. | This issue posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Specifically the violation is being considered a moderate risk due to the potential risks presented by having an unauthorized person unescorted within the control center. Although the unescorted person in this case was an employee with NPCC_URE1’s security vendor, he did not have the proper background check or training, and while he only went to the restroom within the control center, there was no way of knowing whether or not he had any malicious intent. NPCC determined that the issue was appropriate for FFT treatment because NPCC_URE1 had some further controls past the security guard post that could have prevented the supervisor from causing any harm if he intended, including locked doors that prevent access to the control rooms and computer rooms. Video surveillance and card access records were reviewed after the fact and it was determined that the supervisor had not accessed any area in the control center beyond the restroom. Additionally, the technical support team confirmed that no access attempts were made to the operational computer network. No harm is known to have occurred. | To mitigate this issue, NPCC_URE1: 1) modified the security post orders at the control center to indicate that the supervisor is not allowed unescorted access to the control center; 2) required the security vendor to provide corrective actions. The corrective actions provided by the security vendor included a briefing with all supervisors and guards regarding the proper control center visitor and access control protocols. The vendor also prohibited the supervisor and guard involved in this event from working at the control center in the future; and 3) added additional card access to restrict entry in the control center to further prevent unauthorized individuals from gaining unescorted access to the control center. NPCC has verified completion of all mitigating activity.
2016-02-29 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2014014204 | CIP-007-3a | R1 | RFC_URE1 submitted Self-Reports stating that it had issues of CIP-007-3a R1. First, RFC_URE1’s change management program requires pre- and post-test procedures on comparable assets where possible for significant changes to existing Cyber Assets within the Electronic Security Perimeter. RFC_URE1 defines a “significant change” as installation of new software or major version upgrades. A RFC_URE1 employee intended to inspect an asset to see if a certain software utility was installed on the asset. Rather than merely inspect the system (as he intended to do), the employee inadvertently installed the software on the asset due to a typo on the command line. More specifically, the employee accidentally executed the install when he entered a command with the improper suffix. Because the employee did not intend to install the software, he did not execute test procedures prior to the installation. RFC_URE1 discovered the installation on through its detective control activities and immediately uninstalled the software that same day. RFC_URE1 executed pre-test procedures prior to the reinstallation, and the pre-test procedures verified that there was no degradation of security controls prior to the scheduled change, and thus no actual harm is known to have occurred. Second, RFC_URE1 identified four untracked instances of web browser software on one CIP Physical Access Control System (PACS). The asset at issue allows security guards to monitor the physical security system and thus this function would not be available if a patch caused the system to fail. RFC_URE1 learned that some of the web browser instances auto-updated (self-patched) at least once for a period of approximately five months, applying patches from the vendor. Where the web browser auto-updated, RFC_URE1 did not execute test procedures as required for significant changes applied to the PACS asset. As part of other control activities, RFC_URE1 performed daily compliance scans of the asset and there were no signs of degradation of security controls during the scope of this report. Thus, no actual harm is known to have occurred. The violation occurred as a result of human error and lack of controls for this specific application. The web browser is self-contained and does not register itself as “installed” in the operating system and RFC_URE1’s application inspection tools did not look for standalone executables in end-user directories. Thus, there were gaps in preventative measures such as blocking the application on PACS assets and end-user directories and in the additional controls to detect the application. The issue began the first time the patches auto-updated, through the date RFC_URE1 completed its Mitigation Plan. | This issue posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Regarding the first instance, the fact that the individual did not immediately realize that he inadvertently installed the software on the asset indicates a lack of awareness that could lead to other violations in the future. However, RFC_URE1 detected the unapproved installation within four days, which is 31 days earlier than required by CIP version 5 standards, specifically CIP-010 R2. Additionally, while installing untested software on an asset could cause vulnerabilities in the system or could cause the system to fail, RFC_URE1 regularly uses this particular software for troubleshooting and has verified that it does not affect the security controls on the asset. Regarding the second instance, RFC_URE1 did not effectively manage features such as auto-updates on patches which poses a risk to the bulk power system that patches will be automatically installed without RFC_URE1’s knowledge and those undetected patches could cause vulnerabilities in the system or could cause the system to fail. However, the patches related to Chrome would have only been related to internet browsing rather than changing the ports and services on the machine, and thus would not create the serious vulnerabilities that could come with enabling unnecessary ports. Additionally, the Google Chrome software was initially installed prior to the asset becoming designated as “CIP” and once the asset was designated as CIP, it had all of the CIP required protections. ReliabilityFirst determined that the issue was appropriate for FFT treatment because the issue posed only moderate risk to the reliability of the bulk power system and RFC_URE1 detected the issue quickly. No harm is known to have occurred. | Regarding the first issue, RFC_URE1 immediately uninstalled the software upon identification and executed pre-test procedures prior to the reinstallation. To further mitigate this issue, RFC_URE1: 1) investigated the inadvertent installation and documented the root cause; and 2) counseled the employee on the importance of NERC CIP compliance, test procedures, and significant changes to any Cyber Asset in scope for CIP Standards. Regarding the second issue, to mitigate the issue, RFC_URE1: 1) interviewed personnel, documented the instance, and identified the root cause; 2) provided counselling focusing on the proper procedures and controls when dealing with Cyber Assets in scope for CIP standards; 3) implemented firewall rules blocking existing PACs cyber assets located outside an Electronic Security Perimeter (ESP) and physical security perimeter (PSP) from directly accessing the internet; and 4) added a step to RFC_URE1’s current ‘Pre-CIP’ process to ensure controls are implemented for PACs cyber assets located outside an ESP and PSP ensuring there is no internet connectivity. ReliabilityFirst has verified the completion of all mitigation activity.
2016-02-29 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2014013449 | CIP-007-3a | R3.1 | RFC_URE1 submitted a Self-Report stating that it had an issue of CIP-007-3a R3.1. RFC_URE1 failed to implement security patch management programs for tracking, evaluating, testing and installing applicable cyber security software patches for all Cyber Assets within the Electronic Security Perimeter (ESP). This issue relates to three missed patches. RFC_URE1’s patch program involves two main controls. The primary control is a subscription to a third party alerting service which provides notifications when new security patches or security upgrades are released. Then, RFC_URE1 cross-references the list of security patches and security upgrades from the third party alerting service with another source such as vendor notification lists, or US-CERT. The first missed patch relates to a security patch for a Domain Name Service product. RFC_URE1 did not receive notification of the security patch for the DNS product by its third party vendor even though the service was configured to identify and notify RFC_URE1 of any new security patches released for this product. Additionally, although RFC_URE1 routinely checks US-CERT for available patches as a secondary control, US-CERT also did not list the availability of this patch. RFC_URE1 discovered this patch when verifying compliance of new DNS assets being deployed in the ESP. RFC_URE1 assessed and documented the applicability of the patch within 30 days of discovering the patch. As a result, RFC_URE1 did not complete a documented assessment of that patch within 30 calendar days after it was released by the vendor. RFC_URE1 has since subscribed to the vendor’s notification system for new security patches or security upgrades. The second missed patch relates to a security patch for a System Management Homepage product. RFC_URE1 registered this product with its third party patch alerting service, but the service failed to notify RFC_URE1 of this patch when it was released by the vendor. Additionally, although RFC_URE1 routinely checks US-CERT for available patches as a secondary control, US-CERT did not specify that a patch for this product was released by the vendor. RFC_URE1 identified this patch as part of vulnerability assessments. RFC_URE1 completed a documented assessment within two days of identifying the patch availability. As a result, RFC_URE1 did not complete a documented assessment of that patch within 30 calendar days after it was released by the vendor. RFC_URE1 has since subscribed to the vendor’s notification system for new security patches or security upgrades. The third missed patch related to an security patch for an Advanced Management Module. Although the third party service was configured to identify and notify RFC_URE1 of any new security patches released for this product, the service did not identify the patch until four months later. Additionally, although RFC_URE1 routinely checks US-CERT for available patches as a secondary control, US-CERT did not specify that a patch for this product was released by the vendor. Moreover, at the time the patch was released, RFC_URE1 was subscribed to the vendor’s notification system. However, the vendor’s notification system did not send notification of this security patch. Upon notification of the patch, RFC_URE1 reviewed and documented the applicability of the patch within 30 days of discovery of the patch. The issue began on the date of the first missed patch, to the date RFC_URE1 completed its assessment of the latest missed patch. | This issue posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Regarding the first missed patch, the patch fixed vulnerabilities that when exploited could have affected the availability of the DNS assets. The vulnerabilities could be exploited to disclose potentially sensitive information or cause a “denial of service.” RFC_URE1’s existing security controls partially mitigated this potential risk. These DNS assets are not accessible from outside the RFC_URE1 network and only accept DNS queries from inside the ESP. Additionally, administration of these DNS assets is only permitted from specific whitelisted assets from within the RFC_URE1 environment. Regarding the second missed patch, the patch addressed a privilege escalation vulnerability, which, if exploited by malicious parties, could be used to affect the availability, integrity, or confidentiality of the affected Cyber Assets. However, the vulnerability allows for escalation of local System Management Homepage accounts, and because RFC_URE1’s installation of System Management Homepage uses Active Directory for authentication, there were no local accounts to exploit. Additionally, the accounts that have access to the System Management Homepage via Active Directory were already at an elevated-privilege level, so there was no further escalation available. Regarding the third missed patch, the patch addressed denial of service and information disclosure vulnerabilities. However, RFC_URE1’s existing security controls partially mitigated the potential impact of these vulnerabilities because communication to these assets can be initiated only from jump servers that require two-factor authentication. Accordingly the potential risk posed to the Bulk Electric System by these instances was moderate. ReliabilityFirst determined that the issue was appropriate for FFT treatment because the issue posed only moderate risk to the reliability of the bulk power system, RFC_URE1 discovered the first two issues through its internal controls, and RFC_URE1 quickly mitigated the issues upon discovery. No harm is known to have occurred. | To mitigate this issue, RFC_URE1: 1) documented and evaluated the missed patches; and 2) subscribed to the two vendors’ notification systems to which it was not previously subscribed. ReliabilityFirst has verified the completion of all mitigation activity.
2016-02-29 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2014014205 | CIP-007-3a | R3.1 | RFC_URE1 submitted a Self-Report stating that it had an issue of CIP-007-3a R3.1. RFC_URE1 failed to implement security patch management programs for tracking, evaluating, testing and installing applicable cyber security software patches for all Cyber Assets within the Electronic Security Perimeter. Specifically, an Operating System security patch was available from the vendor. RFC_URE1 formally reviewed the patch 25 days later to assess its applicability to the RFC_URE1 environment, but, due to human error, did not document the assessment until 32 days after the patch became available. Thus, RFC_URE1 failed to document the assessment within 30 days of availability of the patch. The issue began on the date RFC_URE1 was required to document the assessment, to the date RFC_URE1 documented is assessment of availability of the patch. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. This is a mere documentation issue. RFC_URE1 assessed the patch within 30 days of its availability, but merely failed to formally document its assessment within the 30-day deadline. Additionally, the vulnerability mitigated by the patch did not exist in the RFC_URE1 environment. ReliabilityFirst determined that the issue was appropriate for FFT treatment because the issue posed only minimal risk to the reliability of the bulk power system and RFC_URE1 quickly discovered and mitigated the issue. No harm is known to have occurred. | To mitigate this issue, RFC_URE1 documented the applicability of the patch on the 32nd day of the patch availability. ReliabilityFirst has verified the completion of all mitigation activity.
2016-02-29 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2014014409 | CIP-007-3a | R3 | RFC_URE1 submitted Self-Reports, stating that it had issues of CIP-007-3a R3. First, certain Critical Cyber Assets (CCAs) at RFC_URE1 run an operating system. In order to limit access to privileged accounts on these CCAs, RFC_URE1 uses a utility, which allows RFC_URE1 to limit elevated access. The root cause of the violation stems from RFC_URE1’s process for tracking patches for the utility. Specifically, RFC_URE1 did not track security patches for the utility separately from the operating system because the utility is typically updated as part of core operating system patches. RFC_URE1's vendor notified RFC_URE1 that it was reviewing a utility patch for compatibility with its software. This led RFC_URE1 to conduct its own investigation and discover that the patch could have been documented and applied to a limited number of RFC_URE1’s CCAs that utilized the utility. RFC_URE1 formally documented this security patch for applicable CCAs. Second, RFC_URE1 identified four untracked instances of web browser software on one CIP Physical Access Control Systems (PACS). RFC_URE1 learned that some of the web browser instances auto-updated (self-patched) at least once for a period of approximately five months, applying patches from the vendor. After learning of the web browser instances, RFC_URE1 reviewed available patches during the report period and identified five web browser patches that were not identified or documented within the required 30 days of availability for the asset. The violation occurred as a result of human error and lack of controls for this specific application. The web browser is self-contained and does not register itself as “installed” in the operating system and RFC_URE1’s application inspection tools did not look for standalone executables in end-user directories. Thus, there were gaps in preventative measures such as blocking the application on PACS assets and end-user directories and in the additional controls to detect the application. The first issue began on the date RFC_URE1 was required to document the security patch, to the date RFC_URE1 documented the security patch. The second issue began on the first time the patches auto-updated, through the date RFC_URE1 completed its Mitigation Plan. | This issue posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Regarding the first instance, the unpatched utility software on RFC_URE1’s CCAs left the potential for compromise on these devices. The risk was partially mitigated because the patch was not as critical because of the nature of the utility software, which requires an initial login to perform its duties. Thus, only authorized users to the operating system itself would have been able to exploit the flaw that the patch fixed. Additionally, the physical console and remote access tools are both protected by two factor authentication. Also, only the utility package was vulnerable. All other aspects of the systems were patched as part of releases. Regarding the second instance, not effectively managing features such as auto-updates on patches poses a risk to the Bulk Electric System that patches will be automatically installed without RFC_URE1’s knowledge and those undetected patches could cause vulnerabilities in the system or could cause the system to fail. However, the patches related to the web browser would have only been related to internet browsing rather than changing the ports and services on the machine, and thus would not create the serious vulnerabilities that could come with enabling unnecessary ports. Additionally, the web browser software was initially installed prior to the asset becoming designated as “CIP” and once the asset was designated as CIP, it had all of the CIP required protections. ReliabilityFirst determined that the issue was appropriate for FFT treatment because the issues posed only moderate risk to the reliability of the bulk power system and the issue does not indicate systemic issues or programmatic weaknesses. No harm is known to have occurred. | To mitigate this issue regarding the system security patch, RFC_URE1: 1) documented the security patch to end the potential violation period; 2) incorporated a verification step into RFC_URE1’s list of security patch identification sources to identify security patches released for separately-installed applications for the operating system; and 3) reviewed CCAs running an installation of the operating system to identify other applications which may also share a separate update path. To mitigate this issue regarding the web browser software, RFC_URE1: 1) interviewed personnel, documented the instance, and identified the root cause; 2) provided counselling focusing on the proper procedures and controls when dealing with Cyber Assets in scope for CIP standards; 3) implemented firewall rules blocking existing PACs cyber assets located outside an Electronic Security Perimeter (ESP) and physical security perimeter (PSP) from directly accessing the internet; and 4) added a step to RFC_URE1’s current ‘Pre-CIP’ process to ensure controls are implemented for PACs cyber assets located outside an ESP and PSP ensuring there is no internet connectivity. ReliabilityFirst has verified the completion of all mitigation activity.
2016-02-29 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2015014790 | CIP-007-3a | R3 | RFC_URE1 submitted a Self-Certification stating that it had an issue of CIP-007-3a R3. The noncompliance relates to two security patches. Two security patches were made available but were not documented within the required thirty day calendar period. Due to human error, the subject matter expert assigned for the technology failed to document the assessment of applicability for both security patches. Upon discovery, RFC_URE1 promptly assessed and documented the security patches. Both patches were deemed applicable to the RFC_URE1 environment. The patches were documented twenty three days past the thirty-day requirement. The issue began on the date RFC_URE1 was required to document the assessment of the security patches, to the date RFC_URE1 documented the assessment of the security patches. | This issue posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The risk was elevated because the first patch applied to a significant number of Critical Cyber Assets. The second patch only applied to three Cyber Assets. The risk was partially mitigated as a result of several factors. First, the vendor rated the risk for both security patches as not high. Additionally, the vulnerabilities mitigated by the patches are not remotely exploitable and RFC_URE1 has multiple layers of physical and logical controls in place to prevent unauthorized access to these systems. With respect to the first patch, the servers are within Electronic Security Perimeter (ESP) in which the ESP firewalls restrict the sources and ports from where the network connection can be initiated. Additionally Intrusion Detection Systems deployed at the perimeter of the ESPs detect known remote exploit attempts. With respect to the second patch, in order for the vulnerability to be exploited, an individual would need local shell access to the server and must have a local account on the server. Additionally, local remote access to a system requires two-factor authentication through an intermediary system. Thus, the likelihood of someone being able to exploit the vulnerabilities mitigated by the patches was reduced. ReliabilityFirst determined that the issue was appropriate for FFT treatment because the issues posed only moderate risk to the reliability of the bulk power system and the issue does not indicate systemic issues or programmatic weaknesses. | To mitigate this issue, RFC_URE1: 1) reviewed and assessed the security patches and documented the applicability of the security patches; and 2) conducted awareness training sessions on RFC_URE1’s policies and controls for NERC CIP-007 R3. ReliabilityFirst has verified the completion of all mitigation activity.
2016-02-29 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2015014791 | CIP-007-3a | R6 | RFC_URE1 submitted a Self-Certification stating that it had an issue of CIP-007-3a R6.2 and R6.5. A patch was applied to two Critical Cyber Assets (CCAs). This patch altered the logging configuration of the CCAs and prevented the logs from being sent to RFC_URE1's alerting tool, which issues automated alerts for detected cyber security incidents and for review of logs of system events related to cyber security. Instead, the CCAs only stored log data locally during the time frame of approximately 8 months, and thus RFC_URE1’s security monitoring controls did not issue alerts for Cyber Security Incidents as required by CIP-007-3a R6.2 and RFC_URE1 did not review logs of systems events as required by CIP-007-3a R6.5. Prior to implementing the patch, RFC_URE1 performed test procedures on the CCAs, but RFC_URE1’s procedures did not sufficiently define the step for verifying the logging configuration. The test procedure called for verifying that the main configuration file for logging was properly configured as well as the remote logging destination. However, RFC_URE1 determined that another configuration, not defined in the test procedure, must be enabled to allow for remote logging. RFC_URE1 fixed the logging issue. RFC_URE1 did not detect this logging issue earlier because it was using a manual reconciliation process to verify that all cyber assets within Electronic Security Perimeters (ESPs) were sending logs to the automated alerting tool and, because of human error, the logs for these two CCAs were missed in the reconciliation. Subsequently, RFC_URE1 implemented automated alerting, but because these two CCAs were not captured in the manual log reconciliation that acted as the baseline for the automation, they were not caught in the automated alerting. RFC_URE1 did retain the local logs on the two CCAs for the entire 8 month period, and thus complied with all of the other requirements of CIP-007 R6. RFC_URE1 subsequently reviewed the local logs that were not sent to the automated alerting tool during the affected time period and found that there were no security alerts that would have been generated during this time frame and no indication of security incidents that would require follow-up. The issue began on the first date RFC_URE1 did not retain logs for the two CCAs at issue, to the date RFC_URE1 completed its Mitigation Plan. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. RFC_URE1 has multiple layers of security for access to the two CCAs that were not sending log data during this timeframe. The CCAs were not physically or logically accessible from outside the Physical Security Perimeter or ESP and RFC_URE1 monitored all systems needed as intermediary devices for obtaining access to the two cyber assets that were not logging. The combination of other security monitoring controls provided situational awareness for potential cyber events during the period in which the local logs were not being sent to the automated alerting tool. ReliabilityFirst determined that the issue was appropriate for FFT treatment because the issue posed only minimal risk to the reliability of the bulk power system. No harm is known to have occurred. | To mitigate this issue, RFC_URE1: 1) corrected the configuration on the two affected cyber assets and verified that they are properly sending audit log data to the automated alerting tool; 2) updated the baseline list of cyber assets that should be sending audit log data to the automated alerting tool to ensure that any lapses in audit logs are identified automatically as part of the automated log reconciliation; 3) updated the test procedures for the affected cyber assets to ensure that the procedure verifies all settings required to properly send audit log data to the automated alerting tool; 4) updated the Log Management Standard, which defines logging requirements for cyber assets, to clarify the requirements for cyber assets to properly send audit log date to the automated alerting tool; and 5) conducted training for systems personnel who are responsible for following those procedures and for verifying the completion of those procedures. ReliabilityFirst has verified the completion of all mitigation activity.
2016-02-29 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2015014617 | CIP-007-3a | R7 | RFC_URE1 submitted a Self-Report stating that it had an issue of CIP-007-3a R7. A Critical Asset, a Storage Switch, failed and was replaced by the vendor. The vendor technician left RFC_URE1’s premises with the original asset before RFC_URE1 erased the data in the device. The RFC_URE1 subject matter expert realized the mistake while closing out the incident. RFC_URE1 notified the technician the next day and requested it return the asset. The vendor returned the asset to RFC_URE1 the same day. At that time, RFC_URE1 reset the asset to factory default settings as required in RFC_URE1’s documented procedures. The root cause of the noncompliance was human error in not following RFC_URE1’s procedure to reset the asset to factory default settings prior to the vendor removing the asset from the premises. The issue began on the date RFC_URE1 was required to reset the asset to factory default settings, to the date RFC_URE1 reset the asset to factory default settings. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The asset did not contain sensitive information that could have been used to compromise RFC_URE1’s systems and RFC_URE1 discovered and fixed the issue within one day. ReliabilityFirst determined that the issue was appropriate for FFT treatment because the issue posed only minimal risk to the reliability of the bulk power system. No harm is known to have occurred. | To mitigate this issue, RFC_URE1: 1) interviewed the subject matter expert, documented the incident, and identified the root cause; 2) provided counseling to the subject matter expert focusing on the proper procedures and controls when dealing with Cyber Assets in scope for CIP-007-3 R7.1; and 3) conducted awareness training sessions for targeted groups on RFC_URE1 policies and controls for NERC CIP-007 R7. ReliabilityFirst has verified the completion of all mitigation activity.
2016-01-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2014014522 | CIP-007-3a | R5 | RFC_URE1 submitted a Self-Report to ReliabilityFirst stating that it was in violation of CIP-007-3a R5 because it did not use a password for a service account on an application hosted on a Critical Cyber Asset. RFC_URE1 determined that its production application no longer required a password to access the service account (which previously was required). The service account is used for support and maintenance of the software, and does not provide any direct physical access to the Cyber Asset. RFC_URE1 discovered that a password was no longer required to access the service account when a RFC_URE1 staff member, believing he was logging into the test system account (for which no password is required), instead logged into the production system (distinguished by the banner on top of the application page). Upon this discovery, the RFC_URE1 staff member notified management that the service account no longer required a password for entry. RFC_URE1 investigated the issue and determined that during normal software administration activities, support personnel did not realize that the authentication parameter had been changed in the production system, left the parameter as it was, and propagated the authentication parameter configuration to the other Inter-Control Center Communications Protocol (ICCP) servers. Specifically, following discussions with the Applications Manager and a review of its authentication parameters, RFC_URE1 determined that the local configuration file for a Cyber Asset had been misconfigured, thereby allowing access to the service account without an associated password. Therefore, the root cause of this noncompliance was a failure to follow established test procedures, which require an authentication method and the associated testing of a login with password. The duration of this noncompliance is from the date RFC_URE1 initiated the data center migration during which the noncompliance occurred, to the date RFC_URE1 modified the user interface configuration to ensure a password is required to log into the service account. | This issue posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the service account is used for support and maintenance of the software application, and does not provide any direct physical access to the Cyber Asset. Second, although the password to the service account was not enabled, RFC_URE1 was protected by defense-in-depth security measures. Specifically, to access the service account, a user would first have to be within RFC_URE1’s Electronic Security Perimeter (ESP) to have access to the application. Additionally, once within the ESP, the user would need to have: (1) proper network access control rights; (2) access rights to the proper security group specific to the application; (3) the client installed on his or her computer to be able to launch the application; and (4) the correct local configuration on file on his or her computer to begin and authenticate. ReliabilityFirst determined that the issue was appropriate for FFT treatment because the RFC_URE1 employee who discovered the issue immediately reported it and RFC_URE1 conducted a thorough investigation and root cause analysis in response. ReliabilityFirst determined that the noncompliance was voluntarily, promptly, and effectively mitigated. RFC_URE1’s mitigation actions will prevent further violations by ensuring that a password is required to log into the application and implementing internal controls defining how configuration changes should be executed during the course of any software or other upgrades to its system. No harm is known to have occurred. | To mitigate this issue, RFC_URE1: 1) repaired the user interface configuration to ensure a password is required to log into the service account; 2) defined a custom display to reduce the choices for the password parameter setting and removed the “no password required” option from the view panel; 3) created a set of Work Level Instructions defining how configuration changes should be executed during the course of any software or other upgrade to the ICCP system; and 4) trained appropriate staff on the implementation of the new Work Level Instructions ReliabilityFirst has verified the completion of all mitigation activity.
2016-01-28 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2014013991 | CIP-007-3a | R8 | During a Compliance Audit, SERC determined that SERC_URE1 had an issue with CIP-007-3a R8. SERC_URE1 did not demonstrate that its agent had performed a Cyber Vulnerability Assessment (CVA) of all Cyber Assets within the Electronic Security Perimeter (ESP) at least annually. SERC_URE1's agent grouped the Cyber Assets used to perform its function and conducted the annual CVAs against a representative Cyber Asset for each grouping. The representative Cyber Asset from each grouping had the baseline configuration (or golden image) for the group of Cyber Assets it represented. As a result, SERC_URE1's agent only conducted the CVA against a representative Cyber Asset for each group of Cyber Assets, and did not perform the CVA against all of the Cyber Assets within the ESP. The root cause of the issue was an inadequate design of the CVA process to address the requirement to include all Cyber Assets. This issue lasted from the first day after SERC_URE1's agent failed to complete the annual CVA on all Cyber Assets within the ESP through seven days later, when SERC_URE1's agent completed a CVA on all Cyber Assets within the ESP. SERC_URE1's agent completed all mitigating activities approximately six months later. | This issue posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC_URE1's agent’s failure to conduct a CVA on all Cyber Assets within the ESP could have resulted in vulnerabilities, such as open ports and services or active default accounts, going undetected on Cyber Assets within the ESP, leaving them available for exploit by malicious individuals. However, the representative Cyber Assets (and associated golden images) were representative of the images deployed on all Cyber Assets within the ESP. SERC_URE1's agent deployed technical controls using virtual equipment and software that would prevent unauthorized changes to the virtual Cyber Assets, which SERC_URE1's agent created off the host machine, thereby reducing the risk that SERC_URE1's agent’s approach would miss vulnerabilities on the Cyber Assets for which SERC_URE1's agent did not directly conduct CVAs. SERC_URE1's agent had protected the Cyber Assets, including the host machines and virtualized workstations, within an ESP and Physical Security Perimeter. No harm is known to have occurred. SERC considered SERC_URE1’s CIP-007 R8 compliance history in determining the disposition track. SERC determined that SERC_URE1’s compliance history should not serve as a basis for applying a penalty and that this issue was appropriate for FFT treatment. The prior noncompliance involved a failure to verify that only ports and services required for operations were enabled on a total of six Cyber Assets. Although the instant issue involved a failure to conduct a CVA against all Cyber Assets within the ESP, SERC_URE1's agent conducted a CVA against a representative Cyber Asset for each grouping of Cyber Assets and compared it to the baseline configuration (or golden image) for that group of Cyber Assets. SERC_URE1's agent also deployed technical controls that would prevent unauthorized changes to the virtual Cyber Assets, thereby reducing the risk that SERC_URE1's agent’s approach would miss vulnerabilities on the Cyber Assets for which SERC_URE1's agent did not directly conduct CVAs. The mitigating activities for the prior violation would not have prevented the instant issue. | To mitigate this issue, SERC_URE1's agent: 1) conducted CVAs on all of the Cyber Assets; and 2) consolidated the CIP-007 R8 CVA process to ensure consistency across its business units to test all applicable Cyber Assets as required.
2016-01-28 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2014014291 | CIP-002-3 | R3; R3.3 | During a Compliance Audit, SPP RE determined that SPPRE_URE1 had two issues with CIP-002-3 R3.3. SPPRE_URE1’s front-end processor (FEP) terminal servers and associated Ethernet server switches located within the primary operations center (POC) and backup operations center (BOC) were neither identified nor fully protected as Critical Cyber Assets because they were not deemed essential to the operation of Critical Assets. The FEP terminal servers had previously been identified and protected as Critical Cyber Assets. However, due to reconfigurations of communication networks and recommendations from SPPRE_URE1’s supervisory control and data acquisition/energy management system (SCADA/EMS) vendor, the FEP servers were relocated from the Electronic Security Perimeter (ESP) to a demilitarized zone (DMZ) network, reclassified as non-Critical Cyber Assets, and taken off the Critical Cyber Asset list. The FEP servers were not deemed essential to the operation of Critical Assets because they are communication devices, which do not run on SCADA software, and the POC and BOC were capable of operations through manual input without the FEP servers. When the Ethernet server switches were deployed, SPPRE_URE1 believed that these the switches could not be Critical Cyber Assets because they are Layer 2 switches and thus unable to perform any routing functions. Notwithstanding, the switches have an Internet Protocol (IP) address, which is used to communicate between the POC and BOC, an explicit characteristic of a Critical Cyber Asset under CIP-002-4 R3.2. The switches are necessary to allow the Critical Cyber Assets comprising the SCADA/EMS to communicate with each other and with the operator consoles in the POC and BOC. The FEP terminal servers and the associated Ethernet server switches are essential to the operation of SPPRE_URE1’s POC due to their functions of real time data support and communications to the POC via routable protocol. The duration of the FEP issue was approximately 30 months. The duration of the issue involving the Ethernet server switches was approximately 14 months. The root cause of the two issues was a misenterpretation of CIP-002-3 R3.3, which led to SPPRE_URE1’s failure to recognize the FEP servers and associated server switches as Critical Cyber Assets. | This instance of noncompliance posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). A violation of CIP-002 R3 has the potential to affect the reliable operation of the BPS by decreasing the likelihood that a Responsible Entity will identify and afford the protections of the CIP Standards to all Critical Cyber Assets. The server switches resided inside SPPRE_URE1’s ESP and thus were afforded all the Critical Cyber Asset protective measures protected per CIP-007-3. Regarding the FEP terminal servers, the risk to the BPS was reduced because all electronic traffic entering the ESP from the FEP terminal servers was required to pass through a firewall. No actual harm occurred as a result of these issues. | To mitigate the minimal risk instance of noncompliance, SPPRE_URE1: 1) moved the FEP terminal servers and associated Ethernet server switches inside the ESP, and updated its ESP diagram to show such devices; 2) reclassified the FEP terminal servers and associated Ethernet server switches as Critical Cyber Assets, and updated its list of Critical Cyber Asset to reflect the reclassification; and 3) ensured that the FEP terminal servers and associated Ethernet server switches are protected as Critical Cyber Assets. SPP RE has verified the completion of all mitigation activity.
2016-01-28 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2015014982 | CIP-005-3a | R1 | WECC determined that WECC_URE1, as a Responsible Entity, had an issue of CIP-005-3a R1. WECC_URE1 failed to identify and document all access points to the perimeter of one ESP, resulting in 30 Critical Cyber Assets (CCAs) within the ESP inheriting mixed trust configurations. WECC reviewed network diagrams, Cyber Asset inventory spreadsheets with IP and subnet information, and Access Point and Cyber Asset configuration files, and discovered a mixed trust configuration. WECC also conducted interviews and site tours with the WECC_URE1 subject matter experts (SMEs) and determined that WECC_URE1 failed to ensure that every Critical Cyber Asset resides within an Electronic Security Perimeter (ESP) and failed to identify and document the ESP and all access points to the perimeter. Specifically, WECC_URE1 employed CCA switches with layer-2 protocol that were connected to several interconnected CCAs with dual network interface connection (NIC). The two NIC interfaces were simultaneously connected to networks of differing trust levels; i.e., the ESP with applicable CIP protections (trusted), and a non-CIP device (not trusted). The mixed trust mode inadvertently resulted in a number of CCAs, within the ESP, inheriting mixed trust configurations. WECC Enforcement reviewed the audit findings and determined that WECC_URE1 has a remediated issue of CIP-005-3a R1, for its failure to identify and document all access points to the perimeter of one ESP, resulting in 30 CCAs within the ESP inheriting mixed trust configurations. The root cause of WECC_URE1's noncompliance is a lack of compliance understanding related to the protections required by the Standard for ESP access points. | This remediated issue posed a moderate risk but did not pose a serious or substantial risk to the reliability of the bulk power system. Specifically, WECC_URE1 did not identify and document the Electronic Security Perimeter and all access points to the perimeter for a number of CCAs. Failing to ensure that every CCA and associated non-critical Cyber Assets reside within an ESP, and to identify and document all access points into the ESPs, could result in possible compromise to the affected Cyber Assets, due to minimum cyber security protections not being afforded, including access controls. The compromise of multiple unprotected CCAs by an adversary could potentially result in the unavailability, instability and/or severe damage to the bulk power system. As a compensating measure, WECC_URE1 implemented a defense-in-depth architecture employing several levels of physical security controls to restrict unauthorized physical access to the affected Cyber Assets. In addition, WECC_URE1 implemented perimeter firewalls to the access points to the ESP. No harm was known to have occurred. | To mitigate this issue, WECC_URE1 disabled all its mixed-trust ports being used for remote access and management of servers. WECC has verified the completion of all mitigation activity.
2016-01-28 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2015014983 | CIP-005-3a | R2 | WECC determined that WECC_URE1, as a Responsible Entity, had an issue of CIP-005-3a R2. A WECC auditor noticed one of WECC_URE1’s subject matter experts (SMEs) establish an interactive remote access (IRA) connection via remote desktop protocol (RDP), from a Cyber Asset residing outside of the ESP, to a Critical Cyber Asset (CCA) residing within the ESP, without using strong technical controls. To access the device, the SME did not use multi-factor authentication or procedural controls. The direct communications access to the CCAs from outside the ESP was a result of a mixed trust configuration of a number of CCAs with dual-NIC interfaces simultaneously connected to the trusted ESP and an untrusted management network outside of the ESP. WECC determined that WECC_URE1 had a remediated issue of CIP-005-3a R2, for its failure to implement strong procedural or technical controls at the access points of its PSP, and to ensure authenticity of the accessing party, where external interactive access into the ESP has been enabled. The root cause of WECC_URE1's noncompliance is a lack of compliance understanding related to the protections required by the Standard for remote electronic access to the ESP. | This remediated issue posed a moderate risk but did not pose a serious or substantial risk to the reliability of the bulk power system. Specifically, WECC_URE1 failed to implement strong procedural or technical controls at access points to ensure authenticity of the accessing party. This violation could potentially result in unauthorized access to Cyber Assets by an adversary, and in the unavailability, instability and/or severe damage to the bulk electric system as a result of misuse. As a compensating measure, WECC_URE1 implemented a defense-in-depth architecture of physical security controls that restricts unauthorized physical access to the affected Cyber Assets and additional perimeter firewalls, in excess of the identified access points to the ESP. No harm was known to have occurred. | To mitigate this issue, WECC_URE1 disabled all devices being used for remote access. To mitigate this issue, WECC_URE1 will also complete the following mitigation activities: 1) validate the number of assets in scope; 2) explore technical solutions to enforce an additional form of authentication; 3) determine necessary changes to move the workstations into the ESP; 4) implement the determined solution for either enforcing multi-factor authentication, or moving the assets into an ESP; and 5) modify the EMS Electronic Access Control procedure to clarify that all interactive remote access to ESPs, including sessions that emanate from within a PSP, must enforce multi-factor authentication.
2015-11-30 | Florida Reliability Coordinating Council (FRCC_URE1) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC_URE12013013127 | CIP-007-3a | R8 | During a Compliance Audit, FRCC_URE1 determined that FRCC_URE1_URE had an issue of CIP-007-3a R8. FRCC_URE1_URE documentation supplied was insufficient to demonstrate that it performed a Cyber Vulnerability Assessment (CVA) of all Cyber Assets within the Electronic Security Perimeter (ESP) at least annually for one year. Specifically, the audit team reviewed the CVA and determined that for some Cyber Assets, FRCC_URE1_URE tested a single asset that was considered a representative image and applied the CVA results of that image to similar devices thereby not performing a CVA for all Cyber Assets inside the ESP as specified in CIP-007-3a R8. FRCC_URE1_URE only performed the CVA on approximately three percent of its Cyber Assets using this method. The root cause of the noncompliance was a less than adequate design of the CVA to address the entire scope of the requirement to include all Cyber Assets. | This issue posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. FRCC_URE1 determined that the noncompliance posed a moderate risk because if a vulnerability scan is executed on the image it will not identify potential risks with actual CCAs. FRCC_URE1 determined that the issue was appropriate for FFT treatment because the risk was reduced as all the Cyber Assets were afforded all other protections of the CIP Standards. No harm is known to have occurred. | To mitigate this issue, FRCC_URE1_URE: 1. performed a CVA for all Cyber Assets as well as the representative golden image, and 2. consolidated its CVA processes into one consistent process for the entire organization. FRCC_URE1 has verified the completion of all mitigation activity.
2015-10-29 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2014013869 | CIP-007-1 | R8 | MRO_URE1 self-reported that it had an issue of CIP-007-1 R8. Subsequent to submission of the Self-Report, a second issue was detected during a compliance audit. The first issue that was self-reported relates to the performance of a Cyber Vulnerability Assessment (CVA) and the requirement that MRO_URE1 scan all available ports. During MRO_URE1's CVA, it only scanned the most commonly used ports instead of all available ports. This same ports and services scanning tool and configuration had been used at MRO_URE1 for years. No documentation exists indicating the basis for the decision to limit the scan to the 1,000 most commonly used ports, other than the fact that it is the utility tool’s default configuration. Failure to understand the reasoning behind the limitation evidences a process weakness and/or lack of understanding of the implemented tool. The second instance, discovered during a compliance audit, was based on MRO_URE1 failing to identify as part of its CVA that an enabled service on 106 workstations was included in the applicable baseline. The CVA gathered the data required to make this determination; however, the information was not adequately reviewed. This enabled service was not included in the list of approved services because MRO_URE1's change control process did not clearly define the process of updating the ports and services documentation after the activation of a new service. The undocumented enabled service was not discovered after the CVA because MRO_URE1 relied upon device-to-device comparisons before and after the change, rather than device-to-baseline comparisons following the change. | This issue posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Specifically, for the first instance, failing to perform the port scan on all 65,535 possible ports limited the ability of the CVA to detect malicious services, resulting in a less effective CVA. The risk was not serious or substantial because MRO_URE1 had a robust installed service documentation process, the applicable services were collected without use of this nmap tool. In addition, the devices were enclosed within an Electronic Security Perimeter (ESP) which limited electronic access to them. For the second instance, the potential risk is related to the decreased value of performing the CVA when the resulting documentation is not thoroughly verified and reviewed. However, the risk was not serious or substantial because, along with being within an ESP, the impacted assets had the additional protection of a local host-based firewall (which is not required by the CIP Standards). The actual risk of the violation was not serious or substantial, as the Entity reported that the service was not automatically enabled (set to manual and not activated). Additionally, a comprehensive review performed by the Entity found no additional discrepancies in the current baseline profiles. No harm is known to have occurred. MRO determined that the issue was appropriate for FFT treatment because this is MRO_URE1's first issue with CIP-007-1 R8, it detected and self-reported the issue, and promptly mitigated the issue. | To mitigate this issue, MRO_URE1: 1) modified the script used to perform a scan on Cyber Assets within the EMS environment to scan for all 65,535 ports available on the TCP and UDP communications protocols. Previously, scans were only performed on the most commonly used ports; 2) under the revised process, the post-installation list of services generated on the Cyber Asset is directly compared to the list of services detailed in the EMS Ports and Services Configuration (baseline) document, and any discrepancies are reconciled; 3) provided coaching regarding the need to reference vendor documentation during the assessments of ports and services on EMS Cyber Assets within the ESP; and 4) EMS System Administrators performed a re-scan of installed and enabled services on Cyber Assets within the EMS environment. The current revision of the EMS Ports and Services Configuration baseline document has been verified to be consistent with the results of this rescan.
2015-10-29 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2014014477 | CIP-007-3a | R3 | SERC_URE1 submitted a Self-Report stating that it had an issue with CIP-007-3a R3.1. SERC_URE1 failed to assess nine security patches for applicability within 30 days of availability. SERC_URE1’s patch management process for workstations required that SERC_URE1 conduct a manual check of the vendor website in order to identify recently released patches, and from that discovery, conduct the assessment for applicability and initiate the deployment. While working to complete a monthly patch review and assessment for workstations, a SERC_URE1 energy management system (EMS) administrator discovered nine security patches that were released approximately one month earlier which SERC_URE1 did not assess as required in its previous month's patch review. The administrator discovered the missed patches assessments in the patch assessment tracking log during the next month's review. The administrator immediately assessed the nine patches and found that three of the patches were not applicable to the secured environment because SERC_URE1 had not installed the involved software on any Cyber Assets. The remaining six patches were applicable and should have been applied to Critical Cyber Assets (CCAs) workstations within the EMS secured environment. These workstations were within multiple separate Electronic Security Perimeters (ESPs) and Physical Security Perimeters (PSPs). The root cause of this issue was lack of a secondary control around the manual process. Although the manual process was documented, there were inadequate controls and reminders to make sure the assessment task was completed timely. This process was implemented in response to previous CIP-007 R3 issues. The effort to search for and conduct the required patch assessments was dependent on the assigned performer’s knowledge to do so. The individual previously responsible for this work voluntarily left SERC_URE1 prior to the missed month's review. The newly assigned individual as well as the supervisor incorrectly believed that SERC_URE1 had already conducted the missed month's review. This issue lasted approximately five days. | This issue posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC_URE1’s failure to assess security patches within 30 days of availability left vulnerable software on the affected CCAs for an extended period, increasing the risk that a cyber-attack or software specific exploit could result in operational impacts and potential negative impacts to the BPS. The missed patches affected approximately 75% of SERC_URE1’s EMS CCAs and approximately 10% of the total CCAs in the SERC_URE1 CIP program. However, all of the affected CCAs resided within secured ESPs and PSPs, and access from outside the ESP was controlled and restricted. SERC_URE1’s electronic access and control monitoring devices were monitoring and alerting for unusual activity and did not identify any malicious activity that would have impacted the affected Cyber Assets. This issue lasted for only five days. No harm is known to have occurred. SERC considered SERC_URE1’s CIP-007 R3 compliance history in determining the penalty. SERC determined that SERC_URE1’s CIP-007 R3 compliance history should not serve as a basis for applying a penalty and that this issue was appropriate for FFT treatment for the following reasons. Under CIP Version 5, this issue would not have been an issue because SERC_URE1 assessed the patches within 35 days of availability. Subsequent to this issue, SERC_URE1 implemented a workflow management alert to back up the manual patch process. This additional control ensures escalation if assessments are not completed within a prescribed time period. In addition, the patch review log documents the previous month's review right above the current month's review, making it likely that personnel performing a patch review and assessment would notice if the prior month's review was not performed as required, thereby limiting the possible duration of an issue. SERC also considered that SERC_URE1 self-reported the issue, fully cooperated with SERC, and mitigated the issue by assessing the missed patches on the same day that the issue was discovered. | To mitigate this issue, SERC_URE1: 1) assessed the security patches; 2) updated the manual patch assessment processes to include automated reminders; 3) trained the EMS administrators on the automated patch assessment reminder process established in step 2; 4) implemented the in-house, centralized, automated patch management solution as a secondary control; and 5) trained EMS administrators on the revised processes associated with Step 4. SERC has verified the completion of all mitigation activity.
2015-08-31 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE2014014428 | CIP-004-3 | R4; R4.1 | TRE_URE1 submitted a Self-Report after receiving notice of an upcoming Compliance Audit stating that it had an issue with CIP-004-3 R4.1. TRE_URE1 did not review the list of its personnel who have access to Critical Cyber Assets (CCAs) quarterly. Specifically, TRE_URE1 failed to perform quarterly reviews on one of its access lists because a shared account was mistakenly removed from the tracking system. The root cause of this issue was that TRE_URE1 lacked administrative processes to transfer accounts from one department to another, creating a miscommunication and unawareness between two teams. Texas RE determined the duration of the issue to be for over two years. | This issue posed a moderate risk and did not pose a serious or substantial potential risk to the reliability of the bulk power system (BPS) because the applicable access list was not reviewed for over two years. TRE_URE1 's failure to perform quarterly reviews of the list of personnel with authorized cyber and/or authorized unescorted physical access to CCAs could have allowed an unauthorized individual to gain access to critical systems leading to misuse of the information or controls, potentially compromising the reliability of the BPS. However, the risk to the reliability of the BPS was reduced because TRE_URE1 employs defense-in-depth to secure CCAs, including Physical Security Perimeters (PSPs), Electronic Security Perimeters (ESPs), firewalls and other protections required pursuant to the NERC CIP Standards. No harm is known to have occurred. | To mitigate this issue, TRE_URE1: 1) developed a checklist that targets new or existing CIP assets to ensure all relevant activities have been completed prior to implementation; 2) completed a manual review (true up) by comparing actual accesses with the approved accesses stored in its tracking system; 3) transferred daily access management and quarterly reviews of the NERC CIP assets into the tracking system; 4) conducted a quarterly manual review of approved accesses; and 5) installed jump stations within the PSP for use by administrators if they are not located within the PSP to add an additional level of security. Texas RE has verified the completion of all mitigation activity.
2015-07-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2015014919 | CIP-007-3a | R8 | NPCC_URE1 submitted a self-report stating that it had an issue of CIP-007-3a R8. NPCC_URE1 did not include all of its CIP Assets in one of its annual Cyber Vulnerability Assessments (CVAs). The root cause was due to powered down assets or unresponsive assets during the vulnerability scan. Additionally, assets were missed because NPCC_URE1 did not cross check its CIP Asset List against the scan results. | This issue posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Failure to perform a CVA on all CIP Assets could lead to vulnerabilities, which could lead to the unavailability or misuse of equipment used by system operators to monitor the BPS and direct appropriate actions. If this occurred, Balancing Authorities and Transmission Operators would work together to operate the BPS. Operations have been unaffected throughout the compliance period. NPCC_URE1 enhanced its CVA process and performed another CVA within a year. All assets were then either scanned or no longer needed to be scanned because they were no longer CIP assets. | To mitigate this issue, NPCC_URE1: 1) enhanced their CVA process to start with the current CIP Asset List and perform a CVA on those assets, ensuring all assets that needed to be scanned were scanned. 2) performed a CVA for all CIP Assets and EACM devices. NPCC has verified the completion of all mitigation activity.
2015-07-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2015015064 | CIP-005-3a | R1; R1.5 | NPCC identified a noncompliance with CIP-005 R1 for NPCC_URE1. NPCC_URE1 did not include all its Electronic Access Control and Monitoring Systems (EACMS) in its annual Cyber Vulnerability Assessment (CVA). The root cause was due to powered down assets or unresponsive assets during the vulnerability scan. Additionally, EACMS were missed because NPCC_URE1 did not cross check its CIP Asset List against the scan results. | This issue posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Failure to perform a CVA on all CIP Assets could lead to vulnerabilities, which could lead to the unavailability or misuse of equipment used by system operators to monitor the BPS and direct appropriate actions. If this occurred, Balancing Authorities and Transmission Operators would work together to operate the BPS. Operations have been unaffected throughout the compliance period. NPCC_URE1 enhanced its CVA process and performed another CVA within a year. All assets were then either scanned or no longer needed to be scanned because they were no longer CIP assets. | To mitigate this issue, NPCC_URE1: 1) enhanced their CVA process to start with the current CIP Asset List and perform a CVA on those assets, ensuring all assets that needed to be scanned were scanned. 2) performed a CVA for all CIP Assets and EACM devices. NPCC has verified the completion of all mitigation activity.
2015-06-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2014013305 | CIP-007-1 | R3 R3.1 R3.2 | During a Compliance Audit, ReliabilityFirst determined that RFC_URE1, had an issue of CIP-007-1 R3.1 and R3.2. RFC_URE1 had a Security Patch Management Program (Program) applicable to all Cyber Assets within its Electronic Security Perimeter (ESP) in place at the time of the Compliance Audit. However, the Program lacked details addressing how RFC_URE1 received: (1) notification of available security patches; (2) validation of security patches; (3) assessment of available security patches for applicability, either manually or using the RFC_URE1 automated security patch management solution; (4) references to the testing of security patches in accordance with RFC_URE1’s test procedures; and (5) deployment of security patches in accordance with RFC_URE1’s change control and configuration management program. At the Compliance Audit, RFC_URE1’s list of non-applied patches included patches for three years. RFC_URE1’s Program did not sufficiently describe how it tracks, evaluates, tests, and installs applicable patches. Therefore, RFC_URE1 did not: (1) provide sufficient evidence that it established, documented and implemented its Program for tracking, evaluating, testing, and installing applicable cyber security software patches for all Cyber Assets within the ESP, (2) document the assessment of security patches and security upgrades for applicability within thirty calendar days of availability of the patches or upgrades, and (3) document the implementation of security patches or compensating measures for devices within the ESP. The root cause of this violation was RFC_URE1’s failure to understand how to achieve and demonstrate compliance with all of the requirements of CIP-007 R3. RFC_URE1 used change tickets from its work request management system to document the review of available patches assessed by its automated patch management system. However, those change tickets did not provide sufficient evidence as to when patches were available and if patches were assessed within 30 days as is required by CIP-007 R3. Additionally, RFC_URE1 explained its intent to install all identified, available, and applicable security patches, but could not explain why security patches that were identified and available had not been installed. Overall, RFC_URE1 believed that it was compliant with CIP-007 R3, but was unable to provide sufficient evidence to demonstrate compliance. The duration of this issue is from the date RFC_URE1 was required to comply with CIP-007-1 R3.1 and R3.2, to the date RFC_URE1 completed its Mitigation Plan. | This issue posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the issue would have continued, except for the Compliance Audit, due to the inadequate processes and procedures that were in place as a result of RFC_URE1’s failure to appreciate the full extent of the requirements of CIP-007 R3.1 and R3.2. Second, RFC_URE1’s inability to assess and implement patches in a timely manner left vulnerabilities in RFC_URE1’s systems and networks for an extended period of time. For example, some patches were still awaiting implementation two years later. The risk posed by the foregoing facts and circumstances was mitigated by the following factors. RFC_URE1 actively and continuously monitors for the release of new security patches for all Cyber Assets within its ESP, Electronic Access Control and Monitoring Systems, and Physical Access Control Systems. RFC_URE1 also invested in an automated patch management system to help it assess and implement patches in a more timely manner. Finally, RFC_URE1 demonstrated at the Compliance Audit that most patches are being assessed and implemented in a timely manner. | To mitigate this issue, RFC_URE1: 1) used the basic structure recommended by the National Institute of Standards and Technology (NIST) in creating a patch management program to enhance its internal documentation and applicable procedures; 2) developed a software inventory list, following NIST’s recommendations, to confirm the current CIP Security patch management landscape and the sources of patches for all inventoried software; 3) revised its Security Patch Management Program Procedure to provide additional detail describing the specific processes implemented for the tracking, evaluation testing, and installation of security patches. One specific addition was the creation of a monthly management review process to ensure documentation is adequate and complete; 4) focused on documenting and implementing specific timeframes by which security patches must be installed or mitigation plans developed; 5) reviewed its deployment process and its testing and change management procedures to identify possible opportunities to improve deployment efficiency. The review revealed the need for a patch installment schedule coordinated with the operations group to address the potential impact of the patching process on operations; 6) began transitioning to a program wherein applicable security patches are installed or documented mitigation is developed for all CIP Cyber Assets within 35 days of the evaluation of a security patch in preparation for CIP-007-5. This program minimizes the potential impact to operations from patching. RFC_URE1 has implemented the NIST concept of prioritization as it builds resources and capabilities necessary to implement the 35-day requirement in CIP-007-5. RFC_URE1 is accomplishing this by shifting the Energy Management System servers to the 35-day deployment requirement first while working toward implementing the 35-day requirement on the rest of RFC_URE1’s CIP Cyber Assets; and 7) analyzed its current testing and change management practices to identify and remove unnecessary barriers to the deployment of the patches. This process allowed RFC_URE1 to establish and achieve specific milestones for implementing all outstanding security patches applicable to the RFC_URE1 CIP environment.
2015-06-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2014013306 | CIP-007-1 | R6 R6.1 R6.2 R6.5 | During a Compliance Audit, ReliabilityFirst determined that RFC_URE1, had an issue of CIP-007-1 R6.1, R6.2 and R6.5. Specifically, RFC_URE1 did not provide sufficient evidence that it had documented organizational processes and technical and procedural mechanisms to monitor for security events on all Cyber Assets within the Electronic Security Perimeter (ESP). RFC_URE1 only provided a one page, high-level, policy-based document that did not describe RFC_URE1’s organizational processes and procedural mechanisms for monitoring system events related to cyber security. The process document did not describe what events were being monitored, what tools and/or solutions were implemented, and how the tools/solutions were being used. Furthermore, RFC_URE1 did not provide sufficient evidence that it was issuing manual or automated alerts for detected Cyber Security Incidents. RFC_URE1 only provided evidence of alerts for failed login attempts and for locked out accounts. RFC_URE1 provided no evidence of automatic or manual alerts for detected Cyber Security Incidents. Lastly, RFC_URE1 did not maintain records documenting log reviews and therefore provided no evidence of the review of logs of system events related to cyber security. The root cause of this violation was RFC_URE1’s failure to understand the full extent of the requirements of CIP-007 R6. RFC_URE1 had a program document that described the processes and procedural mechanisms used for monitoring security events in RFC_URE1’s ESP. However, the program document did not provide enough detail as to what events were monitored, what tools and/or solutions were implemented, and how the tools/solutions were being used. RFC_URE1 provided some evidence of alerts for failed logins and locked accounts, but not sufficient evidence to demonstrate that RFC_URE1 was using manual or automated alerts for detected Cyber Security Incidents. Additionally, the alerts RFC_URE1 provided were not documented in RFC_URE1’s program document. Lastly, RFC_URE1 provided evidence that the log archival system performs an automated review of logs, but RFC_URE1 did not provide sufficient evidence that the logs were reviewed. Overall, RFC_URE1 believed that it was compliant with CIP-007 R6, but was unable to provide sufficient evidence to demonstrate compliance. The duration of this issue is from the date RFC_URE1 was required to comply with CIP-007-1 R6.1, R6.2, and R6.5, to the date RFC_URE1 completed its Mitigation Plan. | This issue posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, RFC_URE1’s processes for security status monitoring were written without sufficient detail to ensure the intent of each process was accomplished. Second, a failure to monitor the security status of protected assets may have led to undetected compromises of those assets and could have created potential harm to the Bulk Electric System (BES). The risks posed by the foregoing facts and circumstances were mitigated by the following factors. First, RFC_URE1 identified all tools used for alerting and monitoring and how the tools were utilized for monitoring, logging, and alerting to meet the Reliability Standard. RFC_URE1’s ESPs were continuously monitored by IDS/IPS and antivirus/malware solutions. Additionally, alerts were sent to appropriate personnel to respond to potential cyber security events. | To mitigate this issue, RFC_URE1: 1) enhanced its documentation to include more detailed information on the organizational processes and technical and procedural mechanisms used in monitoring and alerting for security events on all Physical Access Control Systems (PACS) and Cyber Assets within the RFC_URE1 ESPs; 2) initiated document enhancement by first undertaking an effort to identify all systems currently used to monitor and alert on cyber security events; 3) reviewed both CIP-007-3 R6 and CIP-007-5 R4 to create a specific list of potential cyber security system events for which it would monitor, log, and alert; 4) evaluated the criteria established in the existing tools and adjusted as necessary to ensure that monitoring, logging and alerting functions were capturing what was required; 5) modified the process document to include more detail with regard to the tools and processes used; and 6) developed a documented log review process. RFC_URE1 developed this process by looking at CIP-007-5 R4 for guidance. RFC_URE1 established a process where it will review a report or summarization of the logs (or a sample of the logs), captured in the system monitoring tools, for cyber security events for PACS and Cyber Assets within the RFC_URE1 ESPs at least every 15 days. The log review will be documented in a change management request and records associated with the log review will be retained for at least 90 days. ReliabilityFirst has verified the completion of all mitigation activity.
2015-06-30 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE2015014552 | CIP-004-3 | R4; R4.1 | TRE_URE1 submitted a Self-Report stating that it had an issue with CIP-004-3 R4.1. Specifically, TRE_URE1 failed to review its list of personnel who have access rights to Critical Cyber Assets (CCAs) quarterly, and update the list within seven calendar days of any change of personnel with such access to CCAs, or any change in the access rights. First, TRE_URE1 found a shared administrator account that was accessed by a user that did not have administrator approval. This initial discovery was made when TRE_URE1 was preparing evidence for an upcoming Audit. Second, TRE_URE1 further reviewed the shared accounts and found additional occurrences involving four more support employees. All five employees were approved to log into the systems; however, the employees were not approved for administrator rights. The root cause of this issue was that TRE_URE1 did not follow its process regarding granting new access rights to CCAs, maintaining the completeness and accuracy of existing access rights, and the removal of access rights as required. The issue occurred because an employee did not understand the difference between approved access for admininistrator functions and analyst functions. Specifically, a co-worker provided support employees with passwords to shared administrator accounts. The co-worker mistakenly assumed that access was authorized because the support employees needed to perform administrator functions. TRE_URE1 had an issue with CIP-004-3 R4.1 for two years and two months, from the first day after the deadline at which TRE_URE1 had failed to update its list of personnel access rights to CCAs for the first subject employee that obtained electronic access rights to CCAs until TRE_URE1 reviewed and updated its access list regarding the three employees that were approved for admininistrator access rights to CCAs. | This issue posed a moderate risk and did not pose a serious or substantial potential risk to the reliability of the bulk power system (BPS) because the access list was not properly maintained for over two years and two months. TRE_URE1's failure to perform quarterly reviews of the list of personnel with authorized cyber and/or authorized unescorted physical access to CCAs could have allowed an unauthorized individual to gain access to critical systems and to allow misuse of the information or controls, potentially compromising the reliability of the BPS. Furthermore, there were numerous logged incidents involving multiple shared accounts during the issue duration. The risk to the reliability of the BPS was reduced by the following factors. First, three of the five employees should have been granted administrator access based on the responsibilities of their positions. Second, TRE_URE1 employs defense-in-depth to secure CCAs, including Physical Security Perimeters, Electronic Security Perimeters, firewalls and other protections required pursuant to the NERC CIP standards. No harm is known to have occurred. Texas RE considered TRE_URE1’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, TRE_URE1: 1) reviewed local shared account usage logs and validated the list against authorized access permissions; 2) granted admininistrator access rights to three employees and updated the authorized list within seven calendar dates of the change; 3) created a procedure to address monthly reviews of local shared accounts, which includes: • a list of roles and responsibilities; • how to generate a monthly usage log report for local shared accounts; and • a step for reviewing the report for anomalies and/or unauthorized users. Texas RE has verified the completion of all mitigation activity.
2015-06-30 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE2015014857 | CIP-007-3a | R5; R5.1; R5.2 | TRE_URE1 submitted a Self-Report stating that it had an issue with CIP-004-3 R4.1. After subsequent review, Texas RE determined that certain noncompliance described in TRE_URE1’s Self-Report was also a possible violation of CIP-007-3a R5, R5.1, and R5.2. Specifically, TRE_URE1 discovered that five employees were using shared accounts with administrator access without having authorization to use the shared accounts or to know the passwords. Therefore, TRE_URE1 failed to implement technical and procedural controls that enforce access authentication of, and accountability for, all user activity, and that minimize the risk of unauthorized access (R5). In addition, TRE_URE1 did not ensure that individual and shared system accounts and authorized access permissions are consistent with the concept of “need to know” with respect to work functions performed (R5.1). Furthermore, TRE_URE1 did not implement a policy to minimize and manage the scope and acceptable use of administrator and shared account privileges (R5.2). The root cause of this issue was that TRE_URE1 lacked robust process controls that enforce access authentication for all employees requesting access to its systems. TRE_URE1 did not ensure that access permissions were correct and that they corresponded with the needs and personnel roles and responsibilities for personnel with access to the shared account password list. TRE_URE1 had an issue with CIP-007-3a R5, R5.1, and R5.2 for two years and seven months, from the time the first user logged onto a shared account with administrator access without having authorization to use the shared account or to know its password until TRE_URE1 changed the shared account passwords for all applicable systems. | This issue posed a moderate risk and did not pose a serious or substantial potential risk to the reliability of the bulk power system (BPS). TRE_URE1’s failure to implement technical and procedural controls that enforce access authentication of, and accountability for, all user activity, and that minimize the risk of unauthorized access could have allowed these users to gain access to critical parts of the system that control the power management and to compromise the BES. Furthermore, there were numerous logged incidents involving multiple shared accounts during a period of approximately two years and seven months. The risk to the reliability of the BPS was reduced by the following factors. First, three of the five employees should have been granted administrator access based on the responsibilities of their positions. Second, TRE_URE1 employs defense-in-depth to secure CCAs, including Physical Security Perimeters, Electronic Security Perimeters, firewalls and other protections required pursuant to the NERC CIP standards. No harm is known to have occurred. Texas RE considered TRE_URE1’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, TRE_URE1: 1) approved three employees for admin access to the applicable systems; 2) changed the passwords on the applicable shared accounts; and 3) created a procedure that describes the processes and compliance activities associated with shared local access. Texas RE has verified the completion of all mitigation activity.
2015-06-30 | TRE_URE1liability Entity (TRE_URE1) | Unidentified Registered Entity 2 (TRE_URE2) | NCRXXXXX | TRE2015014553 | CIP-004-3 | R4; R4.1 | TRE_URE2 submitted a Self-Report stating that it had an issue with CIP-004-3 R4.1. Specifically, TRE_URE2 failed to review its list of personnel who have access rights to Critical Cyber Assets (CCAs) quarterly, and update the list(s) within seven calendar days of any change of personnel with such access to CCAs, or any change in the access rights. First, TRE_URE2 found a shared administrator account that was accessed by a user that did not have administrator approval. This initial discovery was made when TRE_URE2 was preparing evidence for an upcoming Audit. Second, TRE_URE2 further reviewed the shared accounts and found additional occurrences involving four more support employees. All five employees were approved to log into the systems; however, the employees were not approved for administrator rights. The root cause of this issue was that TRE_URE2 did not follow its process regarding granting new access rights to Critical Cyber Assets (CCAs), maintaining the completeness and accuracy of existing access rights, and the removal of access rights as required. The issue occurred because an employee did not understand the difference between approved access for Admin functions and Analyst functions. Specifically, a co-worker provided support employees with passwords to shared administrator accounts. The co-worker mistakenly assumed that access was authorized because the support employees needed to perform administrator functions. TRE_URE2 had an issue with CIP-004-3 R4.1 for two years and two months, from the first day after the deadline at which TRE_URE2 had failed to update its list of personnel access rights to CCAs for the first subject employee that obtained electronic access rights to CCAs until TRE_URE2 reviewed and updated its access list regarding the three employees that were approved for admin access rights to CCAs. | This issue posed a moderate risk and did not pose a serious or substantial potential risk to the reliability of the bulk power system (BPS) because the access list was not properly maintained for over two years and two months. TRE_URE2's failure to perform quarterly reviews of the list of personnel with authorized cyber and/or authorized unescorted physical access to CCAs could have allowed an unauthorized individual to gain access to critical systems and to allow misuse of the information or controls, potentially compromising the reliability of the BPS. Furthermore, there were numerous logged incidents involving multiple shared accounts during the issue duration. The risk to the reliability of the BPS was reduced by the following factors. First, three of the five employees should have been granted administrator access based on the responsibilities of their positions. Second, TRE_URE2 employs defense-in-depth to secure CCAs, including Physical Security Perimeters, Electronic Security Perimeters, firewalls and other protections required pursuant to the NERC CIP standards. No harm is known to have occurred. TRE_URE1 considered TRE_URE2’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, TRE_URE2: 1) reviewed local shared account usage logs and validated the list against authorized access permissions; 2) granted admininistrator access rights to three employees and updated the authorized list within seven calendar dates of the change; 3) created a procedure to address monthly reviews of local shared accounts, which includes: • a list of roles and responsibilities; • how to generate a monthly usage log report for local shared accounts; and • a step for reviewing the report for anomalies and/or unauthorized users. TRE_URE1 has verified the completion of all mitigation activity.
2015-06-30 | TRE_URE1liability Entity (TRE_URE1) | Unidentified Registered Entity 2 (TRE_URE2) | NCRXXXXX | TRE2015014858 | CIP-007-3a | R5; R5.1; R5.2 | TRE_URE2 submitted a Self-Report stating that it had an issue with CIP-004-3 R4.1. After subsequent review, TRE_URE1 determined that certain noncompliance described in TRE_URE2’s self-report was also a possible violation of CIP-007-3a R5, R5.1, and R5.2. Specifically, TRE_URE2 discovered that five employees were using shared accounts with administrator access without having authorization to use the shared accounts or to know the passwords. Therefore, TRE_URE2 failed to implement technical and procedural controls that enforce access authentication of, and accountability for, all user activity, and that minimize the risk of unauthorized access (R5). In addition, TRE_URE2 did not ensure that individual and shared system accounts and authorized access permissions are consistent with the concept of “need to know” with respect to work functions performed (R5.1). Furthermore, TRE_URE2 did not implement a policy to minimize and manage the scope and acceptable use of administrator and shared account privileges (R5.2). The root cause of this issue was that TRE_URE2 lacked robust process controls that enforce access authentication for all employees requesting access to its systems. TRE_URE2 did not ensure that access permissions are correct and that they correspond with the needs and personnel roles and responsibilities for personnel with access to the shared account password list. TRE_URE2 had an issue with CIP-007-3a R5, R5.1, and R5.2 for two years and seven months, from the time the first user logged onto a shared account with administrator access without having authorization to use the shared account or to know its password until TRE_URE2 changed the shared account passwords for all applicable systems. | This issue posed a moderate risk and did not pose a serious or substantial potential risk to the reliability of the bulk power system (BPS). TRE_URE2’s failure to implement technical and procedural controls that enforce access authentication of, and accountability for, all user activity, and that minimize the risk of unauthorized access could have allowed these users to gain access to critical parts of the system that control the power management and to compromise the BPS. Furthermore, there were numerous logged incidents involving multiple shared accounts during a period of approximately two years and seven months. The risk to the reliability of the BPS was reduced by the following factors. First, three of the five employees should have been granted administrator access based on the responsibilities of their positions. Second, TRE_URE2 employs defense-in-depth to secure CCAs, including Physical Security Perimeters, Electronic Security Perimeters, firewalls and other protections required pursuant to the NERC CIP standards. No harm is known to have occurred. TRE_URE1 considered TRE_URE2’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, TRE_URE2: 1) approved three employees for admin access to the applicable systems; 2) changed the passwords on the applicable shared accounts; and 3) created a procedure that describes the processes and compliance activities associated with shared local access. TRE_URE1 has verified the completion of all mitigation activity.
2015-05-28 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2014014536 | CIP-005-3a | R5 | WECC_URE1 submitted a Self-Report stating that it had an issue of CIP-005-3a R5. Specifically, WECC_URE1 reported that it failed to document an access point to the Electronic Security Perimeter (“ESP”) within 90 calendar days of the change. WECC determined that WECC_URE1 created a new virtual local area network (VLAN) on switches at control centers. WECC_URE1 connected one device to each of the two VLANs, at which point the switches became electronic access points to the ESP. However, WECC_URE1 did not document the switches as electronic access points for two months after the 90-day period. After review of the configuration, WECC_URE1 decided to discontinue the switches as access points and physically disconnected the devices and removed them from the ESP a month later. WECC determined that WECC_URE1’s failure to ensure that all documentation reflected current system configurations is a remediated issue of CIP-005-3a R5.1. WECC_URE1’s failure to update its documentation to reflect the modification of the network or controls within ninety calendar days of the change is a remediated issue of R5.2. Finally, WECC determined that the remediated issue began when WECC_URE1 should have updated its documentation to reflect the change, and continued until WECC_URE1 included the switches in its documentation. The root cause of the remediated issue was a lack of compliance process to document access points when they are installed. | This issue posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Specifically, WECC_URE1 failed to document a modification to its network or controls within 90 calendar days of the change. Failing to document an access point to the ESP could lead WECC_URE1 to not properly protect the access point. If a vulnerable port or service was present at the access point, and WECC_URE1 did not properly protect against the vulnerability, a malicious person exploit the vulnerability and take control of the device. The malicious person may then send attack packets into the ESP, in an attempt to compromise devices within the ESP. However, WECC_URE1 implemented both preventive and detective controls. As preventive controls, WECC_URE1’s change control procedure included configuring the devices to only enable ports and services necessary, disabling all others, which would allow WECC_URE1 to know which ports and services could potentially be vulnerable and protect against them. Also, WECC_URE1 uses VLAN Access Control Lists on its switches to specify ingress and egress traffic, which could prevent attack packets from successfully passing through the switch. As a preventive and detective control, WECC_URE1 uses an Intrusion Prevention System to look for and stop known attack signatures. Finally, as a detective control, WECC_URE1’s change control process ensured the two devices were monitored and logged to detect and alert for security threats. WECC determined that the issue was appropriate for FFT treatment because WECC_URE1 has identified and self-reported the remediated issues addressed herein, and has provided documentation of its internal compliance program. Also, these are WECC_URE1’s first violations of these Standards and requirements. No harm is known to have occurred. WECC considered WECC_URE1's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, WECC_URE1 disconnected the devices as access points. WECC has verified the completion of all mitigation activity. To address the root cause of the remediated issue, WECC_URE1 implemented prevention measures, including: 1) a quarterly review of ESP port configuration changes; 2) ESP network configuration changes; 3) development of an inventory of documents that require updating whenever there is modification of network or controls; and 4) including documentation updating in the change control process.
2015-05-28 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2014014307 | CIP-009-3 | R2 | WECC_URE1 submitted a Self-Report stating that it had an issue of CIP-009-3 R2. Specifically, WECC_URE1 reported that it employs an overarching recovery plan for Critical Cyber Assets (CCAs) in addition to individualized asset recovery plans that comprise components of the overarching plan. WECC_URE1 reported that it conducts annual exercises of the overarching plan, but that exercises for each individualized asset recovery plan are not conducted annually, but rather on a rotating basis. WECC determined that WECC_URE1’s individualized asset recovery plans are based on the application they control. During two years, WECC_URE1 exercised its overarching plan and some of the individualized asset recovery plans, but did not exercise all of its individualized asset recovery plans. WECC_URE1 is required to perform annual exercises of its recovery plans on devices in each device type category (server, workstation, etc.) that WECC_URE1 defines for Physical Access Control System (PACS), Electronic Access Control and Monitoring (EACMs), CCAs, and non-CCAs in an Electronic Security Perimeter (ESP). WECC_URE1 covered all PACS device types in both years. However, WECC_URE1 failed to exercise plans to cover EACM servers in both years, non-CCA servers in an ESP in one year, and several CCA device types in both years. WECC determined that WECC_URE1 has a remediated issue with CIP-009-3 R2 for failing to annually exercise its recovery plans each year. WECC further determined the remediated issue began on the beginning of the calendar year in which WECC_URE1 was required to exercise its plans, and terminated when WECC_URE1 completed remediating activities. The root cause of the remediated issue was a lack of compliance understanding. Specifically, WECC_URE1 divided its assets into several different recovery plans to address different applications, in addition to having an overarching plan. | This issue posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Specifically, WECC_URE1 failed to exercise its recovery plans. If recovery plans for each device type are not exercised annually, WECC_URE1 personnel may not have the appropriate training to be able to effectively recover the devices used for a specific application in any given instance. WECC_URE1 implemented strong preventive, detective and corrective controls. As a preventive measure, WECC_URE1 did exercise its over-arching recovery plan each year in addition to several of the asset-specific plans. Also, WECC_URE1 ensures its devices are up-to-date on patches to help prevent failures of the device. As a detective measure, WECC_URE1 utilizes detection programs on its devices, which alert WECC_URE1 to problems on the devices. As a corrective control, WECC_URE1 can move operational control from control centers, which would allow WECC_URE1 to remain operational in the event one was compromised. Despite these controls, due to the potential loss of load resulting from the failure to annually exercise asset recovery plans, WECC determined that this violation posed a moderate risk to the reliability of the BPS. WECC determined that the issue was appropriate for FFT treatment because WECC_URE1 has identified and self-reported the remediated issues addressed herein, and has provided documentation of its internal compliance program. Also, these are WECC_URE1’s first violations of these Standards and requirements. No harm is known to have occurred. WECC considered WECC_URE1's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, WECC_URE1: 1) informed and trained all WECC_URE1 managers responsible for individual asset plans that an annual test must be conducted on every subsidiary individual asset plan; 2) developed an annual table-top exercise scenario in which all asset plans will be called into action, exercised, and reviewed; and 3) updated the NERC CIP compliance review project plan to include a task in the evidence review that verifies each plan has been exercised that year. WECC has verified the completion of all mitigation activity.
2015-04-30 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2013013126 | CIP-005-3a | R2; R2.1; R.2.2 | During a Compliance Audit FRCC determined that FRCC_URE11 had an issue of CIP-005-3a R2.1 and R2.2 FRCC_URE1 documentation was insufficient to demonstrate that it uses an access control model which specifies that explicit access permissions are required. In addition, the FRCC_URE11 documentation was insufficient to demonstrate that it enabled only ports and services required for operations and for monitoring Cyber Assets within the Electronic Security Perimeter; and that FRCC_URE11 documented individually or by specified grouping, the configuration of those ports and services. Specifically, FRCC_URE11 documentation illustrates permit statements that include the entire range of ports from 1025 to 65535 as well as ranges of devices (e.g., from 68 to 255) in a subnet using masking. FRCC_URE11 supplied documentation for the justification of the allowed ports were actually the results of a Cyber Vulnerability Assessment that show the open ports discovered during an assessment and did not demonstrate why the entire range of ports from 1025 to 65535 were allowed at the access point. Additionally, the entire range of IP addresses in the subnet mask used could not substantiated as "explicit" given many of the addresses were not used. The root cause of the noncompliance was a less than adequate installation/design configuration of the firewalls. | This issue posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. FRCC determined that the issue posed a moderate risk because failure to use explicit permissions does not limit network communications traffic to specific devices and in addition not evaluating ports/services needed for operations or monitoring can potentially allow for unauthorized traffic. FRCC determined that the issue was appropriate for FFT treatment because the risk was reduced as the Cyber Assets were behind corporate firewalls in addition to requiring authenticated requests. FRCC considered FRCC_URE11's compliance history and determined there were no relevant instances of noncompliance. No harm is known to have occurred. | To mitigate this issue, FRCC_URE11 will will complete the following mitigation activities: 1. perform an extent of condition analysis to determine the scope and identify routing patterns/data flows between data centers; 2. for the substation networks and the Control Center networks, determine the final design and firewall to be utilized and select a vendor; 3. procure necessary equipment for Control Center and Substations and establish an initial baseline of firewall rules for Control Center and Substations, 4. deploy procured equipment and capture network traffic to determine necessary rules, 5. configure the network equipment and finalize and implement firewall rules; and 6. complete testing and artifact collection, verify all necessary network diagrams and Cyber Asset lists are updated to reflect changes.
2015-03-31 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE2014014217 | CIP-006-3c | R8; R8.1 | During a Compliance Audit, Texas RE determined that TRE_URE1 had an issue with CIP-006-3c R8.1. TRE_URE1 did not implement a maintenance and testing program to ensure that all physical security systems function properly by performing testing and maintenance of all physical security mechanisms on a cycle no longer than three years. Specifically, TRE_URE1 failed to provide evidence to show that glass break sensors, which were declared as a control for windows identified as access points, were tested as part of physical security mechanisms with a cycle no longer than three years. The root cause of the issue was the glass break sensors on the windows indicated as access points for several PSPs were never considered “in service” by TRE_URE1 technicians and were not configured to actually alarm in case of window breakage but were included as controls for window access in documents. Texas RE determined that TRE_URE1 had an issue with CIP-006-3c R8.1 for more than two years and nine months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). TRE_URE1 installed the glass break sensors on exterior windows in the several PSPs as part of an effort to protect PSP boundaries. After TRE_URE1 experienced a large number of false alarms from these devices, the decision was made to set the sensors to create log entries but not send any alerts, since both the affected areas are occupied 24/7 with personnel. However, the glass break sensors were listed as part of the of the PSP protection scheme for four document review cycles. The glass break sensors should have been tested within a three-year cycle as indicated by the PSP protection documents. TRE_URE1 has since amended the appropriate documents to remove any glass break sensors from consideration in the several PSPs as these sensors are not necessary. No actual harm is known to have occurred. Texas RE considered TRE_URE1’s compliance history and determined there were no relevant instances of noncompliance. Texas RE determined that this minimal risk issue was appropriate for FFT treatment because it was discovered during a Compliance Audit that included four moderate risk audit findings. | To mitigate this issue, TRE_URE1: 1) amended the appropriate documents to remove any glass break sensors from consideration in several PSPs as these sensors are not necessary; 2) modified the PSP procedure to require that annual reviews of the PSP system include a review of all applicable documentation; and 3) modified the PSP review log document to include a verification checklist that will help prevent future oversights. Texas RE has verified the completion of all mitigation activity.
2015-03-31 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE2014014218 | CIP-007-3a | R1; R1.1; R1.3 | During a Compliance Audit, Texas RE determined that TRE_URE1 had an issue with CIP-007-3a R1.1 and R1.3. TRE_URE1 did not possess pre-defined cyber security test procedures for non-Windows Cyber Assets (R1.1). Additionally, TRE_URE1 did not document all test results of Cyber Assets (R1.3). Although TRE_URE1 documented test results for testing situations which had problems, it did not document testing situations that did not experience problems. The root cause of this issue is a failure by TRE_URE1 to consider non-Windows Cyber Assets for inclusion into its security test procedures and a failure to document all Cyber Asset testing results. Of the CCAs identified in TRE_URE1’s CCA List, 48.3% CCAs did not have defined testing procedures, and none of the CCAs had documented testing results except in the case when a failure was discovered. Texas RE determined that TRE_URE1 had an issue with CIP-007-3a R1.1 and R1.3 for more than two years and ten months. | This issue posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The resulting omissions created a vulnerability in the TRE_URE1 system where 48.3 % of the devices defined as CCAs did not have security test procedures defined for them and no testing performed on them since TRE_URE1 was registered. These devices include elements for TRE_URE1 ESP and PSP protective schemes. The risk to the reliability of the BPS was mitigated by the following factors. TRE_URE1 tested the devices over the audit scope time period and the devices resided in TRE_URE1’s PSP. Although, the results were not recorded except in cases where issues were discovered, TRE_URE1’s security test procedures were performed. Only non-Windows assets were affected (all Windows based elements were included in cyber security test procedures). TRE_URE1 has less than 350 MW of generation. No actual harm is known to have occurred. Texas RE considered TRE_URE1’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, TRE_URE1: 1) created a document to define the steps necessary for upgrading and testing non-Windows devices; 2) modified change control documents to clearly document the steps in the process and to include the results of Cyber Asset testing; 3) added a radio button on the change control form to indicate whether testing was completely successful and added a field to document any test failures; and 4) provided training to reinforce new procedures for testing and recording test data for all non-Windows Cyber Assets Texas RE has verified the completion of all mitigation activity.
2015-03-31 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE2014014219 | CIP-007-3a | R2; R2.2 | During a Compliance Audit, Texas RE determined that TRE_URE1 had an issue with CIP-007-3a R2.2. TRE_URE1 did not disable unapproved ports and services on Cyber Assets. TRE_URE1 created firewall rules on the Electronic Security Perimeter (ESP) to permit approved ports and services and block unapproved ports and services in lieu of disabling ports and services on Cyber Assets inside the ESP. The root cause of this omission was TRE_URE1 failed to provide Cyber Asset-level protective measures for all systems which have access into, and reside in, the ESP. Texas RE determined that TRE_URE1 had an issue with CIP-007-3a R2.2 for more than three years and three months. | This issue posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). TRE_URE1 did not disable any unnecessary ports and services on Cyber Assets, relying instead on its firewalls to deny ingress to the Electronic Security Perimeter. This type of blocking ports and services does not take into account several malicious attack vectors, such as internal disgruntled workers or false origination data. Additionally, since the firewall rules allowed any traffic to leave the ESP to any destination, those rules do not protect TRE_URE1 from “man-in-the-middle” attacks. The risk to TRE_URE1 is that failing to disable unnecessary ports and services on Cyber Assets could lead to operational failure of the TRE_URE1 Energy Management System. Systems with access into the ESP and which have a lower level of protection than CCAs could be compromised through lateral movement in the corporate network and could potentially compromise TRE_URE1 Cyber Assets. TRE_URE1’s documentation indicated a proper approach to addressing the requirements of CIP-007-3a R2 for the firewall only and did not address what was behind the firewall (things in the ESP). TRE_URE1 did not have a process to ensure that only those ports and services required for normal and emergency operations are enabled for all Cyber Assets inside the ESP. This affected all CCAs. TRE_URE1 provided evidence that it used application white-listing to mitigate the damage of malware. However, because TRE_URE1 uses its ESP firewalls to control Cyber Asset ports and services, the impact of the firewall rules is critical. In TRE_URE1’s case, there is a specific firewall rule that allows all outbound traffic to communicate from the ESP to other, less secure networks. No actual harm is known to have occurred. Texas RE took into account that TRE_URE1 had a previous issue with the same Standard and Requirement. Texas RE determined that the instant issue was appropriate for FFT treatment because the underlying conduct of the two instances was different. | To mitigate this issue, TRE_URE1: 1) modified its documentation and procedures to reflect that only those ports and services required for normal and emergency operations on Cyber Assets inside ESPs are enabled; 2) changed its installation procedure to require that required ports and services are documented properly and non-required ports and services are disabled or blocked; and 3) engaged and contracted a third party consultant to assist TRE_URE1 in analyzing open ports and services on its CCAs, and updating documentation as needed. Texas RE has verified the completion of all mitigation activity.
2015-03-31 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE2014014220 | CIP-009-3 | R1; R1.1 | During a Compliance Audit, Texas RE determined that TRE_URE1 had an issue with CIP-009-3 R1.1. TRE_URE1 failed to specify a range of severity levels and corresponding required actions in response to events or conditions of varying duration and severity for defined CCAs. Specifically, TRE_URE1’s documentation revealed that no specific actions were planned in response to events or conditions of varying severity that would activate the recovery of the S2 Netboxes and Controller, comprising 20.6% of all Critical Cyber Assets. The root cause of this omission is TRE_URE1 did not plan for the recovery of these specific CCAs and left them out of its recovery documentation in all years represented in the submitted evidence. Texas RE determined that TRE_URE1 had an issue with CIP-009-3 R1.1 for more than two years and ten months. | This issue posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the CCAs not considered in the TRE_URE1 recovery plans constitute almost 21% of all TRE_URE1 CCAs and control access to control elements for the BES. Failing to identify a range of severity levels that activates its Recovery Plan restricts TRE_URE1 in its response to a range of severity levels from minor to emergency. While TRE_URE1 will make decisions regardless of what is documented, a deliberative process is likely to be more successful than one or more decisions made in the stress of the moment and reliant upon personal knowledge or experience. The risk is that TRE_URE1’s response to a variety of outage conditions will take more time and/or overlook a key ingredient of recovery operations. The risk to the reliability of the BPS was mitigated by the following factors. TRE_URE1 tested the devices over the audit scope time period and the devices resided in TRE_URE1’s PSP. Although, the results were not recorded except in cases where issues were discovered, TRE_URE1’s security test procedures were performed. Only non-Windows assets were affected (all Windows based elements were included in cyber security test procedures). TRE_URE1 has less than 350 MW of generation. No actual harm is known to have occurred. Texas RE took into account that TRE_URE1 had a previous issue with the same Standard and Requirement. Texas RE determined that the instant issue was appropriate for FFT treatment because the underlying conduct of the two instances was different. | To mitigate this issue, TRE_URE1: 1) amended its recovery plans to specifically identify the required actions in response to events or conditions of varying severity that would activate its recovery plan for the S2 Netboxes and Controller; and 2) modified the backup and recovery procedure to require that the annual review of the backup and recovery document also include a comparison with the current CCA list. This will ensure that all types of CCAs are documented. Texas RE has verified the completion of all mitigation activity.
2015-03-31 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE2014014221 | CIP-009-3 | R4 | During a Compliance Audit, Texas RE determined that TRE_URE1 had an issue with CIP-009-3 R4. TRE_URE1 failed to include backup and storage information required to successfully restore its S2 Netboxes and controller, used for PSP access control, as outlined in TRE_URE1’s recovery plans and recovery processes. The Netbox system components represent 20.6% of all TRE_URE1 CCAs. Texas RE determined that TRE_URE1 had an issue with CIP-009-3 R4 for more than two years and ten months. | This issue posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Lacking processes and procedures for the backup and storage of information required to restore Critical Cyber Assets could lead to the inability to successfully restore those Critical Cyber Assets in the event of an outage. In none of the TRE_URE1-provided documents is there a description of the processes and procedures for the backup and storage of information required to restore Critical Cyber Assets. The risk to the reliability of the BPS was mitigated by the following factors. TRE_URE1 does back up Critical Cyber Assets nightly and/or has spare equipment available for replacement of failed devices. Additionally, there are automated server processes that backup configurations for CCA firewalls and switches. No actual harm is known to have occurred. Texas RE considered TRE_URE1’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, TRE_URE1: 1) updated the recovery plans for Cyber Assets documentation to include backups; 2) added steps for backing up information from Cyber Assets as required. This change includes details on the types of backup and frequency of backups for each type of CCA. 3) modified the backup and recovery procedure to require that the annual review of the backup and recovery documentation also include a comparison with the current CCA list. This will ensure that all types of CCAs are documented. Texas RE has verified the completion of all mitigation activity.
2015-03-31 | TRE_URE1liability Entity (TRE_URE1) | Unidentified Registered Entity 2 (TRE_URE2) | NCRXXXXX | TRE2014014222 | CIP-006-3c | R8; R8.1 | During a Compliance Audit, TRE_URE1 determined that TRE_URE2 had an issue with CIP-006-3c R8.1. TRE_URE2 did not implement a maintenance and testing program to ensure that all physical security systems function properly by performing testing and maintenance of all physical security mechanisms on a cycle no longer than three years. Specifically, TRE_URE2 failed to provide evidence to show that glass break sensors, which were declared as a control for windows identified as access points, were tested as part of physical security mechanisms with a cycle no longer than three years. The root cause of the issue was the glass break sensors on the windows indicated as access points for several PSPs were never considered “in service” by TRE_URE2 technicians and were not configured to actually alarm in case of window breakage but were included as controls for window access in documents. TRE_URE1 determined that TRE_URE2 had an issue with CIP-006-3c R8.1 for more than one year and eight months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). TRE_URE2 installed the glass break sensors on exterior windows in the several PSPs as part of an effort to protect PSP boundaries. After TRE_URE2 experienced a large number of false alarms from these devices, the decision was made to set the sensors to create log entries but not send any alerts, since both the affected areas are occupied 24/7 with personnel. However, the glass break sensors were listed as part of the of the PSP protection scheme for four document review cycles. The glass break sensors should have been tested within a three-year cycle as indicated by the PSP protection documents. TRE_URE2 has since amended the appropriate documents to remove any glass break sensors from consideration in the several PSPs as these sensors are not necessary. No actual harm is known to have occurred. TRE_URE1 considered TRE_URE2’s compliance history and determined there were no relevant instances of noncompliance. TRE_URE1 determined that this minimal risk issue was appropriate for FFT treatment because it was discovered during a Compliance Audit that included four moderate risk audit findings. | To mitigate this issue, TRE_URE2: 1) amended the appropriate documents to remove any glass break sensors from consideration in several PSPs as these sensors are not necessary; 2) modified the PSP procedure to require that annual reviews of the PSP system include a review of all applicable documentation; and 3) modified the PSP review log document to include a verification checklist that will help prevent future oversights. TRE_URE1 has verified the completion of all mitigation activity.
2015-03-31 | TRE_URE1liability Entity (TRE_URE1) | Unidentified Registered Entity 2 (TRE_URE2) | NCRXXXXX | TRE2014014223 | CIP-007-3a | R1; R1.1; R1.3 | During a Compliance Audit, TRE_URE1 determined that TRE_URE2 had an issue with CIP-007-3a R1.1 and R1.3. TRE_URE2 did not possess pre-defined cyber security test procedures for non-Windows Cyber Assets (R1.1). Additionally, TRE_URE2 did not document all test results of Cyber Assets (R1.3). Although TRE_URE2 documented test results for testing situations which had problems, it did not document testing situations that did not experience problems. The root cause of this issue is a failure by TRE_URE2 to consider non-Windows Cyber Assets for inclusion into its security test procedures and a failure to document all Cyber Asset testing results. Of the CCAs identified in TRE_URE2’s CCA List, 48.3% CCAs did not have defined testing procedures, and none of the CCAs had documented testing results except in the case when a failure was discovered. TRE_URE1 determined that TRE_URE2 had an issue with CIP-007-3a R1.1 and R1.3 for more than one year and nine months. | This issue posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The resulting omissions created a vulnerability in the TRE_URE2 system where 48.3 % of the devices defined as CCAs did not have security test procedures defined for them and no testing performed on them since TRE_URE2 was registered. These devices include elements for TRE_URE2 ESP and PSP protective schemes. The risk to the reliability of the BPS was mitigated by the following factors. TRE_URE2 tested the devices over the audit scope time period and the devices resided in TRE_URE2’s PSP. Although, the results were not recorded except in cases where issues were discovered, TRE_URE2’s security test procedures were performed. Only non-Windows assets were affected (all Windows based elements were included in cyber security test procedures). TRE_URE2 has less than 350 MW of generation. No actual harm is known to have occurred. TRE_URE1 considered TRE_URE2’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, TRE_URE2: 1) created a document to define the steps necessary for upgrading and testing non-Windows devices; 2) modified change control documents to clearly document the steps in the process and to include the results of Cyber Asset testing; 3) added a radio button on the change control form to indicate whether testing was completely successful and added a field to document any test failures; and 4) provided training to reinforce new procedures for testing and recording test data for all non-Windows Cyber Assets TRE_URE1 has verified the completion of all mitigation activity.
2015-03-31 | TRE_URE1liability Entity (TRE_URE1) | Unidentified Registered Entity 2 (TRE_URE2) | NCRXXXXX | TRE2014014224 | CIP-007-3a | R2; R2.2 | During a Compliance Audit, TRE_URE1 determined that TRE_URE2 had an issue with CIP-007-3a R2.2. TRE_URE2 did not disable unapproved ports and services on Cyber Assets. TRE_URE2 created firewall rules on the Electronic Security Perimeter (ESP) to permit approved ports and services and block unapproved ports and services in lieu of disabling ports and services on Cyber Assets inside the ESP. The root cause of this omission was TRE_URE2 failed to provide Cyber Asset-level protective measures for all systems which have access into, and reside in, the ESP. TRE_URE1 determined that TRE_URE2 had an issue with CIP-007-3a R2.2 for more than two years and two months. | This issue posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). TRE_URE2 did not disable any unnecessary ports and services on Cyber Assets, relying instead on its firewalls to deny ingress to the Electronic Security Perimeter. This type of blocking ports and services does not take into account several malicious attack vectors, such as internal disgruntled workers or false origination data. Additionally, since the firewall rules allowed any traffic to leave the ESP to any destination, those rules do not protect TRE_URE2 from “man-in-the-middle” attacks. The risk to TRE_URE2 is that failing to disable unnecessary ports and services on Cyber Assets could lead to operational failure of the TRE_URE2 Energy Management System. Systems with access into the ESP and which have a lower level of protection than CCAs could be compromised through lateral movement in the corporate network and could potentially compromise TRE_URE2 Cyber Assets. TRE_URE2’s documentation indicated a proper approach to addressing the requirements of CIP-007-3a R2 for the firewall only and did not address what was behind the firewall (things in the ESP). TRE_URE2 did not have a process to ensure that only those ports and services required for normal and emergency operations are enabled for all Cyber Assets inside the ESP. This affected all CCAs. TRE_URE2 provided evidence that it used application white-listing to mitigate the damage of malware. However, because TRE_URE2 uses its ESP firewalls to control Cyber Asset ports and services, the impact of the firewall rules is critical. In TRE_URE2’s case, there is a specific firewall rule that allows all outbound traffic to communicate from the ESP to other, less secure networks. No actual harm is known to have occurred. TRE_URE1 took into account that TRE_URE2’s affiliate had a previous issue with the same Standard and Requirement. TRE_URE1 determined that the instant issue was appropriate for FFT treatment because the underlying conduct of the two instances was different. | To mitigate this issue, TRE_URE2: 1) modified its documentation and procedures to reflect that only those ports and services required for normal and emergency operations on Cyber Assets inside ESPs are enabled; 2) changed its installation procedure to require that required ports and services are documented properly and non-required ports and services are disabled or blocked; and 3) engaged and contracted a third party consultant to assist TRE_URE2 in analyzing open ports and services on its CCAs, and updating documentation as needed. TRE_URE1 has verified the completion of all mitigation activity.
2015-03-31 | TRE_URE1liability Entity (TRE_URE1) | Unidentified Registered Entity 2 (TRE_URE2) | NCRXXXXX | TRE2014014225 | CIP-009-3 | R1; R1.1 | During a Compliance Audit, TRE_URE1 determined that TRE_URE2 had an issue with CIP-009-3 R1.1. TRE_URE2 failed to specify a range of severity levels and corresponding required actions in response to events or conditions of varying duration and severity for defined CCAs. Specifically, TRE_URE2’s documentation revealed that no specific actions were planned in response to events or conditions of varying severity that would activate the recovery of the S2 Netboxes and Controller, comprising 20.6% of all Critical Cyber Assets. The root cause of this omission is TRE_URE2 did not plan for the recovery of these specific CCAs and left them out of its recovery documentation in all years represented in the submitted evidence. TRE_URE1 determined that TRE_URE2 had an issue with CIP-009-3 R1.1 for more than one year and nine months. | This issue posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the CCAs not considered in the TRE_URE2 recovery plans constitute almost 21% of all TRE_URE2 CCAs and control access to control elements for the BES. Failing to identify a range of severity levels that activates its Recovery Plan restricts TRE_URE2 in its response to a range of severity levels from minor to emergency. While TRE_URE2 will make decisions regardless of what is documented, a deliberative process is likely to be more successful than one or more decisions made in the stress of the moment and reliant upon personal knowledge or experience. The risk is that TRE_URE2’s response to a variety of outage conditions will take more time and/or overlook a key ingredient of recovery operations. The risk to the reliability of the BPS was mitigated by the following factors. TRE_URE2 tested the devices over the audit scope time period and the devices resided in TRE_URE2’s PSP. Although, the results were not recorded except in cases where issues were discovered, TRE_URE2’s security test procedures were performed. Only non-Windows assets were affected (all Windows based elements were included in cyber security test procedures). TRE_URE2 has less than 350 MW of generation. No actual harm is known to have occurred. TRE_URE1 took into account that TRE_URE2 had a previous issue with the same Standard and Requirement. TRE_URE1 determined that the instant issue was appropriate for FFT treatment because the underlying conduct of the two instances was different. | To mitigate this issue, TRE_URE2: 1) amended its recovery plans to specifically identify the required actions in response to events or conditions of varying severity that would activate its recovery plan for the S2 Netboxes and Controller; and 2) modified the backup and recovery procedure to require that the annual review of the backup and recovery document also include a comparison with the current CCA list. This will ensure that all types of CCAs are documented. TRE_URE1 has verified the completion of all mitigation activity.
2015-03-31 | TRE_URE1liability Entity (TRE_URE1) | Unidentified Registered Entity 2 (TRE_URE2) | NCRXXXXX | TRE2014014226 | CIP-009-3 | R4 | During a Compliance Audit, TRE_URE1 determined that TRE_URE2 had an issue with CIP-009-3 R4. TRE_URE2 failed to include backup and storage information required to successfully restore its S2 Netboxes and controller, used for PSP access control, as outlined in TRE_URE2’s recovery plans and recovery processes. The Netbox system components represent 20.6% of all TRE_URE2 CCAs. TRE_URE1 determined that TRE_URE2 had an issue with CIP-009-3 R4 for more than one year and nine months. | This issue posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Lacking processes and procedures for the backup and storage of information required to restore Critical Cyber Assets could lead to the inability to successfully restore those Critical Cyber Assets in the event of an outage. In none of the TRE_URE2-provided documents is there a description of the processes and procedures for the backup and storage of information required to restore Critical Cyber Assets. The risk to the reliability of the BPS was mitigated by the following factors. TRE_URE2 does back up Critical Cyber Assets nightly and/or has spare equipment available for replacement of failed devices. Additionally, there are automated server processes that backup configurations for CCA firewalls and switches. No actual harm is known to have occurred. TRE_URE1 considered TRE_URE2’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, TRE_URE2: 1) updated the recovery plans for Cyber Assets documentation to include backups; 2) added steps for backing up information from Cyber Assets as required. This change includes details on the types of backup and frequency of backups for each type of CCA. 3) modified the backup and recovery procedure to require that the annual review of the backup and recovery documentation also include a comparison with the current CCA list. This will ensure that all types of CCAs are documented. TRE_URE1 has verified the completion of all mitigation activity.
2015-03-31 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 3 (TRE_URE3) | NCRXXXXX | TRE2014014379 | CIP-005-3a | R1 | During a Compliance Audit, Texas RE determined that TRE_URE3 had an issue with CIP-005-3a R1. TRE_URE3 failed to ensure that the identified Critical Cyber Assets (CCAs) were within the appropriate Electronic Security Perimeters (ESPs). The root cause was a failure to comprehend the requirements of CIP-005-3 R1. Texas RE determined that TRE_URE3 had an issue with CIP-005-3 R1 for more than two years and two months. | This issue posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Although TRE_URE3 has an air-gapped network, TRE_URE3’s failure to conduct a CVA on all in-scope assets could have resulted in a compromise of the SCADA/EMS network via the ERCOT ICCP link with a remote possibility of a loss of load. The risk to the reliability of the BPS was mitigated by the following six factors. First, TRE_URE3 has multiple networks physically and logically separate from each other, the Internet, and the remaining internal network. The only outside party connected is ERCOT via ICCP link. This “air‐gapped” network design reduces the exposure to cyber threats, and the isolation provides significant security immunity from Internet and corporate internal network-based attacks. Second, TRE_URE3 does not allow remote interactive access (including dial-up) for operation of the SCADA system or vendor support activities. Third, where technically feasible CD/DVD drives and USB interfaces are physically disconnected, blocked or locked. These interfaces are logically disabled in password‐protected BIOS settings. Autoplay features are disabled. When these interfaces are temporarily enabled to perform necessary tasks, antivirus software automatically scans these drives when the media is inserted. The interfaces are then disabled after use. Fourth, if TRE_URE3 loses visibility of its SCADA/EMS systems, neighboring entities that interconnect with TRE_URE3’s infrastructure would be able to monitor and provide TRE_URE3 with real-time information to continue its operations. Fifth, in the event of a total loss of SCADA into TRE_URE3 Control Centers, Substation Technicians would be sent to man all substations and provide direct visibility and control capabilities into the substation transmission and distribution facilities. Communication between the Control Centers and the Substation Technicians can be accomplished through multiple sources. Sixth, TRE_URE3 has less than 200 MW of peak demand. No actual harm is known to have occurred. Texas RE considered TRE_URE3’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, TRE_URE3: 1) applied its RBAM to declare no CAs and CCAs, nullifying the need to establish, implement or document a security patch management program; and 2) evaluated the impact of CIP Version 5 Standards and Requirements and TRE_URE3 compliance. TRE_URE3 will complete the following mitigation activities within six months: 1) identify TRE_URE3 CAs and CCAs impacted by CIP Version 5 Standards and Requirements; 2) identify and establish ESPs to encompass all CCAs identified. This will ensure that TRE_URE3 meets CIP Version 5 Standards and Requirements; and 3) verify that all ESP network diagram documentation accurately depicts each identified CCA and its relation within the ESP.
2015-03-31 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 3 (TRE_URE3) | NCRXXXXX | TRE2014014380 | CIP-007-3a | R8 | During a Compliance Audit, Texas RE determined that TRE_URE3 had an issue with CIP-007-3a R8. TRE_URE3 failed to perform a cyber vulnerability assessment (CVA) of all Cyber Assets (CAs) within the Electronic Security Perimeter (ESP) at least annually. The root cause was a failure to comprehend the requirements of CIP-007-3a R8. Texas RE determined that TRE_URE3 had an issue with CIP-007-3a R8 for more than two years and two months. | This issue posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Although TRE_URE3 has an air-gapped network, TRE_URE3’s failure to conduct a CVA on all in-scope assets could have resulted in a compromise of the SCADA/EMS network via the ERCOT ICCP link with a remote possibility of a loss of load. The risk to the reliability of the BPS was mitigated by the following six factors. First, TRE_URE3 has multiple networks physically and logically separate from each other, the Internet, and the remaining internal network. The only outside party connected is ERCOT via ICCP link. This “air‐gapped” network design reduces the exposure to cyber threats, and the isolation provides significant security immunity from Internet and corporate internal network-based attacks. Second, TRE_URE3 does not allow remote interactive access (including dial-up) for operation of the SCADA system or vendor support activities. Third, where technically feasible CD/DVD drives and USB interfaces are physically disconnected, blocked or locked. These interfaces are logically disabled in password‐protected BIOS settings. Autoplay features are disabled. When these interfaces are temporarily enabled to perform necessary tasks, antivirus software automatically scans these drives when the media is inserted. The interfaces are then disabled after use. Fourth, if TRE_URE3 loses visibility of its SCADA/EMS systems, neighboring entities that interconnect with TRE_URE3’s infrastructure would be able to monitor and provide TRE_URE3 with real-time information to continue its operations. Fifth, in the event of a total loss of SCADA into TRE_URE3 Control Centers, Substation Technicians would be sent to man all substations and provide direct visibility and control capabilities into the substation transmission and distribution facilities. Communication between the Control Centers and the Substation Technicians can be accomplished through multiple sources. Sixth, TRE_URE3 has less than 200 MW of peak demand. No actual harm is known to have occurred. Texas RE considered TRE_URE3’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, TRE_URE3: 1) applied its RBAM to declare no CA and CCAs, nullifying the need to establish, implement or document a security patch management program; and 2) evaluated the impact of CIP Version 5 Standards and Requirements and TRE_URE3 compliance. TRE_URE3 will complete the following mitigation activities within six months: 1) identify TRE_URE3 CAs and CCAs impacted by CIP Version 5 Standards and Requirements; 2) evaluate viable consultant options to perform TRE_URE3 CVA to meet CIP Version 5 Standards and Requirements; and 3) prepare for and schedule a CVA to include all defined TRE_URE3 Critical Cyber Assets within the Electronic Security Perimeter to meet CIP Version 5 Standards and Requirements.
2015-03-31 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 3 (TRE_URE3) | NCRXXXXX | TRE2014014381 | CIP-007-3a | R3; R3.1; R3.2 | During a Compliance Audit, Texas RE determined that TRE_URE3 had an issue with CIP-007-3a R3.1 and R3.2. TRE_URE3 did not establish, document, or implement a security patch management program for all Cyber Assets within the Electronic Security Perimeter (R3). Additionally, TRE_URE3 failed to demonstrate when security patches became available, or when patches were assessed by TRE_URE3 personnel (R3.1). According to TRE_URE3, it reviewed and installed security patches but did not document the implementation of security patches (R3.2). The root cause of the issue is that TRE_URE3 did not complete the steps to establish a patch management program throughout the issue period. While a Cyber Security policy was developed by a third-party consultant, TRE_URE3 determined that it was not effective for its current environment and did not implement the policy. To date, TRE_URE3 does not have a security patch management program. Texas RE determined that TRE_URE3 had an issue with CIP-007-3a R3.1 and R3.2 for more than two years and two months. | This issue posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Although TRE_URE3 has an air-gapped network, TRE_URE3’s failure to conduct a CVA on all in-scope assets could have resulted in a compromise of the SCADA/EMS network via the ERCOT ICCP link with a remote possibility of a loss of load. The risk to the reliability of the BPS was mitigated by the following six factors. First, TRE_URE3 has multiple networks physically and logically separate from each other, the Internet, and the remaining internal network. The only outside party connected is ERCOT via ICCP link. This “air‐gapped” network design reduces the exposure to cyber threats, and the isolation provides significant security immunity from Internet and corporate internal network-based attacks. Second, TRE_URE3 does not allow remote interactive access (including dial-up) for operation of the SCADA system or vendor support activities. Third, where technically feasible CD/DVD drives and USB interfaces are physically disconnected, blocked or locked. These interfaces are logically disabled in password‐protected BIOS settings. Autoplay features are disabled. When these interfaces are temporarily enabled to perform necessary tasks, antivirus software automatically scans these drives when the media is inserted. The interfaces are then disabled after use. Fourth, if TRE_URE3 loses visibility of its SCADA/EMS systems, neighboring entities that interconnect with TRE_URE3’s infrastructure would be able to monitor and provide TRE_URE3 with real-time information to continue its operations. Fifth, in the event of a total loss of SCADA into TRE_URE3 Control Centers, Substation Technicians would be sent to man all substations and provide direct visibility and control capabilities into the substation transmission and distribution facilities. Communication between the Control Centers and the Substation Technicians can be accomplished through multiple sources. Sixth, TRE_URE3 has less than 200 MW of peak demand. No actual harm is known to have occurred. Texas RE considered TRE_URE3’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, TRE_URE3: 1) applied its RBAM to declare no CA and CCAs, nullifying the need to establish, implement or document a security patch management program; 2) evaluated the impact of CIP Version 5 Standards and Requirements and TRE_URE3 compliance. TRE_URE3 will complete the following mitigation activities within six months: 1) identify TRE_URE3 CAs and CCAs impacted by CIP Version 5 Standards and Requirements; 2) evaluate patch management options available for TRE_URE3 defined CCA; and 3) fully implement a patch management evaluation, documentation, and monitoring system for TRE_URE3 defined CCAs to meet CIP Version 5 Standards and Requirements.
2015-03-31 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 3 (TRE_URE3) | NCRXXXXX | TRE2014014382 | CIP-007-3a | R6; R.5 | During a Compliance Audit, Texas RE determined that TRE_URE3 had an issue with CIP-007-3a R6.5. TRE_URE3 failed to maintain records documenting its review of logs. Although TRE_URE3 states that it reviewed logs of monitored system events, TRE_URE3 provided no evidence of documenting such reviews as required in CIP-007-3a R6.5. The root cause of the issue is that TRE_URE3 did not establish a formal method to document the review of system events. Though TRE_URE3 states that it does routinely review these logs, TRE_URE3 has stated that they do not document these reviews. Texas RE determined that TRE_URE3 had an issue with CIP-007-3a R6.5 for more than two years and two months. | This issue posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Although TRE_URE3 has an air-gapped network, TRE_URE3’s failure to conduct a CVA on all in-scope assets could have resulted in a compromise of the SCADA/EMS network via the ERCOT ICCP link with a remote possibility of a loss of load. The risk to the reliability of the BPS was mitigated by the following six factors. First, TRE_URE3 has multiple networks physically and logically separate from each other, the Internet, and the remaining internal network. The only outside party connected is ERCOT via ICCP link. This “air‐gapped” network design reduces the exposure to cyber threats, and the isolation provides significant security immunity from Internet and corporate internal network-based attacks. Second, TRE_URE3 does not allow remote interactive access (including dial-up) for operation of the SCADA system or vendor support activities. Third, where technically feasible CD/DVD drives and USB interfaces are physically disconnected, blocked or locked. These interfaces are logically disabled in password‐protected BIOS settings. Autoplay features are disabled. When these interfaces are temporarily enabled to perform necessary tasks, antivirus software automatically scans these drives when the media is inserted. The interfaces are then disabled after use. Fourth, if TRE_URE3 loses visibility of its SCADA/EMS systems, neighboring entities that interconnect with TRE_URE3’s infrastructure would be able to monitor and provide TRE_URE3 with real-time information to continue its operations. Fifth, in the event of a total loss of SCADA into TRE_URE3 Control Centers, Substation Technicians would be sent to man all substations and provide direct visibility and control capabilities into the substation transmission and distribution facilities. Communication between the Control Centers and the Substation Technicians can be accomplished through multiple sources. Sixth, TRE_URE3 has less than 200 MW of peak demand. No actual harm is known to have occurred. Texas RE considered TRE_URE3’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, TRE_URE3: 1) applied its RBAM to declare no CA and CCAs, nullifying the need to establish, implement or document a security patch management program; and 2) evaluated the impact of CIP Version 5 Standards and Requirements and TRE_URE3 compliance. TRE_URE3 will complete the following mitigation activities within six months: 1) identify TRE_URE3 CAs and CCAs impacted by CIP Version 5 Standards and Requirements; 2) evaluate types of logging and log review software options available for logging system events related to cyber security. 3) implement process of reviewing, logging, and document maintenance of system events related to cyber security.
2015-01-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2013012417 | CIP-003-1 | R5 | ReliabilityFirst conducted a Compliance Audit of RFC_URE1, during which ReliabilityFirst discovered that RFC_URE1 had an issue with CIP-003-1 R5. RFC_URE1 failed to maintain its list of designated personnel who are responsible for authorizing access to protected information. RFC_URE1 uses a network storage drive to securely store a small subset of Critical Cyber Asset (CCA) information. RFC_URE1 controls access to this shared storage through its access management procedure. The information owner for this CCA information reviews and authorizes all the individuals who have access to the storage drive. ReliabilityFirst discovered that for three administrator groups that were identified as having access to this shared storage, the information owner did not explicitly authorize their access to this shared storage. As a result, members of RFC_URE1’s administrator, data administrator, and domain administrator groups had full control to the protected information resulting in unauthorized and excessive access to CCA information. RFC_URE1’s administrators had access (read/write, e.g. full control) to all RFC_URE1 CCAI by nature of the “administrator” role and responsibility. Each of the administrators had RFC_URE1 management approved access to the CCAI. However, the Requirement is that the CCAI owning management must also approve such access, and implied consent based on an employee's designation as an administrator does not meet the language of the Requirement. The root cause of the issue was a documentation oversight, which RFC_URE1 addresses in its Mitigation Plan. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following two factors. First, the administrators with access to the CCA information were long-term trusted employees of RFC_URE1. Second, they had valid personnel risk assessments and current cybersecurity training and received administrator privileges pursuant to RFC_URE1’s access management procedure. No harm is known to have occurred as a result of this issue ReliabilityFirst is committed to using the enforcement process to incent strong compliance programs and encourage the development of robust internal controls. ReliabilityFirst considered that it discovered all but one of the issues through Self-Reports and applied mitigating credit. ReliabilityFirst considered whether the facts of these issues constitute repetitive infractions. This is RFC_URE1's first issue with CIP-003-1 R5, and as a result, ReliabilityFirst did not consider RFC_URE1's violation history. | To mitigate this issue, RFC_URE1: 1) identified all individuals who have administrator or equivalent privileges on the document repositories used for storing CCA information; 2) enhanced its annual process to review and authorize access to CCA information to include certain system administrators; and 3) communicated the process and list of individuals to all information owners. ReliabilityFirst has verified the completion of all mitigation activity.
2015-01-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2013013141 | CIP-004-3 | R3.2 | RFC_URE1 submitted a Self-Report to ReliabilityFirst stating that it had an issue with CIP-004-3 R3.2. RFC_URE1 uses a vendor's system to conduct all personnel risk assessements (PRAs). RFC_URE1's Human Resources (HR) staff maintains access to the vendor's system, which stores background check results. RFC_URE1’s HR specialists also enter PRA completion dates from the vendor's system into RFC_URE1’s centralized HR database. Prior to RFC_URE1’s switch to vendor's system, RFC_URE1 used a prior vendor to conduct PRAs. The prior vendor would send a paper copy of PRA results to RFC_URE1 and, typically, RFC_URE1’s HR staff tracked the successful completion of a PRA using a spreadsheet. As an improvement to the process, RFC_URE1’s HR staff entered the completion dates for PRAs that the prior vendor conducted into RFC_URE1’s centralized HR database. During that transition, RFC_URE1 incorrectly entered into the database one employee’s PRA completion date., two years later than the actual date. As such, the root cause of the issue was human error. During the process of initiating employees’ repeat PRAs, RFC_URE1 discovered that one employee did not appear to have an initial PRA listed in the vendor's system. After further investigation, RFC_URE1 discovered that the prior vendor conducted the initial PRA for this employee. However, the date listed in RFC_URE1’s database for the initial PRA was not the same date as stated in the prior vendor’s PRA report. RFC_URE1 determined that when it transferred the PRAs that the prior vendor conducted into RFC_URE1’s database, RFC_URE1 staff incorrectly entered the actual PRA date. As a result, RFC_URE1 did not conduct a PRA for this employee within seven years of the initial PRA, as required by CIP-004-3a R3.2. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because of the following factors. The employee continues to be in good standing and the PRA did not include any adverse findings. No harm is known to have occured. ReliabilityFirst considered whether the facts of these issues constitute repetitive infractions. RFC_URE1 has had previous issues with CIP-004-1 R3.2. The two previous issues with CIP-004-1 R3.2 are unrelated to the current issue with CIP-004-1 R3.2. The current issue with CIP-004-1 R3.2 relates to an error in moving old data to a new system to track PRAs. One previous issue with CIP-004-1 R3.2 resulted from an error in calculating the date by which a PRA needed to be completed and the other issue resulted from an employee inadvertently administering PRAs to only employees and not contractors, as required by the Standard. Accordingly, ReliabilityFirst did not consider this previous conduct as an aggravating factor in the penalty determination. ReliabilityFirst considered RFC_URE1's compliance history and determined that the instant issue was appropriate for FFT treatment because: ReliabilityFirst considered certain aspects of RFC_URE1’s internal compliance program as mitigating factors. | To mitigate this issue, RFC_URE1: 1) completed the repeat PRA for the employee and requested an updated report from the current vendor; and 2) reviewed all background checks to ensure dates align between the current vendor and the HR database by conducting a reconciliation of the dates listed in the current vendor's system with the information listed in RFC_URE1’s HR database. ReliabilityFirst has verified the completion of all mitigation activity.
2015-01-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2013012171 | CIP-005-1 | R1 | RFC_URE1submitted Self-Reports to ReliabilityFirst stating that it had issues with CIP-005-1 R1. The Self-Reports addressed two instances of noncompliance. Regarding the first instance of noncompliance, RFC_URE1 discovered that four domain name server (DNS) appliances, which RFC_URE1 identified as Critical Cyber Assets (CCAs), were attached to a network that was not located within RFC_URE1’s defined Electronic Security Perimeters (ESPs). The reason the DNS appliances did not reside within a defined ESP was because RFC_URE1 believed that the DNS appliances were “self-contained ESPs.” More specifically, RFC_URE1 believed that the hardened configuration of the DNS appliances provided an ESP design through a network isolation configuration. Accordingly, RFC_URE1 mistakenly believed that the DNS appliances’ hardened configuration was a compliant security controls configuration. The second instance of non-compliance is an issue of not documenting a Cyber Asset as an ESP access point. More specifically, RFC_URE1 discovered that it did not document a router as an ESP access point. While the router’s network security configuration provided ESP boundary control as required by CIP-005-1 R1, RFC_URE1 did not document the router as such. The router provided electronic access control for an ESP that contained Critical Cyber Assets. RFC_URE1 replaced the application, but kept it as a tertiary backup. Despite the application being a tertiary backup, RFC_URE1 continued to maintain CCA designations for each of the Cyber Assets associated with the application. However, while the router’s network security configuration provided ESP boundary control, RFC_URE1 did not identify the router as an electronic access point to the ESP as required by CIP-005-1 R1. Also, when RFC_URE1 did identify the router as an electronic access point to the ESP, this identification necessitated additional configuration changes to RFC_URE1’s ESP. The root cause of the issue was human error as the router was not initially properly identified. | This issue posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. Specifically, although the DNS appliances had many of the security protections as defined by CIP-005-3, they did not have all of the requried security protections. However, risk was mitigated by the fact that the DNS appliances are provided by the vendor as security hardened, which means that they have many of the controls and protections of CCAs within a designated ESP. Also, because RFC_URE1 identified the DNS appliances as CCAs, RFC_URE1 applied security controls required by the CIP Standards to the DNS appliances, including, for example, access authorization. Additionally, while the DNS appliances do not have “deny by default” configuration for their primary function, they have “deny by default” configuration for administrative functions. RF determined that FFT treatment is appropriate because of the mitigating factors, the violation history as discussed below, and RFC_URE1's compliance program as discussed below. ReliabilityFirst determined that the second instance of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because the issue is largely a documentation issue. While RFC_URE1 did not properly document the router, the router’s configuration affords the ESP sufficient security control. No harm is known to have occurred as a result of these issues. ReliabilityFirst considered whether the facts of these issues constitute repetitive infractions. RFC_URE1 has had a previous issue with CIP-005-1 R1. RFC_URE1’s previous issue related to dial-up accessible Cyber Assets in the ESP, while the current issue relates to RFC_URE1’s incorrect belief that it was compliant with respect to DNS appliances because of their configuration and RFC_URE1’s improper documentation with respect to a router. Accordingly, ReliabilityFirst did not consider this previous conduct as an aggravating factor in the penalty determination. RF considered RFC_URE1's compliance history and determined that the instant issue was appropriate for FFT treatment because: ReliabilityFirst considered certain aspects of RFC_URE1’s internal compliance program as mitigating factors. | To mitigate this issue, RFC_URE1: 1) reviewed the system configuration of existing ESP access points; 2) remediated any issues discovered in the review process; and 3) reviewed, revised, and updated its process to establish an ESP.
2015-01-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2013011749 | CIP-007-3a | R5 | RFC_URE1 submitted a Self-Report to ReliabilityFirst stating that it had an issue with CIP-007-3a R5. RFC_URE1 performs an annual validation exercise to review compliance with CIP-007-3 R5.3.3, which includes examining and validating password change records and evidence. This process drives the execution of password change activities for system shared and default accounts in cases where RFC_URE1 is required to annually change passwords. When RFC_URE1 completed its annual password change effort, RFC_URE1 identified nine accounts where RFC_URE1 did not change the passwords within the annual timeframe. For four accounts, RFC_URE1 did not change the passwords because RFC_URE1 believed it was not technically feasible to do so. RFC_URE1 discovered that it had not filed Technical Feasibility Exceptions and that it was, in fact, feasible to change the passwords. For five other accounts, RFC_URE1 inadvertently omitted the accounts from the scope of password changes. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following four factors. First, in six of the nine instances of noncompliance, the accounts at issue are system accounts used by automated functions required for normal operation of the Cyber Assets, reducing the likelihood that these accounts would be shared with unauthorized individuals. The accounts are considered service accounts that are intended only for system function and not administrator use. Also, only those individuals on an authorized list are permitted to know the passwords for these systems. Second, in two of the nine instances of noncompliance, the accounts at issue were accounts that are locked due to the password being configured but unknown, which prevents the password from being reset without operational impact. Third, the last instance of noncompliance is a two-factor identification-enabled account that RFC_URE1 system administrators use for functional testing. Thus, another factor of authentication was required in addition to the expired password. RFC_URE1 has a robust monitoring and alerting infrastructure for its Cyber Assets. Therefore, if there had been any impact from RFC_URE1 failing to annually change system account passwords, this monitoring and alerting infrastructure would likely have detected it. Fourth, RFC_URE1 has multiple layers of security controls, both at the physical access and logical access layers. These security controls include, but are not limited to, technical controls such as physical access controls to buildings and secure rooms through key card access and/or biometric readers, logical access to RFC_URE1’s local area network with an authorized and enabled account, automated tools configured to detect security events such as unauthorized login attempts or actual unauthorized access, and procedural controls for account authorization that include authorized knowledge of shared and system ID account names and passwords for accounts that have access to Cyber Assets subject to compliance with CIP-007-3a R5.3.3. No harm is known to have occurred as a result of this issue. ReliabilityFirst considered whether the facts of these issues constitute repetitive infractions. RFC_URE1 has two previous issues with CIP-007-3a R5, one of which related to password composition criteria, which is not the case here. RFC_URE1’s other previous issue with CIP-007-3a R5 is arguably indicative of repetitive conduct leading to a violation of CIP-007-3a R5, and therefore ReliabilityFirst considered this repetitive conduct as an aggravating factor in its penalty determination. ReliabilityFirst considered RFC_URE1's compliance history and determined that the instant issue was appropriate for FFT treatment because: However, despite this arguably repetitive conduct, ReliabilityFirst determined that a monetary penalty is not warranted because of the nature of the issue, the fact that RFC_URE1 identified it through execution of existing controls and self-reported it to ReliabilityFirst, and RFC_URE1’s clear commitment to strengthening its internal controls and preventing recurrence of noncompliance as demonstrated by RFC_URE1’s mitigation efforts and its compliance program. ReliabilityFirst considered certain aspects of RFC_URE1’s internal compliance program as mitigating factors. | To mitigate this issue, RFC_URE1: 1) changed the passwords at issue; 2) verified password changes; and 3) identified and implemented enhancements for account identification, including modifying existing controls to help ensure that RFC_URE1 does not omit these types of accounts in the future. ReliabilityFirst has verified the completion of all mitigation activity.
2015-01-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2013012172 | CIP-007-3a | R7.1 | RFC_URE1 submitted a Self-Report to ReliabilityFirst stating that it had an issue with CIP-007-3a R7. During RFC_URE1’s review of its Intrusion Detection Systems deployment, RFC_URE1 discovered that it could not locate one Cyber Asset that RFC_URE1 previously retired. The Cyber Asset was used in monitoring ESPs. Upon further investigation, RFC_URE1 discovered that when it replaced the Cyber Asset, RFC_URE1 placed it on the floor in a PSP for disposal on a later date. During that time, RFC_URE1 physically secured it to prevent unauthorized access. However, RFC_URE1 accidentally picked up the Cyber Asset for disposal, stored it in a RFC_URE1 warehouse, and then sent it to a salvage vendor. Prior to the salvage vendor destroying the device, RFC_URE1 tracked down the Cyber Asset and retrieved it from the vendor. After RFC_URE1 retrieved the Cyber Asset from the salvage vendor, RFC_URE1 stored the Cyber Asset in a Physical Security Perimeter (PSP) until it could review the situation. RFC_URE1 erased the data storage media. The root cause of the issue was inadequate training. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following two factors. First, the Cyber Asset was within RFC_URE1’s possession for all but five days of the duration of this issue, which decreased the likelihood of unauthorized access. Additionally, access control to the Cyber Asset was restricted to authorized users using strong passwords. No harm is known to have occurred. ReliabilityFirst considered whether the facts of these issues constitute repetitive infractions. This is RFC_URE1's first issue with CIP-007-3a R7.1, and as a result, ReliabilityFirst did not consider RFC_URE1's violation history. | To mitigate this issue, RFC_URE1: 1) located, retrieved, and secured the missing Cyber Asset; 2) disposed of the Cyber Asset; and 3) conducted training for personnel on the disposal of Cyber Assets used for cybersecurity event monitoring, intrusion detection, and vulnerability scanning. ReliabilityFirst has verified the completion of all mitigation activity.
2015-01-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2013011750 | CIP-007-3a | R9 | RFC_URE1 submitted a Self-Report to ReliabilityFirst stating that it had an issue with CIP-007-3a R9. In accordance with the requirements of CIP-007-3a R7, RFC_URE1 has a formal procedure for disposing and redeploying Cyber Assets within the Electronic Security Perimeter (ESP) that requires RFC_URE1 to destruct or remove all data from internal disks in the event that the Cyber Asset is disposed or redeployed. RFC_URE1 physically relocated two Cyber Assets from their original ESP location to a different ESP location. RFC_URE1 management authorized a diversion from the documented procedure for disposing and redeploying Cyber Assets such that RFC_URE1 did not destroy or erase the Cyber Assets’ internal disks prior to redeploying them into the production ESP environment because the Cyber Assets retained their original function when installed in the destination location. RFC_URE1 management acknowledged and approved this change to the controls documented in the formal procedure. However, despite this acknowledgement, as a result of human error, RFC_URE1 did not update the procedure to address the permitted relocation method within 30 calendar days of authorizing that change as required by CIP-007-3a R9. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because this was only a documentation error, and RFC_URE1 did not use the revised relocation method that constituted a change to the formal procedure during the timeframe of the issue. Thus, no harm is known to have occurred. ReliabilityFirst considered whether the facts of these issues constitute repetitive infractions. This is RFC_URE1's first issue with CIP-007-3a R9, and as a result, ReliabilityFirst did not consider RFC_URE1's violation history. | To mitigate this issue, RFC_URE1: 1) discontinued use of the undocumented control for the relocation of Cyber Assets until it updated the formal procedure; 2) updated the formal procedure; and 3) updated the documentation for other Cyber Assets that were not at issue. ReliabilityFirst has verified the completion of all mitigation activity.
2015-01-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2014014404 | CIP-005-3a | R1 | SPPRE_URE1 submitted a Self-Report stating that it had an issue of noncompliance with CIP-005-3a R1.5. In six instances, SPPRE_URE1 tested changes to access point firewall (firewall) Access Control Lists (ACLs) on a firewall in the production environment instead of testing on the firewall in the development (testing) environment; therefore, SPPRE_URE1 did not ensure that significant changes to Cyber Assets would not adversely affect existing cyber security controls (CIP-007-3 R1). | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System. The access point firewall on which the testing was performed connects a non-critical Cyber Asset server to test devices that are located outside of the Electronic Security Perimeter (ESP). The access point firewall does not send traffic directly to the production SCADA applications. The firewall has security patching and anti-malware. The security controls of the firewall are checked whenever significant changes are implemented. SPPRE_URE1’s electronic access points are configured to only allow network traffic out of the ESP. Because SPPRE_URE1 denies access to devices that attempt to communicate inside the ESP from outside the ESP, the probability of unauthorized access to SPPRE_URE1’s Cyber Assets within the ESP is unlikely. No Cyber Assets within the ESP have internet access. SPPRE_URE1 utilizes a Network Intrusion Detection System (NIDS) within its ESP to monitor and alarm for unauthorized access. The NIDS is monitored during office hours by SPPRE_URE1 personnel and sends alarms to authorized personnel on a 24x7 basis. No harm occurred to any SPPRE_URE1 Cyber Assets as a result of the non-compliance. | To mitigate this issue, SPPRE_URE1: 1) Reviewed its CIP-007-3 R1 test processes with the employee who performed the testing to ensure that the employee tests changes in the test environment. 2) Instructed the employee to perform testing again on a firewall in the development environment according to CIP-007-3 R1 processes. 3) Updated SPPRE_URE1's template used to document the testing process for firewall ACL changes with an initial step to confirm that the test devices reside outside of the ESP. SPP RE has verified the completion of all mitigation activity.
2015-01-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPPRE_URE2) | NCRXXXXX | SPP2014014243 | CIP-004-3a | R3 | SPPRE_URE2 submitted a Self-Report to SPP RE stating that it had an issue of non-compliance with CIP-004-3, R3.1. During a seven-year background check re-screen the identity verification for one contractor was not completed as required by CIP-004-3 R3.1. During the re-screen, the individual’s wife’s name was found, rendering the social security number trace “not verified.” SPPRE_URE2 identified this issue during a proactive review process and contacted the contract company, who employed the individual at issue, for the verified identity information. | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). The contractor’s social security number had been verified on the initial Personnel Risk Assessment (PRA). The contractor’s criminal background check was completed with no issues; only the identity verification was incomplete. The contractor had physical access to two control centers during the period of time the identity verification was incomplete. Both control centers are staffed 24/7, and the individual did not have logical access. This issue has been mitigated with the revocation of access followed by completion of identity verification. All of SPPRE_URE2’s substation Cyber Assets reside within Physical Security Perimeters, and are logically protected behind Electronic Security Perimeter (ESP) firewalls which require network access and authentication for remote access. Unauthenticated access attempts trigger an alert and subsequent cyber security investigation. No actual harm occurred to any SPPRE_URE2 substation Cyber Assets as a result of the noncompliance. | To mitigate this issue, SPPRE_URE2 completed or will complete the following mitigation activities within 90 days: 1) Revoked the contractor’s access, completed identity verification, and then reinstated the contractor’s access; 2) Added a secondary review in its CIP PRA process; and 3) Will update its documented procedure to include the secondary CIP PRA review.
2015-01-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2014013597 | CIP-006-3c | R1 | WECC_URE1 submitted a Self-Certification stating that it had an issue of CIP-006-3c R1. Specifically, WECC_URE1’s Physical Security Perimeter (PSP) checkup, WECC_URE1 discovered that it did not have a completely enclosed border around its Backup Control Center (BCC) PSP-designated area. This area consisted of three rooms. For two of the rooms, three of the four walls incorporated mesh screens to provide full protection from the ground up through the dropped ceiling through the dropped ceiling tiles to the hard ceiling. However, the fourth wall which is the wall shared by the BCC rooms (PSP area) and the backup (non PSP area), had a 96-100 inch square opening just right above the acoustical tiles of the dropped ceiling. The root cause of this was human error, in that WECC_URE1 did verify that the room was in fact, enclosed by six walls. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE1 failed to ensure a completely enclosed (six wall) border was established at an identified PSP, as required by CIP 006-3c R1. Failure to secure CAs within an PSP could result in unauthorized access through the gap in the PSP to the Critical Cyber Assets (CCAs) to go unnoticed. This could possibly allow malicious access to the two CCAs within the PSP. WECC_URE1 had strong preventative controls so that the reliable operation of the BES is not compromised. Specifically, the building the PSP resided within was access controlled by badge readers, thus WECC_URE1 approved access to any individual entering the building where this PSP resided with a badge. The room where the gap existed that was adjacent to the PSP was also access controlled and logged via a badge reader system, limiting the likelihood of outsider threat as the outsider would not have had the access privileges to enter the building. Additionally, there was an onsite security guard 24 hours a day 7 days a week roaming the building that would help deter any individual from exploiting the gap in the ceiling. Lastly, the gap in the perimeter was high above the ground and obstructed by construction equipment, which would delay any individual attempting to use the gap to gain unauthorized access to the PSP. These obstructions would also have given the roaming security guard a better chance to detect and prevent the unauthorized access attempt as a malicious individual would need time and potentially a ladder to move the obstructions and utilize the gap. Furthermore, the gap itself was less than 100 square inches in diameter. Further, WECC_URE1 implemented good detective controls to detect unauthorized access. Specifically, WECC_URE1 implemented cameras located within the PSP monitoring access at the access points. Although, the cameras were not directly monitoring the wall where the gap existed, the presence of the cameras within the PSP gave WECC_URE1 a chance of detecting an unauthorized individual as the individual may have appeared within the camera’s view during the unauthorized entrance. No harm is known to have occured. WECC considered WECC_URE1's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, WECC_URE1: 1) installed a wire mesh between walls, drop ceiling, and fixed the top ceiling to close exposed gap between BCC rooms the area; 2) continue to do an annual check of all PSPs to verify if PSPs are compliant. WECC has verified the completion of all mitigation activity.
2015-01-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2014013970 | CIP-002-3 | R1 | During a Compliance Audit WECC determined that WECC_URE2 had an issue of CIP-002-3 R1. Specifically, WECC_URE2 implemented its Risk-Based Assessment Methodology (RBAM) Version 3. Version 3 used a pure application of the CIP-002-4 Bright Line Criteria and that this approach did not rely on a risk-based assessment methodology to identify Critical Assets. WECC_URE2’s implementation of Version 3 resulted in a minimal change of one substation to WECC_URE2’s list of Critical Assets. The Audit Team determined that the UVLS system was retained as a distinct Critical Asset. WECC_URE2 implemented its Risk-Based Assessment Methodology Version 4. WECC_URE2 removed specific references to the Bright Line Criteria and included rationale to support the use of the criteria, but the Audit Team determined these changes did not significantly add a risk-based component to WECC_URE2’s approach. As a result, Version 4 also used a pure application of the CIP-002-4 Bright Line Criteria instead of a valid CIP-002-3 risk-based approach. The Cyber Security Standards Guidance Approach 1 states that an entity’s RBAM risk-based discussion may reach conclusions supported by the CIP Version 4 bright-line criteria. The root cause of this failure was WECC_URE2’s premature application of the CIP-002-4 Bright Line Criteria approach. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. This failure resulted in the declassification of one substation as a Critical Asset. Consequently, Critical Cyber Assets associated with this one substation may not have been afforded all CIP protections. This could then result in improper control and monitoring of physical and logical access to devices located within this substation. The potential risk associated with this failure is reduced because although WECC_URE2 used Bright Line Criteria, WECC_URE2’s Critical Asset Identification Methodology considered seven asset classes, included evaluation criteria, and included procedures for developing a list of Critical Assets. WECC_URE2 also ensured that Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeters resided within an identified Physical Security Perimeter. WECC_URE2 monitored and logged physical access at all access points to the Physical Security Perimeters twenty-four hours a day, seven days a week. WECC_URE2 implemented anti-virus software and other malicious software prevention tools on all Cyber Assets. WECC_URE2 also implemented controls that minimize the risk of unauthorized entrance. No harm is known to have occured. | To mitigate this issue, WECC_URE2: 1) implemented NERC published Cyber Security Standards Guidance Approach 1 which states that an entity’s RBAM risk-based discussion may reach conclusions supported by the CIP Version 4 bright-line criteria.
2015-01-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2014014235 | CIP-009-3 | R4 | WECC_URE3 submitted a Self-Report stating that it had an issue of CIP-009-3 R4. Specifically, WECC_URE3 failed to manually update its SQL database for four devices with the backup information, such as the time and date of the backup, the name of the device, the type of backup, and the storage location of the backup. The devices in scope are two Energy Management System (EMS) workstations that are classified as Critical Cyber Assets (CCAs) and two Electronic Access Control Monitoring (EACM) devices. WECC_URE3 stated that they had the backups for the devices in scope, but no records of the date and time when the backups were done in their SQL Database. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE3 failed to implement its processes and procedures for the backup and storage of information required to restore CCAs for four devices. Specifically, in 2013 WECC_URE3 failed to follow its internal process to manually update its SQL Database with the latest backup information. Failing to implement its processes and procedures for the backup and storage of information required to restore CCAs could result in WECC_URE3 not having valid backups and the necessary steps to restore the backups to a spare EMS workstation in a timely manner. WECC_URE3 stated that it would take eight hours to rebuild one EMS workstation from scratch with the on-site media. If the EMS workstations were to fail and required recovery, it could delay the restoration for eight hours. WECC_URE3 implemented strong preventative controls to prevent the failure of an EMS workstation from occurring. Specifically, WECC_URE3 stores the EMS backups at alternative sites in case one of the control centers is inaccessible. If a control center were to shut down due to the faulty hardware, bad weather, or a natural disaster, having the physical backups at alternative sites would allow WECC_URE3 to bring up spare EMS workstations in a short period of time. WECC_URE3 also has seven EMS operator workstations available with only four in use on any given shift. This lowers the likelihood of all EMS workstations being down and/or damaged simultaneously and eliminating access to the BES. WECC_URE3 also has a Backup Control Center (BCC) that is two miles away from the Primary Control Center (PCC) as a preventative control. The operators have the capacity of driving to the BCC and maintaining WECC_URE3’s generation. Additionally, WECC_URE3 implemented good detective controls to detect the failure of an EMS workstation. Specifically, WECC_URE3 implemented alert messaging that could notify operators if any of the seven EMS workstations went down at the PCC and/or at the BCC regardless of an operator presence. This could allow WECC_URE3 to restore an EMS image on a spare EMS workstation and be operational in a few hours. No harm is known to have occurred. WECC considered WECC_URE3's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, WECC_URE3: 1) completed re-writing the Cyber Asset Installation Job Plan as a checklist, including a check specific to the completion of backup media testing and verification documentation; 2) completed changing the CIP-009 R5 backup media testing and verification manual process to occur twice annually; and 3) completed instituting a work guideline to perform a peer review of the checklist to ensure completion of required CIP activities prior to placing new assets in-service. WECC has verified the completion of all mitigation activity.
2015-01-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2014014236 | CIP-009-3 | R5 | WECC_URE3 submitted a Self-Report stating that it had an issue of CIP-009-3 R5. Specifically, WECC_URE3 failed to manually update its SQL database with the backup information for four devices. The devices in scope are two Energy Management System (EMS) workstations that are classified as Critical Cyber Assets (CCAs) and two Electronic Access Control Monitoring (EACM) devices. WECC_URE3 stated that they had the backups for the devices in scope, but no records of the date and time when the backups were done in their SQL Database. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE3 failed to annually to test backup media which contained information essential to recovery for four devices. Specifically, in 2013 WECC_URE3 failed to follow its internal process to manually update its SQL Database with the latest backup information. Failing to test and restore backup media that is essential to recover CCAs could result in not having valid backups and the necessary steps to restore the backups to a spare EMS workstation in a timely manner. WECC_URE3 stated that it would take eight hours to rebuild one EMS workstation from scratch with the on-site media. If the EMS workstations were to fail and required recovery, it could delay the restoration for eight hours. WECC_URE3 implemented strong preventative controls to prevent the failure of an EMS workstation from occurring. Specifically, WECC_URE3 stores the EMS backups at alternative sites in case one of the control centers is inaccessible. If a control center were to shut down due to the faulty hardware, bad weather, or a natural disaster, having the physical backups at an alternative site would allow WECC_URE3 to bring up spare EMS workstations in a short period of time. WECC_URE3 also has seven EMS operator workstations available with only four in use on any given shift. This lowers the likelihood of all EMS workstations being down and/or damaged simultaneously and eliminating access to the BES. WECC_URE3 also has a Backup Control Center (BCC) that is two miles away from the Primary Control Center (PCC) as a preventative control. The operators have the capacity of driving to the BCC and maintaining WECC_URE3’s generation. Additionally, WECC_URE3 implemented good detective controls to detect the failure of an EMS workstation. Specifically, WECC_URE3 implemented alert messaging that could notify operators if any of the seven EMS workstations went down at the PCC and/or at the BCC regardless of an operator presence. This could allow WECC_URE3 to restore an EMS image on a spare EMS workstation and be operational in a few hours. No harm is known to have occured. WECC considered WECC_URE3's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, WECC_URE3: 1) completed re-writing the Cyber Asset Installation Job Plan as a checklist, including a check specific to the completion of backup media testing and verification documentation; 2) completed changing the CIP-009 R5 backup media testing and verification manual process to occur twice annually; and 3) completed instituting a work guideline to perform a peer review of the checklist to ensure completion of required CIP activities prior to placing new assets in-service. WECC has verified the completion of all mitigation activity.
2014-12-30 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2013011673 | CIP-004-3 | R2; R2.1 | SERC_URE1 submitted a Self-Report stating that it had an issue with CIP-004-3 R2.1. SERC_URE1 failed to train three employees prior to granting them physical access to Critical Cyber Assets (CCAs). During an internal review SERC_URE1 discovered that three employees had not completed the required training prior to being granted physical access due to being assigned the incorrect training course. SERC learned that courses were assigned manually by a training coordinator, who did not have the correct understanding of the training requirements and administered the wrong course. The three employees were granted access approximately seven months prior to SERC_URE1's discovery of the issue. The same day as the discovery, access was removed. The duration of this issue was from when access was granted to the three employees through when access was revoked. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failure to train personnel could have resulted in unawareness of the proper use of Physical Security Perimeter access, CCAs, and other CCA information in accordance with SERC_URE1’s policies. The three employees had passed the required personnel risk assessment prior to physical access being granted, were long term employees, and in good standing with the company. SERC considered SERC_URE1's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, SERC_URE1: 1) created a new color coded template to prevent granting access to individuals prior to taking the required training.
2014-12-30 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2013011701 | CIP-004-3 | R4; R4.2 | SERC_URE1 submitted a Self-Report to SERC stating that it had an issue with CIP-004-3 R4. SERC_URE1 failed to revoke access within seven calendar days for personnel who no longer required access to Critical Cyber Assets (CCAs). According to SERC_URE1, an employee resigned and access was not revoked until 11 days later. SERC_URE1’s policy required the Human Resources department (HR) to make the appropriate notifications when an employee was terminated with or without cause. While HR made the notification, the receiving manager failed to remove the employee from the access list within seven calendar days. The duration of this issue was from seven days after the employee no longer required access to the CCAs through when access was revoked. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Personnel no longer authorized for access may have been able to gain physical access to CCAs. However, the employee only had physical access to one location, which is a manned twenty-four hours a day, seven days a week. The employee did not attempt to access the area after the employee’s last day. SERC considered SERC_URE1's compliance history and determined that the instant issue was appropriate for FFT treatment because the prior issue with CIP-004 R4 had a different root cause. | To mitigate this issue, SERC_URE1: 1) provided additional training for employees on the roles and responsibilities for adding and removing unescorted personnel.
2014-12-30 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2013012690 | CIP-003-3 | R4; R4.2 | During a Compliance Audit, SERC determined that SERC_URE1 had an issue with CIP-003-3 R4. SERC_URE1 failed to protect hard copies of information associated with Critical Cyber Assets (CCAs). SERC_URE1’s information protection policy addressed electronic forms of Critical Cyber Asset information (CCAI). However, the policy did not address hard copies of CCAI, one of the media types in use by SERC_URE1. The electronic forms were protected in accordance with SERC_URE1’s policy. The hard copies of CCAI were located within a Physical Security Perimeter (PSP) with restricted access. The duration of this issue was from when the Standard became mandatory and enforceable on SERC_URE1 through mitigation completion. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failure to protect all media types of CCAI could result in information being revealed to unauthorized personnel, which could compromise CCAs. However, access to CCAI at issue was limited to authorized personnel with approved personnel risk assessments and security training. In addition, SERC_URE1 maintained the hardcopies of CCAI within its PSPs. SERC considered SERC_URE1's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, SERC_URE1: 1) reviewed guidance documents provided by NERC and compared them to existing company policies for gaps and made corrections, as needed; 2) provided training to applicable personnel on the policy updates; 3) amended the year-end information protection interview forms to include the procedure updates. SERC has verified the completion of all mitigation activity.
2014-12-30 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 2 (SERC_URE2) | NCRXXXXX | SERC2014013858 | CIP-005-1 | R1 | SERC sent SERC_URE2 an initial notice of a compliance audit. Following the notice, SERC_URE2 submitted a Self-Report stating that it had an issue with CIP-005-3a R1. SERC_URE2 failed to properly document the serial communications access from a Remote Terminal Unit (RTU) to Critical Cyber Assets (CCAs) in an Electronic Security Perimeter (ESP) at one Critical Asset. SERC determined that this issue dated back to Version 1 of the Standard. SERC_URE2 identified this issue after comparing existing architecture drawings with actual communication infrastructure while performing a Cyber Vulnerability Assessment. SERC_URE2 identified CCA communication that was leaving and entering an ESP without an identified and documented access point. The CCA devices inside the ESP are serially connected to a RTU located outside the ESP. The RTU in turn provides serial communication to a separate facility over SERC_URE2 owned cables. SERC_URE2 failed to document an access point for the serial communication entering and leaving the ESP because it incorrectly assumed that serial communication was exempt from CIP-005 requirements. SERC_URE2 reviewed the NERC CIP-005 Compliance Analysis Report – Electronic Security Perimeter(s) and then reported this issue to SERC. This issue lasted from when the Standard became mandatory and enforceable until SERC_URE2 competed the mitigating activities. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failing to identify and document an access point to an ESP could lead to a failure to manage and properly protect that access point, potentially reducing the protection provided by the ESP. However, the risk was reduced because electronic access to the ESP requires two factor authentication. A security gateway monitored the ESP activity, controlled access, and created an audit trail of all access. Additionally, SERC_URE2 exclusively owns and operates the communications infrastructure over which the serial communications occurred, which limited potential unauthorized access. Furthermore, a staffed security checkpoint monitored and controlled all ingress and egress at the facility where the devices reside. Lastly, all of the devices involved are located inside of a locked building, which resides behind a locked gate. No harm is known to have occurred. SERC considered SERC_URE2's compliance history and determined that the instant issue was appropriate for FFT treatment. The previous instance involved a different sub-requirement and the underlying conduct in both instances was sufficiently different to warrant FFT treatment for this issue. | To mitigate this issue, SERC_URE2: 1) corrected its architecture drawing to document serial access from the RTU; and 2) conducted additional staff training regarding identification of serial communications as access points. SERC has verified the completion of all mitigation activity.
2014-12-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2014014162 | CIP-007-1 | R2; R2.1; R2.2; R2.3 | WECC_URE1 submitted a Self-Report stating that it had an issue with CIP-007-1 R2. Specifically, WECC_URE1 reported that it had failed to update its Technical Feasibility Exception (“TFE”) report to include switches and printers that were not capable of having only those ports and services required for operations enabled. The root cause of the remediated issue was lack of process. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Specifically, WECC_URE1 failed to update one TFE covering a total of 436 devices in 45 different locations, including switching stations, substations, communication centers, operations centers, and one control center. The devices included switches and printers, some of which are Energy Management System (“EMS”) devices. Failure to update TFEs could lead WECC_URE1 to fail to implement the additional controls needed to compensate for the technical inadequacies of the devices. A malicious person could scan the switches at the control center for vulnerable ports and services, and use malware to launch an attack against the vulnerabilities discovered. If the attack was successful, that person could take control of the switch, scan the devices connected to the switch for vulnerabilities and launch another malware attack against those devices. If the second attack were successful, and if those devices were SCADA devices, the person could take control and open/close relays and trip breakers, potentially resulting in a loss of up to approximately 20,000 MW of load. However, WECC_URE1 implemented good preventive and detective controls. As a preventive measure, WECC_URE1 uses an Intrusion Detection/Prevention System to monitor and alert all known threats. WECC_URE1 also uses separate networks for operations and management of control systems. Finally, WECC_URE1’s firewalls are configured to deny all access to downstream devices. As detective measures, WECC_URE1 uses real-time logging and reviewing to actively monitor all network devices. Also, WECC_URE1 does annual port scans across all Critical Cyber Asset networks and specifically looks and tests for vulnerabilities via open ports and services. No harm is known to have occurred. | To mitigate this issue, WECC_URE1: 1) standardized CIP cyber asset inventory list and updated its Critical Cyber Asset Identification to include list management; 2) coordinated SMEs to update CIP cyber asset inventory with new TFE ID numbers for each cyber asset; 3) scheduled semi-annual task to each asset area to review and update cyber asset TFE information prior to TFE compliance due date; 4) scheduled annual task to NERC Complaince to issue annual WECC TFE report; 5) updated procedure including a semi-annual review to manage CIP TFEs, annual review to report to WECC, and evaluating cyber assets for TFEs prior to commissioning; 6) developed and delivered training and implemented revised procedure using cyber asset inventory list; 7) performed assessment of procedure for effectiveness and stakeholders review results scheduled annual task to NERC Complaince to issue annual WECC TFE report; 8) reviewed, confirmed, and validatee evidence for accuracy, completeness, and relevance; and 9) approved and published revised procedure.
2014-12-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2014014163 | CIP-007-1 | R3 | WECC_URE1 submitted a Self-Report stating that, it had an issue with CIP-007-1 R3. Specifically, WECC_URE1 reported that it failed to file updated TFE reports to include two servers and nine printers. WECC_URE1 failed to update its TFE reports for two servers and nine printers that were unable to have cyber security software patches installed for all Cyber Assets within the Electronic Security Perimeter (“ESP”). The root cause of the violation is lack of process. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Specifically, WECC_URE1 failed to update two TFEs to include two servers and nine printers located at two locations, one of which is a control center. Failure to update TFEs could lead WECC_URE1 to fail to implement the additional controls needed to compensate for the technical inadequacies of the devices. If compensating controls are not in place, it could lead to vulnerabilities that could potentially lead to a loss of WECC_URE1’s approximate 20,000 MW of peak load. However, WECC_URE1 implemented good preventive and detective controls. As a preventive measure, WECC_URE1 uses an Intrusion Detection/Prevention System to monitor and alert all known threats. WECC_URE1 also uses separate networks for operations and management of control systems. Finally, WECC_URE1’s firewalls are configured to deny all access to downstream devices. As detective measures, WECC_URE1 uses real-time logging and reviewing to actively monitor all network devices. Also, WECC_URE1 does annual port scans across all Critical Cyber Asset networks and specifically looks and tests for vulnerabilities via open ports and services. No harm is known to have occured. | To mitigate this issue, WECC_URE1: 1) standardized CIP cyber asset inventory list and updated its Critical Cyber Asset Identification to include list management; 2) coordinated SMEs to update CIP cyber asset inventory with new TFE ID numbers for each cyber asset; 3) scheduled semi-annual task to each asset area to review and update cyber asset TFE information prior to TFE compliance due date; 4) scheduled annual task to NERC Complaince to issue annual WECC TFE report; 5) updated procedure including a semi-annual review to manage CIP TFEs, annual review to report to WECC, and evaluating cyber assets for TFEs prior to commissioning; 6) developed and delivered training and implemented revised procedure using cyber asset inventory list; 7) performed assessment of procedure for effectiveness and stakeholders review results scheduled annual task to NERC Complaince to issue annual WECC TFE report; 8) reviewed, confirmed, and validatee evidence for accuracy, completeness, and relevance; and 9) approved and published revised procedure.
2014-12-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2014014164 | CIP-007-1 | R5 | WECC_URE1 submitted a Self Report stating that it had an issue with CIP-007-1 R5. Specifically, Specifically, WECC_URE1 reported that it had failed to timely submit TFE reports to WECC for newly commissioned devices that do not have the capability to enforce password complexity requirements. WECC_URE1's TFEs covered an additional 2,134 devices, including 2 servers, 2 routers, 84 firewalls, 620 switches, 1209 relays, 4 clocks, 16 temperature modules, 12 printers, 140 communication processors, 13 communication processor IP servers, 13 power line carriers, 4 remote gateway dial-ups, and 13 transfer trip devices. These devices are located in 58 different locations. The root cause of the violation is lack of process. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Specifically, WECC_URE1 failed to update six TFEs covering a total of 4,314 devices in 58 different locations. The devices included servers, routers, firewalls, switches, relays, timekeepers, temperature modules, printers, communications processors, communications processor IP servers, power line carriers, remote gateway dial-ups and transfer trip devices. Failure to update TFEs could lead WECC_URE1 to fail to implement the additional controls needed to compensate for the technical inadequacies of the devices. If compensating controls are not in place, it could lead to vulnerabilities that could potentially lead to a loss of approxmiately 20,000 MW of peak load. However, WECC_URE1 implemented good preventive and detective controls. As a preventive measure, WECC_URE1 uses an Intrusion Detection/Prevention System to monitor and alert all known threats. WECC_URE1 also uses separate networks for operations and management of control systems. Finally, WECC_URE1’s firewalls are configured to deny all access to downstream devices. As detective measures, WECC_URE1 uses real-time logging and reviewing to actively monitor all network devices. Also, WECC_URE1 does annual port scans across all Critical Cyber Asset networks and specifically looks and tests for vulnerabilities via open ports and services. No harm is known to have occured. | To mitigate this issue, WECC_URE1: 1) standardized CIP cyber asset inventory list and updated its Critical Cyber Asset Identification to include list management; 2) coordinated SMEs to update CIP cyber asset inventory with new TFE ID numbers for each cyber asset; 3) scheduled semi-annual task to each asset area to review and update cyber asset TFE information prior to TFE compliance due date; 4) scheduled annual task to NERC Complaince to issue annual WECC TFE report; 5) updated procedure including a semi-annual review to manage CIP TFEs, annual review to report to WECC, and evaluating cyber assets for TFEs prior to commissioning; 6) developed and delivered training and implemented revised procedure using cyber asset inventory list; 7) performed assessment of procedure for effectiveness and stakeholders review results scheduled annual task to NERC Complaince to issue annual WECC TFE report; 8) reviewed, confirmed, and validatee evidence for accuracy, completeness, and relevance; and 9) approved and published revised procedure.
2014-12-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2014014165 | CIP-007-1 | R6 | WECC_URE1 submitted a Self Report stating that it had an issue with CIP-007-1 R6. Specifically, WECC_URE1 reported that if failed to submit updated TFE reports to WECC for devices that cannot use automated tools or organizational process controls to monitor system events that are related to cyber security. WECC_URE1 failed to update six TFE reports for 169 newly commissioned devices, including 2 PCs, 127 servers, 8 controllers, 12 printers, 4 time keepers, and 16 temperature modules. The root cause of the violation is lack of process. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Specifically, Failure to update TFEs could lead WECC_URE1 to fail to implement the additional controls needed to compensate for the technical inadequacies of the devices. If compensating controls are not in place, it could lead to vulnerabilities that could potentially lead to a loss of approximately 20,000 MW of peak load. However, WECC_URE1 implemented good preventive and detective controls. As a preventive measure, WECC_URE1 uses an Intrusion Detection/Prevention System to monitor and alert all known threats. WECC_URE1 also uses separate networks for operations and management of control systems. Finally, WECC_URE1’s firewalls are configured to deny all access to downstream devices. As detective measures, WECC_URE1 uses real-time logging and reviewing to actively monitor all network devices. Also, WECC_URE1 does annual port scans across all Critical Cyber Asset networks and specifically looks and tests for vulnerabilities via open ports and services. No harm is known to have occured. | To mitigate this issue, WECC_URE1: 1) standardized CIP cyber asset inventory list and updated its Critical Cyber Asset Identification to include list management; 2) coordinated SMEs to update CIP cyber asset inventory with new TFE ID numbers for each cyber asset; 3) scheduled semi-annual task to each asset area to review and update cyber asset TFE information prior to TFE compliance due date; 4) scheduled annual task to NERC Complaince to issue annual WECC TFE report; 5) updated procedure including a semi-annual review to manage CIP TFEs, annual review to report to WECC, and evaluating cyber assets for TFEs prior to commissioning; 6) developed and delivered training and implemented revised procedure using cyber asset inventory list; 7) performed assessment of procedure for effectiveness and stakeholders review results scheduled annual task to NERC Complaince to issue annual WECC TFE report; 8) reviewed, confirmed, and validatee evidence for accuracy, completeness, and relevance; and 9) approved and published revised procedure.
2014-12-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2014014303 | CIP-007-1 | R4 | WECC_URE2 submitted a Self Report stating that it had an issue with CIP-007-1 R4. Specifically, WECC_URE2 reported that it failed to timely submit Technical Feasibility Exception (“TFE”) reports to WECC for newly identified Critical Cyber Assets (“CCAs”) that do not have the capability to implement anti-virus software and other malicious software prevention tools to Cyber Assets within an Electronic Security Perimeter (“ESP”). Further, it was determined that WECC_URE2 failed to update four TFEs for sixty-three devices located within four Physical Security Perimeters ("PSP") and six ESPs that are incapable of using anti-virus or other malware prevention tools. The root cause of the remediated issue was human error. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Specifically, WECC_URE2 failed to update TFEs for sixty-three devices in four PSPs and six ESPs. The devices included servers, sensors, firewalls, log collectors, and satellite clocks. Failure to update TFEs could lead WECC_URE2 to fail to implement the additional controls needed to compensate for the technical inadequacies of the devices. If compensating controls are not in place, it could lead to vulnerabilities that could potentially lead to a loss of approximately 6,000 MW of peak load. However, WECC_URE2 implemented strong compensating controls. Specifically, WECC_URE2 implemented an air-gapped operational network that requires two-factor authentication over a remote connection and does not allow any direct access from devices outside of the operational network. WECC_URE2 also has a separate Intrusion Detection System, Intrusion Prevention System, and log collection for the operational network that could detect and/or prevent any potential malicious intrusions. Finally, the devices in scope are behind multiple layers of physical access and are located in a room with around the clock supervision. No harm is known to have occured. | To mitigate this issue, WECC_URE2: 1) submitted TFEs that cover all devices that do not have the capability to implement an anti-virus or malicious software prevention solutions.
2014-12-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2014014304 | CIP-007-1 | R5 | WECC_URE2 submitted a Self Report stating that it had an issue with CIP-007-1 R5. Specifically, WECC_URE2 reported that it had failed to submit timely a Technical Feasibility Exception ("TFE") report to WECC for newly identified Critical Cyber Assets ("CCAs") that do not have the capability to enforce password complexity requirements. Further, WECC_URE2 failed to update one TFE for forty-four devices including workstations, firewalls, intrusion detection and prevention systems ("IDSs"), intrustion prevention systems ("IPSs"), switches, and historical data collection devices. These devices are located in eight Physical Security Perimeters ("PSPs") and seven Electronic Security Perimeter ("ESPs") and are incapable of using passwords that are at least six characters long and use a combination of alpha, numeric, and "special" characters. The root cause of the remediated issue was human error. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Specifically, WECC_URE2 failed to update TFEs for sixty-three devices in four PSPs and six ESPs. The devices included servers, sensors, firewalls, log collectors, and satellite clocks. Failure to update TFEs could lead WECC_URE2 to fail to implement the additional controls needed to compensate for the technical inadequacies of the devices. If compensating controls are not in place, it could lead to vulnerabilities that could potentially lead to a loss of approximately 6,000 MW of peak load. However, WECC_URE2 implemented strong compensating controls. Specifically, WECC_URE2 implemented an air-gapped operational network that requires two-factor authentication over a remote connection and does not allow any direct access from devices outside of the operational network. WECC_URE2 also has a separate Intrusion Detection System, Intrusion Prevention System, and log collection for the operational network that could detect and/or prevent any potential malicious intrusions. Finally, the devices in scope are behind multiple layers of physical access and are located in a room with around the clock supervision. No harm is known to have occured. | To mitigate this issue, WECC_URE2: 1) submitted TFEs that cover all devices that are not able to meet NERC password complexity requirements.
2014-12-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2014014305 | CIP-007-1 | R6 | WECC_URE2 submitted a Self Report stating that it had an issue with CIP-007-1 R6. Specifically, WECC_URE2 reported that if failed to submit timely Technical Feasibility Exception ("TFE") reports to WECC for Cyber Assets within an Electronic Security Perimeter ("ESP") that do not have the capability to monitor, alert, or maintain logs for events related to cyber security. WECC_URE2 failed to update two TFE reports for two Global Positioning System ("GPS") clock devices that are incapable of monitoring system events related to cyber security. The root cause of the remediated issue was human error. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Specifically, WECC_URE2 failed to update two TFEs to include two substation clock devices. Failure to update TFEs could lead WECC_URE2 to fail to implement the additional controls needed to compensate for the technical inadequacies of the devices. If compensating controls are not in place, it could lead to vulnerabilities that could potentially lead to a loss of approximately 6,000 MW of peak load. However, WECC_URE2 implemented strong compensating controls. Specifically, WECC_URE2 implemented an air-gapped operational network that requires two-factor authentication over a remote connection and does not allow any direct access from devices outside of the operational network. WECC_URE2 also has a separate Intrusion Detection System, Intrusion Prevention System, and log collection for the operational network that could detect and/or prevent any potential malicious intrusions. Finally, the devices in scope are behind multiple layers of physical access and are located in a room with around the clock supervision. No harm is known to have occured. | To mitigate this issue, WECC_URE2: 1) submitted a TFE that covers all devices that do not support Security Status Monitoring.
2014-11-25 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2014014267 | CIP-004-3a | R3; R3.2 | During a Compliance Audit, FRCC determined that FRCC_URE1 was in violation of CIP-004-3a R3.2. FRCC_URE documents were insufficient evidence to demonstrate that FRCC_URE1 updated personnel risk assessments (PRAs) at least every seven years after the initial PRA for four individuals who have authorized cyber or authorized unescorted physical access to Critical Cyber Assets (CCAs). During the Audit it was found that FRCC_URE1 failed to update the PRAs for a couple of the individuals sampled. Specifically, FRCC_URE1 identified PRAs which were not timely updated. The root cause for this violation was human error in the coding of FRCC_URE1’s automated reminder system which should have provided the required notifications of upcoming PRA expirations. | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). FRCC_URE1’s failure to update the PRAs within the required intervals could have resulted in not discovering unacceptable risks associated with the individuals. FRCC determined that the violation posed a minimal risk because the PRAs were conducted within three months of the expiration date of the seven year period and uncovered no unacceptable risks to warrant any removal of access. No harm is known to have occurred. | To mitigate this violation, FRCC_URE1: 1) updated the PRAs for all four personnel; 2) corrected the reminder systems for the PRAs to use a seven year based date based on the last PRA date; and 3) modified all employee records to correct the PRA data for future reference by the reminder system.
2014-11-25 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2014014268 | CIP-006-3c | R1; R1.6; R1.6.1; R1.6.2 | During a Compliance Audit, FRCC determined that FRCC_URE1 was in violation of CIP-006-3c R1.6.1 and R1.6.2. FRCC_URE1 failed to maintain visitor logs regarding 28 visitors. FRCC_URE supplied evidence demonstrating that authorized individuals used their electronic card keys to allow others into the Physical Security Perimeter (PSP) and acted as an escort. However, they did not properly complete the visitor log. In some cases the log only listed the first names of visitors and escorts; did not include the name of the escort; were missing exit times for visitors; and were missing the reason for access. The root cause for this violation was human error in not understanding the FRCC_URE1 visitor control program. | This violation posed a moderate risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). FRCC determined that the issue posed a moderate risk because there are a significant number of instances when the visitor logs were not filled out properly and it could not be determine who was the escort, what time the visitor entered or left the PSP, and/or the name of the visitor for multiple locations, one of which was the generation location control room. The risk was reduced because FRCC_URE1 supplied evidence demonstrating that visitors were escorted by authorized individuals. No harm is known to have occurred. | To mitigate this violation, FRCC_URE1: 1) conducted informal training with all of the plant operators; 2) advised FRCC_URE1 Team Members identified as not properly completing the visitor logs that further instances of non-compliance would result in disciplinary action; and 3) issued an e-mail reminder relative to visitor logs to all employees with NERC access.
2014-11-25 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2013012334 | CIP-007-1 | R1 | During a Compliance Audit , MRO determined that MRO_URE1 had an issue with CIP-007-1 R1. Specifically, MRO_URE1 failed to classify software re-installs to existing Cyber Assets in the ESP as 'significant changes' which allowed 'significant changes' to occur without testing procedures being observed. MRO_URE1 failed to perform testing procedures which included tests for user and system accounts and passwords, logging, and ports and services. During the sampled six month timeframe, two software re-installs occurred without the required testing procedures being observed. | This issue posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Implementing system changes without testing existing cyber security controls could result in adversely impacting existing cyber security controls. However, MRO_URE1 had an existing testing procedures policy that effectively functioned for changes MRO_URE1 classified as significant changes. Further, the two software re-installs that were not classified as significant changes were limited to backup or support systems to a device and did not affect functions that were necessary for it to function normally. Additionally, MRO_URE1 provided evidence of limited testing of user and system accounts and passwords, logging, and ports and services, though the evidence did not satisfy the requirement of CIP-007-1 R1 described in its change control and configuration management procedure. MRO determined that the issue was considered appropriate for FFT treatment because MRO_URE1 recognized the importance of testing and performed limited testing of user and system accounts and passwords, logging, and ports and services despite not identifying the software re-installs as significant changes. Additionally, MRO considered MRO_URE1's cooperation and prompt response to mitigate the issue. No harm is known to have occurred. | To mitigate this issue, MRO_URE1: 1) MRO_URE1 updated its Change Control and Configuration Management Procedure for Critical Cyber Assets to re-classify software re-installs as significant changes. MRO has verified the completion of all mitigation activity.
2014-11-25 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 2 (MRO_URE2) | NCRXXXXX | MRO2013012274 | CIP-005-1 | R1; 1.1; 1.2; 1.3; 1.4; 1.5; 1.6 | During a Compliance Audit, MRO_URE2determined that MRO_URE2 had an issue of CIP-005-1 R1. MRO_URE2 failed to ensure that every Critical Cyber Asset resided within an Electronic Security Perimeter (ESP) and failed to provide the required protective measures required by CIP-005-1 R1. The access points into the ESP were not properly identified and documented. An access point is required to be an independent asset. However, MRO_URE2 identified a firewall module within a network switch as an access point to the ESP. MRO_URE2 was not able to demonstrate that it maintains cyber security test procedures that minimize adverse affects on the production system or its operation. While MRO_URE2 provided evidence demonstrating that it performs a pre-and post change analysis of ports and services and functionality tests of each change, evidence of testing for the impact of other cyber security controls, such as passwords, was not available. MRO_URE2 was not able to demonstrate that it assessed security patches and security upgrades for applicability within thirty calendar days of availability. While MRO_URE2 described and documented the process that it follows to assess patches from its vendor for Windows-based security vulnerabilities, evidence of the assessment of non-Windows-based patches was not available. MRO_URE2 also was not able to demonstrate that its process for updating anti-virus and malware prevention "signatures" specifically addressed testing the signatures. MRO_URE2 stated that it automatically deploys anti-virus and malware prevention signatures or patches to immediately protect against any security vulnerabilities. This approach does not allow for a testing delay. Instead, clients are configured for automatic updates of the anti-virus and malware software solutions. Based on this approach, MRO_URE2 performs no further testing to ensure that these signatures do not impact devices within its CIP environment. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The misidentification of the access point was limited to improper documentation and a network implementation that was more complex than required by the CIP Reliability Standards. The MRO_URE2 network implementation utilized a firewall module within a network switch to control network access between all devices within and external to the ESP. While this implementation meets the security goals of CIP-005-1 R1, it is not an implementation that satisfies the requirement that access points are not permitted to also be a Critical Cyber Asset. This configuration added complexity to the identification of the access points to the ESP, but reduced the risk of cyber vulnerabilities on MRO_URE2's network. | To mitigate this issue, MRO_URE2: 1) reviewed its network configuration with regard to CIP version 3 and CIP version 5; 2) configured and identified an independent firewall to control access to the ESP; 3) tested the solution and validated results; 4) activated the new firewall device based on validation of testing; and 5) updated related documentation. MRO_URE2has verified the completion of all mitigation activity.
2014-11-25 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 2 (MRO_URE2) | NCRXXXXX | MRO2013012277 | CIP-006-1 | R1: 1.2; 1.8 | During a Compliance Audit, MRO_URE2determined that MRO_URE2 had an issue of CIP-006-1 R1. MRO_URE2 failed to identify an emergency exit door as an access point into the Physical Security Perimeter (PSP) at the Backup Control Center. Additionally, MRO_URE2 was not able to demonstrate that it maintains cyber security test procedures that minimize adverse affects on the production system or its operation. While MRO_URE2 provided evidence demonstrating that it performs a pre-and post change analysis of ports and services and functionality tests of each change, evidence of testing for the impact of other cyber security controls was not available. Further, MRO_URE2 was not able to demonstrate that it assessed security patches and security upgrades for applicability within thirty calendar days of availability. While MRO_URE2 described and documented the process that it follows to assess patches from its vendor for Windows-based security vulnerabilities, evidence of the assessment of non-Windows-based patches was not available. Finally, MRO_URE2 was not able to demonstrate that its process for updating anti-virus and malware prevention "signatures" specifically addressed testing the signatures. MRO_URE2 stated that it automatically deploys anti-virus and malware prevention signatures or patches to immediately protect against any security vulnerabilities. This approach does not allow for a testing delay. Instead, clients are configured for automatic updates of the anti-virus and malware software solutions. Based on this approach, MRO_URE2 performs no further testing to ensure that these signatures do not impact devices within its CIP environment. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The failure to identify the emergency exit door was limited to outdated documentation. The physical access point was actually being monitored and had the required alarms installed. No harm is known to have occurred. | To mitigate this issue, MRO_URE2: 1) updated its PSP diagram and verified accuracy of the updated diagram; 2) procured software solution; 3) tested and installed software solution; and 4 )updated its test procedure, security patches, and signature update documents. MRO_URE2has verified the completion of all mitigation activity.
2014-11-25 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 2 (MRO_URE2) | NCRXXXXX | MRO2013012279 | CIP-007-3a | R1; 1.1 | During a Compliance Audit, MRO_URE2determined that MRO_URE2 had an issue of CIP-007-3a R1. MRO_URE2 failed to provide evidence that it maintained cyber security test procedures that did not adversely affect existing cyber security controls. MRO_URE2 was not able to provide evidence that its cyber security test procedures did not adversely affect its production system or its operations. MRO_URE2 was conducting pre-change and post-change analysis of ports and services and functionality tests for each change, but was not able to demonstrate that it conducted testing to ensure that significant changes to existing Cyber Assets within its ESP did not adversely affect its existing cyber security controls. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. While the implementation of significant changes to existing Cyber Assets within the ESP may pose significant risk to the bulk power system, in this instance the risk was substantially reduced by MRO_URE2 completing functionality and ports and services evaluations during the testing process. The risk was further reduced because MRO_URE2 has strong procedural controls surrounding password length and complexity. Additionally, MRO_URE2did not identify any logging deficiencies that would have indicated a change had impacted existing cyber security controls. | To mitigate this issue, MRO_URE2: 1) revised its cyber security test procedures to incorporate specific test measures to ensure that significant changes to existing Cyber Assets do not adversely affect existing cyber security controls. MRO_URE2has verified the completion of all mitigation activity.
2014-11-25 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 2 (MRO_URE2) | NCRXXXXX | MRO2013012281 | CIP-007-1 | R3 | During a Compliance Audit, MRO_URE2determined that MRO_URE2 had an issue of CIP-007-1 R3. MRO_URE2 failed to document the assessment of security patches and security upgrades for applicability within thirty calendar days of availability of the patches or upgrades. MRO_URE2 was not able to demonstrate that it assessed security patches and security upgrades for applicability within thirty calendar days of availability. While MRO_URE2 described and provided documentation of the process that it follows to assess patches from its vendor for Windows-based security vulnerabilities, evidence of the assessment of non-Windows-based patches was not available. Non-windows-based computers represent approximately 15% (9 of 54) of the total MRO_URE2 Critical Cyber Assets, including the assets identified for ESP and PSP requirements. | This issue posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. While not assessing available security patches as they become available may expose Critical Assets to unnecessary vulnerabilities, MRO_URE2's reliance on its vendor identifying the availability of the patches assured that the identified vulnerability, as well as any exploit, was well known. The assets with the greatest exposure were Windows-based devices for which security patches and security upgrades were being assessed for applicability within thirty calendar days of availability. Only a subset of assets were not subject to the assessment of security patches and security updates. These non-Windows-based devices represented only 15% of the total devices subject to compliance with CIP-007-1 R3. No harm is known to have occurred. | To mitigate this issue, MRO_URE2: 1) purchased and deployed security management software; and 2) verified security management software includes all required applications to ensure comprehensive assessment of security patches and upgrades within 30 days of availability. MRO_URE2 has verified the completion of all mitigation activity.
2014-11-25 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 2 (MRO_URE2) | NCRXXXXX | MRO2013012282 | CIP-007-1 | R4; 4.2 | During a Compliance Audit, MRO_URE2determined that MRO_URE2 had an issue of CIP-007-3 R4.2. MRO_URE2 failed to provide documentation of its process for updating anti-virus and malware prevention signatures that specifically addresses testing the signatures. MRO_URE2 did not provide evidence of its process for updating anti-virus and malware prevention signatures. MRO_URE2 stated that it automatically deploys anti-virus and malware prevention signatures/patches to immediately protect against any security exposure. However, this approach does not allow for the time to conduct tests of the signatures. Instead, clients are configured for automatic updates of the anti-virus and malicious software solutions to include patterns and engines. Because of the approach it adopted to immediately deploy anti-virus and malware prevention signatures/patches, MRO_URE2 did not perform any testing to ensure that the signatures/patches did not impact devices within its system. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. While the failure to test anti-virus and malware signatures prior to implementation could result in a critical EMS application being identified as malware and quarantined, MRO_URE2's approach to immediately deploying updates addressed the greater risk of introducing a virus or malware on its devices or into its systems. The practice of immediate deployment ensured that anti-virus and malware signatures were up-to-date and thereby substantially reduced the risk of actual malware being introduced. MRO_URE2did not identify any actual events related to the practice of automatically updating anti-virus and malware signatures that impacted availability of MRO_URE2's device. No harm is known to have occurred. | To mitigate this issue, MRO_URE2: 1) revised its anti-virus and malware signature process to incorporate testing of signatures prior to installation of the updates. MRO_URE2has verified the completion of all mitigation activity.
2014-11-25 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2013013183 | CIP-007-3a | R2; R2.1 R2.2 | NPCC_URE1 submitted a self-report stating that it had an issue of CIP-007-3a R2. During the evaluation of its Cyber Vulnerability Assessment (CVA) data, NPCC_URE1 discovered that certain ports and a network switch were found enabled. During their initial implementation, the employee responsible did not perform the steps requiring a comparison of test data with configuration data. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. NPCC_URE1's security strategy includes electronic access for authentication and encryption at the Electronic Security Perimeter (ESP). It has implemented controls to log and monitor access to all cyber assets within the ESP and alerts coming from these controls are reviewed twenty-four hours a day. Only authorized personnel are granted access to these devices. NPCC_URE1's systems residing within an ESP have limited connectivity to outside networks and firewalls that restrict network traffic. Further, NPCC_URE1 has implemented security measures, such as intrusion detection systems and virus scanning on the ESP network to detect unusual activities. Network traffic monitoring is also in place and sends alerts to energy management system/supervisory control and data acquisition personnel when unusual activity is detected. As a result, NPCC_URE1 had monitoring processes in place that provided protection to the ESP by detecting and alerting for unauthorized access. No actual harm is known to have occurred. | To mitigate this issue NPCC_URE1: 1) disabled the specific ports and services; 2) revised its CIP procedures to include an independent verification process to strengthen controls over the implementation and testing of CIP assets for ports and services; and 3) issued a lessons learned that focuses on the importance of independently and properly checking and verifying ports and services data as stipulated in the associated procedure.
2014-11-25 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2014014155 | CIP-007-3a | R1; R1.1 | NPCC_URE1 submitted a self-report stating that it had an issue of CIP-007-3a R1. During the evaluation of their Cyber Vulnerability Assessment (CVA) data, NPCC_URE1 discovered that certain ports and a network switch were found enabled. During their initial implementation, the employee responsible did not perform the steps requiring a comparison of test data with configuration data. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. NPCC_URE1's security strategy includes electronic access for authentication and encryption at the Electronic Security Perimeter (ESP). It has implemented controls to log and monitor access to all cyber assets within the ESP and alerts coming from these controls are reviewed twenty-four hours a day. Only authorized personnel are granted access to these devices. NPCC_URE1's systems residing within an ESP have limited connectivity to outside networks and firewalls that restrict network traffic. Further, NPCC_URE1 has implemented security measures, such as intrusion detection systems and virus scanning on the ESP network to detect unusual activities. Network traffic monitoring is also in place and sends alerts to energy management system/supervisory control and data acquisition personnel when unusual activity is detected. As a result, NPCC_URE1 had monitoring processes in place that provided protection to the ESP by detecting and alerting for unauthorized access. No actual harm is known to have occurred. | To mitigate this issue NPCC_URE1: 1) disabled the specific ports and services; 2) revised its CIP procedures to include an independent verification process to strengthen controls over the implementation and testing of CIP assets for ports and services; and 3) issued a lessons learned that focuses on the importance of independently and properly checking and verifying ports and services data as stipulated in the associated procedure.
2014-11-25 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2014014156 | CIP-007-3a | R8; R8.2 | NPCC_URE1 submitted a self-report stating that it had an issue of CIP-007-3a R8. During the evaluation of their Cyber Vulnerability Assessment (CVA) data, NPCC_URE1 discovered that certain ports and a network switch were found enabled. During their initial implementation, the employee responsible did not perform the steps requiring a comparison of test data with configuration data. NPCC_URE1 contracted a 3rd party vendor to perform their CVAs. The vendor failed to identify the open ports and a network switch as not required for operation of the Cyber Assets within the electronic security perimeter (ESP). A different third party vendor was contracted to perform the CVA which identified the open ports and enabled switch. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. NPCC_URE1's security strategy includes electronic access for authentication and encryption at the Electronic Security Perimeter. It has implemented controls to log and monitor access to all cyber assets within the ESP and alerts coming from these controls are reviewed twenty-four hours a day. Only authorized personnel are granted access to these devices. NPCC_URE1's systems residing within an ESP have limited connectivity to outside networks and firewalls that restrict network traffic. Further, NPCC_URE1 has implemented security measures, such as intrusion detection systems and virus scanning on the ESP network to detect unusual activities. Network traffic monitoring is also in place and sends alerts to energy management system/supervisory control and data acquisition personnel when unusual activity is detected. As a result, NPCC_URE1 had monitoring processes in place that provided protection to the ESP by detecting and alerting for unauthorized access. No actual harm is known to have occurred. | To mitigate this issue NPCC_URE1: 1) disabled the specific ports and services; 2) strengthened language for 3rd party vendors contracted to perform the annual CVA. It included language to specify methodology use, detailed how configuration data is collected, processed, analyzed and reported, and limitations of the tools and techniques to perform the CVA; and 3) issued a lessons learned that focuses on the importance of independently and properly checking and verifying ports and services data as stipulated in the associated procedure. Additionally, the lessons learned was issued to increase awareness on language and requirements for third party vendors.
2014-11-25 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 2 (NPCC_URE2) | NCRXXXXX | NPCC2014014154 | CIP-007-3a | R9 | NPCC_URE2 submitted a self-report stating that it had an issue with CIP-007-3a R9. Ports and services were disabled as part of a firmware update. Documentation was not updated within thirty calendar days of the change. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Documentation discrepancies resulted in ports and services being enabled that are not required for normal and emergency operations. No actual harm is known to have occurred. | To mitigate this issue, NPCC_URE2: 1) revised its document that controls default device settings; 2) revised its change control and configuration management procedure to better define applicability and roles and responsibilities; 3) closed ports and services at all substations in violation; and 4) provided awareness training to operators and protection engineering regarding the change control process on critical cyber assets within the substation environment.
2014-11-25 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 2 (NPCC_URE2) | NCRXXXXX | NPCC2014014153 | CIP-007-3a | R2. | NPCC_URE2 submitted a self-report stating that it had an issue with CIP-007-3a R2. During NPCC_URE2's cyber vulnerability assessment, it identified that certain ports and services were not disabled as part of a firmware update. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. There is no direct access to substation devices from the corporate network or internet. In order to access the device remotely, all technicians must use a secure access gateway. The gateway requires two-factor authentication and creates a secure encrypted tunnel to ensure information is not intercepted. A firewall that protects the corporate network from the SCADA network is monitored by a 3rd party monitoring service. Additionally, there are network intrusion detection sensors installed on the SCADA network to passively monitor all network traffic within the security perimeter. Alerts from these devices are sent to the security event manager. The security event manager console is monitored by staff. If an event was detected, staff would analyze the alert and determine if an investigation was needed. No actual harm is known to have occurred. | To mitigate this issue, NPCC_URE2: 1) revised its document that controls default device settings; 2) revised its change control and configuration management procedure to better define applicability and roles and responsibilities; 3) closed ports and services at all substations in violation; and 4) provided awareness training to operators and protection engineering regarding the change control process on critical cyber assets within the substation environment. To mitigate this issue, NPCC_URE2 will work with its vendor to enhance their statement of work to include all documentation discrepancies.
2014-11-25 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 2 (NPCC_URE2) | NCRXXXXX | NPCC2014014259 | CIP-004-3a | R4. R4.1; R4.2 | NPCC_URE2 submitted a self-report stating that it had an issue with CIP-004-3a R4. An employee with authorized unescorted physical access to critical cyber assets (CCA) transferred to a new position that no longer required such access. The employee's access was removed 2 months later. The oversight was caused by the employee's supervisor not completing a change request form. The quarterly review of the list of personnel with physical access to CCAs was performed but was not able to discover the violation due to the change request form not being processed. The personnel responsible for the quarterly review was unaware of the employee transfer. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The employee transferred departments. Physical access records were reviewed and confirmed that the employee did not access substations after the date of transfer. The employee in question is in good standing with NPCC_URE2 and had a valid background check/risk assessment. No actual harm is known to have occurred. | To mitigate this issue, NPCC_URE2: 1) communicated NERC CIP intranet, CIP access prerequisites, and access revocation to all employees; 2) sent specific communications to all access approvers which includes CIP access revocation requirements; and 3) documented their procedure for quarterly reviews of lists of personnel with authorized unescorted physical access to critical cyber assets.
2014-11-25 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 2 (NPCC_URE2) | NCRXXXXX | NPCC2014014293 | CIP-007-1 | R5. | NPCC_URE2 submitted a self-report stating that it had an issue with CIP-007-1 R5. During its annual cyber vulnerability assessment, NPCC_URE2 identified a discrepancy involving revenue meters across several substations. The revenue meters had passwords that consisted of a combination of alpha and numeric characters but did not include special characters. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The revenue meters had passwords that consisted of a combination of alpha and numeric characters. Revenue meters take measurements on the various circuits and report back to the Energy Monitoring System (EMS) through RTUs. | To mitigate this issue, NPCC_URE2: 1) changed the passwords on all revenue meters to include a special character; 2) revised their password management document to include password complexity requirements; and 3) provided CIP-007 awareness training to the relevant department.
2014-11-25 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 3 (NPCC_URE3) | NCRXXXXX | NPCC2014014292 | CIP-007-3a | R2. | NPCC_URE3 submitted a self-report stating that it had an issue with CIP-007-3a R2. During NPCC_URE3's cyber vulnerability assessment, it identified a discrepancy between printer ports and services documentation and the actual ports of services enabled on printers. The printer ports and services baseline documentation labeled the ports as disabled. Printers on the energy management system were enabled. The printers defaulted back to enabled after the printers were reset. The printer ports and services was disabled. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The printers are located at control centers on the EMS network. There is no external connectivity to the printers. The printers can only be accessed from users that are physically located within the primary or back up control center physical security perimeters. No actual harm is known to have occurred. | To mitigate this issue, NPCC_URE3 submitted a technical feasibility exception. To mitigate this issue, NPCC_URE3 will submit TFEs for other printers found at NPCC_URE3 within 90 days.
2014-11-25 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2013013081 | CIP-004-3a | R2; R2.1 | SERC_URE1 submitted a Self-Report to SERC stating that it had an issue with CIP-004-3a R2.1. SERC_URE1 failed to ensure all personnel having access to Critical Cyber Assets (CCA) were trained prior to their being granted such access. One employee was granted electronic access to CCAs without having completed the required cyber security training. Access was removed within 24 hours after it was discovered and the required cyber security training was completed the next day. The employee had completed the cyber security training while working for an affiliate as required. One employee was granted electronic access to CCAs without having completed the required cyber security training. Access was removed within 24 hours after it was discovered and the required cyber security training was completed six days later. The employee had completed the cyber security training while working for an affiliate as required. One employee was granted physical access to two control centers without having completed the required annual cyber security training. The inappropriate access was discovered the following day and the required cyber security training was completed six days after access had been granted. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System. Failing to properly train individuals prior to granting physical or electronic access to CCAs may result in improper use of Cyber Assets and CCAs inside the Electronic Security Perimeter. However, the employees had the need to know and required access to CCAs to perform their job responsibilities. Each employee had completed the required personnel risk assessment in accordance with CIP-004 R3 and had completed a prior version of cyber security training. No harm is known to have occurred. SERC considered SERC_URE1's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, SERC_URE1: 1) had employees complete the required training; 2) removed the ability for owners and custodians to add, remove or change users in the NERC CIP groups that control access to the assets they manage; and 3) updated its cyber security training program to combine both training courses into one course.
2014-11-25 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2013013104 | CIP-007-3a | R5; R5.1.1 | SERC_URE1 submitted a Self-Report to SERC stating that it had an issue with CIP-007-3a R5.1. SERC_URE1 failed to ensure user accounts were implemented as approved by designated personnel. The Self-Report contained two instances. With regard to the first incident, SERC_URE1 discovered that a manager provisioned electronic access to an employee without following the documented processes. The issue was discovered on the following day via an automated database reporting tool. The employee’s access was revoked a day after it was discovered, and nine days later the manager implemented the formal workflow process and properly provisioned access. Regarding the second incident, SERC_URE1 discovered that an employee provisioned herself electronic access without the proper authorization and approval. The issue was discovered on the same day via an automated database reporting tool. The employee’s access was revoked on the same day as it was provisioned, and then re-provisioned the following day, after the manager followed the formal internal workflow process. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System. Failing to maintain a compliant account management program could present a risk of unauthorized access to and the introduction of exploitable vulnerabilities in SERC_URE1’s Cyber Assets without its knowledge. However, in both incidents, the personnel had completed the required cyber security training and personnel risk assessments. In addition, SERC_URE1’s internal controls promptly identified the issue. The unauthorized access was revoked within one day of discovery and then re-provisioned in accordance with the formal internal workflow process. No harm is known to have occurred. SERC considered SERC_URE1's compliance history and determined that the instant issue was appropriate for FFT treatment. Although, the previous instances were of the same Standard and Requirement, the underlying conduct of the two instances was different than the instant issue. | To mitigate this issue, SERC_URE1: 1) revoked the unauthorized access to CCAs in less than one day for both instances; and 2) removed the administrative ability for managers to add, remove, or change users in the NERC CIP groups that control access to the assets they manage.
2014-11-25 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 2 (SERC_URE2) | NCRXXXXX | SERC2013011765 | CIP-008-3 | R1 | SERC_URE2 submitted a Self-Report to SERC stating that it had an issue with CIP-008-3 R1. SERC_URE2 failed to update its Cyber Security Incident response plan (CSIRP) within 30 calendar days of any changes. Following the results of its CSIRP drill, SERC_URE2 was required to make two updates to its CSIRP. SERC_URE2 documented the pending changes, but decided to postpone the required updates to its CSIRP until a scheduled compliance documentation review was conducted. As a result of this decision, SERC_URE2 failed to update the CSIRP within 30 days of completion of the drill, and instead made the required updates 197 days later. The updates to the CSIRP addressed personnel shift changes during an incident and updated the incident response contact list. The duration of this issue was from when SERC_URE2 went past the 30 days allowed to update the CSIRP through when SERC_URE2 updated the CSIRP. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The failure to update the CSIRP within 30 days could have left SERC_URE2 personnel without adequate information to respond to a Cyber Security Incident. However, all participants in the SERC_URE2 CSIRP drill were briefed and aware of the pending revisions to the CSIRP immediately following the drill. Lastly, SERC_URE2 attested that it has had no actual or suspected Cyber Security Incidents that activated the CSIRP. SERC considered SERC_URE2's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, SERC_URE2: 1) updated its CSIRP and provided training for the individuals affected by the changes; 2) added detail to the process steps within the CSIRP to be certain the update is not overlooked in the future and provided training for the individuals affected by the changes; and 3) added a step in the compliance workflow management tool as a reminder to update the CSIRP within 30 days. SERC has verified the completion of all mitigation activity.
2014-11-25 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 2 (SERC_URE2) | NCRXXXXX | SERC2013012241 | CIP-007-1 | R5 | SERC_URE2 submitted a Self-Report to SERC stating that it had an issue with CIP-007-1 R5.3. SERC_URE2 could not technically meet the password requirements on three database accounts and did not file a Technical Feasibility Exception (TFE) documenting compensating measures. After an internal review of its CIP-007 R5 program, SERC_URE2 identified three database accounts on a system consisting of databases residing on Critical Cyber Asset (CCA) servers. These three accounts were unable to meet the password complexity requirements. SERC_URE2 did not file a TFE documenting the compensating measures put in place upon commissioning of the CCAs. According to the vendor, none of the three accounts could have the password changed annually or meet the complexity requirements. Additionally, the three account names could not be changed and one of the three account passwords could not meet the minimum character length requirement. The duration of this issue was from when the Standard became mandatory and enforceable on SERC_URE2 through when SERC_URE2 submitted a TFE for password requirements on the three accounts. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failure to file a TFE documenting compensating measures when account passwords could not technically meet the requirements of CIP-007 R5.3 could have left SERC_URE2 unaware of the compensating measures in place or inadvertently fail to put compensating measures in place. However, SERC_URE2 had compensating measures in place prior to the commissioning of the CCAs. Anti-malware software was installed on the CCAs containing the databases. SERC_URE2 implemented network segregation, which isolated the CCA servers to a demilitarized zone and only allowed connections to the databases from other Cyber Assets within the SERC_URE2 Electronic Security Perimeter. SERC_URE2 also had a dedicated domain controller for managing access to the implicated CCAs, which was maintained separate and apart from the corporate domain controllers. The failure to request a TFE was an administrative oversight by SERC_URE2. SERC considered SERC_URE2's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, SERC_URE2: 1) improved the account identification methodology in an account management procedure and communicated the changes to affected administrators; 2) applied the revised account management procedure to all affected Cyber Assets; and 3) submitted a TFE for the affected CCAs. SERC has verified the completion of all mitigation activity.
2014-11-25 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 2 (SERC_URE2) | NCRXXXXX | SERC2013012484 | CIP-003-1 | R4 | SERC_URE2 submitted a Self-Report to SERC stating that it had an issue with CIP-003-1 R4. SERC_URE2 failed to implement its documented information protection program and failed to document the annual assessment of its information protection program. SERC_URE2 maintained two separate information protection programs under CIP-003-1 R4. The first program was specific to all those individuals who could access information related to a system. In the first program, SERC_URE2 specified that access to critical information about the system is limited to system support personnel, but this statement was not accurate. Instead, SERC_URE2 allowed personnel outside of system support personnel to access protected information about the system on a need-to-know basis. For the second program, SERC_URE2 did not specify in the procedure how the annual review was to be conducted per CIP-003-1 R4.3. Except for the record in the revision history saying that the review was conducted, there is no evidence that demonstrates that the review actually occurred and how any discovered issues were documented and remediated. The duration of this issue was from when the Standard became mandatory and enforceable on SERC_URE2 through when SERC_URE2 revised its second program's procedure to require an assessment of documentation of remediation activities. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC_URE2’s failure to properly implement and document the annual assessment of its information protection program could prevent SERC_URE2 from properly training individuals on the handling of such information and could lead SERC_URE2 to conduct insufficient reviews and fail to remediate deficiencies in its information protection program. In either case, such failures could lead to the release of SERC_URE2 protected data to personnel without a need to know or to malicious actors. However, for the first program issue, SERC_URE2 was following an overarching procedure to only allow access to CCA information on a need-to-know basis. Furthermore, each of the individuals that met the need-to-know threshold and were granted access were also required to undergo CIP training and pass a personnel risk assessment. For the second program issue, SERC_URE2 had evidence to demonstrate it conducted annual reviews to confirm adherence to the information program, despite the lack of evidence to substantiate the substance and outcomes of those reviews. SERC_URE2 had cyber and physical controls in place to guard protected information for the duration of the issue. SERC_URE2 has had no known compromise of protected information to date. SERC considered SERC_URE2's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, SERC_URE2: For the first program issue: 1) updated the security management controls procedure to address the sharing of information to personnel outside of the group and provided training for individuals affected by the procedural changes; 2) updated the security management controls procedure to include an assessment step to review the IT risk management guideline for information protection and provided training for individuals affected by the procedural changes; and 3) executed and documented the results of the annual assessment of adherence to the information protection program based on the updated procedure. For the second program issue: 1) reviewed and updated the information protection procedures to ensure that steps to assess adherence to the CCA information protection program were included and ensured sufficient evidence to prove the assessment was completed, and provided training for individuals affected by the procedural changes; and 2) executed and documented the results of the annual assessment based on the updated procedure. SERC has verified the completion of all mitigation activity.
2014-11-25 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 2 (SERC_URE2) | NCRXXXXX | SERC2013012492 | CIP-007-1 | R5 | SERC_URE2 submitted a Self-Report to SERC stating that it had an issue with CIP-007-1 R5. SERC_URE2 first identified Cyber Assets which could not technically comply with the password complexity requirements but did not have a Technical Feasibility Exception (TFE) submitted to document the compensating measures, and secondly, SERC_URE2 found a shared account was not afforded all of the technical and procedural controls in accordance with CIP-007-1 R5. Issue 1: Regarding the first issue, SERC_URE2’s systems security management procedure required passwords to be compliant with the requirements specified in CIP-007 R5.3. It also specified that for any passwords that were unable to meet the complexity requirements, that TFEs are submitted internally to the IT risk management group. After an internal compliance review, SERC_URE2 completed an internal review and identified a weakness in its documented procedure. Although the procedure required that the identification of TFE issues around password complexity be made to the IT risk management group, it did not specify how to properly manage the TFEs and file them with the Region. As a result of the insufficient procedure, SERC_URE2 failed to file TFEs to document the compensating measures when the password complexity could not be technically enforced. This oversight applied to vendor supported operating systems involving workstations and servers. This issue affected Windows workstations and Windows servers, all identified as Critical Cyber Assets (CCAs). Issue 2: Regarding the second issue, after the same internal compliance review, SERC_URE2 discovered a single shared account enabled on CCAs. The shared account was not addressed in the SERC_URE2 technical and procedural controls required under CIP-007 R5. SERC_URE2 required through policy that users first authenticate through an authentication server, and once authenticated, the shared account could be accessed and used to elevate privileges and allow changes to be made. The account in question is a local account which allows administrative control to occur should the authentication servers be out of service or the network unavailable due to an outage. In that scenario, the user could log directly into the routers or switches using the shared account password. SERC_URE2 addressed the authentication server access in its technical and procedural controls, which was the primary authentication method, but failed to address the use of the shared account by logging directly into the routers and switches. This omission was an oversight by SERC_URE2, failing to consider the ability to directly access the switches using the shared local user account outside of authenticating through the authentication server. The shared account could be used to directly access the routers and switches, and this aspect was not addressed in the established technical and procedural controls. The shared account was not addressed in the policy under CIP-007 R5.2, however the shared account was on the quarterly review list, and those with access to the shared account were approved for access and tracked. Under CIP-007 R5.3, the shared account password was changed when originally implemented, but was not changed annually as required and could not technically meet the required password complexity requirements. SERC_URE2 did not request a TFE for this issue. The duration of this issue was from when the Standard became mandatory and enforceable on SERC_URE2 until Mitigation Plan completion. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The failure to file TFEs documenting compensating measures when account passwords could not technically meet the requirements of CIP-007 R5.3 could have left SERC_URE2 unaware of the compensating measures in place or inadvertently fail to put compensating measures in place. The failure to request TFEs was an administrative oversight by SERC_URE2. Regarding the first issue, SERC_URE2 had compensating measures in place. The network and host devices were protected by intrusion prevention systems, and the network is isolated from the corporate network with its own Active Directory domain for restricted access control. The workstations and servers at issue were protected within an Electronic Security Perimeter (ESP) and were contained within a Physical Security Perimeter (PSP). Regarding the second issue, the failure to change the password annually increased the risk that the password could be discovered. However, the password for the shared account at issue was a secondary access method to be used if the authentication server was not available. Those individuals approved for shared access to the local account were approved as required by SERC_URE2 procedures and tracked appropriately. In addition, the routers and switches at issue were protected within a ESP and PSP. SERC considered SERC_URE2's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, SERC_URE2: For Issue 1: 1) reviewed all similar Cyber Asset account password controls to determine where password controls cannot technically comply with the requirements pursuant to CIP-007-3 R5.3; 2) submitted a TFE for the affected Cyber Asset account password controls; 3) updated change management procedures to ensure TFEs are submitted prior to implementation for any new Cyber Asset account password controls that cannot technically comply with the requirements; and 4) provided training for the individuals affected by the procedural changes. For Issue 2: 1) decided on a password that was configured for the complexity requirements specified in CIP-007-3 R5.3.1 and CIP-007-3 R5.3.2 and changed it on all affected CCAs. 2) communicated the password change to authorized users only thus limiting usage to those with a need to know; 3) researched options for secondary authentication methods, including working with the asset manufacturers to consider all options and testing in a lab environment; 4) implemented secondary authentication methods on all CCAs based on test results; 5) filed TFEs for the R5.3 subrequirements that could not be technically enforced; 6) updated its CIP-007 R5 procedures to include the secondary authentication methods; and 7) provided training for the individuals affected by the procedural changes. SERC has verified the completion of all mitigation activity.
2014-11-25 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 2 (SERC_URE2) | NCRXXXXX | SERC2013012493 | CIP-006-3c | R1; R1.6.1 | SERC_URE2 submitted a Self-Report to SERC stating that it had an issue with CIP-006-3c R1.6.1. SERC_URE2 failed to properly document the entry and exit of visitors to and from a Physical Security Perimeter (PSP). SERC_URE2 discovered that an authorized employee took a new employee, who was not approved for unescorted access, into a PSP as a part of the training for the new employee’s role. The escorting employee failed to read the posted notification, which explained the automated call logging requirements for logging visitor access at the facility. SERC_URE2 procedures at this and similar PSPs require an escort to call a phone number that is posted on signs on each access door as well as within the secured PSP to provide the required logging information upon entry and exit. In this case, the escort recognized the individual was not authorized for access, but called corporate security instead of calling the posted number for automated logging of the visitor. Security advised the escorting employee that it was acceptable to escort the new employee into the PSP, as long as the individual was properly documented on a visitor log. The escorting employee then badged in and allowed the visitor in, mistakenly assuming that there would be a visitor log book inside the PSP. After failing to find a visitor log book and failing to observe the aforementioned signs, the employee made no further attempt to log the visitor’s access.. The escort and the visitor accessed two facilities, but failed to properly log either access. Both employees accessed a PSP and left six minutes later. Both then accessed a PSP and left three minutes later. The times were attested to by the escorting employee, and confirmed by corporate security after a review of the closed circuit television video footage. SERC_URE2 confirmed through a review of video footage from three weeks before through one week after this issue that no other instances of failure to log visitors had occurred at these facilities. The duration of this issue was from when a SERC_URE2 visitor was permitted escorted physical access into the PSP but failed to properly log the visit through the automated phone log through when the SERC_URE2 visitor left the PSP. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The failure to properly log the visitor’s access to the PSPs could have delayed the identification of the visitor if an incident had occurred. However, SERC_URE2 confirmed through video footage that the visitor was continuously escorted the entire time while within the PSP. SERC_URE2 reviewed video footage and also confirmed that no Cyber Assets were accessed or approached while the visitor was within a PSP and the escorting employee attested to that fact. The total time that the visitor was within a PSP was nine minutes. SERC considered SERC_URE2's and its affiliate's compliance history and determined that the instant issue was appropriate for FFT treatment because, while the instances were of the same Standard and Requirement, the underlying conduct of the two instances was different. | To mitigate this issue, SERC_URE2: 1) developed an awareness communication that includes the visitor logging process and distributed it to the personnel who have authorized access to the PSP at issue; 2) developed an awareness communication that includes the visitor logging process and distributed it to the remaining personnel who have authorized access to the PSP at issue; 3) developed an awareness communication that includes the visitor logging process and delivered it to personnel at a similar power station who have authorized access to a similar PSP; and 4) updated the annual cyber security training to include a slide with specific instructions on how to log visitors into similar facilities to avoid misinterpretations that all visitor logging is through paper logs. SERC has verified the completion of all mitigation activity.
2014-11-25 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 2 (SERC_URE2) | NCRXXXXX | SERC2013012494 | CIP-007-1 | R6 | SERC_URE2 submitted a Self-Report to SERC stating that it had an issue with CIP-007-1 R6. SERC_URE2 identified communication and system protection Cyber Assets that were not technically capable of monitoring system events related to cyber security, and SERC_URE2 failed to file a Technical Feasibility Exception (TFE) with SERC to document the compensating measures. SERC_URE2, through an internal risk management review, discovered that the Critical Cyber Assets (CCAs) within some of its Critical Assets failed to have the required TFEs for the monitoring of system events related to cyber security. None of these devices had the technical capabilities to monitor for and log cyber security events to meet the requirements of CIP-007-1 R6. Some devices had no local logging capabilities while other devices had a limited ability to log but did not have adequate log file size to ensure 90 days worth of logs were retained. SERC_URE2 established organizational process controls to monitor system events related to cyber security, but it failed to document these compensating measures through the established TFE process. These compensating measures have been in place since the date of mandatory compliance. The duration of this issue was from when the Standard became mandatory and enforceable on SERC_URE2 through when SERC_URE2 submitted the final TFE requests to SERC. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failure to file a TFE documenting compensating measures when Cyber Assets could not technically meet the logging requirements of CIP-007 R6 could have left SERC_URE2 unaware of the compensating measures in place or inadvertently fail to put compensating measures in place. However, SERC_URE2 had compensating measures in place. SERC_URE2 required that all remote electronic access to any of the affected devices be controlled and monitored through a jump-host that requires two-factor authentication to log-in. The jump-host runs special interface software that further restricts user access based on authorizations assigned to the specific user. Any physical access to any of the affected devices is governed by the Physical Security Perimeter access controls that alert on any unauthorized access attempts. Additional monitoring of the affected devices is performed by the SERC_URE2 energy management system, which has alarms that indicate communication or device failures. A device failure alarm is sent to the system operator whenever a device is put in configuration mode, a precursor to modifications or changes to the CCA. SERC considered SERC_URE2's and its affiliate's compliance history and determined that the instant issue was appropriate for FFT treatment because, while the instances were of the same Standard and Requirement, the underlying conduct of the two instances was different. | To mitigate this issue, SERC_URE2: 1) assessed all Cyber Assets’ ability to monitor system events related to cyber security identifying those that cannot meet the requirements and categorized Cyber Assets based on functionality and compensating and mitigating measures; 2) created and submitted TFEs for half the categories of Cyber Assets identified; 3) created and submitted TFEs for the remaining categories of Cyber Assets identified; 4) updated change control process to ensure that security status monitoring capabilities are reviewed when adding a new device type to the program. Any new device type unable to monitor system events related to cyber security without an existing TFE will have a new TFE submitted; and 5) provided training for individuals affected by the procedural changes. SERC has verified the completion of all mitigation activity.
2014-11-25 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 2 (SERC_URE2) | NCRXXXXX | SERC2013012519 | CIP-006-3c | R6 | SERC_URE2 submitted a Self-Report to SERC stating that it had an issue with CIP-006-3c R6. SERC_URE2 failed to log and record sufficient information to uniquely identify an individual at the time of access to a Physical Security Perimeter (PSP). An employee entered a secured PSP but did not properly badge in on two separate occasions that day. The employee at issue was allowed in by another employee, who properly badged in and then held the door open. Corporate security discovered this issue eighteen days later through a review of video footage for an unrelated investigation they were conducting. Corporate security identified the employee who failed to properly badge, and determined that the employee was approved and authorized for unescorted physical access. The employees entered the PSP for the first time and exited one minute later. The employee entered the PSP a second time and exited three minutes later. These access times were validated by a review of video footage. The duration of this issue was from when a SERC_URE2 employee first accessed the PSP without properly badging in through when the SERC_URE2 employee left the PSP for the first time and from when a SERC_URE2 employee accessed the PSP a second time without properly badging in through when the SERC_URE2 employee left the PSP for the second time. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The SERC_URE2 employee that failed to properly badge into the PSP was approved and authorized for unescorted physical access at the PSP in question. The SERC_URE2 employee was with another approved and authorized employee. There was a supervisor on site within the PSP upon arrival of the employees that spoke to both individuals about their work. Video footage documented the arrival and departure of both employees, and provided unique identification of the employee that failed to badge in. SERC considered SERC_URE2's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, SERC_URE2: 1) conducted a counseling session with the two employees involved in this issue; and 2) provided awareness training to a wider population of personnel with access to Critical Cyber Assets and modified cyber security training materials to reinforce individual responsibility for logging access. SERC has verified the completion of all mitigation activity.
2014-11-25 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 3 (SERC_URE3) | NCRXXXXX | SERC2013011756 | CIP-008-3 | R1 | SERC_URE3 submitted a Self-Report to SERC stating that it had an issue with CIP-008-3 R1. In 2011, SERC_URE3 failed to update its Cyber Security Incident response plan (CSIRP) within 30 calendar days of any changes. SERC_URE3 conducted its CSIRP drill. Following the results of its CSIRP drill, SERC_URE3 was required to make two updates to its CSIRP. SERC_URE3 documented the pending changes, but decided to postpone the required updates to its CSIRP until a scheduled compliance documentation review was conducted. As a result of this decision, SERC_URE3 failed to update the CSIRP within 30 days of completion of the drill, and instead made the required updates 197 days later. The updates to the CSIRP addressed personnel shift changes during an incident and updated the incident response contact list. The duration of this issue was from when SERC_URE3 went past the 30 days allowed to update the CSIRP through when SERC_URE3 updated the CSIRP. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The failure to update the CSIRP within 30 days could have left SERC_URE3 personnel without adequate information to respond to a Cyber Security Incident. However, all participants in the SERC_URE3 CSIRP drill were briefed and aware of the pending revisions to the CSIRP immediately following the drill. Lastly, SERC_URE3 attested that it has had no actual or suspected Cyber Security Incidents that activated the CSIRP. SERC considered SERC_URE3's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, SERC_URE3: 1) updated its CSIRP and provided training for individuals affected by the procedural changes; and 2) added detail to the process steps within the CSIRP to be certain the update is not overlooked in the future and provided training for individuals affected by the procedural changes. SERC has verified the completion of all mitigation activity.
2014-11-25 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 3 (SERC_URE3) | NCRXXXXX | SERC2013012497 | CIP-007-1 | R5 | SERC_URE3 submitted a Self-Report to SERC stating that it had an issue with CIP-007-1 R5. SERC_URE3 discovered a single default shared account that was not afforded all of the technical and procedural controls in accordance with CIP-007 R5. SERC_URE3 discovered a single shared account enabled on CCAs. The shared account was not addressed in the SERC_URE3 technical and procedural controls required under CIP-007 R5. SERC_URE3 required through policy that users first authenticate through an authentication server, and once authenticated, the shared account could be accessed and used to elevate privileges and allow changes to be made. The account in question is a local account which allows administrative control to occur should the authentication servers be out of service or the network unavailable due to an outage. In that scenario, the user could log directly into the switches using the shared account password. SERC_URE3 addressed the authentication server access in its technical and procedural controls, which was the primary authentication method, but failed to address the use of the shared account by logging directly into the switches. This omission was an oversight by SERC_URE3, failing to consider the ability to directly access the switches using the shared local user account outside of authenticating through the authentication server. The shared account could be used to directly access the switches, and this aspect was not addressed in the established technical and procedural controls. The shared account was not addressed in the policy under CIP-007 R5.2, however the shared account was on the quarterly review list, and those with access to the shared account were approved for access and tracked. Under CIP-007 R5.3, the shared account password was changed when originally implemented, but was not changed annually as required and could not technically meet the required password complexity requirements. SERC_URE3 did not request a TFE for this issue. The duration of this issue was from when the Standard became mandatory and enforceable on SERC_URE3 through when SERC_URE3 removed connectivity to its Cyber Assets and executed an out of cycle risk-based assessment methodology and determined it had no CCAs. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The failure to clearly document the procedures for when to use the account in question presented a risk that a user might log directly into the switches even if the authentication servers were available, make unauthorized changes, and SERC_URE3 might be unable to determine which user made the changes. The failure to change the password annually increased the risk that the password could be discovered. However, the password for the shared account at issue was a secondary access method to be used if the authentication server was not available. Those individuals approved for shared access to the local account were approved as required by SERC_URE3 procedures and tracked appropriately. In addition, the switches at issue were protected within an Electronic Security Perimeter (ESP) and a Physical Security Perimeter. SERC considered SERC_URE3's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, SERC_URE3: 1) removed connectivity to its Cyber Assets and executed an out of cycle RBAM which resulted in a determination that it no longer had any CCAs. SERC has verified the completion of all mitigation activity.
2014-11-25 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2014013588 | CIP-003-3 | R6 | WECC_URE1 submitted a Self-Certification stating that it had an issue with CIP-003-3 R6. Specifically, WECC_URE1 stated that it failed to follow its change control procedures for three events. In the first event, WECC_URE1 failed to remove four network encryption devices from a WECC_URE1 Electronic Security Perimeter (ESP) and failed to complete and submit a Change Request Form. In the second event, WECC_URE1 failed to complete and submit the Change Request Form during an upgrade, which led WECC_URE1 to not follow other procedures, including a Change Advisory Team (CAT) meeting, a formal recommendation from the Critical Asset T to the Change Manager, Change Manager Approval, and release by the Change Manager to move forward. The Devices in scope were three combustion turbine controller units tied to one Critical Asset (CA). In the third event, WECC_URE1 failed to implement its change control procedures for installation and removal of one application on 9 Critical Cyber Assets (CCAs) during a CCA upgrade. This application was used to gather configuration information in order to facilitate an upgrade. The root cause of this issue is human error. | The issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE1 failed to follow its change control procedures in three instances. Failure to follow change control procedures in three instances could result in the CCAs controlling the functions of the critical assets having no or improper security controls. An attacker could use this to their advantage to compromise WECC_URE1’s total generation of approximately 400 MW. On the other hand, WECC_URE1 implemented preventative controls to prevent the compromise of generation from occurring. WECC_URE1 notified local Transmission Owners and Transmission Operators that the unit was unavailable and not to count on its generation during the project duration. The new devices were never brought back online, instead, WECC_URE1 rolled back to the existing systems where the proper controls were in place prior to the upgrade. Additionally, WECC_URE1 implemented compensating measures. WECC_URE1 installed anti-virus on all CCAs along with 24 hours 7 days a week logging and monitoring on local devices and all access points into the ESP. WECC_URE1 also installed software to scan each system every four hours and alert of any device that did not match configured and approved baselines. No harm is known to have occured. WECC considered WECC_URE1's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, WECC_URE1: 1) submitted the change request and rolled back update to previous version; and 2) personnel has completed formal CIP-003-3 R6 Change Control and Configuration Management training.
2014-11-25 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2014013585 | CIP-004-3a | R2 | WECC_URE1 submitted a Self-Certification stating that it had an issue with CIP-004-3a R2. Specifically, WECC_URE1 retained a contractor to perform an upgrade to WECC_URE1’s human machine interface (HMI) control platform. The contractor employee did not undergo cyber security training prior to upgrading the firmware to CCAs. The root cause of this issue is human error. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE1 failed to train one contractor on Critical Infrastructure Protection before being given authorized logical access to three (3) CCAs. The three CCAs can control the operation of one Critical Asset which has a generating capacity of approximately 130 MW. Allowing someone to access these CCAs without proper CIP training could have allowed improper use and loss of up to approximately 130 MW of WECC_URE1’s generation. WECC_URE1 implemented strong preventative measures to prevent the above consequence from occurring. WECC_URE1 escorted the contractor the entire time while he was performing his authorized work functions. The contractor was a trusted vendor who supported WECC_URE1’s CCAs and recognizes the proper methods to handle and use the CCAs. The contractor had a current personnel risk assessment and was accessing the CCAs for only a short period of time. Further, since WECC_URE1 was with the contractor the entire time, the escort was positioned to prevent any serious misuse from occurring. No harm is known to have occured. WECC considered WECC_URE1's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, WECC_URE1: 1) revoked unescorted access to contract employee and provided necessary training to the contract employee.
2014-11-25 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2014013587 | CIP-007-3a | R1 | WECC_URE1 submitted a Self-Certification stating that it had an issue with CIP-007-3a R1. Specifically, WECC_URE1 failed to test significant changes to Critical Assets within the Electronic Security Perimeter (ESP). The first instance occurred during an upgrade project where WECC_URE1 failed to perform testing for one application installed on nine (9) Critical Cyber Assets (CCAs). This application was used to gather configuration information on the CCAs in order to facilitate an upgrade. In the second instance, WECC_URE1 failed to perform testing for a significant change relating to the installation of a non-critical assets into an air-gapped network containing CCAs. This installation was part of an upgrade. The root cause of this issue is human error. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE1 failed to test significant changes to Critical Assets within the ESP on two occasions. Failure to follow testing procedures in these two instances could result in the CCAs controlling the functions of the Critical Assets having no or improper security controls. An attacker could use this to their advantage to compromise WECC_URE1’s total generation of approximately 400 MW. On the other hand, WECC_URE1 implemented good preventative controls to prevent the compromise of generation from occurring. Local Transmission Owners and Transmission Operators were notified that the unit was unavailable and not to count on its generation during the project duration. The new devices were never brought back online, instead, WECC_URE1 rolled back to the existing system where the proper controls were in place prior to the upgrade. Additionally, WECC_URE1 implemented good compensating measures. WECC_URE1 installed anti-virus on all CCAs along with 24 hours 7 days a week logging and monitoring on local devices and all access points into the ESP. WECC_URE1 also installed software to scan each system every 4 hours and alert of any device that did not match configured and approved baselines. No harm is known to have occured. WECC considered WECC_URE1's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, WECC_URE1: 1) rolled back operating system to the existing systems; and 2) system state for the unit CCAs was restored to its original pre-upgrade configuration, removing the risk of compromise.
2014-11-25 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2014013586 | CIP-007-3a | R2 | WECC_URE1 submitted a Self-Certification stating that it had an issue with CIP-007-3a R2. WECC_URE1 stated that during an upgrade project on a Critical Cyber Asset (CCA), it failed to ensure only those ports and services necessary were enabled on 11 Critical Asset devices installed to control within the Electronic Security Perimeter. Specifically, WECC_URE1 failed to ensure that only those ports and services necessary were enabled when WECC_URE1 installed 11 CCA devices on a Critical Asset . The root cause of this issue is human error. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE1 failed to establish and document a process of change control, as per CIP 003-3 R6, which led to WECC_URE1 failing to enable only those ports and services required for normal and emergency operations on 11 Critical Assets which could control the operation of a Critical Asset, as per CIP 007-3a R2. This could lead to the CCAs controlling the functions of the Critical Assets having no or improper security controls, which an attacker could use to compromise WECC_URE1’s total generation of approximately 400MW. On the other hand, WECC_URE1 implemented good preventive measures to prevent the compromise approximately 400MW of generation from occurring. Specifically, the unit was isolated from the network during the upgrade project and could have only affected approximately 130 MW of generation. Local Transmission Owners and Transmission Operators were notified that the unit was unavailable and not to count on its generation during the project duration. The new devices were never brought back online, instead, WECC_URE1 rolled back to the existing systems, where the proper controls were in place prior to the upgrade. Additionally, WECC_URE1 implemented good compensating measures. WECC_URE1 installed anti-virus on all CCAs along with 24 hours 7 days a week logging and monitoring on local devices and all access points into the ESP. WECC_URE1 also installed software to scan each system every 4 hours and alert of any device that did not match configured and approved baselines. No harm is known to have occured. WECC considered WECC_URE1's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, WECC_URE1: 1) rolled back operating system to the existing systems; and 2) system state for the unit CCAs was restored to its original pre-upgrade configuration, removing the risk of compromise.
2014-11-25 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2014013581 | CIP-007-3a | R5 | WECC_URE1 submitted a Self-Certification stating that it had an issue with CIP-007-3a R5. WECC_URE1 stated that it failed to implement account management procedures on three occasions. Specifically, WECC_URE1 failed to change passwords on Critical Cyber Assets (CCAs). In the first instancet, during an upgrade project, WECC_URE1 failed to remove default accounts on three windows workstations (CCAs) which could control WECC_URE1’s generator. The accounts were default user and administrator accounts. In the second instance, WECC_URE1 failed to change one shared account password after three personnel changes. The shared account could be used to access three CCAs that could control five generators. In the last instance, WECC_URE1 failed to change annually change the passwords on 16 CCAs for three local administrator accounts. All devices were network switches located within the Electronic Security Perimeter (ESP) and the Physical Security Perimeter (PSP). The root cause of this issue is human error. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE1 failed to change its passwords on CCAs on three different occasions. By failing to change passwords on its CCAs, WECC_URE1 failed to implement account management procedures as per CIP 007-3a R5. The root cause of this issue is human error. Failure to implement account management procedures three instances could result in the CCAs controlling the functions of the Critical Assets having no or improper security controls. An attacker could use this to their advantage to compromise WECC_URE1’s total generation of approximately 400 MW. On the other hand, WECC_URE1 implemented good preventative controls to prevent the compromise of generation from occurring. Specifically, the unit was isolated from the network during the upgrade project and therefore only the remaining generators could have been affected with a generation of approximately 130 MW. WECC_URE1 notified local Transmission Owners and Transmission Operators that the unit was unavailable and not to count on its generation during the project duration. The new devices were never brought back online, instead, WECC_URE1 rolled back to the existing systems where the proper controls were in place prior to the upgrade. Additionally, WECC_URE1 implemented good compensating measures. WECC_URE1 installed anti-virus on all CCAs along with 24 hours 7 days a week logging and monitoring on local devices and all access points into the ESP. WECC_URE1 also installed software to scan each system every 4 hours and alert of any device that did not match configured and approved baselines. No harm is known to have occured. WECC considered WECC_URE1's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, WECC_URE1: 1) changed the passwords on two of the three administrator accounts on the switches; and 2) access was revoked from the employee responsible for sending the notices.
2014-11-25 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2014013583 | CIP-007-3a | R6 | WECC_URE1 submitted a Self-Certification stating that it had an issue with CIP-007-3a R6. Specifically, WECC_URE1 failed to enable security logging on 11 Cyber Assets (CAs) during an upgrade and therefore could not monitor system events related to cyber security. WECC_URE1 was upgrading multiple CCAs. The root cause of this issue is human error. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE1 failed to enable security logging on 11 Critical Assets and therefore could not monitor system events related to cyber security as per CIP 007-3a R6. These devices could control the operation of a Critical Asset. The Critical Asset has a total generation capacity of approximately 130 MW. Failure to implement security status logging on 11 Critical Assets could result in the devices controlling the functions of the Critical Asset have no or improper security controls. An attacker could use this to their advantage to compromise WECC_URE1’s total generation of approximately 400 MW and with no logging in place, there would be nothing to alert WECC_URE1. On the other hand, WECC_URE1 implemented good preventative controls to prevent the compromise of generation from occurring. Specifically, the unit was isolated from the network during the upgrade project and could have only affected 130 MW of generation. WECC_URE1 notified local Transmission Owners and Transmission Operators that the unit was unavailable and not to count on its generation during the project duration. The new devices with the unit were never brought back online, instead, WECC_URE1 rolled back to the existing systems where the proper controls were in place prior to the upgrade. Additionally, WECC_URE1 implemented good compensating measures. WECC_URE1 installed anti-virus on all CCAs along with 24 hours 7 days a week logging and monitoring on local devices and all access points into the ESP. WECC_URE1 also installed software to scan each system every 4 hours and alert of any device that did not match configured and approved baselines. No harm is known to have occured. WECC considered WECC_URE1's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, WECC_URE1: 1) rolled back operating system to the existing Windows XP systems; and 2) system state for the unit CCAs was restored to its original pre-upgrade configuration, removing the risk of compromise.
2014-11-25 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2014013582 | CIP-007-3a | R9 | WECC_URE1 submitted a Self-Certification stating that it had an issue with CIP-007-3a R9. Specifically, WECC_URE1 failed to document one software installation within 30 days of the change being completed. WECC_URE1 installed software on 9 CCAs and removed the software from all but one server device on that same day. The software remained on the server for approximately 17 months. The root cause of this issue is human error. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE1 installed software on 9 CCAs and removed all software except on one device server on that same day. The software remained on the one device until January 31, 2014 and was not documented within 30 days of the change being made. Failure to update system documentation could result in the CCAs controlling the functions of the Critical Assets having no or improper security controls. An attacker could use this to their advantage to compromise WECC_URE1’s total generation of approximately 400 MW. On the other hand, WECC_URE1 implemented good preventative controls to prevent the compromise of generation from occurring. Specifically, the Critical Asset was isolated from the network during the upgrade project and could have only affected approximately 130 MW of generation. Local Transmission Owners and Transmission Operators were notified that the unit was unavailable and not to count on its generation during the project duration. The new devices with the unit were never brought back online, instead, WECC_URE1 rolled back to the existing systems. Additionally, WECC_URE1 implemented good compensating measures. WECC_URE1 installed anti-virus on all CCAs along with 24 hours 7 days a week logging and monitoring on local devices and all access points into the ESP. WECC_URE1 also installed software to scan each system every 4 hours and alert of any device that did not match configured and approved baselines. No harm is known to have occured. WECC considered WECC_URE1's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, WECC_URE1: 1) removed software from device; and 2) appropriate personnel completed formal training on CIP-007-3 R9 Documentation Review and Maintenance.
2014-11-25 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2014013584 | CIP-009-3 | R5 | WECC_URE1 submitted a Self-Certification stating that it had an issue with CIP-009-3 R5. Specficially, WECC_URE1 failed to test backup media for the 2013 calendar year. WECC_URE1 has a procedure requiring annual backup media testing to be performed on CCAs. These CCAs manage network communication within the combustion turbine Electronic Security Perimeter (ESP) and between all CCAs within the ESP. The root cause of this issue is human error. | The issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE1 failed to perform annual backup media testing on 16 CCA switch devices as required by CIP 009-3 R5. These CCAs manage network communication within the combustion turbine ESP and between all CCAs within the ESP. Failure to test backup media on 16 CCAs could result in the recovery of these CCAs being delayed resulting in inoperable switches. This would cause the CCAs to lose connectivity to the Critical Asset controller. This could affect WECC_URE1's total generation of approximately 400 MW. WECC_URE1 did implement good preventative controls to prevent the loss of approximately 400 MW of generation. Specifically, previous backups still existed that WECC_URE1 could have used to restore the switches in the event a recovery was needed. No harm is known to have occured. WECC considered WECC_URE1's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, WECC_URE1: 1) tested the backup media for the switches in accordance with WECC_URE1's CIP-009 Cyber Asset recovery plan backup media testing procedure.
2014-11-25 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2014013861 | CIP-006-3c | R2 | WECC_URE2 submitted a Self-Report stating that it had an issue with CIP-006-3c R2. Specifically, WECC_URE2 had moved a SCADA console Critical Cyber Asset (CCA) from its previous Physical Security Perimeter (PSP) to a new location. As the sole CCA for a Critical Asset, this effectively moved the Critical Asset to the new building. As a consequence of this move, three new PSPs were created with the addition of a CCA to the room. The three card readers controlled access to two PSPs, and those PSPs contained six cyber assets, two of which are CCAs. The devices were four switches and two clients located at the backup control center. As a result of the move, the one controller did not have all the required CIP 006-3c R2.2 protections. The root cause of this issue is human error. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE2 failed to provide one controller the protections of CIP 007 R6 and CIP 005 R2 and R3. The controller provided access and functionality to three card readers controlling access to two PSPs. The two PSPs contained six Cyber Assets, two of which are CCAs. The devices were four switches and two clients located at the backup control center. The clients were used to control Automatic Generation Control, Automatic Dispatch System, Remote Start/Stop Capability, or Curtailment/tripping. The switches provided communication for the clients from the backup control center. The total amount of WECC_URE2’s generation that could have been controlled from the clients is approximately 800 MW out of a total of 3,000 MW. Failure to provide the protections of CIP-007 R6, CIP-005 R2 and R3, to the controllers for two PSPs containing the clients could potentially result in security events on the controllers going unnoticed and unchecked for extended periods of time. If cyber security events for the controllers were not monitored and if port and services restrictions were not implemented, an attacker could attempt to gain logical access to the controllers and have additional time to break into the panels since alerts would go unnoticed to security personnel. Also, if unauthorized logical access was gained, the attacker could potentially unlock the PSP access points to allow physical access to the PSP and clients in scope. On the other hand, WECC_URE2 did implement strong preventative and detective controls to prevent security events on the controllers to go unnoticed and unchecked for extended periods of time. Specifically, WECC_URE2 implemented 24 hours 7 days a week monitoring at the PSP building with cameras and door alarms. Also the PACS server which controls access to the controller was physically secured and had logging, monitoring, and user access restrictions. The only way to access the controller was from the PACS server over specific ports. Additionally, the clients and switches in scope had monitoring, logging, user access restrictions, were physically monitored, and WECC_URE2 has implemented a network monitoring application which provides real time alerting on the network status of the switches and the consoles. If physical access to the PSPs and clients was detected, WECC_URE2 would have likely prevented further logical access in a timely manner before someone could attempt to disrupt WECC_URE2's generation. No harm is known to have occured. WECC considered WECC_URE2's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, WECC_URE2 will complete the following mitigation activities within 90 days: 1) setup the new firewall to control and monitor electronic access to the PACS controller for the relevant card readers; 2) connect the new firewall to the SIEM for Security Status Monitoring.
2014-11-25 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2014014090 | CIP-002-3 | R4 | During a Compliance Audit, WECC determined that WECC_URE3 had an issue of CIP-002-3 R4. Specifically, WECC_URE3 was only able to produce evidence that a manager approved the RBAM, list of CCAs, and list of Critical Assets for 2012 and no other years since the beginning of the standard and therefore has an issue with CIP 002 R4 (even if such lists are null). The root cause of this issue was human error. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE3 failed to provide evidence that a signed and dated record of senior manager or delegate has approved the RBAM, the list of CCAs, and the list of Critical Assets (even if such lists are null) per CIP-002-3 R4. The failure to develop a list of Critical Assets and CCAs and have it approved by senior management could potentially result in non-identification and protection of Critical Assets and CCAs. Therefore, critical systems may not be afforded all the CIP protections. WECC_URE3 is a Generator Owner and Generator Operator and based on its RBAM does not have any Critical Assets or CCAs, therefore the entity has no impact to the BPS based upon the application of their RBAM to its assets. WECC_URE3 has documented and updated their RBAM annually which addresses all the R1 requirements. It has also identified its potential assets and demonstrated its application of the RBAM against all of WECC_URE3’s assets resulting in a null list of Critical Assets . WECC_URE3 has also verified with it Balancing Authority that it can have no negative impact to the BES in case of loss or misuse of any of its assets. No harm is known to have occured. WECC considered WECC_URE3's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, WECC_URE3 will complete the following mitigation activities within 90 days: 1) develop a list of CCAs and list of Critical Assets (even if the lists are null); 2) create and provide a signed and dated record of senior manager or delegate has approved the RBAM.
2014-11-25 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2014014089 | CIP-003-3 | R2 | During a Compliance Audit, WECC determined that WECC_URE3 had an issue of CIP-002-3 R4. Specifically, WECC_URE3 was asked to produce evidence that a single senior manager has signed and approved the risk-based methodology (RBAM), the list of Critical Assets (CAs), and the list of Critical Cyber Assets (CCAs) (even if such lists are null). WECC_URE3 identified two positions held by one person, but was not able to demonstrate that there was a single CIP Senior Manager as the signees. A manager did sign a previous year methodology. WECC_URE3 believed that since no CCAs or Critical Assets were identified in its RBAM; no senior manager had to approve a null list. The root cause of this issue was human error. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE3 failed to provide evidence that it assigned a senior manager for leading and managing WECC_URE3’s implementation of CIP standards. Failure to assign a senior manager for leading and managing WECC_URE3’s implementation of CIP Standards increases the risk that, due to a lack of executive supervision, the protective measures required by CIP standards may not be adequately implemented for the CCAs essential to the operation of the BPS, thereby negatively impacting the reliability of the BPS. Based on WECC_URE3's RBAM, they do not have any Critical Assets or CCAs, therefore the entity has no impact to the BES based upon the application of their RBAM to its assets. As compensating measures, WECC_URE3 has documented and updated their RBAM annually which addresses all the R1 requirements. It has also identified and evaluated all of its assets and demonstrated its application of the RBAM against all of WECC_URE3’s assets resulting in a null list of Critical Assets . WECC_URE3 has also verified with its Balancing Authority that it can have no negative impact to the BES in case of loss or misuse of any of its assets. No harm is known to have occured. WECC considered WECC_URE3's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, WECC_URE3 will complete the following mitigation activities within 90 days: 1) designate a CIP Senior Manager to review and sign RBAM.
2014-10-30 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2014014254 | CIP-007-3a | R1 | FRCC_URE submitted a Self-Report stating that it was in violation of CIP-007-3a R1. FRCC_URE1 failed to ensure that a significant change to existing Cyber Assets within the Electronic Security Perimeter did not adversely affect existing cyber security controls. No testing was performed with a manual software installation mechanism to ensure that it applied the same policies that an automated installation method would apply. A Cyber Vulnerability Assessment (CVA) was performed on all CCAs at a FRCC_URE1 facility to ensure there were no lingering cyber security controls issues introduced by installing certain software. The CVA script for desktops did not run properly on some CCAs. Upon further investigation, it was determined that the software configuration policy settings on those Cyber Assets prevented the CVA script from executing properly. In addition, that software was preventing a logging application from forwarding logs. The logs were still collected, but they were not being forwarded in real-time and were not manually reviewed. The faulty software configuration policy also caused the affected Cyber Assets to miss two updates. The affected CCAs were immediately corrected. The remaining CCAs at the facility were not affected as they used the automated software installation mechanism. The root cause of this was a failure to follow testing procedures for the CCAs. | This issue posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Specifically, FRCC_URE1’s failure to follow testing procedures with regard to the manual implementation of software changes left the CCAs vulnerable to threats and susceptible to attacks going undetected while the logs were not being forwarded or reviewed. The risk was decreased because the CCAs were still protected by software for all but the most current threats. Furthermore, all CCAs are located within an Electronic Security Perimeter and Physical Security Perimeter. No actual harm was known to have occurred. | To mitigate this violation, FRCC_URE1 corrected the software configuration policy settings, updated with latest changes, tested changes, and confirmed the CVAs and logging forwarding application could then be successfully executed. FRCC_URE will complete the following mitigating activities to address prevention of future recurrence: 1) create a checklist that addresses a manual install of the software; 2) communicate the checklist to the individual(s) responsible for installs; and 3) gather signoff/acknowledgment that the checklist was communicated.
2014-10-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2012010957 | CIP-002-1 | R3 | During a Compliance Audit, SPP RE determined that SPPRE_URE1 had an issue of noncompliance with CIP-002-1 R3 because it did not identify and document all of its Critical Cyber Assets. The affected Critical Cyber Assets included: (1) SPPRE_URE1 relays serially connected to an associated communications processor which utilizes routable protocols to communicate with the SPPRE_URE1 Control Center; and (2) the Inter-Control Center Communications Protocol (ICCP) servers, which are essential for exchanging real-time operational data with SPPRE_URE1’s Reliability Coordinator (RC). Because these devices were not identified as Critical Cyber Assets, SPPRE_URE1 did not afford them all the protections specified in CIP Standards CIP-003 through CIP-009, and in particular, the protections specified in CIP-007 R3, R4, and R8. With regard to the ICCP servers, the root cause of the issue is SPPRE_URE1’s misinterpretation of CIP-002-1 and its application to ICCP servers. SPPRE_URE1 attested that when it applied its RBAM, it determined that its ICCP servers were not Critical Cyber Assets because it could still provide ICCP data to its RC if the servers went down and could still perform its registered functions. Regarding the identification of the serially connected relays as Critical Cyber Assets, SPPRE_URE1 incorrectly assumed that because the relays were serially connected to a communications processor and not, by themselves routable, they were not cyber assets that used routable protocol as described in CIP-002-1 R3.2. | This issue posed a moderate risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System. The failure to identify the substation relays and ICCP servers as Critical Cyber Assets presented a risk that such assets would not be afforded enhanced security protections as required by the standard and exposed to potential cyber attack. Nevertheless, the relays and ICCP servers were afforded some protective measures. The ICCP servers were housed in a Physical Security Perimeters (PSPs), and were isolated on a segmented network away from SPPRE_URE1’s designated Electronic Security Perimeter (ESP) and were protected by firewalls. Additionally, SPPRE_URE1 limited the servers’ open ports and services, relying on several sources to determine the ports and services necessary for normal and emergency operations. The communications devices the relays were serially connected to were identified as Critical Cyber Assets, and were afforded all CIP-007 protective measure; thus, any compromise to the relays most likely would have been detected by the communications devices. No actual harm occurred as a result of the noncompliance. | To mitigate this issue, SPPRE_URE1: 1) Classified and documented its ICCP servers and the relays associated with its communications processor as Critical Cyber Assets; 2) Afforded these devices all associated compliance requirements; and 3) Upgraded diagrams and other documentation as a result of classifying these devices as Critical Cyber Assets. SPP RE has verified the completion of all mitigation activity.
2014-10-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2014013961 | CIP-003-3 | R2 | WECC_URE1 submitted a Self Report to WECC stating that it had an issue with CIP-003-3 R2. Specifically, WECC_URE1 reported that it did not have a document assigning a single senior manager with overall responsibility and authority for leading and managing WECC_URE1’s implementation of and adherence to the CIP Standards. The root cause of this remediated issue was the lack of communication between owners during a transfer of ownership. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE1 failed to assign a senior CIP manager to oversee implementation and compliance with the CIP Standards. Failure to assign a CIP senior manager could result in the CIP protections not being provided to Bulk Electric System assets which could then leave WECC_URE1’s approximately 80 MW of wind generation vulnerable and potentially unavailable. However, WECC_URE1 implemented detective controls by conducting quarterly reviews for potential CIP violations. WECC_URE1 discovered this violation during one such quarterly review. No harm is known to have occurred. WECC considered WECC_URE1's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, WECC_URE1: 1) assigned a single senior CIP manager with overall responsibility and authority for leading and managing the entity’s implementation of, and adherence to, the CIP Standards. WECC has verified the completion of all mitigation activity.
2014-09-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2012011630 | CIP-007-1 | R5; R5.3.3 | During a Compliance Audit, NPCC determined that NPCC_URE1 had an issue of CIP-007-3a R5.3.3. NPCC_URE1 had a set of devices that support annual password changes but do not technically enforce the change. A Technical Feasibility Exception (TFE) was not filed. The duration of the issue was from when the Standard became mandatory and enforceable on NPCC_URE1 to when NPCC approved the TFEs. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. NPCC_URE1's passwords are changed annually, contain special characters, and are a minimum of six characters. No harm is known to have occurred. | To mitigate this issue, NPCC_URE1: 1) filed TFEs that were approved by NPCC.
2014-09-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 2 (NPCC_URE2) | NCRXXXXX | NPCC2014014091 | CIP-005-3a | R1 | During a Compliance Audit NPCC determined that NPCC_URE2 had an issue with CIP-005-3a R1. A stacked network switch that connects the Energy Management System (EMS) to the Dispatch Training System (DTS) was classified as a Critical Cyber Asset (CCA). Consequently, the switch is both an access point and a CCA. This is a violation of R1 because CCAs are required to be in an ESP and cannot also be an Electronic Security Perimeter (ESP) access point. The root cause of the issue was an incorrect interpretation of the Standard. The duration of the issue was from when NPCC_URE2 reconfigured its Cyber Assets creating the noncompliant configuration to when NPCC_URE2 completed its mitigating activities. | The issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although the network switch is labeled a CCA and an Access Point, it is an Access Point for the DTS which resided inside the ESP and was protected in the same manner as NPCC_URE2's CCAs. Additionally, the DTS is a network endpoint and is not accessible from the public internet. The switch has access control lists in place that properly segment the ESP from the DTS. Lastly, the switch is a pair of switches or a "stacked switch." If one switch were to fail or otherwise be unavailable, traffic would be instantly re-routed to the other switch. No harm is known to have occurred. | To mitigate this issue, NPCC_URE2: 1) removed the connection from the switch to the DTS; and 2) routed traffic from the EMS to the DTS through an existing ESP access point.
2014-09-30 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2013012827 | CIP-008-3 | R1 | SERC_URE1 submitted a Self-Report stating that it had an issue with CIP-008-3 R1. SERC_URE1 failed to update its cyber security incident response plan (plan) within thirty days of a change, as required. SERC learned that SERC_URE1 failed to update its plan with the correct contact information after the senior network systems engineer left the company. The contact information was not updated until approximately two months later. | The issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The announcement of the employee’s departure was distributed within SERC_URE1 so personnel were aware of the change despite the failure to update the plan. There was role redundancy in the plan meaning that in the event of an emergency, other personnel with the same or similar role were available and would have been involved in execution of the plan. In addition, no Cyber Security incidents that would have resulted in the use of the plan were reported during the timeframe of this issue. SERC considered SERC_URE1's compliance history and determined that the instant issue was appropriate for FFT treatment because, although SERC_URE1 has a previous violation of CIP-008-R1 which contains facts similar to this issue, the instant issue was a documentation error and appropriate personnel would have been notified. | To mitigate this issue, SERC_URE1: 1) updated the CIP-008 Cyber Security Incident Response Plan to reflect the changes; 2) created an automated tracking list using the SERC_URE1’s proprietary database that lists the members of the computer incident response team; and 3) set up the proprietary database to generate a notification to IT Security and compliance personnel to update the plan.
2014-09-30 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2014014095 | CIP-004-3a | R2 | SERC_URE1 submitted a Self-Report stating that it had an issue with CIP-004-3a R2. While reviewing CIP access reports, SERC_URE1 identified an individual who was granted unescorted physical access to two Physical Security Perimeters (PSPs) prior to completing cyber security training. SERC_URE1 maintains an internal access list of individuals with authorized cyber or authorized unescorted physical access to Critical Cyber Assets (CCAs) in a central repository. All SERC_URE1 access requests for unescorted physical access or electronic access are submitted and compared against another database table that keeps track of qualifying conditions such as legitimate need for access, successful completion of a Personnel Risk Assessment, and successful completion of the required cyber security training. Once these three confirmations are provided, management can approve unescorted physical access or electronic access to CCAs. SERC_URE1 conducted compliance program training. At this time an individual erroneously added the NERC standards compliance program training to the course number list for cyber security training that is kept in the central repository table. Due to this error, one month later, the central repository automatically approved one individual’s cyber security training portion of the central repository approval process, because the individual had completed the NERC standards compliance program training. However, the employee did not complete the required annual cyber security training prior to being granted unescorted physical access to CCAs within two PSPs. SERC_URE1 reviewed all database entries and verified that this was the only instance of incorrect authorization. The individual's unauthorized access lasted for approximately two weeks and was resolved when the individual completed the required cyber security training. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failing to properly train individuals prior to granting physical or electronic access to CCAs may result in improper use of Cyber Assets and CCAs inside the Electronic Security Perimeter. However, the access issue was limited to physical access to two PSPs and no electronic access was granted. The unescorted physical access that was granted was needed and the individual immediately completed cyber security training upon discovery of the issue. The employee had undergone a Personnel Risk Assessment prior to access being granted. Finally, both PSP locations are manned 24 hours a day, 7 days a week by SERC_URE1 personnel, further minimizing the potential for impacts resulting from a lack of training. The Physical Access Control Logs revealed that the employee’s access card was not used to gain access to either PSP during the issue. SERC considered SERC_URE1’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, SERC_URE1 had the individual complete Cyber Security Training.
2014-09-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2012010647 | CIP-004-3 | R4; R4.1 | SPPRE_URE1 submitted a Self-Report to SPP RE stating that it was in violation of CIP-004-3 R4. SPPRE_URE1’s access control list of personnel with authorized cyber or authorized unescorted physical access to Critical Cyber Assets was not accurate as required by R4. The employee maintaining the access control list was using it to track the initiation and progress of the access control process. Specifically, there were: 1. Fourteen instances of personnel being added to the list prior to required training and/or personnel risk assessment being completed. 2. Twenty instances of personnel being removed from the list beyond the required 7-day deadline. 3. One instance of the list not being updated within a 7-day timeframe for a change in access rights. 4. Four instances of personnel on the list as having incorrect electronic access rights. 5. Two instances of the name of personnel with authorized access rights being overwritten when making a list addition. The root cause of this issue of non-compliance was documentation error. | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System. SPPRE_URE1’s inaccurate access control list was due to documentation error and not an actual mistake in granted access. SPPRE_URE1 only granted logical access and unescorted physical access to Critical Cyber Assets upon completion of security awareness training and personnel risk assessment. Only authorized personnel had access to the Cyber Assets. The SPPRE_URE1 Physical Security Perimeter is completely within a secure complex with additional layers of security and access control. No actual harm occurred to any SPPRE_URE1 Cyber Assets as a result of the noncompliance. | To mitigate this issue and prevent recurrence, SPPRE_URE1: 1) established a process for the Access Control List (List) maintenance that follows the order of steps in the access request process as outlined in the Access Request form. 2) provided training to its staff with responsibilities in the access control process. 3) added a quality control checklist to the process for updating its List for personnel changes or changes in access rights. 4) revised the List to include the data that was overwritten, and established a process to add new personnel data at the bottom of the List. SPP RE has verified the completion of all mitigation activity.
2014-09-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2012011406 | CIP-005-1 | R3; R3.2 | During a Compliance Audit, SPP RE determined that SPPRE_URE1 had an issue of non-compliance with CIP-005-1 R3, inclusive of R3.2. Regarding R3, SPPRE_URE1 had not implemented electronic or manual processes for monitoring and logging access at access points to its Electronic Security Perimeter(s) (ESP) 24 x 7. Specifically, SPPRE_URE1 did not have a defined process to capture electronic access logs when the syslog server was unavailable. Regarding R3.2, SPPRE_URE1 did not review the electronic access logs that were not captured when the syslog server was unavailable. The root cause of this issue of non-compliance was not having an alternate process for storing and reviewing electronic access logs when the syslog server was unavailable. | This issue of non-compliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Because SPPRE_URE1 did not have a defined process to capture and review electronic access logs to the ESP when the syslog server was unavailable, there was the risk that unauthorized electronic access or access attempts into SPPRE_URE1’s ESPs might go undetected. This could result in SPPRE_URE1 failing to address suspicious access attempts into the ESP. Nevertheless, no unauthorized electronic access occurred. SPPRE_URE1’s access control and monitoring devices are configured to deny all access attempts originating from outside the ESP, thereby limiting the risk that unauthorized access could occur. SPPRE_URE1’s ESP network is continuously monitored by a network intrusion detection system, which increases the likelihood that SPPRE_URE1 would detect unauthorized access attempts into the SPPRE_URE1 ESPs. No harm to SPPRE_URE1’s Cyber Assets occurred as a result of the noncompliance. | To mitigate this issue, SPPRE_URE1: 1) added an additional syslog server that monitors and logs access at the access points. 2) instructed staff not to reboot the two servers at the same time to ensure one server remains in service at all times to capture logs. SPP RE has verified the completion of all mitigation activity.
2014-09-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2012011409 | CIP-005-1 | R5; R5.3 | During a Compliance Audit , SPP RE determined that SPPRE_URE1 had an issue of non-compliance with CIP-005-1 R5.3. SPPRE_URE1 did not maintain evidence that electronic access logs were retained for at least ninety days. The root cause of this issue of non-compliance was the lack of an alternate process to store logs when the primary syslog server was unavailable. | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Because SPPRE_URE1 did not retain electronic access logs in accordance with CIP-005-3 R5.3, there was the risk that unauthorized electronic access or access attempts into SPPRE_URE1’s ESPs might go undetected. This could result in SPPRE_URE1 failing to address suspicious access attempts into the ESP. Nevertheless, no unauthorized electronic access occurred. SPPRE_URE1’s access control and monitoring devices are configured to deny all access attempts originating from outside the ESP, thereby limiting the risk that unauthorized access could occur. SPPRE_URE1’s ESP network is continuously monitored by a network intrusion detection system, which increases the likelihood that SPPRE_URE1 would detect unauthorized access attempts into the SPPRE_URE1 ESPs. No harm to SPPRE_URE1’s Cyber Assets occurred as a result of the noncompliance. | To mitigate this issue, SPPRE_URE1: 1) added an additional syslog server that monitors and logs access at the access points. 2) instructed staff not to reboot the two servers at the same time to ensure one server remains in service at all times to capture logs. SPP RE has verified the completion of all mitigation activity.
2014-09-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2012011411 | CIP-007-1 | R3; R3.1 | During a Compliance Audit , SPP RE determined that SPPRE_URE1 had an issue of non-compliance with CIP-007-1 R3. SPPRE_URE1 was unable to provide evidence demonstrating that all applicable security patches were assessed within thirty calendar days of availability. The root cause of this issue of non-compliance is that SPPRE_URE1 was unable to provide documentation of security patch assessments for Windows and third-party applications because the list of assessed patches for such applications was not maintained. | This violation posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The failure to document the assessment of patches created the risk that a patch may not be fully vetted and therefore posed a risk to existing cyber security controls in SPPRE_URE1’s Electronic Security Perimeter (ESP). Despite the lack of patch assessment documentation, SPPRE_URE1 does monitor for applicable patches and evaluates them for approval before implementation. SPPRE_URE1 denies access to devices that attempt to communicate from outside the ESP, and no Cyber Assets or Critical Cyber Assets within the ESP have internet access. Therefore, the probability of unauthorized access to SPPRE_URE1’s Cyber Assets within the ESP is remote. SPPRE_URE1’s ESP network is continuously monitored by a network intrusion detection system, which increases the likelihood that SPPRE_URE1 would detect unauthorized access. Only authorized personnel have access to the Cyber Assets. No actual harm occurred to any SPPRE_URE1 Cyber Assets as a result of the noncompliance. | To mitigate this issue and prevent recurrence, SPPRE_URE1: 1) developed a third-party patch assessment process and tracking spreadsheet for documenting the assessment of third-party security patches. 2) implemented a process to utilize a monthly Microsoft Security Bulletin Summary and the Windows Server Update Services report to assess and document the applicability of Windows security patches for Windows-based Cyber Assets within the ESP. SPP RE has verified the completion of all mitigation activity.
2014-09-30 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE2014013925 | CIP-004-3a | R4; R4.1; R4.2 | TRE_URE1 submitted a Self-Report stating that it had an issue with CIP-004-3a R4.2. Texas RE reviewed the evidence and determined that TRE_URE1 also had an issue with CIP-004-3a R4.1. TRE_URE1 failed to update the list(s) within seven calendar days of the change of personnel with access to Critical Cyber Assets (R4.1). Additionally, TRE_URE1 did not revoke such access to Critical Cyber Assets within seven calendar days for personnel who no longer require such access to Critical Cyber Assets (R4.2). Specifically, TRE_URE1 discovered that one of its vendor employees with unescorted physical access to TRE_URE1 PSPs had voluntarily separated from the vendor twenty-one days earlier. TRE_URE1 revoked the employee’s access and changed its access list on the same day that TRE_URE1 discovered the employee had separated from the vendor. The root cause of this issue was mainly the vendor’s reliance on a single individual to process employee separations, which introduced a single point of failure. The vendor’s separation process also contributed to this issue because it did not utilize a checklist to ensure that all steps associated with a separation were performed. Texas RE determined that TRE_URE1 had an issue with CIP-004-3a R4.1 and R4.2 for approximately two weeks. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following four factors. First, the individual in question had successfully completed the PRA and CIP training and was in good-standing with TRE_URE1 and the vendor upon voluntary separation. Second, a review of electronic badge logging indicated that the vendor employee did not access, nor attempt to access, the PSP in the fourteen days after voluntary separation. Third, TRE_URE1 quickly revoked access and changed its access list upon discovery of the subject issue. Fourth, the vendor has a history of uniform compliance with TRE_URE1 CIP obligations and proactively participates in enforcement of TRE_URE1’s CIP program with its staff, completes annual and individual CIP training, receives and disseminates CIP security awareness notices and updates, reviews and responds to quarterly CIP Audits of personnel access requirements, maintains an understanding of onboarding and separation processes associated with access to TRE_URE1 PSPs, and has successfully processed five previous employee separations. Texas determined that the instant issue was appropriate for FFT treatment. Although TRE_URE1 and its affiliates had prior noncompliance issues with CIP-004, the root causes were different and did not indicate a pattern of conduct that would constitute a repetitive infraction. | To mitigate this issue and prevent recurrence, TRE_URE1 completed the following actions: 1) the vendor trained a second employee in the separation processes associated with access to TRE_URE1 PSPs so that a single individual is not wholly responsible for managing these processes; 2) the vendor created a Termination Checklist and implemented a process that requires the vendor to complete a separate checklist for each employee separation, regardless of whether the employee has TRE_URE1 CIP Access; 3) the vendor implemented an addition to its semi-monthly staff meeting with the TRE_URE1 Facilities Services Representative who manages this Vendor contract. This addition will require the TRE_URE1 Facilities Services Representative to validate the number of Vendor employees working on the TRE_URE1 contract. This will serve as a reminder of the separation process associated with access to TRE_URE1 PSPs and will increase the likelihood that any separations not immediately reported to TRE_URE1 are quickly identified and reported; and 4) TRE_URE1 disseminated a Security Awareness Reinforcement bulletin concerning this issue to all vendors with employees who have unescorted physical or cyber access to TRE_URE1 CIP areas and systems. This reinforcement will be disseminated during the first week of the last month of the second and fourth quarters of each year. Texas RE has verified the completion of all mitigation activity.
2014-09-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2014014136 | CIP-002-3 | R1 | During a Compliance Audit, WECC determined that WECC_URE1 had an issue of CIP-002-3 R1. Specifically, WECC_URE1 adopted the CIP-002-4 Bright Line Criteria prematurely. This early adoption had no impact to the entity’s Critical Asset determinations. WECC_URE1 failed to identify and document a Risk-Based Assessment Methodology (RBAM) that included procedures and evaluation criteria and considered all asset types. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE1 failed to identify and document a RBAM that included procedures and evaluation criteria and considered all asset types due to the fact that it prematurely adopted the CIP-002-4 Bright Line Criteria. WECC_URE1 produces approx. 20 MW of generation and does not have any Critical Assets or Critical Cyber Assets. WECC_URE1 did not remove any Critical Assets from its list in making this early transition to the CIP-002-4 Bright Line Criteria. No harm is known to have occurred. WECC considered WECC_URE1's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, WECC_URE1 will complete the following mitigation activities: 1) identify and document a RBAM that includes procedures and evaluation criteria that considers all asset types.
2014-09-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2014013473 | CIP-007-3a | R5 | WECC_URE2 submitted a Self-Certification to WECC stating that it had an issue with CIP-007-3a R5. Specifically, WECC_URE2 has two devices used to synchronize time and frequency for its Energy Management System (EMS) that were put into service these devices were located in the Control Centers. WECC_URE2 determined it was not technically feasible for these devices to require and use passwords as outlined in CIP-007-3a R5.3.1, R5.3.2, and R5.3.3. As a result, WECC_URE2 was required to file Technical Feasibility Exceptions (TFEs) for these devices prior to the date the devices were put in service. WECC_URE2 submitted two password related TFEs to WECC after the devices were already in service. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE2 failed to file TFEs on time for two devices used to synchronize time and frequency for its Energy Management System (EMS). These devices are located within WECC_URE2’s primary and backup control centers. Failing to file TFEs in a timely manner could result in improper compensating controls afforded to these devices. If those controls are not applied, then these devices could be used as an attack vector to potentially gain logical access into the Electronic Security Perimeter (ESP). The devices could then be used to allow access to other devices within the ESP. If an attacker was able to gain unauthorized logical access to Critical Cyber Assets (CCAs), then up to approximately 20,000 MW of system peak area load could be affected. However, WECC_URE2 implemented compensating measures. Specifically, WECC_URE2 employs a Defense in Depth cyber security designed to guard against any potential impact to the BES. Intrusion Detection System and Intrusion Prevention System appliances are in place on WECC_URE2’s corporate side connection of the firewall. This separates WECC_URE2’s control system network (the private domain) from the corporate domain. WECC_URE2’s private domain is located behind dedicated firewall appliances using a standard demilitarized zone (DMZ) architecture. As additional controls, the devices require two factor authentication for external interactive access. The devices are also located in physically secure areas where physical access is restricted by security guards and/or special door locks. No harm is known to have occurred. | To mitigate this issue, WECC_URE2: 1) submitted TFEs for the two devices in scope.
2014-09-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2014013598 | CIP-007-1 | R5 | WECC_URE3 submitted a Self Certification to WECC stating that it had an issue with CIP-007-1 R5. Specifically, WECC_URE3 reviewed its Cyber Asset access list at its peaker plants. During the review, WECC_URE3 noticed that for one employee there was a discrepancy between the access list and the employee’s access privileges. Further, WECC_URE3 had not been properly reviewing the employee’s access privileges for WECC_URE3’s Cyber Assets at its peaker plants. WECC_URE3 could not demonstrate that managers conducted a detailed analysis of the employee’s specific access privileges. However, WECC_URE3 could demonstrate that WECC_URE3 properly performed quarterly reviews of all other employees’ privileges and properly maintained its access list. In addition, all employees with access to WECC_URE3’s Cyber Assets at its peaker plants, including the employee at issue, had the correct access privileges during the time period at issue. The root cause of this remediated issue was human error when entering data. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE3 failed to review, at least annually, one employee’s account privileges. WECC_URE3’s access order system contained the incorrect access type for this employee. By failing to review user account privileges to ensure they are in accordance with Standard CIP-003 R5 and Standard CIP-004 R4, WECC_URE3 may have been unaware of the access privileges each employee had. This could also allow personnel to maintain elevated access to WECC_URE3’s Cyber Assets when elevated access is no longer needed. If personnel who no longer require access to Cyber Assets retain that access, or if personnel have elevated access that management is not aware of, then these personnel could misconfigure devices or perform unauthorized actions. In this instance, the employee at issue had access to peaker plants that have a total generation capacity of approx. 200 MW. However, WECC_URE3 implemented preventive and detective controls. Specifically, the employee in question was granted the correct access and was authorized for that access. The employee had CIP training and a personnel risk assessment (PRA), which reduced the likelihood that the employee would cause harm to the devices in scope. WECC_URE3 also uses industrial defender to monitor and alert network administrators of unauthorized behavior. If any of the peaker plants began to ramp up or down unexpectedly, WECC_URE3’s real-time desk would receive alarms. WECC_URE3 also implemented corrective controls. Specifically, WECC_URE3’s employees are trained to implement WECC_URE3’s incident response process if an incident occurs. WECC_URE3 also has backups and spare devices on hand, and if necessary, could use the backups to restore impacted devices. No actual harm is known to have occurred. | To mitigate this issue, WECC_URE3: 1) updated the employee's rights in its system; 2) revised procedures for quarterly review of the Electronic Security Perimeter (ESP) Access List to include a cross check to ensure accounts are properly provisioned.
2014-09-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC2014014212 | CIP-002-3 | R3 | During a Compliance Audit WECC determined that WECC_URE4 had an issue with CIP-002-3 R3. Specifically, WECC_URE4 identified two EMS workstations as Critical Cyber Assets (CCAs) that WECC_URE4 did not consider essential to the operation of a Critical Asset (CA), resulting in an inaccurate list of CCAs. WECC_URE4 failed to remove two energy management system (EMS) workstations. The root cause of this issue is human error. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE4 failed to remove two EMS workstations from its list. Failure to update the CCA list and have it approved by senior management could potentially result in non-identification and protection of CAs and CCAs. Therefore, critical systems may not be afforded all the CIP protections. WECC_URE4 has documented and updated its Risk-Based Assessment Methodology (RBAM) annually which addresses all the R1 requirements. Further, WECC_URE4 maintains multiple layers of protection for Electronic Security Perimeter assets, including multi-factor authentication, strict user account controls, change control and configuration management and monitoring of system events. Additionally, WECC_URE4 implemented compensating measures. WECC_URE4’s PSA group did have an accurate and updated list but it was not the list signed and reviewed by the senior manager. The senior manager had a list, but it still had the two EMS workstations on it. No actual harm is known to have occurred. WECC considered WECC_URE4's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, WECC_URE4 will complete the following mitigation activities: 1) remove the two EMS workstations from its CCA list.
2014-09-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 5 (WECC_URE5) | NCRXXXXX | WECC2013012581 | CIP-007-3a | R1.3 | While preparing a response to a random sample Data Request from WECC, WECC_URE5 could not produce security test results for a significant change that took place on two domain controllers. Further, WECC_URE5 discovered two additional instances where test results were not documented for all four domain controllers. WECC_URE5 found all other significant changes to Critical Cyber Assets (CCAs) to have the required test results recorded, however, three changes to these four CCA’s did not have the required test results documented. The significant change was made to a total of 10 domain controllers, but only four were inside the Electronic Security Perimeter (ESP). The root cause of this issue was human error caused by the absence of a procedural checklist as well as sufficient peer review for test procedures before and after changes were made. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, WECC_URE5 failed to produce security test results for a significant change that took place on six domain controllers. Failure to document test results for a significant change on four domain controllers (CAs) in the ESP may lead to future changes being conducted without a clear understand of the current configuration of the domain controllers, thus leading to potential device failures as new changes are applied. Alternatively, WECC_URE5 has established and implemented a robust change control and configuration management program which includes security controls testing for all significant changes made to all CAs. Additionally, WECC_URE5 updated their change control program and associated documentation after the violations occurred, and no additional instances of possible non-compliance were found at audit. No actual harm is known to have occurred. WECC considered WECC_URE5's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, WECC_URE5: 1) added an IT security and compliance review to the change management procedures; 2) created a testing checklist; 3) added a close out peer review to the change management procedures; and 4) trained personnel on peer reviewing. WECC has verified the completion of all mitigation activity.
2014-08-27 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2014013358 | CIP-007-1 | R5; R5.2; R5.2.2; R5.3.3 | FRCC_URE1 submitted a Self-Report stating that it had an issue of CIP-007-1 R5; R5.2, R5.2.2, and R5.3.3. During the third party cyber vulnerability assessment (CVA) performed, FRCC_URE1 discovered that several accounts implemented on the Cyber Assets did not have their passwords changed annually as required by CIP-007, R5.3.3. In addition, several shared accounts were not documented on the shared accounts lists as required by CIP-007, R5.2.2. An additional compliance assessment also revealed that some accounts that were supposed to be disabled, had not been disabled. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System. The risk was reduced because all the accounts identified were of two categories that limited risk exposure; 1. accounts used by internal system processes to communicate with other systems or application, and can not be used for user interactive logins; 2. accounts that were only available after the user has securely logged on to the server. Furthermore, all Cyber Assets were located in an Electronic Security Perimeter (ESP), within a Physical Security Perimeter (PSP), and access to the accounts was limited to a small number of authorized FRCC_URE1 personnel that all had current personnel risk assessments and annual cyber security training. No actual harm is known to have occurred. | To mitigate this issue, FRCC_URE1: 1) identified all in-scope Cyber Assets where non-compliant accounts were identified; 2) reconciled all in-scope accounts with the list of shared and system accounts; 3) implemented corrective measures (change of passwords where technically feasible); 4) submitted required TFE's for the balance of the accounts; 5) implemented additional control requiring the control owners to check passwords every six months and provide a completed report to compliance; 6) identified the root cause and provide recommendations to prevent recurrence; and 7) implemented corrective measures identified to address the root cause. FRCC has verified the completion of all mitigation activity.
2014-08-27 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2014013359 | CIP-002-3 | R3; R3.2 | FRCC_URE1 submitted a Self-Report stating that it had an issue of CIP-002-3 R3 and R3.2. FRCC_URE1 incorrectly identified integrated lights out (ILO) interfaces on new Cyber Assets commissioned as Critical Cyber Assets (CCA) on its CCA list. These ILO Cyber Assets were not required to be on the list as they had been disabled prior to the commission date. The error was discovered during FRCC_URE1's quarterly review of the CCA list and corrected. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System. FRCC_URE1's incorrect identification of the ILOs as CCAs was a documentation only error. There was no risk to the Bulk Power System as the interface cards were never enabled. No actual harm is known to have occurred. | To mitigate this issue, FRCC_URE1: 1) updated the CCA list to remove ILOs; 2) submitted TFE for cases where ILO could not be disabled; and 3) added a CCA attestation process to be completed periodically requiring attestation from all the directors involved with change management of the Cyber Assets. FRCC has verified the completion of all mitigation activity.
2014-08-27 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2014013986 | CIP-002-3 | R3 | During a Compliance Audit SPP RE determined that SPPRE_URE1 had an issue of noncompliance with CIP-002-3 R3 because it did not develop a list of Critical Cyber Assets using the list of Critical Assets determined through an application of its risk-based assessment methodology (RBAM). Specifically, SPPRE_URE1 did not develop a null list for its Critical Cyber Assets. The root cause of this issue was due to oversight because SPPRE_URE1 has no Critical Cyber Assets. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. This documentation issue could have delayed an individual, unfamiliar with SPPRE_URE1’s operation, from determining whether SPPRE_URE1 had any Critical Cyber Assets. However, SPPRE_URE1 does not own any Critical Assets or Critical Cyber Assets that support the reliability of the Bulk Electric System. No harm is known to have occurred as a result of this issue. | To mitigate this issue, SPPRE_URE1 created a null Critical Cyber Asset list. SPP RE has verified the completion of all mitigation activity.
2014-08-27 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPPRE_URE2) | NCRXXXXX | SPP2012010961 | CIP-006-1 | R1; R1.8 | During a Compliance Audit, SPP RE determined that SPPRE_URE2 had an issue of noncompliance with CIP-006-1 R1.8. SPPRE_URE2 had not identified workstations and door control panels used in the access control and monitoring of its Physical Security Perimeters (PSPs) as physical access control system (PACS) cyber assets, and may not have afforded these devices the protective measures listed in R1.8. Upon further investigation, SPP RE determined that SPPRE_URE2 did afford its door control panels the appropriate protective measures, but did not afford its workstations the protective measures of CIP-007-1 R2 and CIP-007-1 R8.2. Regarding CIP-007-3 R2, SPPRE_URE2 did not ensure that only ports and services required for normal and emergency operations were enabled on the workstations. Regarding CIP-007-1 R8, SPPRE_URE2 did not subject its workstations to an annual Cyber Vulnerability Assessment. This issue stemmed from an oversight by SPPRE_URE2 personnel to recognize that the workstations were PACS devices. | This issue of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The potential risk with not performing an annual Cyber Vulnerability Assessment or not ensuring that only ports and services required for normal and emergency operations are open is that SPPRE_URE2 may miss a vulnerability that could expose its devices to malicious activity. However, the associated PACS server was afforded all of the protective measures specified in CIP-006-1 R1.8. Furthermore, the workstations were afforded all other required CIP protections, including anti-virus and malware protections, and regular patching and updating to mitigate electronic security risks. Furthermore, SPPRE_URE2’s most recent CVA conducted on its workstations showed that all enabled ports and services were necessary for normal and emergency operations. The workstations resided within both an Electronic Security Perimeter, which used Firewalls and Intrusion Detection technology to monitor network traffic, and a Physical Security Perimeter-like building and were afforded multiple physical protection measures, including six-wall borders secured by electronic locks and card readers, door alarms, and 24/7 monitoring by armed staff, limiting physical access to the workstations and door control panels. No actual harm occurred to SPPRE_URE2’s PACS server or associated devices as a result of this issue. | To mitigate this issue, SPPRE_URE2: 1) performed analysis on securing its workstations; 2) redesigned workstation network architecture and implemented network changes; 3) classified all appropriate workstation devices as Cyber Assets and completed associated compliance requirements; 4) performed analysis on securing door control panels; and 5) classified all appropriate door control panels as Cyber Assets and completed associated compliance requirements. SPP RE has verified the completion of all mitigation activities.
2014-08-27 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 3 (SPPRE_URE3) | NCRXXXXX | SPP2012011249 | CIP-007-3a | R1 | During a Compliance Audit, SPP RE determined that SPPRE_URE3 had an issue of noncompliance with CIP-007-3a R1 because SPPRE_URE3 failed to ensure that the installation of a new Cyber Asset within an Electronic Security Perimeter (ESP) did not adversely affect existing cyber security controls. Specifically, an SPPRE_URE3 employee brought his work laptop computer into SPPRE_URE3’s physical security perimeter and connected it to a management port on a Critical Cyber Asset within the ESP to show the audit team virtual machines. In doing so, the laptop became a “new Cyber Asset” within the ESP, but SPPRE_URE3 did not test the laptop as required by CIP-007-3a R1. The violation stemmed from the SPPRE_URE3 employee’s failure to recognize that the connection of the laptop to the Critical Cyber Asset represented the installation of a “new Cyber Asset” within the ESP per CIP-007-3a R1. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The failure to test the laptop presented a risk of introducing malware onto SPPRE_URE3’s ESP network, which could have resulted in the loss of sensitive data, corruption of data, manipulation of applications or data, thereby placing the reliability of the BPS at risk. Notwithstanding, this was an isolated incident, which lasted approximately two minutes, and occurred only because the audit team requested to see additional information, not an act that SPPRE_URE3 routinely performs. No routable network connection within the ESP was made; therefore, the only Critical Cyber Asset accessed was that which was connected to the laptop. SPPRE_URE3’s ESP was continuously monitored and protected by an intrusion prevention/detection system, which provided real-time log analysis, event alerting, and blocking of both internal and external malicious transmissions on Cyber Assets within the ESP. SPPRE_URE3’s ESP, security control systems, and the laptop serially connected to the Critical Cyber Asset were protected by anti-virus software to prevent malware intrusion. The employee had authorized physical and electronic access rights to the Critical Cyber Asset, and multi-factor authentication measures predicated access to the Critical Cyber Asset, which was also logged and monitored. No actual harm occurred as a result of the noncompliance. | To mitigate this violation and to prevent recurrence, SPPRE_URE3: 1) updated its processes to define this type of connection as adding a device to the ESP; 2) developed a form to be completed that will document transient connections of devices to the ESP; 3) notified affected employees that this type of connection is now considered adding a device to the ESP; and 4) decommissioned the laptop to prevent recurrence.
2014-08-27 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 4 (SPPRE_URE4) | NCRXXXXX | SPP2012010240 | CIP-007-1 | R1; R1.1 | During a Compliance Audit, SPP RE and another regional entity determined that SPPRE_URE4 and affiliates had an issue of non-compliance with CIP-007-1, R1.1. For some duration, SPPRE_URE4 did not have documented cyber security test procedures for Cyber Assets within its substations. Due to corporate structuring, this issue is applicable to SPPRE_URE4 and its affiliates in their respective regions. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). The lack of documented cyber security test procedures creates the risk that SPPRE_URE4’s testing of its Cyber Assets may not be conducted in accordance with SPPRE_URE4’s procedural requirements. However, the only technically applicable requirements for these Cyber Assets are firmware updates, which occur infrequently and only affect operational settings, not security controls. SPPRE_URE4 evaluates and tests firmware updates before implementing them on its substation Cyber Assets. All of SPPRE_URE4’s substation Cyber Assets reside within Physical Security Perimeters, and are logically protected behind Electronic Security Perimeter (ESP) firewalls which require network access and authentication for remote access. Unauthenticated access attempts trigger an alert and subsequent cyber security investigation. No actual harm occurred to any SPPRE_URE4 substation Cyber Assets as a result of the noncompliance. | To mitigate this violation and prevent recurrence, SPPRE_URE4: 1) documented its cyber security test plan; 2) updated its Router Switch Procedure to document the cyber security test plan for the primary routable security devices; 3) developed a Substation Security Patch Testing form to provide additional controls for security patch procedures and documentation; 4) updated Cyber Security testing procedures for all Cyber Assets within the ESP, and Cyber Assets used in access control and/or monitoring; 5) updated the testing procedures for significant changes; and 6) conducted training and awareness for affected personnel regarding SPPRE_URE4’s improvements to controls and procedure changes.
2014-08-27 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 4 (SPPRE_URE4) | NCRXXXXX | SPP2012010244 | CIP-007-1 | R8 | During a Compliance Audit, SPP RE and another regional entity determined that SPPRE_URE4 and affiliates had an issue of non-compliance with CIP-007-1 R8. For some duration, SPPRE_URE4’s cyber vulnerability assessment procedure specifically excluded substation Critical Cyber Assets that were dial‐up accessible only. Additionally, when SPPRE_URE4 performed its annual inspections of substation Cyber Assets, it did not verify that the relay password had been changed from the system default. Due to corporate structuring, this issue is applicable to SPPRE_URE4 and its affiliates in their respective regions. | This issue posed a moderate risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). The documented cyber vulnerability assessment procedure and password changes are meant to lower the risk of a successful cyber attack being launched against the devices. Although SPPRE_URE4 had excluded the substation dial-up accessible Cyber Assets from the documented annual vulnerability assessment and did not verify that the relay passwords had been changed, SPPRE_URE4 has specific procedures when relays are installed or updated to change the password. Additionally, all Cyber Assets reside within Physical Security Perimeters, and are logically protected behind ESP firewalls that require network access and authentication for remote access. No actual harm occurred to any of SPPRE_URE4’s substation Critical Cyber Assets as a result of the noncompliance. | To mitigate this violation and prevent recurrence, SPPRE_URE4: 1) revised its cyber vulnerability assessment procedures to include dial-up accessible Cyber Assets at substations; 2) updated its vulnerability assessment process to verify necessary account controls are in place; 3) updated its vulnerability assessment process to ensure only necessary connections are present by checking all ports within the ESP; 4) updated its change control process and change control form for installation and/or modification of substation Cyber Assets to include verification that default passwords have been changed; and 5) conducted training and awareness of control improvements and procedure changes for impacted personnel.
2014-08-27 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 5 (SPPRE_URE5) | NCRXXXXX | SPP2014014175 | CIP-003-1 | R2; R2.1 | During a Compliance Audit , SPP RE determined that SPPRE_URE5 had an issue of noncompliance with CIP-003-1 R2, R2.1. SPPRE_URE5 appointed a senior manager to oversee its NERC compliance program via a city memorandum. However, the senior manager was not properly identified by title, address, and date of designation. The root cause of this issue was oversight in not fully documenting the senior manager as prescribed by CIP-003 R2. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Not properly identifying and documenting the senior manager could have caused the senior manager to be unaware of his responsibilities related to implementation of the CIP Standards. However, the Senior Manager was made aware of his responsibilities per a memorandum. Furthermore, the designated senior manager from 2007 continues to act as senior manager responsible for leading SPPRE_URE5’s CIP implementation. SPPRE_URE5 does not own any critical assets or critical cyber assets. No actual harm occurred to the BPS as a result of this issue. | To mitigate this issue, SPPRE_URE5 properly identified and documented its senior manager as prescribed by CIP-003 R2. SPP RE has verified the completion of all mitigation activity.
2014-08-27 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE2014013790 | CIP-004-3a | R2; R2.1 | TRE_URE1 submitted a Self-Report stating that it had an issue with CIP-004-3a R2.1. During a quarterly review of its access list, TRE_URE1 discovered that that two contractors were granted authorized unescorted physical access to Critical Cyber Assets (CCAs) prior to completing all required cyber security training modules. When an inquiry was made regarding the physical access status of two contract employees, a TRE_URE1 Compliance employee inadvertently granted authorized unescorted physical access to both contractor employees before completion of all required NERC training. This error was caused by the TRE_URE1 Compliance employee reviewing the wrong data field within the TRE_URE1 training system when determining whether the contractor employees’ training was complete. TRE_URE1 had an issue with CIP-004-3a R2.1 for approximately two weeks (when the two contract employees were granted authorized unescorted physical access to restricted areas until both contract employees completed all required cyber security training modules). | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on two factors. First, the contractor employees had both successfully completed Personnel Risk Assessments (PRAs) before the standard became enforceable. Second, the two contractors did not receive badges for unescorted physical access to Critical Cyber Assets (CCAs) prior to completing all required cyber security training modules. Therefore, the contractors never gained access to CCAs until all training was complete. No harm is known to have occurred. Although TRE_URE1 has prior violations of CIP-004, the root causes were different and did not indicate a pattern of conduct that would constitute a repetitive infraction. Therefore, Texas RE did not consider TRE_URE1’s violation history an aggravating factor. | To mitigate this issue, both TRE_URE1 contractor employees completed all required cyber security training modules. To prevent recurrence, TRE_URE1 completed the following actions: 1) reviewed and updated its process for granting authorized cyber or authorized unescorted physical access to Critical Cyber Assets; 2) streamlined its cyber security training program from three modules to one module in order to reduce confusion and the risk of granting access before any person completes all required training; and 3) revised its procedure document to require that all vendors and contractors have Personnel Risk Assessments (PRAs) processed through TRE_URE1’s third-party PRA provider. This requirement applies a uniform PRA process and improves checks and balances. Texas RE has verified completion of all mitigating activity.
2014-08-27 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2013012733 | CIP-006-3c | R1.6.2 | WECC_URE1 submitted a Self-Report to WECC stating that it had an issue with CIP-006-3c R1. Specifically, WECC_URE1 reported three unescorted visitors were discovered by a WECC_URE1 employee within the Physical Security Perimeter (“PSP”). Three visitors and two escorts were performing work on the Air Conditioning system inside the basement mechanical room. The mechanical room does not contain any Critical Cyber Assets (“CCA”) but does contain the air conditioning unit and several circuit breakers that control power not only to the air conditioning unit, but also to a variety of other mechanical equipment. The visitors split into two groups, with one escort in each group. One escort temporarily left his group to go to an adjacent room to discuss the work being performed with the other escort and visitors. While the escort was absent, a WECC_URE1 employee noticed the unescorted visitors and reported them to security, who then escorted the visitors out of the area. Security personnel remained with the visitors until the escort responsibilities could be transferred back to the original two escorts. The root cause of the issue was human error. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE1 briefed the visitors on the visitor policy and code of conduct prior to allowing the visitors entry to the PSP. WECC_URE1 required the visitors to wear bright yellow badges that identified them as visitors. There were several authorized personnel working in the area that would have noticed and prevented the visitors from causing harm to any critical assets within the PSP. Finally, WECC_URE1’s facility is equipped with battery UPS systems and a generator that would have kicked in if any of the circuit breakers in the control room had been tampered with. No harm is known to have occurred. WECC considered WECC_URE1's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, WECC_URE1: 1) visitors were removed from the facility upon discovery; 2) the two escorts that left visitors unsupervised were written up for the violation; and 3) to prevent recurrence by following its procedures and reprimanding the escorts WECC_URE1 has provided consequences for not following proper protocol . WECC has verified the completion of all mitigation activity.
2014-08-27 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2013013068 | CIP-007-3a | R8.1 | During a Compliance Audit WECC determined that WECC_URE1 had an issue with CIP-007-3a R8. WECC_URE1 performs Cyber Vulnerability Assessments (“CVAs”) for all Cyber Assets within the Electronic Security Perimeters (“ESPs”) at least annually. However, WECC_URE1’s documented assessment procedure does not mirror actual processes used. Specifically, WECC_URE1 performs continuous vulnerability assessments on all Critical Cyber Assets (“CCAs”). WECC_URE1’s documented assessment procedure did not contain a description of the continuous vulnerability assessments actually being performed. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE1’s documentation stated that it performs annual CVAs on a system wide basis whereas WECC_URE1 actually performs continuous CVAs on a device level basis. While WECC_URE1’s documentation identified an inaccurate procedure for performing CVAs, WECC verified that WECC_URE1 was nonetheless performing the CVAs as required under the Standard. In doing so, WECC_URE1 ensured that only those ports and services required for operation of the Cyber Assets within the ESA were enabled; reviewed the controls for default accounts; and documented the results of the assessment and any action plans required for identified vulnerabilities. WECC_URE1 also implemented additional physical and logical cyber security controls, including physical security mechanisms, special locks, CCTV, and logical perimeter and internal cyber security controls, including firewalls, vulnerability scanning tools and a Security Events Management system. Failure to properly document the cyber vulnerability process can lead to inconsistencies in the CVA process. Changes in tools or staff performing the CVA can lead to devices being missed or improperly assessed. Also, Cyber Assets, ports and/or services that do not have controls for annual review pose an increased risk for successful cyber-attacks against CCAs. No harm is known to have occurred. WECC considered WECC_URE1's compliance history and determined there were no relevant issues of noncompliance. | To mitigate this issue, WECC_URE1 will complete the following mitigation activities within 90 days: 1) document its cyber vulnerability assessment process and include process in CVA process documentation.
2014-08-27 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2014013528 | CIP-004-3a | R3 | WECC_URE2 submitted a Self-Certification stating that it had an issue of CIP-004-3a R3. Specifically, WECC_URE2 failed to update Personnel Risk Assessments ("PRAs") for four employees at least every seven years. The four employees’ PRAs expired and were not renewed for 175, 53, and 9 days, respectively. The root cause of the violation was that WECC_URE2 did not have a comprehensive list of PRA expiration dates. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE2 failed to ensure that a PRA was conducted on four personnel at least every seven years. The four employees in scope had logical and physical access to seventy Critical Cyber Assets ("CCAs"). Failure to conduct a PRA could have allowed individuals with malicious intent to have access to CCAs which control WECC_URE2’s entire Supervisory Control and Data Acquisition ("SCADA") system, potentially leading to disruption or loss of WECC_URE2’s peak load of approximately 3,000 MW. By not keeping the PRAs current, WECC_URE2 could not ensure that the employees did not or would not have malicious intent while using the CCAs. However, WECC_URE2’s preventative controls aided in preventing malicious access. Specifically, each of these four individuals had been with WECC_URE2 for over seven years and had the appropriate CCA training. Each of the four individuals were in good standing and their employment status has not changed over the course of the last seven years. Because of the extensive employment history, WECC_URE2 had full employment history of these individuals and knew these individuals were unlikely to cause harm to WECC_URE2’s cyber systems. No harm is known to have occurred. | To mitigate this issue, WECC_URE2: 1) implemented a new process to review future PRA due dates; and 2) implemented a master list containing all PRA due dates. WECC has verified the completion of all mitigation activity.
2014-08-27 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2014013530 | CIP-004-3a | R3.2 | WECC_URE3 submitted a Self-Certification stating that it had an issue of CIP-004-3a R3. Specifically, one employee's Personnel Risk Assessment ("PRA") expired and was not renewed for 26 days. The root cause of the issue was that WECC_URE3 did not have a comprehensive list of PRA expiration dates. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE3 failed to ensure that a PRA was conducted on one employee at least every seven years. The employee in scope had logical and physical access to WECC_URE3’s main control center, including the Supervisory Control and Data Acquisition ("SCADA") system. Failure to conduct a PRA could have allowed the individual with malicious intent to have access to Critical Cyber Assets ("CCAs") which control WECC_URE3’s SCADA system, potentially leading to disruption or loss of WECC_URE3’s peak load of approximately 1,500 MW. By not keeping the PRA current, WECC_URE3 could not ensure that the employee did not or would not have malicious intent while using the CCAs. However, WECC_URE3’s preventative controls aided in preventing malicious access. Specifically, this individual had been with WECC_URE3 for over seven years and had the appropriate CCA training. The individual was in good standing and his employment status has not changed over the course of the last seven years. Because of the extensive employment history, WECC_URE3 had full employment history of this individual and knew this individual was unlikely to cause harm to WECC_URE3’s cyber systems. No harm is known to have occurred. | To mitigate this issue, WECC_URE3: 1) completed the PRA renewal process for the individual scope; 2) implemented a new process to review future PRA due dates; and 3) implemented a master list containing all PRA due dates. WECC has verified the completion of all mitigation activity.
2014-08-27 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC2014013792 | CIP-007-3a | R4 | WECC_URE4 submitted a Self-Report to WECC stating that it had an issue with CIP-007-3a R4. Specifically, WECC_URE4 changed the network location of 118 assets from outside the Electronic Security Perimeter ("ESP") to inside the ESP. WECC_URE4 reported that at the time of the network location change, two devices were improperly classified as non-CCAs outside the ESP. WECC_URE4 discovered these two devices were on the same network as other assets inside the ESP, but were not categorized as such in WECC_URE4’s Cyber Asset list. WECC_URE4 reported these two devices should have been classified as Cyber Assets (non-CCAs) within an ESP. These two devices were incapable of having anti-virus or other malicious software prevention tools installed. WECC_URE4 filed TFEs for both devices. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE4 failed to file TFEs for two of its Cyber Assets. Failing to file TFEs on time could cause WECC_URE4 to improperly track the compensating measures necessary for devices where it is technically infeasible to install anti-virus software and other malicious software prevention tools. However, WECC_URE4 implemented strong compensating controls. The devices in question are all in the Physical Security Perimeter and are protected from physical and logical access. Access is approved by authorized personnel. Personnel with authorized access have completed CIP training and Personnel Risk Assessments. Before being placed in the production environment, the devices are tested to ensure that they do not adversely impact existing cyber security controls. All other assets within the ESP have anti-virus and antimalware tools installed. The devices are also subject to a cyber-security incident response plan and recovery plans. No harm is known to have occurred. WECC considered WECC_URE4's compliance history and determined there were no relevant issues of noncompliance. | To mitigate this issue, WECC_URE4: 1) submitted TFEs for both devices in scope; and 2) designed and implemented a form-based view for adding or modifying a cyber asset.
2014-08-27 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC2014013793 | CIP-007-3a | R6 | WECC_URE4 submitted a Self-Report to WECC stating that it had an issue with CIP-007-3a R6. Specifically, on WECC_URE4 changed the network location of 118 assets from outside the Electronic Security Perimeter ("ESP") to inside the ESP. WECC_URE4 reported that at the time of the network location change, two devices were improperly classified as non-CCAs outside the ESP. WECC_URE4 discovered these two devices were on the same network as other assets inside the ESP, but were not categorized as such in WECC_URE4’s Cyber Asset list. WECC_URE4 reported these two devices should have been classified as Cyber Assets (non-CCAs) within an ESP. These two devices were incapable of implementing automated tools or organizational process controls to monitor system events that are related to cyber security (these devices collect traffic statistics (bandwidth and usage) they do not collect cyber security data). Since the two devices were improperly categorized, WECC_URE4 failed to file TFEs before the devices were put into production. WECC_URE4 filed TFEs for both devices. | The issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE4 failed to file TFEs for two of its Cyber Assets. Failing to file TFEs on time could cause WECC_URE4 to improperly track the compensating measures necessary for devices where it is technically infeasible to implement automated tools or organizational process controls to monitor system events that are related to cyber security. However, WECC_URE4 implemented strong compensating controls. The devices in question are all in the Physical Security Perimeter and are protected from physical and logical access. Access is approved by authorized personnel. Personnel with authorized access have completed CIP training and Personnel Risk Assessment. Before being placed in the production environment, the devices are tested to ensure that they do not adversely impact existing cyber security controls. All other assets within the ESP have anti-virus and antimalware tools installed. The devices are also subject to a cyber-security incident response plan and recovery plans. Additionally, WECC_URE4’s failure to file TFEs on time caused no actual harm. WECC considered WECC_URE4's compliance history and determined there were no relevant issues of noncompliance. | To mitigate this issue, WECC_URE4: 1) submitted TFEs for both devices in scope; and 2) designed and implemented a form-based view for adding or modifying a cyber asset.
2014-08-27 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 5 (WECC_URE5) | NCRXXXXX | WECC2014013516 | CIP-007-3a | R2 | WECC_URE5 submitted a Self-Certification to WECC stating that it had an issue with CIP-007-3a R2. WECC_URE5 personnel failed to implement a process to ensure that only those ports and services required for normal and emergency operations were enabled. Specifically, WECC_URE5 installed eight new devices for which it could not disable ports and services not needed. WECC_URE5 did not file the appropriate Technical Feasibility Exceptions (TFEs) by the installation date. WECC_URE5 completed the submission of TFEs for all applicable devices. The root cause of this issue was human error. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE5 failed to file TFEs for eight devices. Failing to file TFEs in a timely manner could result in improper compensating controls being afforded to these devices. If those controls are not being applied, these devices could be used as an attack vector to potentially gain logical access into the Electronic Security Perimeter ("ESP") and to allow access to other devices within the ESP. If an attacker was able to gain unauthorized logical access to Critical Cyber Assets ("CCAs"), then up to approximately 2,000 MW of generation could be affected. WECC_URE5 did implement good compensating measures. Specifically, all devices exist on isolated networks that are subject to periodic security assessments and reviews. WECC_URE5 also has a planned compensating measure to upgrade ESP switches to restrict access to any of the internal devices by blocking all unnecessary traffic. No harm is known to have occurred. WECC considered WECC_URE5's compliance history and determined there were no relevant issues of noncompliance. | To mitigate this issue, WECC_URE5: 1) submitted TFEs for all applicable devices.
2014-08-27 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 5 (WECC_URE5) | NCRXXXXX | WECC2014013517 | CIP-007-3a | R4 | WECC_URE5 submitted a Self-Certification to WECC stating that it had an issue with CIP-007-3a R4. WECC_URE5 personnel failed to use anti-virus software and other malicious software ("malware") prevention tools, where technically feasible, to detect, deter, and mitigate the introduction, exposure, and propagation of malware on all Cyber Assets within the Electronic Security Perimeter ("ESP"). Specifically, WECC_URE5 installed nine new devices for which it could not install anti-virus software. WECC_URE5 did not file the appropriate Technical Feasibility Exceptions ("TFEs") by the installation date. WECC_URE5 completed the submission of TFEs for all applicable devices. The root cause of this issue was human error. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE5 failed to file TFEs for nine devices. Failing to file TFEs in a timely manner could result in improper compensating controls being afforded to these devices. If those controls are not being applied, these devices could be used as an attack vector to potentially gain logical access into the ESP and to allow access to other devices within the ESP. If an attacker was able to gain unauthorized logical access to Critical Cyber Assets ("CCAs"), then up to approximately 2,000 MW of generation could be affected. WECC_URE5 did implement good compensating measures. Specifically, all devices exist on isolated networks that are subject to periodic security assessments and reviews. WECC_URE5 also has a planned compensating measure to upgrade ESP switches to restrict access to any of the internal devices by blocking all unnecessary traffic. No harm is known to have occurred. WECC considered WECC_URE5's compliance history and determined there were no relevant issues of noncompliance. | To mitigate this issue, WECC_URE5: 1) submitted TFEs for all applicable devices.
2014-08-27 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 5 (WECC_URE5) | NCRXXXXX | WECC2014013518 | CIP-007-3a | R6 | WECC_URE5 submitted a Self-Certification to WECC stating that it had an issue with CIP-007-3a R6. WECC_URE5 personnel failed to ensure that all Cyber Assets within the Electronic Security Perimeter ("ESP"), as technically feasible, implemented automated tools or organizational process controls to monitor system events that are related to cyber security. WECC_URE5 installed nine new devices for which it could not perform security logging. WECC_URE5 did not file the appropriate Technical Feasibility Exceptions (TFEs) by the installation date. WECC_URE5 completed the submission of TFEs for all applicable devices. The root cause of this issue was human error. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE5 failed to file TFEs for nine devices. Failing to file TFEs in a timely manner could result in improper compensating controls being afforded to these devices. If those controls are not being applied, these devices could be used as an attack vector to potentially gain logical access into the ESP and to allow access to other devices within the ESP. If an attacker was able to gain unauthorized logical access to CCAs, then up to approximately 2,000 MW of generation could be affected. WECC_URE5 did implement good compensating measures. Specifically, all devices exist on isolated networks that are subject to periodic security assessments and reviews. WECC_URE5 also has a planned compensating measure to upgrade ESP switches to restrict access to any of the internal devices by blocking all unnecessary traffic. No harm is known to have occurred. WECC considered WECC_URE5's compliance history and determined there were no relevant issues of noncompliance. | To mitigate this issue, WECC_URE5: 1) submitted TFEs for all applicable devices.
2014-08-27 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 6 (WECC_URE6) | NCRXXXXX | WECC2013012792 | CIP-004-3a | R3 | WECC_URE6 submitted a Self-Report to WECC stating that it had an issue with CIP-004-3a R3. Specifically, WECC_URE6 failed to ensure a Personnel Risk Assessment ("PRA") was conducted for one employee prior to being granted access to one WECC_URE6 Physical Security Perimeter ("PSP") that contained three workstations classified as Critical Cyber Assets ("CCAs"). These workstations do not control or issue commands to Supervisory Control and Data Acquisition ("SCADA"). WECC_URE6 stated that two individuals with similar names applied for access. When one PRA was completed, the WECC_URE6 Security team gave access in error to the wrong individual and revoked access within a period of 11 days. The root cause of this issue was human error. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE6 failed to conduct a PRA for one individual prior to granting physical access to one PSP containing three workstations classified as CCAs. These actions could potentially result in improperly vetting the identity and criminal history of personnel with access to or managing CCAs. However, WECC_URE6 only granted physical access in error to one employee, to three CCA workstations used to monitor historical Supervisory Control and Data Acquisition ("SCADA") data for marketing purposes. These workstations could not control the WECC_URE6 SCADA system, generation or transmission system. Further, WECC_URE6 implemented preventative controls to prevent malicious access. Specifically, WECC_URE6 implemented strong passwords to prevent an individual from gaining logical access to the workstations. Additionally, authorized personnel were within the facility 24 hours 7 days a week, and although the employee associated with the remediated issue did need access to the PSP, the employee did not need access to the CCAs, and personnel within the PSP knew who should or should not physically access those workstations. No harm is known to have occurred. | To mitigate this issue, WECC_URE6: 1) revoked access from the individual in scope; 2) provided training to the responsible individuals; and 3) developed a checklist of all information necessary for WECC_URE6 staff to process access requests. WECC has verified the completion of all mitigation activity.
2014-08-27 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 6 (WECC_URE6) | NCRXXXXX | WECC2013012980 | CIP-004-3a | R4 | WECC_URE6 submitted a Self-Report to WECC stating that it had an issue with CIP-004-3a R4. Specifically, an employee of an organization with joint access to three WECC_URE6 substations retired. WECC_URE6 and this organization have a Joint Access Agreement that contractually obligates the organization to notify WECC_URE6 when access to WECC_URE6 facilities is no longer required. The organization did not notify WECC_URE6 of this employee’s retirement in time for WECC_URE6 to revoke access within the required seven days. WECC_URE6 did not revoke access for 72 days. In addition, another WECC_URE6 employee changed jobs no longer required CIP access to WECC_URE6’s CCAs. The employee’s access was not revoked within the required seven calendar days for the WECC_URE6 system, which is used as the access control and monitoring of the access points to the WECC_URE6 Transmission Substation Electronic Security Perimeters ("ESPs"). Upon discovery, WECC_URE6 revoked access 17 calendar days later. In addition, WECC_URE6 identified another employee who had been granted unescorted physical access, and subsequently retired. This individual was from an organization that participates with WECC_URE6 in a Joint Access Agreement. In this case, WECC_URE6 did not revoke access within the required seven days. The employee retired and access was not revoked for 24 calendar days. The root cause of this issue was human error. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE6 failed to revoke access within seven days for two individuals from other entities who had been granted physical access to three of WECC_URE6's PSPs. The individuals did not have logical access to WECC_URE6’s CCAs. These individuals had retired and no longer needed such access. WECC_URE6 also failed to revoke logical access for one employee who changed jobs and no longer required CIP access to WECC_URE6’s CCAs. Although WECC_URE6 failed to timely revoke access for three individuals who no longer needed access to WECC_URE6’s CCAs, WECC_URE6 had implemented the following internal controls. WECC determined WECC_URE6 implemented preventive controls. Specifically, WECC_URE6 implemented strong passwords on the devices in question which would likely prevent anyone from gaining logical access or maliciously using the CCAs. WECC_URE6 also implemented detective controls, such as quarterly access reviews of all external personnel with access to CCAs, to verify external personnel’s need for access, and potentially limiting the time personnel may maintain access after no longer requiring such access to three months. Additionally, all devices within the PSP were monitored by WECC_URE6’s operations, and would have been able to detect changes made to devices or alerts for access attempts to devices. Access for these employees was not revoked for cause. Two employees retired and one changed jobs within the organization; none of the employees had malicious intentions. No harm is known to have occurred. | To mitigate this issue, WECC_URE6: 1) revoked access from the individuals in scope; 2) established a system to improve its access management process including creating an automatically generated access removal tickets as a part of WECC_URE6's change and access revalidation process. WECC has verified the completion of all mitigation activity.
2014-08-27 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 7 (WECC_URE7) | NCRXXXXX | WECC2014013573 | CIP-005-3a | R3 | WECC_URE7 submitted a Self-Report to WECC stating that it had an issue with CIP-005-3a R3. Specifically, WECC_URE7 stated that although the Security Information and Event Management (SIEM) system appeared to be logging as normal, it had subsequently ceased logging events on WECC_URE7 Cyber Assets (CAs) including Electronic Access Control and Monitoring (EACM) devices. The two SIEM servers in scope are responsible for collecting and monitoring all logs from all devices within the Electronic Security Perimeter (ESP). The application was tested by WECC_URE7 and found to have no negative impacts to the security controls on the server. However, the temporary disk space the application required caused the SIEM server to run out of space for maintaining logs. Thus, the access points logs being sent to the SIEM server were dropped and permanently lost. The root cause was lack of processes, WECC_URE7 ensured no security controls were impacted, but had no set process to verify there was enough space for new logs. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE7 failed to implement a process to verify that there was enough space on the SIEM servers for logging access at access points within the ESP. WECC_URE7’s servers were used to collect and monitor access data from the entity’s identified Access Points, and generate alerts if necessary. Loss of the data sent by the access points would allow malicious attempts to gain access to the ESP to go unnoticed and unchecked, as WECC_URE7 would be essentially blind to what data is traversing or attempting to traverse its ESP boundary. If such attempts were successful, the access could be used to compromise WECC_URE7’s generators with a system peak of approximately 200 MW. Alternatively, WECC_URE7 did implement good preventative controls to prevent the compromise of its generators. Specifically, WECC_URE7 ensured all devices within the ESP where technically feasible implemented Anti-Virus software and strong passwords. WECC_URE7 also made sure all access points in scope were configured for security as such that only specific access permissions were allowed through, and the ports/services through the devices was actively restricted to only what was necessary for normal operations and monitoring. No harm is known to have occurred. WECC considered WECC_URE7's compliance history and determined there were no relevant issues of noncompliance. | To mitigate this issue, WECC_URE7: 1) restarted its SIEM devices and contacted the SIEM vendor for remediation and to resolve the storage issue; and 2) updated testing procedures to better address log retention testing. WECC has verified the completion of all mitigation activity.
2014-07-31 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2012011479 | CIP-006-1 | R1; R1.8 | During a Compliance Audit, MRO determined that MRO_URE1 had an issue with CIP-006-1 R1.8. Specifically, MRO_URE1 failed to afford the protective measures of CIP-007-1 R2.1, R5, R5.3.2, R5.3.3, R6.5, and R8.2 to Cyber Assets used in the access control and monitoring of the Physical Security Perimeter (PSP), as required by CIP-006-1 R1.8. During the Compliance Audit, MRO discovered that MRO_URE1 failed to enable only ports and service required for normal and emergency operations, as required by CIP-007-1 R2.1. MRO_URE1 provided a baseline list of ports and services. However, it did not provide any documentation as to why a port or service was enabled. Additionally, when MRO_URE1 added justifications for ports and services, it discovered one unnecessary application on one device and one unnecessary service on five devices. The application and service were disabled upon discovery. MRO also discovered that MRO_URE1 failed to require the use of passwords with a combination of alpha, numeric, and "special" characters, as required by CIP-007-1 R5.3.2, and failed to change passwords annually, as required by CIP-007-1 R5.3.3. Additionally, MRO_URE1 had procedural controls for passwords, but it did not have technical controls as required by CIP-007-1 R5. As a result, two accounts associated with MRO_URE1's physical access control system (PACS) device did not have passwords changed in 2010 and 2011. The device was removed from service in 2012. MRO also discovered that MRO_URE1 did not review logs of system events related to cyber security and maintain records documenting review of logs, as required by CIP-007-1 R6.5. MRO_URE1 reported that it did not review logs on its PACS device because it was recently commissioned, and its logging functionality had been giving a lot of false positives. However, when MRO_URE1 performed a review of the logs it discovered four instances which met it's classification of a "cyber event." MRO_URE1 reported that there were 10 failed login attempts within 10 minutes on four occasions. MRO_URE1 investigated each of the four "cyber events" and determined that each attempt was from an approved individual with cyber security training and a personnel risk assessment. MRO also discovered that MRO_URE1 failed to annually perform a cyber vulnerability assessment (CVA) that included a review of ports and services required for operation of the Cyber Assets within the Electronic Security Perimeter, as required by CIP-007-1 R8.2. MRO_URE1's CVA compared the list of ports and services against the prior list from the previous CVA instead of against the baseline of required ports and services. | This issue posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system. MRO_URE1 failed to monitor cyber events and did not change passwords on its PACS device. Failure to review logs and change passwords can increase the risk of a successful unauthorized access attempt. However, the cyber events did not warrant any action, and the password issue was limited to two accounts. Additionally, MRO_URE1's failure to enable ports and services for normal and emergency operations was limited to six devices. No harm is known to have occurred. MRO determined that the issue was appropriate for FFT treatment because MRO reviewed MRO_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in the penalty determination. MRO_URE1's ICP is managed at a high level in the company, with strong support and engagement from senior management. | To mitigate this violation, MRO_URE1: 1) added justifications for its required ports and services; 2) disabled ports and services that were unnecessary; 3) completed a CVA; 4) filed technical feasibility exceptions for the inability to enforce technical controls on PACS devices; 5) revised its procedural controls for passwords; 6) reviewed logs and investigated any previously overlooked cyber events; 7) updated its procedures for reviewing logs; 8) provided training to administrators responsible for reviewing logs; and 9) implemented internal controls to prevent recurrence, including additional testing associated with security logging when new assets are commissioned, and an approval process for testing performed by a supervisor. MRO has verified the completion of all mitigation activity.
2014-07-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2014013633 | CIP-004-3a | R4.2 | RF_URE1 submitted Self-Reports to ReliabilityFirst stating that it had issues with CIP-004-3a R4.2. RF_URE1 failed to revoke access to CCAs within the required seven-day timeframe for two employees. The first instance of non-compliance relates to an employee who RF_URE1 transferred to another position within the company, while the second instance of non-compliance relates to an employee who retired. Regarding the first instance of non-compliance, the employee transferred to a different position within RF_URE1, and, as a result, required different Physical Security Perimeter (“PSP”) and Physical Access Control Systems (“PACS”) access rights than he required for his previous position. With respect to the employee’s PSP access rights, the employee’s new position required him to have access to only three of five PSP areas for which he previously had access rights. However, RF_URE1 failed to revoke his access to the two PSP areas to which he was no longer authorized to have access. On the effective date of the employee’s transfer, Corporate Security received authorization to keep the employee’s access rights for only three PSP areas. However, Corporate Security inadvertently failed to remove the employee’s access to the other two PSP areas. Eleven days, RF_URE1 discovered the issue as a result of a follow-up email regarding the employee’s access and subsequently removed the employee’s access to the two PSP areas. Therefore, RF_URE1 did not remove the employee’s PSP access within seven calendar days of date of his transfer. With respect to the employee’s PACS access rights, the employee no longer required PACS access for his new position. The Cyber Security Compliance Group worked with the Cyber Security Support Group on-call technician to submit an access request ticket to remove the employee’s PACS access. However, the on-call technician failed to monitor the PACS access request queue for approximately 10 days. As a result, the Cyber Security Support Group on-call technician did not process the request until 11 days after the access request ticket was submitted. Therefore, RFC_URE1 did not remove the employee’s PACS access within seven calendar days of the date of his transfer. Regarding the second instance of non-compliance, an employee retired. Approximately seven days prior to the employee retiring, the Cyber Security Compliance Group emailed the Cyber Security Support Group to direct the Cyber Security Support Group on-call technician to submit an access request ticket to remove the employee’s ESP access. The Cyber Security Support Group on-call technician did not monitor the Cyber Security Support Group’s inbox and therefore did not submit the appropriate access request ticket to remove ESP access within seven calendar days. Approximately two months later, in performing the quarterly review, the Cyber Security Compliance Group discovered the issue and removed the employee’s ESP access that same day. The duration of the first instance of non-compliance is from the date by which RF_URE1 should have revoked the transferred employee’s access to CCAs to the date that RF_URE1 revoked the employee’s access to CCAs. The duration of the second instance of non-compliance is from the date by which RF_URE1 should have revoked the retired employee’s access to CCAs to the date that RF_URE1 revoked the employee’s access to CCAs. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. One employee was a trusted employee who transferred to a position that required him to retain authorized access to certain CCA information. The other employee was a long-term trusted employee who retired. Additionally, RF_URE1 quickly discovered and corrected the issues. RFC_URE1 discovered and corrected the issue with the transferred employee within several days and RF_URE1 discovered and corrected the issue with the retired employee within several weeks. ReliabilityFirst considered that it discovered the issues through Self-Reports. Effective oversight of the reliability of the Bulk Power System depends on robust and timely self-reporting by Registered Entities. ReliabilityFirst also considered certain aspects of RF_URE1’s compliance program as mitigating factors. Additionally, ReliabilityFirst considered whether the facts of this issue constitute a repetitive infraction. RF_URE1 has four previous violations of CIP-004 R4.2. The previous violations concerned RF_URE1's failure to remove access to CCAs within seven days of the employees’ transfers. Three previous violations resulted from RF_URE1's failure to remove physical access to CCAs, while only one previous violation resulted from RF_URE1's failure to remove cyber access to CCAs. ReliabilityFirst determined that the conduct described herein, although arguably repetitive conduct, does not warrant a monetary penalty for the reasons set forth above and in the following paragraph. Despite the violation history outlined above, ReliabilityFirst determined that FFT treatment is appropriate and that a monetary penalty is not warranted. This is based on a number of factors. The Self-Reported issues identified by RF_URE1 were uncovered by controls that RF_URE1 already had in place to detect and mitigate instances of non-compliance. Moreover, RF_URE1 has demonstrated a clear commitment to strengthening its internal controls and preventing recurrence of noncompliance upon identification of the subject issues and analysis of their root causes. In its Mitigation Plan, as outlined above, RF_URE1 committed to take significant steps to prevent recurrence. Further, neither a monetary penalty nor a negotiated settlement agreement would incent desired behavior, discourage undesired behavior, or send any important signals to RF_URE1 or the industry. | To mitigate this issue, RF_URE1: 1) modified the transfer process such that Human Resources will communicate to the transferring employee and his or her supervisor that a Building Access Request must be completed or access will be automatically disabled; 2) modified its transfer process such that, upon notification to Corporate Security, Corporate Security will set the employee’s badge to automatically expire within seven calendar days from the effective date of the transfer; 3) added a measurable objective related to timely processing of CIP-related access requests to Employee Performance Appraisals for personnel responsible for processing physical and cyber access to CCAs; 4) added an additional manual control related to cyber access revocation associated with personnel transfers. This will consist of staff confirming that the on-call technician completed cyber access revocation within the requisite time period; 5) ensured that only current procedures reside in its NERC CIP documentation repository so that employees use only current procedures; 6) counseled and trained all on-call personnel responsible for revoking access regarding revocation of cyber access within the requisite time period; and 7) updated its procedures to clarify roles and responsibilities for task ownership for tasks associated with the access revocation process.
2014-07-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2013012528 | CIP-004-3 | R4 | RFC_URE2 submitted a Self-Report to ReliabilityFirst stating that it had issues with CIP-004-3 R4. A RFC_URE2 substation supervisor (the “supervisor”) entered a Critical Asset substation without first being granted formal unescorted physical access rights to that substation. The issue arose when the supervisor attempted to distribute quarterly NERC Awareness materials to the Critical Asset substation at the direction of his manager, the individual responsible for authorizing unescorted physical access to RFC_URE2 substations. In attempting to distribute the materials, the supervisor accessed the substation premises by swiping his badge at the card-key reader at the entrance to the perimeter fence. He then proceeded to swipe his badge at the entrance to the control house Physical Security Perimeter (“PSP”). When his badge did not function as anticipated, he used a physical key reserved for card-key reader failures and entered the substation. Corporate Security directed the supervisor to vacate the premises because he was not on the access list for that substation and he immediately exited the substation premises. This isolated issue occurred on one day and was addressed immediately. The root cause of the issue was human error. The employee at issue was given material to deliver to a substation from his manager, who was authorized to grant the individual with access. The employee was qualified to receive access and was not listed on the access list due to an oversight. | RFC_URE2 and its affiliates self-reported each of the issues identified within this FFT Report to ReliabilityFirst due to their application of an ongoing cyber security risk using an analysis tool to review their cyber security policies and procedures, which lead RFC_URE2 and its affiliates to identify, minimize, and eliminate their CIP compliance failures. Additionally, RFC_URE2 and its affiliates' implementation of the compliance initiative highlighted in a prior Settlement Agreement with ReliabilityFirst, contributed to the identification and remediation of these four self-reported issues. Therefore, ReliabilityFirst determined that these issues were the result of RFC_URE2 and its affiliates' application of more rigorous processes and oversight, which led them to aggressively review their compliance with CIP Reliability Standards and self-report these issues to ReliabilityFirst. These important factors help explain both the age (almost a year old) for some of the issues resolved in this FFT Report as well as their qualification for FFT treatment. This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following three factors. First, the supervisor met all the requirements for access to the Critical Asset substation PSP and would have been granted such rights if not for an oversight. Specifically, the Critical Asset substation fell within the supervisor’s job purview; the supervisor had successfully passed a personnel risk assessment; and the supervisor had completed all annual CIP training modules required for unescorted physical access to Critical Asset prior to the date of this issue. Following to this administrative oversight, RFC_URE2 granted the supervisor with access rights within one week of this issue. Second, RFC_URE2 has detective controls in place, namely alarms, to notify Corporate Security when individuals bypass the card reader controls, which activated as designed when the supervisor bypassed the card-key reader in this instance. Third, the scope of this issue was limited to one individual in an isolated incident that RFC_URE2 detected and corrected immediately. ReliabilityFirst considered certain aspects of RFC_URE2 and its affiliates' compliance program as mitigating penalty factors. ReliabilityFirst considered that it discovered this issue through Self-Report and applied mitigating credit. In addition, ReliabilityFirst considered that RFC_URE2 and its affiliates diligently assessed their compliance with the Reliability Standards, and reported the deficiencies they discovered to ReliabilityFirst. Effective oversight of the reliability of the Bulk Power System depends on robust and timely self-reporting by Registered Entities. ReliabilityFirst seeks to encourage this type of behavior, which includes timely detection and correction unconnected to a pending regional compliance monitoring action, by imposing no monetary penalty for these issues. | To mitigate this issue, RFC_URE2: 1) secured the PSP; 2) assessed the PSP for unauthorized access; 3) retrained implicated personnel on the security awareness and physical security of PSPs; 4) removed direct key access to the PSP by installing new doors with card readers rather than mechanical locks; 5) modified the PSP door signs to remind employees of proper access procedures; 6) ensured the proper operation of alarms at the implicated PSP; and 7) replaced the faulty door at issue.
2014-07-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC2013012754 | CIP-006-3c | R4 | RFC_URE3 submitted a Self-Report to ReliabilityFirst stating that it had issues with CIP-006-3c R4 (RFC_URE3 and RF_URE4 first informed ReliabilityFirst of their issues with CIP-006-3c R4 through a conference call). RFC_URE3 and RF_URE4 had a period of 14 hours during which the locking mechanism for one access point to a PSP was disabled. The access point consisted of a door that could be opened from outside the PSP only through the use of an authorized card-key. In the months immediately prior to the incident, RFC_URE3 and RF_URE4 had experienced increasing difficulties with the door, which deteriorated and became difficult to open because the door and locking mechanism were not designed to handle the volume of traffic entering and exiting through the access point. Employees involved in the incident explained that they had taped over a portion of the door, including the locking mechanism, to remedy the problem. An employee discovered the issue when he was able to enter the PSP without first swiping his card key. Immediately upon realizing the problem, the employee removed the tape from the door, re-enabling the locking mechanism, and contacted Corporate Security. RF_URE2 and RFC_URE3 submitted a Self-Report to ReliabilityFirst stating that they had issues with CIP-006-3c R4 (RF_URE2 first informed ReliabilityFirst of this CIP-006-3c R4 issue through a conference call). RF_URE2 and RFC_URE3 identified several instances in which employees entered a Critical Asset substation PSP using a key rather than a corporate-issued ID card. Under the corporate Physical Security Plan for Protection of CCAs required by CIP-006-3c R4, all persons attempting to access a PSP through a card-reader-controlled door are required to present their corporate-issued ID card at the card reader, except in the event of an emergency. On separate occasions, four RF_URE2 employees and one RFC_URE3 employee did not follow these procedures (The four implicated RF_URE2 employees had authorized unescorted physical access to the PSPs. The RFC_URE3 employee did not have authorized unescorted physical access to the Critical Asset substation). RF_URE2 submitted a Mitigation Plan to ReliabilityFirst identifying an additional issue with CIP-006-3c R4. RF_URE2 identified an additional instance where two employees gained unauthorized access to a RF_URE2 substation PSP when the door locking mechanism failed (These two individuals were previously granted authorized unescorted physical access until two weeks prior to this instance, but their access was removed because RF_URE2 determined that they no longer required it). The first issue, involving RFC_URE3 and RF_URE4, occurred for fourteen hours. The second issue, involving RFC_URE3 and RF_URE2, implicated RFC_URE3 for one day (the day on which RFC_URE3 had its one instance of unmanaged physical access at an access point), while RF_URE2's issues occurred four times during the time period of approximately six months. The third issue, involving only RF_URE2, occurred for six hours. In the first instance, the PSP was occupied with authorized users during the full 14 hour period and the occupants confirmed that only individuals with authorized physical access entered the PSP. Additionally, the issue was immediately identified and occurred for a short duration of fourteen hours before it was remedied. In the second instance, RFC_URE3 and affiliates' security controls to detect and respond to alarms worked as designed and the employees entering the PSPs were immediately identified, contacted and instructed to vacate the premises. In the third instance, the two implicated individuals met all the requirements for access to the Critical Asset substation PSP and had previously been granted access that was only removed due to the misunderstanding that these individuals no longer required access. Upon realizing their continued need for access, RF_URE2 restored access for both individuals, but the request to grant them access was being processed at the time of this issue. Similarly to the second instance, here RF_URE2's security controls to detect and respond to alarms worked as designed and the employees entering the PSPs were immediately identified and the issue with the faulty door lock was remediated the same day. | RFC_URE3 and affiliates self-reported each of the issues identified within this FFT Report to ReliabilityFirst due to their application of an ongoing cyber security risk using an analysis tool to review their cyber security policies and procedures, which lead the RFC_URE3 and affiliates to identify, minimize, and eliminate their CIP compliance failures. Additionally, RFC_URE3 and affiliates' implementation of the compliance initiative highlighted in a prior Settlement Agreement with ReliabilityFirst, contributed to the identification and remediation of these four self-reported issues. Therefore, ReliabilityFirst determined that these issues were the result of RFC_URE3 and affiliates' application of more rigorous processes and oversight, which led them to aggressively review their compliance with CIP Reliability Standards and self-report these issues to ReliabilityFirst. These important factors help explain both the age (almost a year old) for some of the issues resolved in this FFT Report as well as their qualification for FFT treatment. These issues posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. In the first instance, the PSP was occupied with authorized users during the full 14 hour period and the occupants confirmed that only individuals with authorized physical access entered the PSP. Additionally, the issue was immediately identified and occurred for a short duration of fourteen hours before it was remedied. In the second instance, RFC_URE3 and affiliates' security controls to detect and respond to alarms worked as designed and the employees entering the PSPs were immediately identified, contacted and instructed to vacate the premises. In the third instance, the two implicated individuals met all the requirements for access to the Critical Asset substation PSP and had previously been granted access that was only removed due to the misunderstanding that these individuals no longer required access. Upon realizing their continued need for access, RF_URE2 restored access for both individuals, but the request to grant them access was being processed at the time of this issue. Similarly to the second instance, here RF_RE2's security controls to detect and respond to alarms worked as designed and the employees entering the PSPs were immediately identified and the issue with the faulty door lock was remediated the same day. ReliabilityFirst considered certain aspects of RFC_URE3 and affiliates' compliance program as mitigating penalty factors. ReliabilityFirst considered that it discovered this issue through Self-Report and applied mitigating credit. In addition, ReliabilityFirst considered that RFC_URE3 and affiliates diligently assessed their compliance with the Reliability Standards, and reported the deficiencies they discovered to ReliabilityFirst. Effective oversight of the reliability of the Bulk Power System depends on robust and timely self-reporting by Registered Entities. ReliabilityFirst seeks to encourage this type of behavior, which includes timely detection and correction unconnected to a pending regional compliance monitoring action, by imposing no monetary penalty for these issues. | To mitigate this issue, RFC_URE3 and affiliates: 1) secured and replaced the faulty doors; 2) evaluated implicated PSPs to ensure their security; 3) retrained employees on security awareness and physical security requirements for PSPs; 4) modified PSP door signs to remind employees of access procedures; 5) reevaluated their access lists to provide access to individuals implicated by these issues who should have previously been provided with authorized access; 6) replaced any faulty doors; 7) ensured PSP doors were secure; 8) posted signs indicating the limited use of certain doors for emergency use only; 9) reviewed video footage of the PSP entry points to ensure all instances of unauthorized access had been identified; 10) reinforced security awareness training for all system operations supervisors, managers, and other necessary personnel.
2014-07-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 4 (RFC_URE4) | NCRXXXXX | RFC2013012755 | CIP-006-3c | R4 | RF_URE3 submitted a Self-Report to ReliabilityFirst stating that it had issues with CIP-006-3c R4 (RF_URE3 and RF_URE4 first informed ReliabilityFirst of their issues with CIP-006-3c R4 through a conference call). RF_URE3 and RF_URE4 had a period of 14 hours during which the locking mechanism for one access point to a PSP was disabled. The access point consisted of a door that could be opened from outside the PSP only through the use of an authorized card-key. In the months immediately prior to the incident, RF_URE3 and RF_URE4 had experienced increasing difficulties with the door, which deteriorated and became difficult to open because the door and locking mechanism were not designed to handle the volume of traffic entering and exiting through the access point. Employees involved in the incident explained that they had taped over a portion of the door, including the locking mechanism, to remedy the problem. An employee discovered the issue when he was able to enter the PSP without first swiping his card key. Immediately upon realizing the problem, the employee removed the tape from the door, re-enabling the locking mechanism, and contacted Corporate Security. RF_URE2 and RF_URE3 submitted a Self-Report to ReliabilityFirst stating that they had issues with CIP-006-3c R4 (RF_URE2 first informed ReliabilityFirst of this CIP-006-3c R4 issue through a conference call). RF_URE2 and RF_URE3 identified several instances in which employees entered a Critical Asset substation PSP using a key rather than a corporate-issued ID card. Under the corporate Physical Security Plan for Protection of CCAs required by CIP-006-3c R4, all persons attempting to access a PSP through a card-reader-controlled door are required to present their corporate-issued ID card at the card reader, except in the event of an emergency. On separate occasions, four RF_URE2 employees and one RF_URE3 employee did not follow these procedures (The four implicated RF_URE2 employees had authorized unescorted physical access to the PSPs. The RF_URE3 employee did not have authorized unescorted physical access to the Critical Asset substation). RF_URE2 submitted a Mitigation Plan to ReliabilityFirst identifying an additional issue with CIP-006-3c R4. RF_URE2 identified an additional instance where two employees gained unauthorized access to a RF_URE2 substation PSP when the door locking mechanism failed (These two individuals were previously granted authorized unescorted physical access until two weeks prior to this instance, but their access was removed because RF_URE2 determined that they no longer required it). The first issue, involving RF_URE3 and RF_URE4, occurred for fourteen hours. The second issue, involving RF_URE3 and RF_URE2, implicated RF_URE3 for one day (the day on which RF_URE3 had its one instance of unmanaged physical access at an access point), while RF_URE2's issues occurred four times during the time period of approximately six months. The third issue, involving only RF_URE2, occurred for six hours. In the first instance, the PSP was occupied with authorized users during the full 14 hour period and the occupants confirmed that only individuals with authorized physical access entered the PSP. Additionally, the issue was immediately identified and occurred for a short duration of fourteen hours before it was remedied. In the second instance, the corporate security controls to detect and respond to alarms worked as designed and the employees entering the PSPs were immediately identified, contacted and instructed to vacate the premises. In the third instance, the two implicated individuals met all the requirements for access to the Critical Asset substation PSP and had previously been granted access that was only removed due to the misunderstanding that these individuals no longer required access. Upon realizing their continued need for access, RF_URE2 restored access for both individuals, but the request to grant them access was being processed at the time of this issue. Similarly to the second instance, here RF_URE2's security controls to detect and respond to alarms worked as designed and the employees entering the PSPs were immediately identified and the issue with the faulty door lock was remediated the same day. | RF_URE4 and affiliates self-reported each of the issues identified within this FFT Report to ReliabilityFirst due to their application of an ongoing cyber security risk using an analysis tool to review their cyber security policies and procedures, which lead RF_URE4 and affiliates to identify, minimize, and eliminate their CIP compliance failures. Additionally, RF_URE4 and affiliates' implementation of the compliance initiative highlighted in a prior Settlement Agreement with ReliabilityFirst, contributed to the identification and remediation of these four self-reported issues. Therefore, ReliabilityFirst determined that these issues were the result of RF_URE4 and affiliates' application of more rigorous processes and oversight, which led them to aggressively review their compliance with CIP Reliability Standards and self-report these issues to ReliabilityFirst. These important factors help explain both the age (almost a year old) for some of the issues resolved in this FFT Report as well as their qualification for FFT treatment. This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following three factors. First, the supervisor met all the requirements for access to the Critical Asset substation PSP and would have been granted such rights if not for an oversight. Specifically, the Critical Asset substation fell within the supervisor’s job purview; the supervisor had successfully passed a personnel risk assessment; and the supervisor had completed all annual CIP training modules required for unescorted physical access to Critical Asset substations prior to the date of this issue. Following to this administrative oversight, RF_URE2 granted the supervisor with access rights within one week of this issue. Second, RF_URE2 has detective controls in place, namely alarms, to notify Corporate Security when individuals bypass the card reader controls, which activated as designed when the supervisor bypassed the card-key reader in this instance. Third, the scope of this issue was limited to one individual in an isolated incident that RF_URE2 detected and corrected immediately. ReliabilityFirst considered certain aspects of RF_URE4 and affiliates' compliance program as mitigating penalty factors. ReliabilityFirst considered that it discovered this issue through Self-Report and applied mitigating credit. In addition, ReliabilityFirst considered that RF_URE4 and affiliates diligently assessed their compliance with the Reliability Standards, and reported the deficiencies they discovered to ReliabilityFirst. Effective oversight of the reliability of the Bulk Power System depends on robust and timely self-reporting by Registered Entities. ReliabilityFirst seeks to encourage this type of behavior, which includes timely detection and correction unconnected to a pending regional compliance monitoring action, by imposing no monetary penalty for these issues. | To mitigate this issue, RF_URE4 and affiliates: 1) secured and replaced the faulty doors; 2) evaluated implicated PSPs to ensure their security; 3) retrained employees on security awareness and physical security requirements for PSPs; 4) modified PSP door signs to remind employees of access procedures; 5) reevaluated their access lists to provide access to individuals implicated by these issues who should have previously been provided with authorized access; 6) replaced any faulty doors; 7) ensured PSP doors were secure; 8) posted signs indicating the limited use of certain doors for emergency use only; 9) reviewed video footage of the PSP entry points to ensure all instances of unauthorized access had been identified; 10) reinforced security awareness training for all system operations supervisors, managers, and other necessary personnel.
2014-07-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2013013029 | CIP-006-3c | R4 | RF_URE3 submitted a Self-Report to ReliabilityFirst stating that it had issues with CIP-006-3c R4 (RF_URE3 and RF_URE4 first informed ReliabilityFirst of their issues with CIP-006-3c R4 through a conference call). RF_URE3 and RF_URE4 had a period of 14 hours during which the locking mechanism for one access point to a PSP was disabled. The access point consisted of a door that could be opened from outside the PSP only through the use of an authorized card-key. In the months immediately prior to the incident, RF_URE3 and RF_URE4 had experienced increasing difficulties with the door, which deteriorated and became difficult to open because the door and locking mechanism were not designed to handle the volume of traffic entering and exiting through the access point. Employees involved in the incident explained that they had taped over a portion of the door, including the locking mechanism, to remedy the problem. An employee discovered the issue when he was able to enter the PSP without first swiping his card key. Immediately upon realizing the problem, the employee removed the tape from the door, re-enabling the locking mechanism, and contacted Corporate Security. RFC_URE2 and RF_URE3 submitted a Self-Report to ReliabilityFirst stating that they had issues with CIP-006-3c R4 (RFC_URE2 first informed ReliabilityFirst of this CIP-006-3c R4 issue through a conference call). RFC_URE2 and RF_URE3 identified several instances in which employees entered a Critical Asset substation PSP using a key rather than a corporate-issued ID card. Under the corporate Physical Security Plan for Protection of CCAs required by CIP-006-3c R4, all persons attempting to access a PSP through a card-reader-controlled door are required to present their corporate issued ID card at the card reader, except in the event of an emergency. On separate occasions, four RFC_URE2 employees and one RF_URE3 employee did not follow these procedures (The four implicated RFC_URE2 employees had authorized unescorted physical access to the PSPs. The RF_URE3 employee did not have authorized unescorted physical access to the Critical Asset substation). RFC_URE2 submitted a Mitigation Plan to ReliabilityFirst identifying an additional issue with CIP-006-3c R4. RFC_URE2 identified an additional instance where two employees gained unauthorized access to a RFC_URE2 substation PSP when the door locking mechanism failed (These two individuals were previously granted authorized unescorted physical access until two weeks prior to this instance, but their access was removed because RFC_URE2 determined that they no longer required it). The first issue, involving RF_URE3 and RF_URE4, occurred for fourteen hours. The second issue, involving RF_URE3 and RFC_URE2, implicated RF_URE3 for one day (the day on which RF_URE3 had its one instance of unmanaged physical access at an access point), while RFC_URE2's issues occurred four times during the time period of approximately six months. The third issue, involving only RFC_URE2, occurred for six hours. In the first instance, the PSP was occupied with authorized users during the full 14 hour period and the occupants confirmed that only individuals with authorized physical access entered the PSP. Additionally, the issue was immediately identified and occurred for a short duration of fourteen hours before it was remedied. In the second instance, RFC_URE2 and affiliates' security controls to detect and respond to alarms worked as designed and the employees entering the PSPs were immediately identified, contacted and instructed to vacate the premises. In the third instance, the two implicated individuals met all the requirements for access to the Critical Asset PSP and had previously been granted access that was only removed due to the misunderstanding that these individuals no longer required access. Upon realizing their continued need for access, RFC_URE2 restored access for both individuals, but the request to grant them access was being processed at the time of this issue. Similarly to the second instance, here RFC_URE2's security controls to detect and respond to alarms worked as designed and the employees entering the PSPs were immediately identified and the issue with the faulty door lock was remediated the same day. | RFC_URE2 and affiliates self-reported each of the issues identified within this FFT Report to ReliabilityFirst due to their application of an ongoing cyber security risk using an analysis tool to review their cyber security policies and procedures, which lead RFC_URE2 and affiliates to identify, minimize, and eliminate their CIP compliance failures. Additionally, RFC_URE2 and affiliates' implementation of the compliance initiative highlighted in a prior Settlement Agreement with ReliabilityFirst, contributed to the identification and remediation of these four self-reported issues. Therefore, ReliabilityFirst determined that these issues were the result of RFC_URE2 and affiliates' application of more rigorous processes and oversight, which led them to aggressively review their compliance with CIP Reliability Standards and self-report these issues to ReliabilityFirst. These important factors help explain both the age (almost a year old) for some of the issues resolved in this FFT Report as well as their qualification for FFT treatment. This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following three factors. First, the supervisor met all the requirements for access to the Critical Asset substation PSP and would have been granted such rights if not for an oversight. Specifically, the Critical Asset substation fell within the supervisor’s job purview; the supervisor had successfully passed a personnel risk assessment; and the supervisor had completed all annual CIP training modules required for unescorted physical access to Critical Asset substations prior to the date of this issue. Following to this administrative oversight, RFC_URE2 granted the supervisor with access rights within one week of this issue. Second, RFC_URE2 has detective controls in place, namely alarms, to notify Corporate Security when individuals bypass the card reader controls, which activated as designed when the supervisor bypassed the card-key reader in this instance. Third, the scope of this issue was limited to one individual in an isolated incident that RFC_URE2 detected and corrected immediately. ReliabilityFirst considered certain aspects of RFC_URE2 and affiliates' compliance program as mitigating penalty factors. ReliabilityFirst considered that it discovered this issue through Self-Report and applied mitigating credit. In addition, ReliabilityFirst considered that RFC_URE2 and affiliates diligently assessed their compliance with the Reliability Standards, and reported the deficiencies they discovered to ReliabilityFirst. Effective oversight of the reliability of the Bulk Power System depends on robust and timely self-reporting by Registered Entities. ReliabilityFirst seeks to encourage this type of behavior, which includes timely detection and correction unconnected to a pending regional compliance monitoring action, by imposing no monetary penalty for these issues. | To mitigate this issue, RFC_URE2 and affiliates: 1) secured and replaced the faulty doors; 2) evaluated implicated PSPs to ensure their security; 3) retrained employees on security awareness and physical security requirements for PSPs; 4) modified PSP door signs to remind employees of access procedures; 5) reevaluated their access lists to provide access to individuals implicated by these issues who should have previously been provided with authorized access; 6) replaced any faulty doors; 7) ensured PSP doors were secure; 8) posted signs indicating the limited use of certain doors for emergency use only; 9) reviewed video footage of the PSP entry points to ensure all instances of unauthorized access had been identified; 10) reinforced security awareness training for all system operations supervisors, managers, and other necessary personnel.
2014-07-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 5 (RFC_URE5) | NCRXXXXX | RFC2013012604 | CIP-003-1 | R6 | ReliabilityFirst conducted a Compliance Audit of RFC_URE5, during which ReliabilityFirst discovered that RFC_URE5 had an issue of CIP-003-1 R6. RFC_URE5 did not demonstrate that it implements supporting configuration management activities to identify, control and document all entity or vendor-related changes to hardware and software components of CCAs pursuant to the change control process. Specifically, although RFC_URE5’s process for configuration management requires that RFC_URE5 update baseline configuration records for changed systems, RFC_URE5 failed to evidence that it completed this process step. Additionally, RFC_URE5’s configuration management process applies only to ports and services and does not apply to all hardware and software components of CCAs, as required by CIP-003-1 R6. Finally, RFC_URE5 failed to implement supporting configuration management activities to identify, control and document all vendor related changes to hardware and software components of CCAs. The RFC_URE5 change control and configuration management process states that it applies to vendors, however, RFC_URE5 does not provide vendors with the ability to access the systems required for implementing its change control and configuration management process. The duration of this issue was from the date RFC_URE5 was required to comply with CIP-003-1 R6 to the date RFC_URE5 completed its Mitigation Plan. | ReliabilityFirst determined that these issues were not indicative of any sort of systemic failure at RFC_URE5. They are isolated instances of noncompliance with unrelated root causes, and each pose a minimal risk to the reliability of the Bulk Power System. They are grouped together because they were discovered at the same Compliance Audit, because they are all worthy of FFT treatment, and for the sake of efficient resolution. This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following two factors. First, although RFC_URE5 failed to document and implement its change management procedure, RFC_URE5 represents that it did complete all configuration data for Cyber Assets subject to CIP Reliability Standard Requirements, but failed to retain the documentation in a consolidated location. Second, RFC_URE5’s footprint within the Bulk Power System is relatively insubstantial. This relatively minimal impact on the Bulk Power System decreases the inherent risk posed by the subject issue. Effective oversight of the reliability of the Bulk Power System depends on robust and timely self-reporting by Registered Entities. ReliabilityFirst considered that it discovered these issues through a Compliance Audit and was therefore unable to assign self-reporting credit as a mitigating factor. ReliabilityFirst considered certain aspects of the RFC_URE5’s compliance program as mitigating factors. ReliabilityFirst considered the RFC_URE5’s overall cooperation with ReliabilityFirst during the compliance monitoring and enforcement process to constitute a mitigating factor for penalty purposes. ReliabilityFirst considered whether the facts of these issues constitute a repetitive infraction. RFC_URE5 has two prior violations of CIP-004 R4 which arguably constitute repetitive infractions, which dealt with a failure to include specific access rights on the access lists and with a failure to properly update access during quarterly reviews. Despite these previous issues, ReliabilityFirst determined that a monetary penalty was not warranted due to its determination that the issues posed a minimal risk to the Bulk Power System and based on the other adjustment factors set forth above. | To mitigate this issue, RFC_URE5: 1) modified its change ticket templates in its change management system to require a verification that RFC_URE5 personnel that updated configuration files for the changed Cyber Asset have collected and stored the information appropriately; 2) utilized automated tools to collect complete configuration information for Windows-based servers and workstations and to collect updated configurations after personnel apply changes; 3) collected and stored configuration data files for non-Windows devices subject to CIP and collected and stored updated configurations after it applied changes; and 4) updated its change control and configuration management document to reflect enhanced configuration management procedures. RFC_URE5 will utilize automated tools to store files in its change management system or document management system.
2014-07-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 5 (RFC_URE5) | NCRXXXXX | RFC2013012605 | CIP-004-2 | R4 | ReliabilityFirst conducted a Compliance Audit of RFC_URE5, during which ReliabilityFirst discovered that RFC_URE5 had an issue of CIP-004-2 R4. RFC_URE5 failed to provide sufficient evidence to demonstrate that it reviews access lists for vendor personnel on a quarterly basis. Additionally, RFC_URE5 failed to update access lists to reflect a change of access privileges within seven days of a change, as required by CIP-004 R4, on at least one occasion. Finally, in many cases RFC_URE5 failed to maintain lists of personnel with authorized cyber or authorized unescorted physical access to CCAs, including their specific electronic and physical access rights to CCAs. The duration of this issue was from the date RFC_URE5 was required to review and update its access lists to the date RFC_URE5 completed its Mitigation Plan for this issue. | ReliabilityFirst determined that these issues were not indicative of any sort of systemic failure at RFC_URE5. They are isolated instances of noncompliance with unrelated root causes, and each pose a minimal risk to the reliability of the Bulk Power System. They are grouped together because they were discovered at the same Compliance Audit, because they are all worthy of FFT treatment, and for the sake of efficient resolution. This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following four factors. First, in relation to RFC_URE5’s failure to perform a quarterly review of vendor access lists, RFC_URE5 does not permit its vendors to have cyber access to the CCAs they support. Instead, the vendors have view-only access, so that RFC_URE5 employees must engage them in WebEx sessions, during which the vendor then can recommend that the employee make certain changes to CCAs. Second, in relation to RFC_URE5’s failure to update an access list within seven days of the change, this area of noncompliance was a documentation issue. The individual was transferred to a new position within RFC_URE5, but RFC_URE5 failed to update the access list to reflect his new title. RFC_URE5 kept this individual on the access list due to its determination that he continued to need access and was appropriately suited to maintain it. Third, in relation to RFC_URE5’s failure to maintain access lists that include specific electronic and physical access rights to CCAs, these access lists are limited to a very small population of seven employees within RFC_URE5 with physical or electronic access to CCAs. Fourth, in relation to RFC_URE5’s failure to maintain access lists, RFC_URE5 does utilize revision history to record the evidence of its quarterly reviews, so it does have some evidence of its completion of quarterly reviews, even though this evidence did not establish compliance with CIP-004-2 R4. Therefore, RFC_URE5 has some measures in place to protect its CCAs against unauthorized access which reduce the risk to the Bulk Power System. Effective oversight of the reliability of the Bulk Power System depends on robust and timely self-reporting by Registered Entities. ReliabilityFirst considered that it discovered these issues through a Compliance Audit and was therefore unable to assign self-reporting credit as a mitigating factor. ReliabilityFirst considered certain aspects of the RFC_URE5’s compliance program as mitigating factors. ReliabilityFirst considered the RFC_URE5’s overall cooperation with ReliabilityFirst during the compliance monitoring and enforcement process to constitute a mitigating factor for penalty purposes. ReliabilityFirst considered whether the facts of these issues constitute a repetitive infraction. RFC_URE5 has two prior violations of CIP-004 R4 which arguably constitute repetitive infractions, which dealt with a failure to include specific access rights on the access lists and dealt with a failure to properly update access during quarterly reviews. Despite these previous issues, ReliabilityFirst determined that a monetary penalty was not warranted due to its determination that the issues posed a minimal risk to the Bulk Power System and based on the other adjustment factors set forth above. | To mitigate this issue, RFC_URE5: 1) is using a workflow process to facilitate quarterly reviews and will provide stacking evidence in addition to the revision history to show that quarterly reviews were performed; and 2) updated its change procedure to require that access requests be routed through a corporate CIP access database to ensure that all terminations or revisions will use the same database.
2014-07-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 5 (RFC_URE5) | NCRXXXXX | RFC2013012606 | CIP-006-2 | R2 | ReliabilityFirst conducted a Compliance Audit of RFC_URE5, during which ReliabilityFirst discovered that RFC_URE5 had an issue of CIP-006-2 R2. RFC_URE5 did not afford the Physical Access Control System (“PACS”) workstations and control panels with the protections required by CIP-006-2 R2. The duration of this issue was from the date RFC_URE5 was required to comply with CIP-006-2 to the date RFC_URE5 completed its Mitigation Plan for this issue. | ReliabilityFirst determined that these issues were not indicative of any sort of systemic failure at RFC_URE5. They are isolated instances of noncompliance with unrelated root causes, and each pose a minimal risk to the reliability of the Bulk Power System. They are grouped together because they were discovered at the same Compliance Audit, because they are all worthy of FFT treatment, and for the sake of efficient resolution. This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following four factors. First, the workstations that access the PACS servers and local control panels are both located within the PSP. Second, in order to access the PACS servers to grant or remove access, an individual must have an authorized identification and password to do so. RFC_URE5 has only granted one individual with the required identification and password functions. Third, RFC_URE5 does provide its PACS workstations with antivirus software. Fourth, the control panels have limited capability and, if compromised, could not be utilized to alter existing physical access permissions or establish new permissions. Therefore, RFC_URE5 implements multiple layers of controls to protect its PACS and thereby prevent unauthorized individuals to physically access CCAs. Effective oversight of the reliability of the Bulk Power System depends on robust and timely self-reporting by Registered Entities. ReliabilityFirst considered that it discovered these issues through a Compliance Audit and was therefore unable to assign self-reporting credit as a mitigating factor. ReliabilityFirst considered certain aspects of the RFC_URE5’s compliance program as mitigating factors. ReliabilityFirst considered the RFC_URE5’s overall cooperation with ReliabilityFirst during the compliance monitoring and enforcement process to constitute a mitigating factor for penalty purposes. ReliabilityFirst considered whether the facts of these issues constitute a repetitive infraction. RFC_URE5 has two prior violations of CIP-004 R4 which arguably constitute repetitive infractions, which dealt with a failure to include specific access rights on the access lists and dealt with a failure to properly update access during quarterly reviews. Despite these previous issues, ReliabilityFirst determined that a monetary penalty was not warranted due to its determination that the issues posed a minimal risk to the Bulk Power System and based on the other adjustment factors set forth above. | To mitigate this issue, RFC_URE5: 1) protected its PACS devices from unauthorized physical access; 2) updated its list of Cyber Assets with the inclusion of PACS workstations and control panels; 3) filed a Technical Feasibility Exception (“TFE”) request for its control panels that do not support anti-virus software; and 4) installed antivirus software on PACS workstations; and established and documented required ports and services.
2014-07-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 5 (RFC_URE5) | NCRXXXXX | RFC2013012607 | CIP-009-2 | R2 | ReliabilityFirst conducted a Compliance Audit of RFC_URE5, during which ReliabilityFirst discovered that RFC_URE5 had an issue of CIP-009-2 R2. RFC_URE5 failed to demonstrate that it exercised its recovery plans at least annually, as required by CIP-009-2 R2. The duration of the issue of CIP-009-2 R2 was from the date RFC_URE5 first failed to comply with CIP-009-2 R2 to the date RFC_URE5 completed its Mitigation Plan for this issue. | ReliabilityFirst determined that these issues were not indicative of any sort of systemic failure at RFC_URE5. They are isolated instances of noncompliance with unrelated root causes, and each pose a minimal risk to the reliability of the Bulk Power System. They are grouped together because they were discovered at the same Compliance Audit, because they are all worthy of FFT treatment, and for the sake of efficient resolution. This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following three factors. First, RFC_URE5 was performing an annual exercise, but the documentation failed to demonstrate that the exercise was of RFC_URE5’s recovery plan. Second, RFC_URE5 has a backup facility to which it can failover if needed. Third, RFC_URE5 tests its backup facility several times each year. Effective oversight of the reliability of the Bulk Power System depends on robust and timely self-reporting by Registered Entities. ReliabilityFirst considered that it discovered these issues through a Compliance Audit and was therefore unable to assign self-reporting credit as a mitigating factor. ReliabilityFirst considered certain aspects of the RFC_URE5’s compliance program as mitigating factors. ReliabilityFirst considered the RFC_URE5’s overall cooperation with ReliabilityFirst during the compliance monitoring and enforcement process to constitute a mitigating factor for penalty purposes. ReliabilityFirst considered whether the facts of these issues constitute a repetitive infraction. RFC_URE5 has two prior violations of CIP-004 R4 which arguably constitute repetitive infractions, which dealt with a failure to include specific access rights on the access lists and dealt with a failure to properly update access during quarterly reviews. Despite these previous issues, ReliabilityFirst determined that a monetary penalty was not warranted due to its determination that the issues posed a minimal risk to the Bulk Power System and based on the other adjustment factors set forth above. | To mitigate this issue, RFC_URE5: 1) performed and documented the recovery plan exercise and lessons learned from that exercise; 2) also developed and executed an action plan to address the lessons learned; and 3) updated its recovery plan process to reflect changes to the annual exercise requirements resulting from its upgrading of SCADA/EMS software.
2014-07-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 5 (RFC_URE5) | NCRXXXXX | RFC2013012608 | CIP-009-1 | R5 | ReliabilityFirst conducted a Compliance Audit of RFC_URE5, during which ReliabilityFirst discovered that RFC_URE5 had an issue of CIP-009-2 R2. RFC_URE5 failed to demonstrate that it annually tested its backup media to ensure the information is available, as required by CIP-009-1 R5, when it failed to provide evidence of backing up operational and configuration data. The duration of the issue of CIP-009-1 R5 was from the date RFC_URE5 was required to comply with CIP-009-1 R5 to the date RFC_URE5 completed its Mitigation Plan for this issue. | ReliabilityFirst determined that these issues were not indicative of any sort of systemic failure at RFC_URE5. They are isolated instances of noncompliance with unrelated root causes, and each pose a minimal risk to the reliability of the Bulk Power System. They are grouped together because they were discovered at the same Compliance Audit, because they are all worthy of FFT treatment, and for the sake of efficient resolution. This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following four factors. First, although RFC_URE5 failed to demonstrate its implementation of a process for annually testing backup media, RFC_URE5 did have a process in place for this testing which ReliabilityFirst determined to be a substantial process. Second, as stated above, RFC_URE5 has a backup facility to which it can failover if needed and which it tests several times each year. Third, in order to realize any actual harm, there would first need to be an instance that requires a recovery and second, the data would have to be unrecoverable. Therefore, the likelihood of harm is low in this instance. Fourth, RFC_URE5 represents that it verifies backup media integrity after every backup job. Fifth, RFC_URE5 implements some measures to response to recover a failed CCA. Effective oversight of the reliability of the Bulk Power System depends on robust and timely self-reporting by Registered Entities. ReliabilityFirst considered that it discovered these issues through a Compliance Audit and was therefore unable to assign self-reporting credit as a mitigating factor. ReliabilityFirst considered certain aspects of the RFC_URE5’s compliance program as mitigating factors. ReliabilityFirst considered the RFC_URE5’s overall cooperation with ReliabilityFirst during the compliance monitoring and enforcement process to constitute a mitigating factor for penalty purposes. ReliabilityFirst considered whether the facts of these issues constitute a repetitive infraction. RFC_URE5 has two prior violations of CIP-004 R4 which arguably constitute repetitive infractions, which dealt with a failure to include specific access rights on the access lists and dealt with a failure to properly update access during quarterly reviews. Despite these previous issues, ReliabilityFirst determined that a monetary penalty was not warranted due to its determination that the issues posed a minimal risk to the Bulk Power System and based on the other adjustment factors set forth above. | To mitigate this issue, RFC_URE5 implemented a new backup and recovery process and updated its recovery plan to include the new process and performed a bare metal restoration to demonstrate its completion of backup media testing.
2014-07-31 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2012010963 | CIP-007-3a | R5; R5.3.3 | During a Compliance Audit, SPP RE determined that SPPRE_URE1 had an issue of noncompliance with CIP-007-3a R5.3.3. SPPRE_URE1 had not changed two passwords associated with two domain accounts for an entire year. The two accounts, and passwords, were used as part of an authentication process to allow “single sign on” verification to SCADA servers. The cause of the issue of non-compliance was due to confusion created by the proximity of the deadline to change the password and the decommissioning the single sign on capability. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although the two passwords to the two domain accounts were not changed per CIP-007-3 R5.3.3, the passwords did comply with the length and complexity requirements of CIP-007-3a R3. Furthermore, the passwords were stored in a hashed form, a form of encryption that protects the integrity of a password as well as its confidentiality. Because the two domain accounts acted as a layer of authentication, they did not belong to any active directory groups that would have allowed them to directly access any cyber assets or critical cyber assets. Finally, the duration of this issue lasted only a month, when SPPRE_URE1 disabled the single sign on capability of the two accounts. | To mitigate this issue, SPPRE_URE1: 1) disabled the single sign on capability to its SCADA servers; and 2) removed the two domain accounts. SPP RE has verified the completion of all mitigation activity.
2014-07-31 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPPRE_URE2) | NCRXXXXX | SPP2013011783 | CIP-003-3 | R6 | SPPRE_URE2 submitted a Self-Report to SPP RE stating that it had an issue of non-compliance with CIP-003-3 R6 because it did not implement supporting configuration management activities to identify, control and document all entity or vendor related changes to hardware and software components of Critical Cyber Assets pursuant to its change control process. Specifically, SPPRE_URE2 was unable to locate the required documentation for one significant change to its SCADA system; therefore, it could not demonstrate its change management process was consistently followed. The cause of the issue of non-compliance was an employee’s failure to document the necessary information for the one significant change to SPPRE_URE2’s SCADA system. | The issue of non-compliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System. Although SPPRE_URE2 lacked the required documentation of one significant SCADA change, its change management program has defined internal controls and performs according to its internal compliance program. Management has to approve changes prior to implementation. Additionally, the CIP Senior Manager monitors all significant changes in real-time throughout the change management process. No actual harm occurred. | To mitigate this issue, SPPRE_URE2: 1) Revised its change management process to reflect feedback from prior experiences implementing change management; 2) Incorporated its change management process into its automated change management tool; and, 3) Trained affected personnel on the revised change management process and the automated change management tool. SPP RE has verified the completion of all mitigation activity.
2014-07-31 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPPRE_URE2) | NCRXXXXX | SPP2013011787 | CIP-006-3c | R1; R1.6.1 | SPPRE_URE2 submitted a Self-Report to SPP RE stating that it had an issue of non-compliance with CIP-006-3c R1.6.1. Specifically, SPPRE_URE2 discovered that the manual visitor access logs for its Physical Security Perimeters (PSPs) did not consistently include all information required by its Cyber Security-Physical Security of Critical Cyber Assets operating procedure (Procedure), such as the visitor’s first and last name (legible), date, times of ingress and egress, and name of authorized escort (legible). The cause of the issue of non-compliance was that SPPRE_URE2 personnel failed to verify the manual visitor access logs for SPPRE_URE2’s PSPs prior to proceeding into the PSPs. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System. SPPRE_URE2 was logging visitor access to the PSPs, even though some of the entries were illegible or were missing information as required by SPPRE_URE2’s Procedure. Additionally, SPPRE_URE2 has few visitors to its PSPs, many of whom are repeat visitors such as janitorial staff. All visitors were documented in the visitor log and were escorted by authorized SPPRE_URE2 employees that had approved personnel risk assessments and completed cyber security training. Furthermore, once SPPRE_URE2 discovered the manual log inconsistencies, it quickly implemented additional internal controls to ensure that the manual logs were properly completed, including training of PSP escorts and more frequent reviews of the visitor logs. No actual harm occurred. | To mitigate this issue, SPPRE_URE2: 1) Updated the visitor access log document to ensure instructions are specific to completing the form properly; 2) Retrained affected employees who provide escorted access in the PSP on the importance of completing the visitor log when entering and exiting the PSP; and 3) Implemented a process requiring weekly, monthly, and quarterly reviews of the manual logs to ensure the logs are being properly completed. SPP RE has verified the completion of all mitigation activity.
2014-07-31 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPPRE_URE2) | NCRXXXXX | SPP20130013046 | CIP-007-3a | R2; R2.1 | SPPRE_URE2 submitted a Self-Report to SPP RE stating that it had an issue of non-compliance with CIP-007-3 R2.1 because it did not have evidence that it had enabled only those ports and services required for normal and emergency operations for a specific time-frame. Several default ports were opened as a result of a software upgrade to five Layer-2 switches located within SPPRE_URE2’s Electronic Security Perimeters (ESPs) and SPPRE_URE2 did not document the justification for the open ports as defined in its process. A Notice of Possible Violation (NPV) was issued, assigning NERC Identification Number SPP2013012521. The cause of the issue of non-compliance was that SPPRE_URE2 employees did not document justifications for open ports on the SPPRE_URE2 system. Subsequently, during a Compliance Audit, the SPP RE Audit Team stated that SPPRE_URE2 had an issue of non-compliance with CIP-007-3 R2.1. Specifically, the Audit Team found that SPPRE_URE2 did not have a documented process that included an assessment of services not associated with a logical port for certain Windows and RedHat Cyber Assets within the ESPs. SPPRE_URE2 utilizes automated port scanning to evaluate its ports and services by running a “Netstat” command on the Windows and RedHat systems. Automated port scanning does not identify services that are not associated with a logical port running on the Windows and RedHat systems. Therefore, SPPRE_URE2 could not confirm that all active services that are not associated with a logical port on its Windows and RedHat systems were required for normal or emergency operations. A NPV was issued, assigning NERC Identification Number SPP20130013046. Since the Compliance Audit, the Federal Energy Regulatory Commission (FERC) has approved Version 5 of CIP-007 R2.1 which removes local services from consideration . Therefore, the Compliance Audit findings concerning local services will not be included in the issue of non-compliance. Because the facts and circumstances for SPP20130012521 involved the same standard and requirement as SPP20130013046, the SPP RE administratively dismissed SPP20130012521, and included the facts and circumstances pertaining to the issue of non-compliance in SPP20130013046. | The issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). SPPRE_URE2 would not have allowed ports that were opened after the software upgrade to the five Layer-2 switches or open local services, to allow network communication outside the ESPs. SPPRE_URE2 had confirmed that all other enabled ports and services were required for normal or emergency operations. Additionally, access to SPPRE_URE2 devices is limited to the EMS/SCADA administrators. Also, SPPRE_URE2 utilizes security monitoring analysis and response systems and system performance software to continuously monitor and alert for malicious activity. No actual harm occurred. | To mitigate this issue, SPPRE_URE2: 1) Assessed the enabled ports and services for the Layer-2 switches for normal and emergency operations; and, 2) Documented justification for the open ports (or closed the ports). SPP RE has verified the completion of all mitigation activity.
2014-07-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2013012187 | CIP-005-3 | R3 | WECC_URE1 submitted a Self-Report stating that it had an issue with CIP-005-3 R3. Specifically, WECC_URE1 stated that its Plant Inter‐Control Center Communications Protocol ("ICCP") server was supposed to forward any alerts, and logs of the alerts, to its Electronic Mail ("ELM") server; however, WECC_URE1 stated that the Plant ICCP server was not properly configured to forward the alerts. As a result, WECC_URE1 stated that the alerts were not being logged and therefore did not provide proper notification. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE1 power plants that contain Critical Cyber Assets are manned 24 hours a day 7 days a week. WECC_URE1 operators are also trained to immediately contact maintenance staff if the Generic Data Acquisition and Control System ("GDACS") system is not running as it should or if it is not responsive. Furthermore, WECC_URE1’s neighboring utility dispatchers also monitor WECC_URE1’s plants to ensure that the plants are responsive 24 hours a day 7 days a week. Moreover, if the neighboring dispatchers saw that the plant was not meeting its target set point or it was not receiving information from the plant, they would immediately contact the plant. WECC_URE1’s GDACS system is hardened to only have required ports and services running and only the standard set of authorized software required for the GDACS system to operate is installed. WECC_URE1’s GDACS system is routinely patched with the tested applicable security updates and Anti-virus is installed and running. Finally, user accounts and passwords are managed by authorized maintenance personnel and only authorized GDACS maintenance staff have administrative privileges to the GDACS network and devices. No harm is known to have occurred. In this instance, WECC_URE1 failed to detect and alert for attempts at or actual unauthorized access to six access points to its Electronic Security Perimeters ("ESPs"). The access points in scope protect WECC_URE1’s Supervisory Control and Data Acquisition ("SCADA") system and are located with WECC_URE1’s server room at three different facilities. WECC_URE1 has a single generating facility. WECC_URE1’s failure to detect and alert unauthorized access at all access points to the ESP exposed its Critical Cyber Assets within the ESP to malicious access attempts. WECC considered WECC_URE1's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, WECC_URE1: 1) configured alerts on the Plant ICCP server; and 2) added cyber alert testing for future Cyber Vulnerability Assessments (CVAs). WECC has verified the completion of all mitigation activity.
2014-07-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2013012769 | CIP-007-3a | R2 | During a Compliance Audit WECC determined that WECC_URE2 had an issue of CIP-007-3a R2. Specifically, WECC determined that WECC_URE2 was unable to produce evidence that three devices had all ports and services not required for normal and emergency operations disabled prior to production use. | The issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Specifically, WECC_URE2 has implemented a defense-in-depth architecture of physical and logical Cyber Security Controls. WECC_URE2 has implemented an Intrusion Detection System and has a Security Events Management System which aid in detecting potential malicious attacks. No harm is known to have occurred. In this instance, WECC_URE2 failed to properly document that ports and services not required for normal and emergency operations were disabled prior to production use of all Cyber Assets within an Electronic Security Perimeter. WECC_URE2’s failure created an opportunity for the introduction of vulnerabilities on devices located within the Electronic Security Perimeter ("ESP"). The potential risks posed by WECC_URE2’s noncompliance were limited due to additional measures implemented by WECC_URE2. | To mitigate this issue, WECC_URE2: 1) disabled all ports and services not required for normal and emergency operation on devices in scope; and 2) updated the CVA procedure and subsequent training on the proper storage of the pre and post scans. WECC has verified the completion of all mitigation activity.
2014-06-26 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2013013033 | CIP-005-3a | R1; R1.5 | During a Compliance Audit, FRCC determined that FRCC_URE1 had an issue of CIP-005-3a R1.5. At the time of the site visit, FRCC_URE1 had not filed Technical Feasibility Exceptions (TFEs) for CIP-007 R5.3.2 (password complexity), R3 (patch management), and R4 (malicious software prevention) for several servers at the security operations center site and at the transmission control center site that monitor FRCC_URE1 Cyber Assets. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The risk was reduced because FRCC_URE1 had mitigating and compensating controls applied and were afforded all other protective measures as required by the Standards. This is a documentation only issue and the required TFEs have now been submitted. No actual harm is known to have occurred. | To mitigate this violation, FRCC_URE1 filed the missing TFEs for the Cyber Assets. FRCC has verified the completion of all mitigation activity.
2014-06-26 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2012011640 | CIP-007-2a | R5.3 R5.3.3 | FRCC_URE1 submitted a Self-Report to FRCC that it had an issue of CIP-007-2a R5.3 and R5.3.3. FRCC_URE1 failed to change a password at least annually for two employees on a Critical Cyber Asset (CCA) account. The account passwords were expired, but the employees did not log into the account and change the password until after one year. | The issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk was reduced because the passwords on the accounts were already expired (within three months from previous change) making them unusable. Furthermore, the CCAs are within a defined Electronic Security Perimeter (ESP) and Physical Security Perimeter, and there is no remote access from outside the ESP. No actual harm is known to have occurred. | To mitigate this violation, FRCC_URE1: 1) changed password for accounts; 2) updated account review procedure to require password change dates be reviewed by administrator every 90 days to ensure annual compliance; 3) completed a review of all Cyber Assets to ensure that no accounts have a password over 365 days old; and 4) developed a reocurring maintenance work order to track password age review. FRCC has verified the completion of all mitigation activity.
2014-06-26 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 2 (FRCC_URE2) | NCRXXXXX | FRCC2014013688 | CIP-004-3a | R2; R2.3 | FRCC_URE2 submitted a Self-Report stating that it had an issue of CIP-004-3a R2.3. FRCC_URE2 failed to ensure the required cyber security training was conducted for all personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets. FRCC_URE2 had an employee that had previously received annual training, and had not complete the required annual training by the required timeframe. The missed training was discovered during a review of the training records and completed one day after the discovery. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk was reduced because FRCC_URE2 had trained the employee in prior years and there were no significant changes to the training since last taken. The employee in question initially received initial cyber security training and was recertified the following year. Furthermore, the employee has a current personnel risk assessment on file. No actual harm is known to have occurred. | To mitigate this violation, FRCC_URE2: 1) immediately trained employee with required annual CIP Cyber Security training; and 2) enhanced its internal controls to require a quarterly review of all training expiration dates. FRCC has verified the completion of all mitigation activities.
2014-06-26 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 3 (FRCC_URE3) | NCRXXXXX | FRCC2014013854 | CIP-004-3 | R4; R4.2 | FRCC_URE3 submitted a Self-Report stating that it had an issue of CIP-004-3 R4.2. FRCC_URE3 discovered, in researching data in preparation for an internal mock audit that it had failed to remove physical access for a transferred employee and update the personnel list of access to Critical Cyber Assets (CCAs) four days late. This was due to an oversight of the access removal request that was received when the access administration team unexpectedly lost a team member. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk-Power System. Failure to remove access in a timely fashion could have resulted in unauthorized physical access to CCAs. The risk was reduced because the employee was a long-term, trusted employee. Additionally, their NERC Cyber training and personnel risk assessment were current, the employee did not attempt to gain access to the room after access should have been removed. No actual harm is known to have occurred. | To mitigate this violation, FRCC_URE3: 1) removed inappropriate access; 2) automated notification process for termination and transfer request; and 3) communicated changes to relevant staff. FRCC has verified the completion of all mitigation activities.
2014-06-26 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2013011714 | CIP-006-1 | R1; R1.8 | MRO_URE1 submitted a Self-Report stating that it had an issue with CIP-006-1 R1.8. Specifically, MRO_URE1 failed to afford the protective measures specified in CIP-007-1 R1, R2, R3, R4, and R8, and CIP-009-1 R1, R2, and R5 for Cyber Assets used in the access control and monitoring of the Physical Security Perimeter (PSP), as required by CIP-006-1 R1.8. MRO_URE1 reported that it had a policy to perform vulnerability scans to test ports after changes to the physical access control system (PACS), but the policy did not include user account testing or log testing as required by CIP-007-1 R1. However, MRO_URE1 stated that it did not change the PACS device aside from patch updates. MRO_URE1 also reported that it performed port scans on the PACS device and reviewed ports. However, MRO_URE1 did not go through the process to ensure that it had a baseline of approved ports and services. MRO_URE1 was using the firewall ports as the baseline instead of a device specific baseline. MRO_URE1 did not have ports or services in the scan. Therefore, MRO_URE1 did not establish a baseline set of ports and services for normal and emergency operations, as required by CIP-007-1 R2. Additionally, MRO_URE1 reported that it failed to annually review ports and services for the PACS device, as required by CIP-007-1 R8. MRO_URE1 also reported that it had a patch management program to assess and apply patches. However, the program did not satisfy NERC CIP requirements of assessing patches within 30 days, as required by CIP-007-1 R3. MRO_URE1 also reported that it used an antivirus software for the PACS server. MRO confirmed through policy screens that the PACS was included and running antivirus. However, MRO_URE1 failed to test the antivirus signature updates prior to installing them as required by CIP-007-1 R4.2. MRO_URE1 also reported that its PACS device was not included in the documented recovery plan, as required by CIP-009-1 R1. However, it was managed as such prior to that time by the information protection group. Additionally, the MRO_URE1 PACS device was not included in the annual exercise of the recovery plan, as required by CIP-009-1 R2. However, MRO_URE1 reported that it ran a table top/paper drill for the PACS. Furthermore, the MRO_URE1 PACS device was not included in the recovery plan to perform testing of backup media, as required by CIP-009-1 R5. However, MRO_URE1 stated that the PACS server was backed up using a third party backup and storage company. The root cause of this issue was that MRO_URE1 managed its PACS outside of its formal CIP program. MRO_URE1 was using a separate group (information protection department) to manage CIP compliance of its PACS device. To mitigate the issue, MRO_URE1 changed CIP compliance management of the PACS device to the energy management system (EMS) group. | This issue posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). MRO_URE1's PACS device is a key control used to manage physical access to its Cyber Assets and Critical Cyber Assets. Additionally, the issue lasted for approximately four and a half years. However, MRO determined that the issue was appropriate for FFT treatment because MRO_URE1 self-identified and reported the issue to MRO, and MRO_URE1 had protective measures in place to mitigate and reduce the risk posed to the BPS. For example, MRO_URE1 performed personnel risk assessments on employees with access to the PACS device. MRO_URE1 verified that every individual with access to the PACS device was authorized. MRO_URE1 also had physical protective measures in place based on its physical security perimeter. Finally, the PACS device was behind an effective firewall with firewall logging turned on to reduce and limit unauthorized access. No harm is known to have occurred. MRO reviewed MRO_URE1's internal compliance program (ICP) and considered it to be a mitigating factor in assessing the noncompliance. MRO_URE1's ICP is managed at a high level in the company, with strong support and engagement from senior management. MRO_URE1's ICP also included internal self-auditing on a set periodic basis. | To mitigate this issue, MRO_URE1: 1) performed a full assessment on current security and compliance measures implemented to provide resolution options to mitigate identified areas of non-compliance; 2) moved the PACS program under the direction of MRO_URE1’s EMS group; 3) designed and migrated the PACS network infrastructure into the EMS operations CIP environment, and designed the PACS network infrastructure and support environment as an isolated network environment, completely separate of MRO_URE1’s EMS operations supervisory control and data acquisition network; 4) procured additional network appliances (firewalls, switches, etc.) and support system hardware and software (servers, network cabinets, workstations, logging software, etc.) to secure the environment and meet compliance requirements; and 5) validated compliance requirement activities related to the PACS. MRO has verified the completion of all mitigation activity.
2014-06-26 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2014013395 | CIP-008-3 | R1 | SERC_URE1 submitted a Self-Certification to SERC stating that it had an issue with CIP-008-3 R1.4. SERC_URE1 failed to update its Cyber Security Incident response plan within thirty calendar days of any changes. SERC_URE1 conducted an annual Cyber Security Incident response plan test and documented lessons learned and action items in its final report as required. The final report was completed approximately three weeks later; however, the Cyber Security Incident response plan was not updated within thirty calendar days of SERC_URE1 identifying the action items and lessons learned. SERC learned that SERC_URE1 updated its plan approximately six months later. SERC reviewed SERC_URE1’s documentation outlining the tabletop exercise and the report that was generated upon completion. The Cyber Security Incident response plan in effect at the time of the incident contained a process for updating within thirty calendar days, but SERC_URE1 personnel failed to update until six months later. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC_URE1 did successfully test the annual Cyber Security Incident Response and there were minimal changes to the plan. Of the three lessons learned, only one required a modification to the plan for personnel to follow during an event while two were changes to improve the exercise process. The personnel who conducted the exercise were the same individuals who identified and updated the modification; therefore, they were already aware that the modification had taken place. | To mitigate this issue, SERC_URE1 developed a process document that details the steps for performing annual exercises, tests, and other periodic activities. This includes a procedure that specifies follow-up activities for action items, and assigns clear ownership of those activities.
2014-06-26 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2012010960 | CIP-005-1 | R4; R4.2 | During an SPP RE CIP compliance audit, SPP RE determined that SPPRE_URE1 had an issue with CIP-005-1 R4.2. Although SPPRE_URE1 performed a cyber vulnerability assessment (CVA) in 2012, it could not demonstrate that it had performed a review to verify that only ports and services required for operation at SPPRE_URE1 access points were enabled. The cause of this issue was an oversight to maintain supporting evidence. | This issue posed a minimal risk and did not pose a serious or substantial risk to the bulk power system (BPS). SPPRE_URE1 performed a CVA in 2012 consistent with all the requirements of CIP-005-1 but could not provide documentation of the review of its ports and services. SPPRE_URE1 subsequently provided an attestation that it had performed the review of ports and services during the 2012 CVA consistent with the requirements of R4.2. The issue did not cause any actual harm to SPPRE_URE1’s access points. When SPPRE_URE1 did provide documentation of a review of ports and services at its access points in a follow-up CVA, the findings were consistent with its earlier attestations. | To mitigate this issue, SPPRE_URE1: 1) Reassigned responsibility for the Cyber Vulnerability Assessment (CVA), which is an independent security group. 2) Enhanced the CVA process itself for the review of all applicable ports and services. This new CVA process will analyze all open ports and services and compare them with the authorized configurations. This ports and services analysis will be retained as evidence for the review process. 3) Implemented the new process and had the Inteam conduct an assessment of the ports and services for the applicable Cyber Assets related to this finding. SPP RE has verified the completion of all mitigation activity.
2014-06-26 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE2014013404 | CIP-006-3c | R1; R1.6; R1.6.1; R1.6.2 | TRE_URE1 submitted a Self-Report stating that it had an issue with CIP-006-3c R1.6.1 and R1.6.2. Specifically, TRE_URE1 did not maintain logs to document the entry and exit of a visitor, including the date and time, to and from Physical Security Perimeters (PSP), as required by R1.6.1. Additionally, TRE_URE1 failed to continuously provide escorted access of a visitor within the PSP, as required by 1.6.2. TRE_URE1 discovered this issue while reviewing video feed and observed a security officer allowing an unauthorized vendor unescorted entry to a Physical Security Perimeter (PSP). Additionally, the security officer failed to log the entry and exit of this unauthorized individual. The root cause of this issue was human error by the security officer on duty. Texas RE has determined that TRE_URE1 had an issue with CIP-006-3c R1.6.1 and R1.6.2 for approximately 13 minutes. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The risk is mitigated by the following factors: a) the duration of the issue was short (13 minutes); b) the security officer on duty was aware that the unescorted vendor was in the PSP; c) the in-scope Critical Cyber Assets (CCAs) within this PSP used for operation were located in an area that was continuously occupied by TRE_URE1 operators. The operators would have immediately known if any unauthorized person attempted to tamper with or login to the devices thereby preventing CCA access; d) there are no CCAs in the area that the vendor was servicing and that area was on the opposite side of the building floor from the CCAs; and e) the devices at issue also had the other protections of the CIP standards. No actual harm occurred as a result of this issue. Texas RE considered TRE_URE1's compliance history and determined that it was not an aggravating factor. | To mitigate this issue, TRE_URE1’s vendor exited the PSP. To prevent recurrence, TRE_URE1 completed the following actions: 1) Removed the security officer from the TRE_URE1 contract; 2) Notified the vendor manager of the incident and reinforced the obligation to send only authorized employees to service TRE_URE1 PSP areas; 3) The applicable vendor manager distributed a communication to all employees of the company reminding them that only authorized individuals may enter the PSP; 4) The security vendor conducted complete review of procedures and post orders associated with TRE_URE1 PSPs; 5) Security vendor management met with each security officer assigned to TRE_URE1 PSPs to provide counseling and discuss the critical importance and consequences of disregarding post orders; and 6) The security vendor implemented an internal training program on procedures and post orders associated with managing TRE_URE1 PSPs. Texas RE has verified the completion of all mitigation activity.
2014-06-26 | TRE_URE1liability Entity (TRE_URE1) | Unidentified Registered Entity 2 (TRE_URE2) | NCRXXXXX | TRE2014013723 | CIP-007-3a | R4; 4.1 | TRE_URE2 submitted a Self-Report stating that it had an issue with CIP-007-3a R4.1. TRE_URE2 did not implement anti-virus and malware prevention tools or document compensating measure(s) applied to mitigate risk exposure for those devices. TRE_URE2 discovered that anti-virus software was not operational on two log management servers the day after the two servers had entered a production environment. For approximately 12 days, TRE_URE2 made multiple attempts to install third party anti-virus software on two log management servers, but the attempts failed due to inoperability problems between vendor specific software on the log servers and the anti-virus software packages. The log management servers are not components of the Energy Management System (EMS) and are not Critical Cyber Assets, but did reside inside the same Electronic Security Perimeter (ESP) as the EMS. TRE_URE2 determined the root cause to be a flaw in its Change Management Process that failed to include a step that requires the Compliance group to check for Technical Feasibility Exception applicability before deploying devices into production. TRE_URE2 had an issue with CIP-007-3a R4.1 for approximately two weeks (when the two servers had entered a production environment until the anti-virus software was successfully installed and tested on the two servers). | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because of the following mitigating and preventive measures: a) the log management servers were located on an isolated network with no direct access to the internet or the corporate network, and all traffic to and from the network traversed secured access points; b) there were no Critical Cyber Assets essential to the operation of the BPS on the network segment where the log management servers reside; c) only necessary ports and services were enabled on the log management servers to limit communications beyond the network segment; d) the log management servers’ communications paths allowed by the internal firewalls ended only with other devices that were running anti-virus protection software; e) Intrusion Prevention Systems and Intrusion Detection System signature based systems in addition to firewall rules, protect the network where the log management servers reside; f) the log management servers physically reside within a highly restricted room within the PSP that requires two factor authentication for access only by a limited number of individuals and is monitored by security cameras 24 x 7; and g) electronic access to the log management servers was limited to Systems Administrators only and no external remote access is allowed. Additionally, TRE_URE2 provided a separate segment of the network where the devices with anti-virus problems reside. Furthermore, once the third party anti-virus software was operational, scans were performed on the servers to confirm no malware or viruses were running on the devices. Lastly, no harm is known to have occurred. TRE_URE1 considered TRE_URE2’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, TRE_URE2 installed anti-virus software on the servers that make up the log management system. To prevent recurrence, TRE_URE2: 1) updated the Change Management Process to include steps that require the Compliance group to check for Technical Feasibility Exception applicability at the beginning of the process and to review CIP-005 and CIP-007 requirements at the end of the process before deploying devices into production; 2) created an improved Change Management Process Checklist; and 3) required system administration personnel to attend training on the new process guidelines. TRE_URE1 has verified the completion of all mitigation activity.
2014-06-26 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2013013062 | CIP-004-1 | R4 | WECC_URE1 submitted a Self-Report to WECC stating that it had an issue with CIP-004-1 R4. Specifically, WECC_URE1 reported they had two incidences in which WECC_URE1 failed to timely update its list of personnel with authorized cyber or unescorted physcial access to Critical Cyber Assets within seven calendar days of any changes in personnel access rights. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE1 undertook preventive measures that could have allowed WECC_URE1 to avoid unauthorized access and a subsequent attack. Namely, WECC_URE1 has around the clock personnel, video cameras and guard support that would recognize and report suspicious activity. The devices in scope are located within locked racks. If an attack on equipment occurred, operators would receive alarms and would implement response procedures. WECC_URE1's system is fully redundant, such that if primary devices were damaged, data would automatically be transferred to secondary devices, leaving the Supervisory Control and Data Acquisition (SCADA) system unaffected. WECC_URE1 also has EOP-008 procedures that would become effective if an unauthorized individual were able to take out both facilities. Finally, in both instances, the access revocation was not for cause and each individual had CIP training and valid personnel risk assessments. This issue posed no actual harm to the bulk power system. | To mitigate this issue, WECC_URE1: 1) worked with Microsoft to evaluate and fix the email delivery problem; 2) implemented a Change Request that eliminated the option to close and complete rather than approve an Access/Removal Request.
2014-05-29 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2012011419 | CIP-003-1 | R6 | MRO_URE1 submitted a Self-Certification stating that it had an issue with CIP-003-3 R6 because it failed to follow its Change Control and Configuration Management (CCCM) process for 19 Critical Cyber Assets (CCAs). Specifically, MRO_URE1 failed to document and test 17 relays within one substation and failed to document backout and testing plans for two network switches within its control center, which were required under its CCCM process. MRO_URE1 discovered the issue of noncompliance during an annual self-certification process. The cause of noncompliance was failure to follow the CCCM process when placing these devices into service. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The 17 relays at issue were located within one substation and an established Physical Security Perimeter (PSP) and Electronic Security Perimeter (ESP). The two network switches at issue were located within one control center and an established PSP and ESP. The exposure of all 19 CCAs was to trusted network and physical traffic. Potential risk to the BPS was further minimized because the CCAs were protected by existing measures that required individuals to have domain identification, password, and roles based on privileges to external systems in order to manage the CCAs. In addition, MRO_URE1 had backup and restore procedures in place in the event there was a failure with any CCAs at the substation or the control center. A Settlement Agreement covering violations of CIP-006-1 R6 for an affiliate of MRO_URE1 was filed with FERC under NP13-41-000 on June 27, 2013. On July 26, 2013, FERC issued an order stating it would not engage in further review of the Notice of Penalty. MRO considered MRO_URE1's compliance history and determined that the instant issue was appropriate for FFT treatment because while the instances were of the same Standard and Requirement, the underlying conduct of the two instances was different. The prior violation of its affiliate was related to a substation router missing a configuration baseline per its CCCM process while the instant issue was related to substation relays lacking testing and software documentation and network switches at a control center lacking documented backout and testing plans. | To mitigate this issue, MRO_URE1: 1) conducted tests required under its CCCM process on the 17 relays at issue; 2) designed and implemented enhanced features of a software tool to use before asset commissioning to better ensure adherance to the CCCM process; 3) directly linked the policy and procedures for change management to the ticketing system; and 4) established an internal process for requesting and tracking Cyber Asset hardware and firmware. MRO has verified the completion of all mitigation activity.
2014-05-29 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 2 (MRO_URE2) | NCRXXXXX | MRO2013012342 | CIP-006-3c | R7 | MRO_URE2 submitted a Self-Report stating that it had an issue with CIP-006-3c R7. Specifically, MRO_URE2 did not retain physical access logs for at least 90 calendar days as required by CIP-006-3c R7. During an internal investigation, MRO_URE2 discovered that its database associated with the electronic access card reader logging activity on the dispatch office door to the Physical Security Perimeter (PSP) of its control center failed to log the entrance of authorized personnel for 72 days due to a network upgrade. MRO_URE2 was unable to provide a log of physical access to its PSP of its control center for 25 days. MRO_URE2 was able to re-create the log of individuals who entered the PSP during the remaining 47 days. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. During the 72-day period that the database associated with the electronic access card reader logging activity on the dispatch office door to the PSP of its control center failed to log the entrance of authorized personnel, the locking mechanism associated with the door to the control center continued to operate, which prevented access without a key card. Manual observation by the system operators continued during the timeframe in addition to manually logging individuals entering the PSP who did not have authorized unescorted physical access. Manual logs were assembled for 47 days, which did not indicate unauthorized access to the control center. MRO_URE2considered MRO_URE2's compliance history and determinted that there were no relevant instances of noncompliance. | To mitigate this issue, MRO_URE2: 1) updated its procedures addressing software for its electric access card reader; and 2) installed a new card key access system to protect its PSPs, which replaced its old system that also controlled access to the building containing PSPs. MRO_URE2has verified the completion of all mitigation activity.
2014-05-29 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 2 (MRO_URE2) | NCRXXXXX | MRO2014013725 | CIP-004-3a | R4 | MRO_URE2 submitted a Self-Report stating that it had an issue with CIP-004-3a. MRO_URE2determined that CIP-004-3a R4 is applicable to the facts and circumstances of this issue. MRO_URE2considered FERC Order Number 706, paragraph 464, (Docket No. RM06-22-000) and guidance attached to CIP-004-3a in Appendix 1 in its determination to process the matter under CIP-004-3a R4. Specifically, MRO_URE2 granted physical access to Critical Cyber Assets (CCAs) to an employee who was not on the list(s) of personnel with authorized cyber or authorized unescorted physical access to CCAs as required by CIP-004-3a R4. During a quarterly review, MRO_URE2 discovered that an employee who had access to CCAs was not on the list of personnel with authorized access to CCAs. The employee was inadvertently provided access during an access change request to grant multiple employees 24-hour access to the Physical Security Perimeter (PSP) containing CCAs. The employee did not access the PSP containing CCAs during this 63-day period. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In the event the employee attempted to access the control center, the employee would have been observed by on-duty system operators who would have challenged the employee's presence. In the event the employee attempted to access the training room, the system operator would have received a notification. MRO_URE2 conducted a comprehensive review and determined no additional individuals were inadvertently provided access to CCAs via the PSP, which included the control center and training room. MRO_URE2reviewed a document signed by the employee at issue attesting he did not access the PSP containing CCAs. PSP access logs did not indicate the employee at issue accessed the training room. A Find, Fix, Track and Report (FFT) information filing addressing remediated issues for certain registered entities including noncompliance with CIP-004-3 R4 for MRO_URE2 (see MRO201100370) was filed with FERC under RC12-1-000 on October 31, 2011, and approved with the March 15, 2012, FERC order establishing the 60-day review period. MRO_URE2considered MRO_URE2's compliance history and determined that the instant issue was appropriate for FFT because the underlying conduct of the two instances was different. The prior remediated issue related to a failure to update the access list for CCAs for a contractor within seven days from when the contractor no longer required access due to an MRO_URE2 employee missing a voicemail while the instant issue was related to inadvertently granting access to CCAs to an employee who was not on the list of personnel with authorized access to CCAs. An Administrative Citation addressing noncompliance with CIP-004-1 R4 for MRO_URE2 (see MRO201100248) was filed with FERC under NP11-253-000 on July 29, 2011, and accepted without further review by FERC on August 29, 2011. MRO_URE2determined the underlying conduct of this instant issue and this previous noncompliance was different. This prior noncompliance was related to a failure to revoke access to CCAs for a terminated employee of a vendor within seven days, while the instant issue was related to a current employee inadvertently being granted access to CCAs. | To mitigate this issue, MRO_URE2: 1) updated its procedures addressing software for its electric access card reader; and 2) installed a new card key access system to protect its PSPs, which replaced its old system that also controlled access to the building containing PSPs. MRO_URE2has verified the completion of all mitigation activity.
2014-05-29 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 3 (MRO_URE3) | NCRXXXXX | MRO2012011289 | CIP-007-1 | R5; R5.3 | MRO_URE3 submitted a Self-Report stating that it had an issue with CIP-007-1 R5.3. Specifically, MRO_URE3 failed to implement technical controls that enforce the password requirements in CIP-007-1 R5.3 for two servers. In the process of reviewing password controls as part of the annual cyber vulnerability assessment, MRO_URE3 discovered that it did not implement technical controls of the local password configuration on two servers. MRO_URE3 had documented procedural controls, and the passwords used on the two servers had a minimum of six characters, had a combination of alpha, numeric, and "special" characters, and were changed at least annually, or more frequently based on risk. However, MRO_URE3 did not implement any technical controls to enforce password length or complexity for the two servers. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although MRO_URE3 failed to establish technical controls for passwords on two servers in accordance with CIP-007-1 R5.3, MRO_URE3 had procedural controls in place at the time of the issue. Additionally, the passwords had a minimum of six characters, had a combination of alpha, numeric, and "special" characters, and were changed at least annually, or more frequently based on risk. Furthermore, upon discovering the issue, MRO_URE3 implemented the technical controls and self-reported the issue to MRO. | To mitigate this issue, MRO_URE3: 1) fixed the inconsistencies discovered in the two servers identified and checked any other systems that were not part of the CIP domain to ensure configuration was enforced and consistent; 2) replaced the old environment with a new domain and equipment; and 3) enhanced the control enforcement verification procedure process used for any significant change to prevent recurrence.
2014-05-29 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2014013422 | CIP-007-3a | R5; R5.3 | NPCC_URE1 had an issue with CIP-007-3a R5. During NPCC_URE1's annual review of shared accounts, NPCC_URE1 discovered that one password to an administrative account was not changed annually. The account is shared by five administrators. NPCC_URE1 discovered the issue and performed an analysis to determine the impact of changing the password. Once NPCC_URE1 determined that a password change was of low impact to its infrastructure, the password was changed. | The issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The account is not accessible outside of the electronic security perimeter (ESP). The authorized personnel list is maintained by IT Security, including their specific electronic and physical access rights to Critical Cyber Assets (CCA) and CCA Information. The shared account's access list is reviewed at least annually. In the event of personnel changes through transfers or terminations, physical and cyber access is removed and high risk account passwords are changed within 24 hours. NPCC_URE1 has implemented controls to log and monitor access to all Cyber Assets within the ESP. Physical and electronic alerts coming from these controls are reviewed twenty-four hours a day. NPCC_URE1 implemented security measures such as intrusion detection systems and virus scanning on the ESP network to detect unusual activities. Additionally, network traffic monitoring is in place and sends alerts to energy management system/supervisory control and data acquisition personnel when unusual activity is detected. There were no security alerts or incidents that were directly related to the specific account throughout the non-compliance period. | To mitigate this issue, NPCC_URE1: 1) performed a risk assessment and an evaluation of the impact for the outstanding password; 2) changed the password; 3) specified who is responsible to change shared account passwords in NPCC_URE1's account management procedure; 4) implemented a web-based action tracking software tool to ensure completion on password changes; 5) implemented a quarterly review of password expirations; 6) developed a lessons learned and communicated it to appropriate IT personnel.
2014-05-29 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2013012089 | CIP-004-3 | R2 | SERC_URE1 submitted a Self-Report to SERC stating that it had an issue with CIP-004-3 R2. Two employees did not receive annual cyber security training, as required. SERC learned that two employees, whose cyber security training was due to expire, mistakenly took the enterprise-wide training module instead of the Critical Infrastructure Protection (CIP) training, which is required for compliance with CIP-004 R2 as it addressed the policies, access controls, and procedures developed for CIP. SERC_URE1 discovered the issue during a quarterly review. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Both employees were in good standing with the company, had valid personnel risk assessments in place and had taken the required cyber security training the previous year, as required. Also, the two employees only had administrative access to electronic access control and monitoring devices and not to Critical Cyber Assets directly. SERC reviewed SERC_URE1's compliance history and determined that it was not an aggravating factor. | To mitigate this issue, SERC_URE1: 1) had employees complete required cyber security training course; 2) updated quarterly review email template and report to specifically reference required training course number; and 3) developed instructions on how to access required training and included in its quarterly review.
2014-05-29 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2013012547 | CIP-005-3a | R1 | SERC_URE1 submitted a Self-Report to SERC stating that it had an issue with CIP-005-3a R1.5. SERC_URE1 failed to afford the protections of CIP-007-3 R4 and R5 to one Cyber Asset used in the access control and/or monitoring of the Electronic Security Perimeter (ESP). While reviewing existing Technical Feasibility Exceptions (TFE), SERC_URE1 discovered that a logging and monitoring device did not have anti-virus or malware protection SERC_URE1 deployed and was not technically enforcing complex passwords, as required. SERC learned that the device was classified as an electronic access control and monitoring (EACM) device for approximately one year and was not included in the existing TFEs. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Compensating measures had been implemented for the device even though the TFE documentation had not been submitted and it had been afforded all of the other protections pursuant to CIP-005-3a R1.5. The compensating measures included Access Control Lists deployed to block or restrict administrative access from un-trusted networks, and vendor security advisories actively being monitored. In addition, the device was configured to use Active Directory for user authentication which enforces a complex password that exceeds the complexity requirements of CIP-007 R5.3.1 and CIP-007 R5.3.2. SERC reviewed SERC_URE1's compliance history and determined that it was not an aggravating factor. | To mitigate this issue, SERC_URE1: 1) amended two TFEs that are in place for like assets; and 2) sent an email communication out on to individuals who have the responsibility for classifying/reclassifying assets notifying them of a procedural update which also reemphasized consideration of when to file TFEs.
2014-05-29 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2013012993 | CIP-005-1 | R1 | SERC_URE1 submitted a Self-Report to SERC stating that it had an issue with CIP-005-1 R1.5. SERC_URE1 failed to afford the protections of Standard CIP-007-3 R5.3 to two Cyber Assets used in the electronic access control and/or monitoring (EACM) of the Electronic Security Perimeter (ESP), as required. SERC_URE1 discovered that two EACM devices, each of which utilized a local administrative account, were not capable of enforcing the password requirements of CIP-007 R5.3. SERC learned that utilizing accounts through Active Directory was the primary method to authenticate to these devices; however, a local account was employed to access each device during initial installation and configuration. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Access to the local account was limited to two personnel, who had authorized electronic access personnel risk assessment and cyber security training. The devices were afforded the other CIP protections as required by CIP-005 R1.5. SERC reviewed SERC_URE1's compliance history and determined that it was not an aggravating factor. | To mitigate this issue, SERC_URE1: 1) drafted TFE Part A and Part B forms and submitted for CIP-007-3 R5.3.2 for the two assets; and 2) updated the Add-Remove Checklist to include a review of both device and application-level accounts, thus covering all local accounts regardless of privilege level.
2014-05-29 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2014013656 | CIP-006-3c | R1; R1.4 | SPPRE_URE1 submitted a Self-Report stating that it had an issue of noncompliance with CIP-006-3c R1.4 because employees did not follow SPPRE_URE1’s physical security plan. Specifically, three employees with authorized access to SPPRE_URE1’s Physical Security Perimeter (PSP) failed to swipe their access cards upon entry into the PSP and failed to log two other employees without authorized unescorted access in and out of the PSP. The group of employees was performing building maintenance and propped open an access point door for sixteen minutes as they worked in the PSP. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The duration of the temporary lapse in compliance was brief and ingress and egress was confirmed using SPPRE_URE1’s physical access monitoring video system. The SPPRE_URE1 PSP is completely within a complex with additional layers of security and access control. The offending employees were employees with current personnel risk assessments and cyber security training. The employees without authorized access were escorted when inside the PSP by employees with authorized access. No actual harm occurred as a result of this issue. No violation history | To mitigate this issue, SPPRE_URE1: 1) Counselled the personnel involved with this incident to document entry for personnel with authorized access, and to log both entry and egress for personnel without authorized access. SPP RE has verified the completion of all mitigation activity.
2014-05-29 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE2014013514 | CIP-005-3a | R5; R5.3 | TRE_URE1 submitted a Self-Report stating that it had an issue with CIP-005-3a R5.3. Specifically, TRE_URE1 failed to retain electronic access logs for at least ninety calendar days at its backup control center. The EMS administrator discovered the issue three days after the firewall logs on the subject server at its backup control center stopped collecting because the Tripwire service had stopped running. The EMS administrator restarted the Tripwire service and the logs started collecting again. The root cause of the issue is uncertain, but TRE_URE1 believes that the Tripwire service may have not restarted correctly after the annual password change was performed on the server just prior to the time frame of the issue. Texas RE determined that TRE_URE1 had an issue with CIP-005-3a R5.3 for three days (when the firewall logs were no longer retained until the firewall logs were collected and retained). | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The firewall logs stopped collecting at the backup control center but not at the primary control center where unauthorized intrusions could have passed undetected and could have comprised the reliability of the BPS. Additionally, TRE_URE1 discovered that the firewall logs had stopped collecting within a few days of the issue, and TRE_URE1 restarted the Tripwire service immediately. Furthermore, TRE_URE1 reviewed the logs from other servers, and no suspicious activity was detected during the issue duration. Compliance History Texas RE considered TRE_URE1’s compliance history and determined that although TRE_URE1 had a previous instance of CIP-005-3a R5.3, the instant issue is appropriate for FFT. The current issue may have been caused by the service not restarting correctly after the annual password change. The previous instance is distinguishable because the firewall configuration was incorrectly set up during installation. Texas RE reviewed TRE_URE1's internal compliance program (ICP) and considered it to be a mitigating factor during the penalty determination. Texas RE also took into consideration that TRE_URE1 self-reported the issue; and TRE_URE1 remediated the issue in a short time frame and performed preventative measures in order to prevent the likelihood of recurrence. | To mitigate this issue, TRE_URE1 restarted the Tripwire service. To prevent or minimize the probability of incurring further issues of the same or similar standards requirements and to address the root cause of the issue, TRE_URE1 has taken the following actions: 1) Changed the recovery settings for the service to require restart after failure. 2) Configured the system to monitor the log location for file age and to send an email and text message alert to the EMS administrator if the log file is older than two hours. This will allow the appropriate contact to be alerted if the logs are not collected and retained timely. Texas RE has verified the completion of all mitigation activity.
2014-05-29 | TRE_URE1liability Entity (TRE_URE1) | Unidentified Registered Entity 2 (TRE_URE2) | NCRXXXXX | TRE2014013351 | CIP-004-1 | R3; R3.2 | TRE_URE2 submitted a self-report stating it had an issue with CIP-004-1 R3.2. TRE_URE1 determined there was one instance in which TRE_URE2 did not perform a Personnel Risk Assessment (PRA) on a seven year basis per R3.2 for an employee who was a re-hire. TRE_URE2 failed to re-perform the PRA because, at the time of the rehire, TRE_URE2 did not have a procedure to do PRAs on re-hires. The re-performance due date was over-written when the employee was re-hired, causing the re-performance date to be pushed back, past the seven year mark. The issue duration period is for approximately three years and 10 months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The risk to the bulk power system was mitigated by the following factors. There was only instance of a failure to perform a PRA. Furthermore, the employee is currently employed by TRE_URE2 and has a valid PRA with no findings. TRE_URE1 determined that the violation posed no actual harm to the reliability of the bulk power system. TRE_URE1 considered Texas_URE2’s compliance history and determined that although TRE_URE2 had a previous instance of CIP-004-1 R3, the instant issue is appropriate for FFT. The current issue was due to TRE_URE2 not having a process on rehires. The prior violation was a failure to renew a criminal background check in seven years on a non-employee. | To mitigate this issue, TRE_URE2 performed the missing Personnel Risk Assessment (PRA) on the employee in question. To prevent or minimize the probability of incurring further issues of the same or similar standards requirements and to address the root cause of the issue, TRE_URE2 has taken the following actions: 1) Updated its procedure to include a PRA for all external candidates, including re-hires. 2) Reviewed all PRA’s for other re-hires and did not identify any other instances of a failure to perform a PRA within a 7-year (calendar) interval. TRE_URE1 has verified the completion of all mitigation activity.
2014-05-29 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2013013124 | CIP-006-3c | R1 | WECC_URE1 submitted a Self-Report to WECC stating that it had an issue with CIP-006-3c R1. Specifically, WECC_URE1 reported that a contracted employee failed to provide continuous escorted access to one visitor within a Physical Security Perimeter (“PSP”) at WECC_URE1’s substation. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The root cause of the remediated issue was human error. Such failure could allow an unauthorized visitor to interrupt power generation and/or take all assets within the building offline. However, WECC_URE1 has around the clock monitoring systems. If malicious activity is identified or suspected, control center personnel are positioned to contact its Security Control Center, and operators can then remotely view the site. Additionally, WECC_URE1’s assets have security tools that log and monitor events, including invalid access attempts. Finally, all of WECC_URE1’s assets have active Disaster Recovery Plans in place that WECC_URE1 reviews, updates and tests on an annual basis. This issue posed no actual harm to the bulk power system. | To mitigate this issue, WECC_URE1: 1) met with contractors management and reviewed WECC_URE1's NERC CIP visitor access control process; 2) confirmed that Telecom updated its documentation and met with Telecom employees regarding the policy; 3) provided a security awareness bulletin to all NERC access card holders communicating awareness, importance and potential risk associated with the escorted access procedures; and 4) published and posted a revised Visitor Control Access Program.
2014-05-29 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2014013364 | CIP-007-3a | R8 | WECC_URE2 submitted a Self-Report to WECC stating that it had an issue with CIP-007-3a R8. Specifically, WECC_URE2 reported that it had completed and documented the results of its Cyber Vulnerability Assessment (“CVA”), but that it had failed to finalize Corrective Action Plans to remediate or mitigate the identified vulnerabilities. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE2 has several protective measures in place to prevent the potential exploitation of vulnerabilities. First, all the devices are located behind a firewall that has been configured to only allow certain traffic through. WECC_URE2 also has an intrusion detection system located behind the firewall and trend micro anti-virus on each Critical Cyber Asset ("CCA") that would alert WECC_URE2 to anomalous behavior. Second, the network switches have policies that only allow configured MAC address to connect. Third, none of the devices have an internet connection. Fourth, WECC_URE2 maintains full back up images of each device for restoration purposes in the event a device is compromised. Fifth, WECC_URE2 has the capability to operate manually if any of the devices require being taken out of service. Finally, WECC_URE2 implemented its Corrective Action Plans, but did so 17 days into the next calendar year. This issue posed no actual harm to the bulk power system. | To mitigate this issue, WECC_URE2 1) documented and implemented its Corrective Action Plans for the nine devices identified in the CVA. WECC has verified the completion of all mitigation activity.
2014-05-29 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2013013239 | CIP-007-3a | R6 | WECC_URE3 submitted a Self-Report to WECC stating that it had an issue with CIP-007-3a R6. Specifically, WECC_URE3 reported that review of cyber security logs was not occurring for a single Critical Cyber Asset (“CCA”) located at one substation. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. First, WECC_URE3’s system has data threshold boundaries that send alerts to operators if thresholds are exceeded. The operators can then manually intervene and prevent anomalous data from being sent. Second, WECC_URE3 has backup sources of automatic generation control ("AGC") data to run the power system. WECC_URE3 also has a backup configuration and some fully configured and redundant devices that can be swapped with a compromised device to replace or restore the device, if necessary. Finally, the device is located within a Physical Security Perimeter ("PSP") and is protected from unauthorized physical access. This issue posed no actual harm to the bulk power system. | To mitigate this issue, WECC_URE3: 1) improved the approval process with network IT staff by adding a specific approver for the last step of the change control process; 2) provided training for its SME's on the change control process; and 3) modified the change control process and provided training and orientation on the modified change control process.
2014-04-30 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2013012364 | CIP-006-3c | R1; R1.6.2 | MRO_URE1 submitted a Self-Report stating that it had an issue with CIP-006-3c R1.6.2. Specifically, MRO_URE1 did not continuously escort one visitor when the visitor was inside an MRO_URE1 Physical Security Perimeter (PSP). The visitor was not escorted for eight minutes. The visitor was an MRO_URE1 telecommunication technician (similar to the escort) and was an employee of MRO_URE1. The issue occurred at MRO_URE1's backup control center (BUCC). This issue occurred because the MRO_URE1 escort did not follow the MRO_URE1 policy to provide a continuous escort for individuals not authorized to access a PSP. The unescorted access was identified by an MRO_URE1 technical analyst while reviewing security logs the next day. MRO_URE1 technical analysts generally review security logs the next business day. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although the visitor had physical access to the Critical Cyber Assets (CCAs), the visitor did not have electronic access to CCAs and the CCAs were logged off at the time of the incident. Additionally, the visitor was an MRO_URE1 employee, and was doing work for MRO_URE1 in a newly defined PSP. Furthermore, the issue was discovered by MRO_URE1 within 24 hours due to internal security log review practices. | To mitigate this issue, MRO_URE1: 1) emphasized procedures on how to escort and monitor visitors within the PSP; 2) developed a separate training module specifically on responsibilities while in a PSP; and 3) posted signs at the BUCC and primary control center. MRO has verified the completion of all mitigation activity.
2014-04-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2013012195 | CIP-005-1 | R2; R2.2 | NPCC_URE1 had an issue with CIP-005-1 R2. During its annual Cyber Vulnerability Assessment (CVA), the IT security group identified ports and services that were not required for operations or for monitoring cyber assets. After further analysis, firewall rules were identified that were not required for operations or for monitoring cyber assets. NPCC determined the duration of the issue to be from the date the Standard became mandatory and enforceable on NPCC_URE1 through when NPCC_URE1 addressed its remaining open ports. | The issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Originally, the vendor recommended a range of ports to be open for the efficient operation of NPCC_URE1's cyber assets. After reviewing port traffic, NPCC_URE1 was able to remove or adjust firewall rules that affected ports with little to no traffic. The classification of corporate network is in reference to the "network zone" where the traffic originates. In the instances of a corporate network to ESP, the source in the firewall rule is defined to a specific source server, specific destination, and specific ports. The majority of the rules in this category were put in place for the purpose of monitoring ESP network equipment, but analysis showed no usage for some of the source IP addresses and network ports that were originally defined. The firewall rules were tightened in response to these findings. The servers that are allowed to access the ESP are patched regularly, monitored, have limited administrators, and run anti-virus. With respect to the instances of a protected network to an ESP, the protected networks have their own firewalls. The protected networks are not defined as ESPs because they do not contain any CIP qualifying assets. They are small networks that contain assets for CIP support functions such as logging, Anti-Virus, and remote access. | To mitigate this issue, NPCC_URE1: 1) resolved specific issues identified during the CVA; 2) acquired a new tool to help determine configuration items that are not absolutely required for operations. The tool captures log data from firewalls and reports on network rules and objects; 3) strengthened the firewall change request process to require approval for any changes that involve network access crossing the ESP. The asset configuration is reviewed to ensure that NPCC_URE1 only opens ports that are documented as required for operation; 4) resolved the additional ports found open with the new tool; and 5) revised procedures to include semi-annual firewall rules review.
2014-04-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 2 (NPCC_URE2) | NCRXXXXX | NPCC2013012196 | CIP-005-1 | R2; R2.2 | NPCC_URE2 had an issue with CIP-005-1 R2. During its annual Cyber Vulnerability Assessment (CVA), the IT security group identified ports and services that were not required for operations or for monitoring cyber assets. After further analysis, firewall rules were identified that were not required for operations or for monitoring cyber assets. NPCC determined the duration of the issue to be from the date the Standard became mandatory and enforceable on NPCC_URE2 through when NPCC_URE2 addressed its remaining open ports. | The issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Originally, the vendor recommended a range of ports to be open for the efficient operation of NPCC_URE2's cyber assets. After reviewing port traffic, NPCC_URE2 was able to remove or adjust firewall rules that affected ports with little to no traffic. The classification of corporate network is in reference to the "network zone" where the traffic originates. In the instances of a corporate network to ESP, the source in the firewall rule is defined to a specific source server, specific destination, and specific ports. The majority of the rules in this category were put in place for the purpose of monitoring ESP network equipment, but analysis showed no usage for some of the source IP addresses and network ports that were originally defined. The firewall rules were tightened in response to these findings. The servers that are allowed to access the ESP are patched regularly, monitored, have limited administrators, and run anti-virus. With respect to the instances of a protected network to an ESP, the protected networks have their own firewalls. The protected networks are not defined as ESPs because they do not contain any CIP qualifying assets. They are small networks that contain assets for CIP support functions such as logging, Anti-Virus, and remote access. | To mitigate this issue, NPCC_URE2: 1) resolved specific issues identified during the CVA; 2) acquired a new tool to help determine configuration items that are not absolutely required for operations. The tool captures log data from firewalls and reports on network rules and objects; 3) strengthened the firewall change request process to require approval for any changes that involve network access crossing the ESP. The asset configuration is reviewed to ensure that NPCC_URE2 only opens ports that are documented as required for operation; 4) resolved the additional ports found open with the new tool; and 5) revised procedures to include semi-annual firewall rules review.
2014-04-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2013012202 | CIP-006-3c | R1 | On April 4, 2013, RFC_URE1 submitted a Self-Report stating that it had an issue of CIP-006-3c R1. RFC_URE1 reported that its physical security plan (the Plan) includes a requirement to review the security plan, review the security infrastructure with a walk-through, and conduct a test. During its February 2013 review of the Plan’s procedure, RFC_URE1 discovered it had not conducted the test as required by the Plan. As a result, RFC_URE1 failed to maintain its Plan as required by CIP-006-3c R1. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. ReliabilityFirst determined that this issue posed a minimal risk to the reliability of the Bulk Power System based on the following two factors. First, RFC_URE1 tested its physical security systems as required by CIP-006-3c R8, which has a much greater impact on prevention of problems with the physical security system. Second, this was an administrative issue that was unlikely to affect RFC_URE1's ability to ensure the safe and reliable operation of its facility. RFC_URE1 has one prior issue of CIP-006-2 R1.3. However, that issue was distinct from the instant issue because it involved a failure to document certain elements of the Plan as opposed to a failure to test as required by the Plan. | To mitigate this issue, RFC_URE1: 1) tested its Plan; 2) re-trained employees on CIP-006-3c compliance; and 3) reviewed the related procedure, as necessary.
2014-04-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2013013195 | CIP-004-3a | R4 | On November 22, 2013, RFC_URE2 submitted a Self-Report stating that it had an issue of CIP-004-3c R4. On August 30, 2013, due to a clerical error, an individual was erroneously given access to a Physical Security Perimeter. This individual did not have training or a Personnel Risk Assessment (PRA). During RFC_URE2’s periodic access privileges review on September 13, 2013, RFC_URE2 discovered the issue and began corrective action. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. ReliabilityFirst determined that this issue posed a minimal risk to the reliability of the Bulk Power System based on the following two factors. First, RFC_URE2 discovered the issue only two weeks after its occurrence, minimizing the time the error could have been exploited. Second, the individual who received the access privileges never used them and was not aware that they were granted. Although RFC_URE2 has prior violations of CIP-004, the root causes were different and did not indicate a pattern of conduct that would constitute a repetitive infraction. Therefore, ReliabilityFirst did not consider RFC_URE2’s violation history an aggravating factor. | To mitigate this issue, RFC_URE2: 1) revoked the access privileges to the incorrect individual; 2) provided re-training to the employee who made the error; and 3) instituted a new review process to cross-check access change activity against access request documents.
2014-04-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2013013196 | CIP-004-3a | R2 | On November 22, 2013, RFC_URE2 submitted a Self-Report stating that it had an issue of CIP-004-3c R2. During RFC_URE2’s periodic Physical Security Perimeter access review, it discovered that 12 employees’ training dates exceeded 15 months in violation of CIP-004-3c R2.3. In each case, the individual had changed position, and the new position did not have an indicator in the data system that it required NERC CIP training, allowing the individual’s prior training credentials to become overdue. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. ReliabilityFirst determined that this issue posed a minimal risk to the reliability of the Bulk Power System based on the following two factors. First, RFC_URE2 discovered the issue through an effective quarterly review process, minimizing the time the error could have been exploited. Second, all individuals whose training was overdue had previously been trained. Although RFC_URE2 has prior violations of CIP-004, the root causes were different and did not indicate a pattern of conduct that would constitute a repetitive infraction. Therefore, ReliabilityFirst did not consider RFC_URE2’s violation history an aggravating factor. | To mitigate this issue, RFC_URE2: 1) provided training as needed; 2) revoked access privileges where training could not be completed; and 3) performed an additional cross-check between the access list and the training database.
2014-04-30 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2014013385 | CIP-003-3 | R2; R2.2 | SERC_URE1 submitted a Self-Report to SERC stating that it had an issue with CIP-003-3 R2. SERC_URE1 failed to document, within thirty calendar days of the effective date, changes to the senior manager assignment with overall responsibility and authority for leading and managing its implementation of, and adherence to, Standards CIP-002-3 through CIP-009-3. SERC_URE1’s designated CIP senior manager with overall responsibility and authority for leading and managing SERC_URE1’s implementation of, and adherence to, Standards CIP-002-3 through CIP-009-3 (CIP senior manager) resigned from SERC_URE1. The CIP senior manager emailed SERC_URE1’s consultant two days prior to the effective date of the resignation, communicating that the consultant should contact the SERC_URE1 officer regarding SERC compliance issues going forward. The consultant is designated by SERC_URE1 as an Alternate Compliance Contact in the SERC Portal. One day before the date of effective resignation, SERC_URE1’s officer emailed the consultant confirming that the SERC_URE1 officer would fill the compliance role until a replacement for the single senior manager is named. However, SERC_URE1 failed to document changes to the CIP senior manager until approximately four months later when it formally re-assigned the CIP senior manager duties to another employee. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC_URE1 has no Critical Assets and SERC_URE1 communicated to its consultant an interim senior manager contact for SERC compliance issues prior to the assigned CIP senior manager's resignation. | To mitigate this issue, SERC_URE1: 1) updated the procedures to align with SERC_URE1 compliance documents; and 2) updated the review process of the procedures.
2014-04-30 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2014013392 | CIP-002-3 | R2 | SERC_URE1 submitted a Self-Report to SERC stating that it had an issue with CIP-002-3 R2. SERC_URE1 failed to develop a list of its identified Critical Assets determined through an annual application of the risk-based assessment methodology (RBAM) required in R1 in 2012 and 2013. SERC determined that SERC_URE1 had an issue with CIP-002-3 R2 because it failed to develop a list of its identified Critical Assets determined through an annual application of the RBAM required in R1 in 2012 and 2013. For 2009 through 2011, SERC_URE1 applied its RBAM to develop a list of identified Critical Assets and Critical Cyber Assets (CCA). In all three years, SERC_URE1 identified no Critical Assets and no associated CCAs, annually reviewed the RBAM, and signed a null list of Critical Assets and CCAs. SERC_URE1, however, failed to do so in 2012 and 2013. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC_URE1 has no Critical Assets. For 2009 through 2011, SERC_URE1 applied its RBAM to develop a list of identified Critical Assets and CCAs. For each of these years, SERC_URE1 annually reviewed the RBAM and signed a null list of Critical Assets and CCAs. Further, there were no changes to the SERC_URE1 system during this time period. | To mitigate this issue, SERC_URE1: 1) completed an evaluation and certified a list of Critical Assets and CCAs; 2) set up reminders in Outlook calendars of multiple employees to make sure the review is completed by the required date.
2014-04-30 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 2 (SERC_URE2) | NCRXXXXX | SERC201000680 | CIP-003-1 | R1 | SERC_URE2 submitted a Self-Report to SERC stating that it had an issue with CIP-003-2 R1.3. SERC_URE2 failed to perform the required annual review of its cyber security policy. SERC reviewed the initial SERC_URE2 Cyber Security Policy. SERC learned that SERC_URE2 defined annual as once per 12 month plus 25%, or 3 month grace period, meaning that any annual activities must be completed no later than 15 months from the previous performance date. As evidence of its annual review of its Cyber Security Policy, SERC_URE2 provided SERC with two versions of its Cyber Security Policy. SERC_URE2 underwent an organizational effectiveness initiative, which required it to realign the organizational structure and update many of its compliance procedures. This initiative required an update to the prior Cyber Security Policy to cover all of SERC_URE2’s Cyber Assets. This updated Cyber Security Policy did not indicate an annual review date or approval by the assigned senior manager for the year it was updated. SERC_URE2’s later version of its Cyber Security Policy indicated that annual reviews had been completed for the years after the year it was updated. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although not officially approved, SERC_URE2 did have a cyber security policy in place for the year at issue. The fact that SERC_URE2 revised its cyber security policy in the year at issue based on the results of a corporate-wide initiative indicates organizational awareness of and support for the goals of that policy. SERC_URE2 had approved and reviewed cyber security policies in place for the years before and after the year at issue. | To mitigate this issue, SERC_URE2: 1) Replaced its cyber security policy with an updated version; and 2) Implemented an intranet application that organized all SERC_URE2 procedures into a central online repository, including listing a review date to ensure reviews are conducted by the required date.
2014-04-30 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 2 (SERC_URE2) | NCRXXXXX | SERC201000681 | CIP-004-2 | R1 | SERC_URE2 submitted a Self-Report to SERC stating that it had an issue with CIP-004-2 R1. Specifically, SERC_URE2 could not demonstrate that several contractors were included in the security awareness reinforcement program. SERC_URE2 had an established enterprise-wide security awareness program that required all SERC_URE2 personnel with access to Physical Security Perimeters (PSPs) to complete cyber security awareness training. SERC learned that SERC_URE2 implements this awareness program by distributing security awareness email notifications to all SERC_URE2 personnel and contractors on a quarterly basis. Additionally, the awareness program requires all facilities and plants with PSPs to display awareness posters in visible areas throughout the facility. The individuals at issue were contractors who had been approved for unescorted physical and electronic access. However, none of the mechanisms employed by SERC_URE2 for security awareness reinforcement applied to these individuals. The individuals did not have SERC_URE2 email addresses to receive SERC_URE2 awareness updates and none of them had physically visited a SERC_URE2 PSP site to view displayed awareness posters. SERC_URE2 completed personnel risk assessments (PRA) for the individuals in question. SERC_URE2 completed cyber security training for all the individuals. SERC learned that the individuals had physical access to PSP facilities with Critical Cyber Assets (CCAs). | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. All the contractor personnel at issue had successfully undergone a PRA and completed cyber security training. In addition, all personnel involved were remote contractors and did not attempt to gain physical access to CCAs at any time. | To mitigate this issue, SERC_URE2: 1) Sent cyber security awareness reinforcement communications to the applicable contracting companies on a quarterly basis and confirmed that the contracting companies distributed these emails to applicable staff; and 2) Posted cyber security awareness reinforcement posters throughout facilities, to prevent similar issues involving individuals with physical access to SERC_URE2 facilities.
2014-04-30 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 2 (SERC_URE2) | NCRXXXXX | SERC201000684 | CIP-006-3a | R5 | SERC_URE2 submitted a Self-Report to SERC stating that it had an issue with CIP-006-3a R5. Following a building fire drill, the alarm monitors for one Physical Security Perimeter (PSP), comprised of a door to a server room and a door to the system control center, were inadvertently left unlocked for approximately 7 hours. At the time, in accordance with SERC_URE2’s physical security plan, door locks were programmed to fail open for safety reasons in the event of a fire drill or other emergency. While the doors were in this open state, they would not alarm for any additional events. It was SERC_URE2’s standard practice to reset the alarms and locks after the completion of the drill. In this instance, the responsible individuals failed to reset the alarms and doors to the PSP at the conclusion of the fire drill, resulting in a failure to review immediately an unauthorized access attempt. SERC_URE2 reviewed video footage and access logs to determine that the doors to the server room and operations center were unsecured for approximately 9 hours, which included the drill and approximately 7 hours thereafter. SERC_URE2 also found that two contractors had accessed the PSP without proper authorization during this period. The contractors in question were performing maintenance on lighting fixtures, and had general access into the building, but did not have authorized access into the system operations center PSP. SERC_URE2 normally escorted these individuals into the controlled area, but in this instance, the individuals scanned for badge access, which was denied, and proceeded to open the unlocked doors. The two contractors’ badge attempts were logged and an alarm was generated, but it was not received and responded to immediately due to the fire drill efforts taking place. SERC_URE2 submitted a second Self-Report to SERC stating that it had an issue with CIP-006-3c R5. SERC determined that the second Self-Report was related to the first Self-Report and decided to treat the second Self-Report as an expansion of scope. SERC_URE2 inadvertently left a physical security door in an unlocked state for approximately 2.5 hours. At a generating facility, after receiving a door held open alarm at a PSP access point, SERC_URE2 discovered a card reader in an unsecure state, with a green light illuminated, meaning it was unlocked. The alarm monitoring personnel, who are responsible for responding to the alarm, inadvertently changed the status of the card reader to an unsecure state while attempting to clear an alarm. Video footage of the PSP access point did not show any unauthorized access to the PSP during the 2.5 hours at issue. | These issues posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC_URE2 had multiple cameras with recorded video feeds monitoring the room during the scheduled event. Physical access logging was enabled and functional during and after the scheduled fire drill. The contractors had a background check completed and were approved for general access, although not for electronic access to CCAs. The contractors were in good standing with the company. No Cyber Assets within the PSP were compromised during the pendency of these issues. | To mitigate the first issue, SERC_URE2: 1) Modified the card reader and alarm configuration of PSP access points to remain secured in the event of a fire drill; 2) Changed the command center’s alarm procedure to automatically require reset of the alarms or locks when the access points of the PSP indicate a compromised position, including physical dispatch and verification and functional testing of access points; 3) Ensured that the building emergency response plan contained steps to manually verify the security of PSP access points using in house security personnel after the drills conclude; and 4) Trained all building security personnel to promptly re-secure and document that all PSP doors have been returned to normal function following a fire alarm or drill. To mitigate the second issue, SERC_URE2: 1) Conducted an internal investigation and reviewed video footage of the incident; 2) Removed the ability for alarm monitoring staff to override the door status to all PSP access points; and 3) Provided additional training for monitoring personnel on proper PSP alarm responses.
2014-04-30 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 2 (SERC_URE2) | NCRXXXXX | SERC2011008632 | CIP-003-3 | R5 | SERC_URE2 submitted a Self-Report to SERC stating that it had an issue with CIP-003-3 R5. SERC_URE2 had granted a user access to protected Critical Cyber Asset (CCA) information without the required clearance to view the information. SERC_URE2 inadvertently granted access to protected CCA information to a new employee. SERC_URE2 failed to follow its own established procedures for granting such access. The new employee was an entry-level engineer who was hired through an approved SERC_URE2 process, which included yearly cyber security training. The individual, however, was mistakenly allowed access to CCA information, but not to CCAs, without having the need for it. SERC_URE2 became aware of this issue during a scheduled annual review of protected CCA information access. The next day, SERC_URE2 removed this individual’s access, 50 days after it was mistakenly granted. SERC_URE2 did not uncover any additional instances during the scheduled annual access review. SERC_URE2 had a documented policy for protected CCA information management, which was approved by SERC_URE2. This policy was reviewed and updated on an annual basis and stated that access to CCA information was granted on a “need to know” basis. SERC determined that SERC_URE2 maintains a list of designated personnel who are responsible for authorizing logical or physical access to protected information, including name, title, and the information for which they are responsible. SERC_URE2 also reviews this list on an annual basis and accounts for that review in the revision history of the list document, as required by CIP-003-3 R5. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC_URE2 had strong physical and electronic access controls in place that limited CCA access to only authorized personnel. SERC_URE2 had documentation and procedural controls in place regarding the protection of CCA information, and the individual in question completed annual cyber security training. Finally, SERC_URE2 reported that the individual did not utilize or attempt to utilize the mistakenly granted access, and was unaware of the mistakenly granted access. | To mitigate this issue, SERC_URE2: 1) Removed the access inadvertently granted; 2) Conducted an internal investigation as to cause; 3) Retrained personnel responsible for executing access requests; and 4) Configured the security monitoring and integrity system to monitor and report on global group changes.
2014-04-30 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 2 (SERC_URE2) | NCRXXXXX | SERC2012009646 | CIP-005-3a | R5 | SERC_URE2 submitted a Self-Report to SERC stating that it had an issue with CIP-005-3a R5. SERC_URE2 discovered that its Electronic Security Perimeter (ESP) documentation that was not updated within 90 calendar days of a change. SERC_URE2 conducted an internal review of its CIP-005 documentation. This review revealed that a Critical Cyber Asset (CCA) was added to the system without updating the associated Electronic Security Perimeter (ESP) drawings within 90 calendar days. SERC_URE2 added the CCA in question, a server, to the ESP. SERC_URE2 did not update the associated ESP diagram to reflect this change until 266 days later, as evidenced by a work ticket associated with this addition and a subsequent reconciliation of SERC_URE2’s CCA lists with its ESP diagrams. SERC_URE2’s procedures required SERC_URE2 to update documentation within 30 days of a change or modification of the system or controls. SERC noted that the documentation provided noted revisions and annual reviews in the revision history of the documents. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The issue involved one drawing at a single ESP. This drawing was missing a single CCA located in the same Physical Security Perimeter (PSP) and ESP. In addition, SERC_URE2’s procedures enforced the review of CIP-005 documentation every 30 days, despite failing in this instance. Furthermore, SERC_URE2 had the CCA in question on the established CCA list. Additionally, SERC_URE2 submitted Technical Feasibility Exceptions for this CCA for its technical inability to comply with certain CIP requirements, indicating that the device was known to and tracked by the entity. | To mitigate this issue, SERC_URE2: 1) Updated the appropriate ESP drawing; and 2) Created a change ticket for monthly reconciliation of the ESP drawings and the CCA list.
2014-04-30 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 2 (SERC_URE2) | NCRXXXXX | SERC2012011012 | CIP-006-3a | R5 | During a Compliance Audit of SERC_URE2, SERC determined that SERC_URE2 had an issue with CIP-006-3a R5. SERC_URE2 failed to implement technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeter (PSP) twenty-four hours per day, seven days per week. Specifically, SERC_URE2 failed to receive and investigate a forced entry alarm from an access point at a PSP. During a physical walk down of the facility, SERC tested a forced entry alarm on a sampled PSP access door and the system did not generate an alarm. SERC_URE2 investigated the issue immediately and found that the interior motion detector was aimed near the door and detected the motion of the forced open door before the alarm contact of the door itself was activated. The door sensors logged this event as a valid exit and did not generate a forced open alarm even though the sensors were configured correctly. SERC_URE2 corrected this issue immediately and performed a full assessment to verify that this issue did not hinder the function of any other PSP access points. SERC_URE2 had a plant security plan documented for the purpose of providing guidance on physical security measures for its facilities. This document applied to all personnel and visitors who have access to the facilities. The security plan defined the management of logging and monitoring physical access twenty-four hours per day, including requiring immediate responses to unauthorized access and alarms, video monitoring, and routing of the alarms to the monitoring and notification centers for response. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The access point at issue has cameras with recorded video feeds monitoring at all times. The access point was locked and had logging functionality configured and working correctly. SERC_URE2 had in place procedures requiring appropriate measures to ensure the functionality of its physical security systems. Finally, the issue was limited to a single access point to one PSP. | To mitigate this issue, SERC_URE2: 1) Modified the alarm function testing procedure to simulate an actual forced door opening, allowing the system to be tested in a way that replicates what would occur during an unauthorized access attempt; and 2) Retrained the security inspectors on the new alarm function testing procedure.
2014-04-30 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 2 (SERC_URE2) | NCRXXXXX | SERC2012011583 | CIP-006-3c | R6 | SERC_URE2 submitted a Self-Report to SERC stating that it had an issue with CIP-006-3c R6. SERC_URE2 failed to follow internal procedures for logging information to uniquely identify individuals and the time of access 24 hours a day, seven days a week. An authorized employee entered a Physical Security Perimeter (PSP) with two visitors. The authorized employee failed to log access on the visitor log as required by SERC_URE2’s policy. The authorized employee and visitors signed the facility visitor log upon entry to the facility. These individuals, however, did not sign the required PSP visitor log. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. While the visitors never logged into the PSP, they did sign the visitor log for the overall facility and were continuously escorted. The visitors did not have access to Critical Cyber Assets while inside the PSP. Additionally, SERC_URE2 had multiple cameras with recorded video feeds monitoring the PSP in question. | To mitigate this issue, SERC_URE2: 1) Updated the NERC CIP visitor logs; 2) Had a cyber security representative contact the employee who escorted the visitors to provide instructions regarding the requirements for PSP access control; 3) Had the employee who escorted the visitors re-take certain training; 4) Updated training materials to include photos of NERC CIP visitor log cabinets and sign-in sheets; and 5) Instructed personnel with authorized unescorted physical access of the difference between NERC CIP and facility visitor’s logs.
2014-04-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPPRE_URE2) | NCRXXXXX | SPP2014013406 | CIP-002-3 | R4 | SPPRE_URE1 submitted a Self-Report stating that it had an issue of noncompliance with CIP-002-3 R4. Specifically, SPPRE_URE1 did not have a signed and dated record of its senior manager’s annual approval of its risk-based assessment methodology (RBAM) between 2010 and 2013. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although SPPRE_URE1 did not keep a signed and dated record of its senior manager’s annual approval of its RBAM, SPPRE_URE1 did apply its RBAM annually between 2010 and 2013, producing a null Critical Asset and Critical Cyber Asset list for each year.SPPRE_URE1’s senior manager approved, signed, and dated the null Critical Asset and Critical Cyber Asset lists for each of the aforementioned years. Finally, SPPRE_URE1’s senior manager approved its RBAM in 2014, and there were no significant changes. | To mitigate this issue, SPPRE_URE1: 1) Reviewed its RBAM; and 2) Added a signature and date line for the senior manager’s approval on its annual review documents. SPP RE has verified the completion of all mitigation activity.
2014-04-30 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE2014013352 | CIP-006-3c | R4 | TRE_URE1 submitted a Self-Report stating that it had an issue with CIP-006-3c R4. Specifically, TRE_URE1 reported it failed to implement the operational and procedural controls to manage physical access at one access point to a Physical Security Perimeter (PSP) twenty-four hours a day, seven days a week. The secure turnstile requires card key access by authorized personnel which was designed with a “fail secure” mechanism that locks the turnstile to prevent access during an outage. However, it was discovered that the “fail secure” mechanism on the turnstile did not operate as designed; therefore, the turnstile was not locked for less than eight hours before the issue was discovered. As soon as TRE_URE1 realized the turnstile was unlocked, TRE_URE1’s Incident Response Plan (IRP) was initiated to evaluate the possible security impact. Security tape was immediately installed and the turnstile entrance was guarded until it was physically bolted in place. Additionally, the security video and the card access log were reviewed, and it was confirmed that there was no unauthorized access while the turnstile was not operational and believed to be “fail secure” but was not physically bolted in place. Texas RE determined that TRE_URE1 had an issue with CIP-006-3c R4 for less than eight hours (when the secure turnstile into the PSP was taken out of service for repair until the time the turnstile entrance was physically bolted in place). | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Physical access was not controlled by TRE_URE1 for a short duration, less than eight hours. The failed turnstile resided behind many layers of security. The TRE_URE1 Data Center is a facility secured by guards, fences, lighting, security card access system, security CCTV cameras, security procedures, and employees sensitized to security issues. To get to the point of entry of the turnstile, a person must go through multiple secure entry points. Additionally, the security video and the card access log were reviewed, and it was confirmed that there was no unauthorized access while the turnstile was not operational. | To mitigate this issue, TRE_URE1: 1) installed security tape, guarded and bolted turnstile; 2) repaired turnstile and returned to operation; 3) formalized a turnstile troubleshooting procedure; and 4) conducted training for applicable Facilities Department personnel to ensure that the turnstile is secured should a malfunction occur in the future. Texas RE has verified the completion of all mitigation activity.
2014-04-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2013013113 | CIP-007-1 | R5 | WECC_URE1 submitted a Self Report to WECC stating that it had an issue with CIP-007-1 R5. Specifically, WECC_URE1 failed to change passwords on shared accounts prior to putting systems (cyber assets) into service. In addition, WECC_URE1 failed to annually change passwords. WECC_URE1 stated it conducted a review of its password records and discovered it failed to change default passwords and generate audit trails of shared account usage for multiple devices. WECC_URE1 failed to change the default password for one shared account prior to putting the asset into service and failed to annually change the password. Additionally, WECC_URE1 failed to change the default passwords and generate an audit trail of shared account usage for two windows system accounts used in the electronic access control and monitoring of Electronic Security Perimeters (ESPs). | The issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. This issue posed no actual harm to the bulk power system. The devices in scope were used by system administrators to perform IT support tasks and collect logs from Cyber Assets. These devices are located on the Energy Management System (EMS) network at the Control Center. Although WECC_URE1 failed to implement account management controls for three shared accounts, it did ensure that all devices in the EMS network are behind a physical perimeter. Physical access is restricted to individuals with Personnel Risk Assessments (PRA) and restricted to individuals through the use of card key access that restricts and monitors all physical access. Finally, the devices in scope are actively monitored by WECC_URE4’s Security Information Events Management (SIEM) System. | To mitigate this issue, WECC_URE1: 1) affected accounts had their passwords changed to ensure that an accurate record exists reflecting a password change in the current annual cycle; and 2) included the previously unidentified accounts to the password age tracking forms.
2014-04-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2013013097 | CIP-006-3c | R1 | WECC_URE2 submitted a Self-Report to WECC stating that it had an issue with CIP-006-3c R1. Specifically, WECC_URE1 did not include a physical access point in its Back-Up Control Center’s (BUCC) Physical Security Perimeter (PSP) designation in its Physical Security Plan, that identifies and documents the PSP. The BUCC was commissioned and WECC_URE2’s physical security plan was updated to include this access point identification in less than two months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. This issue posed no actual harm to the bulk power system.WECC_URE2 implemented a defense-in-depth architecture with physical security controls, including locks and security guards in the building surrounding the BUCC. WECC verified that WECC_URE2 applied protections to the access point in. Therefore, although WECC_URE2 did not timely include one access point in its documentation, WECC_URE2 did ensure that all attempts at and, actual access through, the access point into the PSP were controlled, monitored, and logged. | To mitigate this issue, WECC_URE2: 1) updated its Physical Security Plan to include the access point for the PSP to its BUCC; 2) restructured its Physical Security Plan; and 3) created a checklist for Critical Cyber Assets or PACS devices that are added or moved and identify and train responsible personnel. WECC has verified the completion of all mitigation activity.
2014-04-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2013012778 | CIP-004-3a | R4 | WECC_URE2 submitted a Self Report to WECC stating that it had an issue with CIP-004-3a R4. Specifically, the access list identified an individual with an incorrect unique employee identifier. As a result of this error, WECC_URE2 granted unauthorized access to one employee to two Physical Security Perimeters (PSP) containing a total of approximately 60 Critical Cyber Assets (CCA) used to control WECC_URE2’s Energy Managment System (EMS). The employee was also given access to the System Operating Center and the Distribution Operating Center. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. This issue posed no actual harm to the bulk power system.WECC_URE2 implemented preventive controls to prevent unauthorized physical or logical access to its EMS devices. Specifically, WECC_URE2’s physical access control system requires both a unique PIN and an activated badge to gain access to a PSP. The employee associated with the issue had an activated badge to the PSP, but a PIN was never administered. Thus, the employee could not have accessed the PSP. WECC_URE2 implemented compensating, detective, and corrective controls in that all PSP access points monitor all access attempts and are configured to send an alert for excessive unauthorized attempts. Alerts are sent to security personnel who will immediately respond to any detected incident. If a person attempted to guess the PIN, personnel would have immediately responded, thereby preventing physical access into the PSP. Additionally, WECC_URE2 implemented controls on the devices within the PSP including username/password that would prevent someone with physical access only from maliciously using the CCA. And, WECC_URE2 has anti-tailgating procedures and recurring training in place to discourage employees from allowing others to enter a PSP without approved credentials. | To mitigate this issue, WECC_URE2: 1) immediately revoked access for the unauthorized employee. After a thorough review of the mitigating activities associated with this issue, WECC determined WECC_URE2 remediated the issue, and as a result WECC determined a formal mitigation plan is not necessary for tracking remediation for this specific issue.
2014-04-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2012010526 | CIP-005-3 | R1.5 | WECC_URE3 submitted a Self-Report citing possible noncompliance with CIP-005-3 R1. Specifically, WECC reviewed WECC_URE3's Self-Report and determined that WECC_URE3 granted a single contractor access to Cyber Assets provisioning electronic access control and monitoring in violation of CIP-005-3 R1. | WECC determined that the issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because the instance spanned a period of 24 hours. The contractor subsequently completed a Personnel Risk Assessment (PRA) and was given access to Cyber Assets and Critical Cyber Assets. All Critical Cyber Assets and Cyber Assets were located within an Electronic Security Perimeter (ESP). All access was logged and monitored. | WECC_URE3 terminated the contractor’s access rights to Cyber Assets provisioning access control and monitoring to the ESP thereby remediating possible violation of CIP-005-3 R1.
2014-04-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2012010527 | CIP-006-3 | R2.2 | WECC_URE3 submitted a Self-Report citing possible noncompliance with CIP-006-3 R2. Specifically, WECC reviewed WECC_URE3's Self-Report and determined that WECC_URE3 granted a single contractor access to Cyber Assets provisioning physical access control and monitoring in violation of CIP-006-3 R2. | WECC determined that the issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because the instance spanned a period of 24 hours. The contractor subsequently completed a Personnel Risk Assessment (PRA) and was given access to Cyber Assets and Critical Cyber Assets. All Critical Cyber Assets and Cyber Assets were located within a Physical Security Perimeter (PSP). All access was logged and monitored. | WECC_URE3 terminated the contractor’s access rights to Cyber Assets provisioning physical access control and monitoring to the PSP thereby remediating the possible violation of CIP-006-3 R2.
2014-04-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC2013012884 | CIP-003-3 | R6 | WECC_URE4 submitted a Self-Report to WECC stating that it had an issue with CIP-003-3 R6. Specifically, WECC_URE4 implemented configuration changes outside the parameters of its change control and configuration management process established. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. This issue posed no actual harm to the bulk power system. All cyber assets within the ESP have password protection, port restrictions and are protected with antivirus and anti-malware controls. Having these controls could detect an attacker and prevent malicious software from being installed. WECC_URE4 also has a Security Information and Event Management (SIEM) and syslogs that are used to monitor the devices and network traffic, which could detect and alert on suspicious behavior that occurred within the ESP. | To mitigate this issue, WECC_URE4: 1) reviewed and updated its CIP-003-3 R6 program and associated training materials to ensure change control and configuration processes and expectations of performance are adequately described therein; 2) established preventative controls for electronically managing CIP scope Cyber Asset network connection; 3) improved detective controls to better automate the evaluation of security events on CIP scope Cyber Assets; and 4) established preventative controls for physcially managing CIP scope Cyber Asset network connections. WECC has verified the completion of all mitigation activity.
2014-04-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC2013013189 | CIP-005-3 | R1 | WECC_URE4 submitted a Self-Report to WECC stating that it had an issue with CIP-005-3 R1. Specifically, WECC_URE4 reported that it implemented configuration changes to an ESP network cable inadvertently creating a new, unidentified access point to the ESP. WECC_URE4 reported that a security technician reviewed ESP event logs and identified the access point. WECC_URE4 disconnected the cable and eliminated the access point 16 days later. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Specifically, all cyber assets within the ESP have password protection, port restrictions and are protected with antivirus and anti-malware controls. Such controls are designed to detect an intentional or unintentional misuses and prevent malicious software from being installed. WECC_URE4 also has a Security Information and Event Management (SIEM) and syslogs that are used to monitor the devices and network traffic, which could detect and alert on suspicious behavior that occurred within the ESP. | To mitigate this issue, WECC_URE4: 1) reviewed and updated its CIP-005-3 R1 program and associated training materials to ensure change control and configuration processes and expectations of performance are adequately described therein; 2) established preventative controls for electronically managing CIP scope Cyber Asset network connection; 3) improved detective controls to better automate the evaluation of security events on CIP scope Cyber Assets; and 4) established preventative controls for physcially managing CIP scope Cyber Asset network connections. WECC has verified the completion of all mitigation activity.
2014-04-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 5 (WECC_URE5) | NCRXXXXX | WECC2013013287 | CIP-004-3a | R4 | WECC_URE5 submitted a Self-Report to WECC stating that it had an issue with CIP-004-3a R4. Specifically, WECC_URE5 failed to follow its NERC CIP Physical Security Perimeter (PSP) access process and revoke physical access for one employee within the seven day requirement. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. This issue posed no actual harm to the bulk power system. Specifically, WECC_URE5 stated that all facilities are equipped with cameras and alarms that monitor 24 hours a day 7 days a week and alert security personnel if unauthorized access is detected. WECC_URE5 further stated the facilities are staffed on weekdays, and that personnel would alert security or would be able to intervene if they noticed an unauthorized employee centering a PSP. WECC_URE5 also implemented detective and corrective controls. Specifically, WECC_URE5 has a heartbeat monitoring system that would alert system operators and sound an audible alarm through the SCADA system if the system protection schemes are not functioning as expected, and WECC_URE5 has physical security and incident response procedures that it would activate if an incident occurred. WECC_URE5 also stated that its system operators have contingency plans and additional system protections on devices that would prevent a cascading outage if devices are damaged. Additionally, as a further compensating control, the employee was in good standing and is still employed by WECC_URE5 in a different role, reducing the risk of the employee intentionally causing harm to WECC_URE5's CCAs. | To mitigate this issue, WECC_URE5: 1) revoked access to the employee in question. After a thorough review of the mitigating activities associated with this issue, WECC determined WECC_URE5 remediated the issue and as a result, WECC determined a formal mitigation plan is not necessary for this remediated issue.
2014-03-31 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2013012090 | CIP-004-3 | R2; R2.3 | FRCC_URE1 submitted a Self-Report to FRCC that it had an issue of CIP-004-3 R2.3. FRCC_URE1 had a couple of employees that did not complete annual training as required. Both were initially notified to retrain as a result of an internal control quarterly review. Those employees had mistakenly taken enterprise-wide NERC training instead of the required NERC annual training. | The issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk was reduced because FRCC_URE1 had trained the employees on prior years and there were no significant changes to the training since last taken. Furthermore, the employees had valid personnel risk assessments (PRAs). | To mitigate this violation, FRCC_URE1: 1) had employees complete required cyber security training course; 2) updated quarterly review email template and report to specifically reference required training course number; and 3) developed instructions on how to access required training and included in quarterly review. FRCC has verified the completion of all mitigation activity.
2014-03-31 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2013012091 | CIP-007-3a | R5; R5.3; R5.3.1; R5.3.3 | FRCC_URE1 submitted a Self-Report to FRCC that it had an issue of CIP-007-3 R5.3, R5.3.1, R5.3.3. FRCC_URE1 did not enforce the password rules for length (R5.3.1) or age (R5.3.3) to a single Cyber Asset nor did it submit an appropriate technical feasibility exception (TFE) due to an administrative error. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk was reduced because FRCC_URE1 has procedural controls in place to manually enforce the password requirements. Similar TFEs for this Cyber Asset type had been submitted under CIP-007 R5.3 which covered all password rules set forth by CIP-007 R5.3 (password length, complexity, and age), and an existing TFE covered the Cyber Asset's inability to enforce password complexity. Furthermore, the Cyber Asset is contained within the protection of an Electronic Security Perimeter (ESP), Physical Security Perimeter (PSP) and communications failures, loss of power, or the re-initialization of this Cyber Asset produces an alert which is monitored. | To mitigate this violation, FRCC_URE1 submitted an appropriate TFE under CIP-007 R5.3 to cover all password rules set forth by CIP-007 R5.3 (password length, complexity, and age). FRCC has verified the completion of all mitigation activity.
2014-03-31 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2013013032 | CIP-004-3a | R4; R4.1; R4.2 | During a Compliance Audit, FRCC determined that FRCC_URE1 had an issue of CIP-004-3a R4.1 and R4.2. FRCC_URE1 documents were insufficient evidence to demonstrate that it revoked access to Critical Cyber Assets (CCAs) within within seven calendar days for personnel who no longer require such access to CCAs. The documents submitted to demonstrate the access revocation showed a few contractors with CIP access had a normal separation during the audit period. However, FRCC_URE1 did not revoke access to CIP assets within seven calendar days as required by CIP-004 R4.2 nor update the access list as required by R4.1. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The risk was reduced because the security information and event management tool which logged access is capable of identifying malicious activity. Furthermore, the contractors did not have access to shared accounts, and had current annual cyber security training and personnel risk assessments. | To mitigate this violation, FRCC_URE1: 1) terminated the contractor access and updated the access list; and 2) revised the process for handling contract employee terminations to an automated revocation of physical access rights once human resources processes terminations. FRCC has verified the completion of all mitigation activity.
2014-03-31 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2013013053 | CIP-005-1 | R1; R1.5 | FRCC_URE1 submitted a Self-Report stating that it had an issue of CIP-005-1 R1.5. FRCC_URE1 failed to file a Technical Feasibility Exception (TFE) for a local administrative account on one Cyber Asset used in the access control and/or monitoring of the Electronic Security Perimeters that could not meet the strict compliance of password complexity requirements for CIP-007-3 R5.3.2. The underlying cause of this potential violation was the failure to identify the local account on this Cyber Asset. As a result, a TFE was not submitted timely for this Cyber Asset. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk electric system. The risk was reduced because this Cyber Asset was afforded all other protective measures required by the Standards. Furthermore, the Cyber Asset is located in both an Electronic Security Perimeter and a Physical Security Perimeter. All personnel with access to the local administrative account have current personnel risk assessments and required annual cyber security training. | To mitigate this violation, FRCC_URE1: 1) drafted and submitted TFEs Part A and Part B forms for CIP-007-3 R5.3.2 for the cyber asset; and 2) updated the FRCC_URE1 add-remove checklist to include a review of both device and application-level accounts regardless of privilege level. FRCC has verified the completion of all mitigation activity.
2014-03-31 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2012011421 | CIP-003-3 | R5 | MRO_URE1 submitted a Self-Certification stating that it had an issue with CIP-003-3 R5. Specifically, MRO_URE1 failed to follow its implemented program for managing access to protected Critical Cyber Asset (CCA) information, as required by CIP-003-3 R5. MRO_URE1 reported that one employee was granted access to protected CCA information prior to receiving the proper approval, as required by MRO_URE1's program for managing access to protected CCA information. The employee had access to view a list of individuals with access to CCAs. MRO_URE1 classified the list of individuals with authorized access to CCAs as protected CCA information. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The employee did not have physical or electronic access to any real time information, control systems, or CCAs. The employee had access to a list of individuals with access to CCAs. The information was located on a controlled server that is not a CCA. Additionally, MRO_URE1 performed a manual examination of the server logs and verified that the employee did not access the server that contained the protected CCA information. Furthermore, MRO_URE1 performed a personnel risk assessment on the employee prior to hiring the employee. | To mitigate this issue, MRO_URE1: 1) removed the employee's access to the protected CCA information; and 2) provided training on cyber security and NERC CIP protected information access authorization to corporate information technology employees.
2014-03-31 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 2 (MRO_URE2) | NCRXXXXX | MRO2012011422 | CIP-003-3 | R4 | MRO_URE2 submitted a Self-Certification stating that it had an issue with CIP-003-3 R4. Specifically, MRO_URE2 failed to follow its implemented program to protect information associated with a Critical Cyber Asset (CCA), as required by CIP-003-3 R4. In an attempt to resolve a software implementation issue, one MRO_URE2 employee sent a non-encrypted communication protocol (email) with confidential CCA host names and IP address information to a third party vendor. MRO_URE2's program to protect information associated with a CCA required encryption for emails containing CCA host names and IP address information. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The email was sent to the proper party and the vendor that received the email is bound by a confidentiality agreement. Additionally, although the information was protected by MRO_URE2's program at the time that it was sent to the vendor, MRO_URE2 subsequently removed the plant from its Critical Asset list. Therefore, the information at issue is no longer governed by MRO_URE2's program to protect information associated with a CCA. | To mitigate this issue, MRO_URE2: 1) revised its control management program documentation to reflect information protection guidelines and to include the use of encryption software and the process of submitting protected information to vendors; and 2) revised its CIP security training to highlight information protection requirements.
2014-03-31 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2013013057 | CIP-004-3a | R4 | SERC_URE1 submitted a Self-Report to SERC stating that it had an issue with CIP-004-3a R4. SERC_URE1 failed to revoke access to Critical Cyber Assets (CCAs) within seven calendar days for an employee who no longer required such access to CCAs. SERC_URE1 upgraded its Physical Access Control System (PACS) to provide additional control over physical access to its CCAs. During this upgrade, a SERC_URE1 employee voluntarily retired. This employee had physical access to several Energy Management System (EMS) workstation CCAs. This employee’s physical access was limited to the primary energy control center building hallway and did not include either the control room or EMS equipment areas. SERC_URE1 documented the access revocation in its security access request system. However, further review of the PACS records revealed the employee’s access was not actually revoked. SERC_URE1 attributed this error to the fact that it was in the midst of upgrading its PACS system. According to SERC_URE1, this resulted in a failure to properly request access revocation for this employee and a failure to properly implement this request. SERC_URE1 removed the employee’s access upon completing the PACS upgrade. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. At the time of the subject employee’s retirement, the employee had a current Personnel Risk Assessment and was in good standing with the company. Further, the subject employee only had access to the primary energy control center building hallway with seven CCAs and did not have physical access to either the control room or EMS equipment areas. The seven CCAs were EMS application screens which required electronic credentials, which the employee did not have. The employee did not attempt to enter the PSP after access should have been revoked. | To mitigate this issue, SERC_URE1: 1) installed a new PACS to proactively meet new CIP version 5 requirements for both ingress and egress monitoring and control; 2) upgraded the Security Access Request (SAR) system to support group based account architecture. Employee access is now managed based on functional group requirements rather than individual based account profiles; 3) transferred PACS administrative control from one department to another department. The new PACS admin group consists of a department manager, a security supervisor, and security support staff; and 4) set up the SAR system so that email notifications from the SAR system now includes critical and priority flagging in the subject text header to expedite NERC CIP related access modifications. Emails are sent twice daily to the security administrator group and processed by the designated on-call group member.
2014-03-31 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 2 (SERC_URE2) | NCRXXXXX | SERC2013013084 | CIP-007-3a | R2 | SERC_URE2 submitted a Self-Report to SERC stating that it had an issue with CIP-007-3a R2. SERC_URE2 enabled a service on a Critical Cyber Asset (CCA) that was not required. Prior to moving a workstation designated as a CCA inside an Electronic Security Perimeter (ESP), a technician failed to disable a service used for rebuilding workstations. This service ran on a single port and was used by a tool for the maintenance of network computers. SERC_URE2 used the tool for initial setup and configuration of computers used on the control system, but should have disabled it before moving it to the control system network. SERC_URE2 disabled the CCA approximately seven months after adding it to the ESP. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The issue involved one port on one device. The device in question resided within an ESP, and access to that ESP was prevented by a firewall for the duration of the issue. Further, SERC_URE2 performed an internal audit of previous CCA deployments and no additional issues were discovered. | To mitigate this issue, SERC_URE2: 1) disabled the service that was left open and removed it from the CCA; 2) trained all computer and control system personnel on CIP-007 requirements; 3) created a new VLAN that does not require the service; and 4) conducted an audit of previous CCA deployments.
2014-03-31 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 3 (SERC_URE3) | NCRXXXXX | SERC2013013152 | CIP-005-3a | R1, R1.5 | SERC_URE3 submitted a Self-Report to SERC stating that it had an issue with CIP-005-3a R1.5. SERC_URE3 failed to afford the protective measures of CIP-007 R5.3.3 to Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeter (ESP). During SERC_URE3’s annual 2013 Critical Infrastructure Protection internal audit, SERC_URE3 discovered two devices for which it did not change a local shared account password as required. Both devices were Cyber Assets used in the access control and monitoring of ESPs. Pursuant to CIP-005-3a R1.5, SERC_URE3 was required to change shared account passwords associated with such devices annually. SERC_URE3 utilizes an internal application for documenting, storing, and managing shared account passwords. SERC_URE3 properly documented the account within the application, but due to human error, SERC_URE3 failed to annually change the shared account password. SERC_URE3 did not change the account password for approximately two years and eight months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Electronic access into SERC_URE3’s ESPs require two-factor authentication, and the account in question is not configured to allow two-factor authentication. Therefore, it is not possible to use the account to access the ESP remotely. Based on a review of the application records, the account was not accessed during the timeframe of the issue. The account in question provided device status updates and alerts (functionality checks) and not administrator level access. | To mitigate this issue, SERC_URE3: 1) changed the shared account password in question; 2) added an agenda item to specifically discuss outstanding shared account password changes on a routine basis during weekly CIP change control; and 3) submitted a Technical Feasibility Exception under CIP-007-3 R5.3.3 for the accounts.
2014-03-31 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 3 (SERC_URE3) | NCRXXXXX | SERC2014013363 | CIP-007-3a | R1 | SERC_URE3 submitted a Self-Report to SERC stating that it had an issue with CIP-007-3a R1. SERC_URE3 failed to implement its cyber security test procedures in a manner that minimized adverse effects on the production system or its operation. A SERC_URE3 subject matter expert (SME) was attempting to install antivirus software on a newly procured non-CIP server. The SME mistakenly connected the non-CIP server to the supervisory control and data acquisition (SCADA) network, which is subject to the CIP Reliability Standards. The SCADA network and non-CIP network are physically separated on different network switches. In addition, the switches are color coded for ease of identification. SERC_URE3’s internal controls detected an unauthorized device on the SCADA network and immediately notified the appropriate personnel. Within two to three minutes of being notified, the SME removed the device from the SCADA network. The following day a different SME performed a vulnerability scan on all of the Cyber Assets within the CIP environment. In addition, SERC_URE3 manually reviewed the security log events. The review consisted of pre- and post-events and confirmed there was no unusual or significant activity. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC_URE3’s internal alerting tool immediately detected the introduction of the new server into the CIP environment and alerted system administrators via email as designed by SERC_URE3’s internal process. The server was only connected to the SCADA network for approximately two to three minutes by a CIP-certified SERC_URE3 SME. SERC_URE3 had cyber security test procedures in place that minimized adverse effects on the production system or its operation. Finally, the review conducted by SERC_URE3 of the incident confirmed there was no unusual or significant activity as a result of this issue. | To mitigate this issue, SERC_URE3: 1) performed scans of all the Cyber Assets in the CIP environment using a vulnerability scanning tool; 2) reviewed intrusion detection system and security events reports for the Cyber Assets in the CIP environment for the relevant time period; 3) reviewed the issue with the SME who initiated the issue and the system administration team; and 4) conducted training focused on the issue with the system administration team and other CIP support functionaries.
2014-03-31 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2013012525 | CIP-007-1 | R4 | SPPRE_URE1 submitted a Self-Report stating that it had an issue of noncompliance with CIP-007-1 R4 because five switches (non-critical Cyber Assets) that resided within two Electronic Security Perimeters (ESPs) were not running malicious software prevention. Upon discovery, SPPRE_URE1 determined that it was not technically feasible to install malicious software prevention on the five switches. SPPRE_URE1 had not requested a Technical Feasibility Exception (TFE) for the switches. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The five switches are non-critical assets that are located inside SPPRE_URE1 ESPs and Physical Security Perimeter; therefore, access to the switches was limited to those individuals with authorized electronic and/or physical access rights. SPPRE_URE1’s electronic access points are configured to restrict communications to the enclosed ESPs and require all user access to be performed on-site and from workstations within the ESPs. Connections for external interactive access from any network, including the SPPRE_URE1 Local Area Network, are impossible. Therefore, because the five switches resided within SPPRE_URE1’s ESPs, a malicious software intrusion was unlikely. | To mitigate this issue, SPPRE_URE1: 1) applied for a TFE upon discovery that it was not technically feasible to install malware prevention software on the five switches; 2) monitors the marketplace for the availability of switches with antivirus capability; and, 3) will comply with the requirements of the TFE-Part B and provide reports as required by the TFE program until the TFE can be successfully eliminated or is no longer required. SPP RE has verified the completion of all mitigation activity.
2014-03-31 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2013013043 | CIP-005-3 | R4; R4.2 | During a Compliance Audit, SPP RE determined that SPPRE_URE1 had an issue of noncompliance with CIP-005-3 R4.2. Specifically, in SPPRE_URE1’s 2011 cyber vulnerability assessment (CVA), it did not perform a review to verify that User Datagram Protocol (UDP) ports were required for the operation of access points to its Electronic Security Perimeters (ESPs). | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SPPRE_URE1 performed a CVA in 2011 for its electronic access points to the ESP, albeit not including the UDP ports in its R4.2 review. SPPRE_URE1 did perform a review to verify that all other ports and services required for operations at its access points were enabled. Also, SPPRE_URE1 properly identified vulnerabilities and created corrective action plans for the vulnerabilities that were identified in the 2011 CVA. Finally, SPPRE_URE1 performed a proper review of the UDP ports in the 2012 and 2013 CVAs. | To mitigate this issue, SPPRE_URE1: 1) performed a review to verify that the UDP ports were required for the operation of access points to its ESP in its 2012 and 2013 CVAs; and 2) implemented CVA procedures that require the review of both TDP and UDP ports for proper identification and verification. SPP RE has verified the completion of all mitigation activity.
2014-03-31 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2013013049 | CIP-007-3 | R8; R8.2 | SPPRE_URE1 submitted a Self-Report stating that it had an issue of noncompliance with CIP-007-3 R8 because it did not perform a cyber vulnerability assessment (CVA) in 2011 and 2012 on five switches (non-critical Cyber Assets) that reside within two SPPRE_URE1 Electronic Security Perimeters (ESPs). Additionally, during a Compliance Audit, SPP RE determined that SPPRE_URE1 had an issue of noncompliance with CIP-007-3 R8.2. Specifically, in SPPRE_URE1’s 2011 CVA, it did not perform a review to verify that User Datagram Protocol (UDP) ports were required for the operation of Cyber Assets within its Electronic Security Perimeters (ESPs) were enabled. | SPPRE_URE1’s issue with CIP-007-3 R8 posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The five switches are non-critical assets that are located inside SPPRE_URE1 ESPs and Physical Security Perimeter; therefore, access to the switches was limited to those individuals with authorized electronic and/or physical access rights. SPPRE_URE1’s electronic access points are configured to restrict communications with its ESPs and require all user access to be performed on-site and from workstations within the ESPs. Connections for external interactive access from any network, including the SPPRE_URE1 Local Area Network, are impossible. In addition, SPPRE_URE1’s 2013 CVA included the five switches. SPPRE_URE1’s issue of CIP-007-3 R8.2 posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SPPRE_URE1 performed a CVA in 2011 for the electronic access points to its ESPs, albeit not including the UDP ports in its R8.2 review. SPPRE_URE1 did perform a review to verify that all other ports and services required for operation of Cyber Assets within the SPPRE_URE1 ESPs were enabled. Also, SPPRE_URE1 properly identified vulnerabilities and created corrective action plans for the vulnerabilities that were identified in the 2011 CVA. Finally, SPPRE_URE1 performed a proper review of the UDP ports in the 2012 and 2013 CVAs. | To mitigate this issue, SPPRE_URE1: 1) Performed a 2013 CVA that included the five switches; 2) performed a review to verify that the UDP ports were required for the operation of Cyber Assets within its ESPs in its 2012 and 2013 CVAs; and 3) implemented CVA procedures that require the review of both TDP and UDP ports for proper identification and verification. SPP RE has verified the completion of all mitigation activity.
2014-03-31 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPPRE_URE2) | NCRXXXXX | SPP2014013298 | CIP-004-3a | R4; R4.2 | SPPRE_URE2 submitted a Self-Report stating that it had an issue of noncompliance with CIP-004-3a R4.2 because a temporary employee’s physical access to Critical Cyber Assets was not revoked within seven days from the last date of his employment. The employee’s termination occurred in December 2013, because he reached his maximum allowed hours for employment. On that date, his supervisor collected his badge; however, due to a personnel oversight, his physical access rights were not revoked until January 2014. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The failure to revoke the former employee’s physical access within seven days from the last date of his employment presented a risk of unauthorized physical access to Critical Cyber Assets. However, the former employee’s card was collected upon his termination, and SPPRE_URE2 confirmed that he did not gain access to any Critical Cyber Asset after the date of his termination. Additionally, even had another individual confiscated his badge and attempted to gain physical access to Critical Cyber Assets, such an attempt would have been futile because such access also requires the assigned badge holder’s fingerprint. Moreover, the employee was not terminated for cause, and his access badge was deactivated approximately three weeks after the date of his termination. | To mitigate this issue, SPPRE_URE2: 1) deactivated the former employee’s physical access badge; 2) revoked the former employee’s physical access rights; and 3) retrained affected personnel on its termination and access revocation process. SPP RE has verified the completion of all mitigation activity.
2014-03-31 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 3 (SPPRE_URE3) | NCRXXXXX | SPP2012010988 | CIP-009-1 | R1; R1.1 | During a North American Electric Reliability Corporation (NERC) Compliance Investigation, the Compliance Investigation Team determined that SPPRE_URE3 had an issue of noncompliance with CIP-009-1 R1 (1.1). SPPRE_URE3’s Recovery Plan (Plan) is only activated under severe conditions that require evacuation of the Primary Control Center (PCC), and is not activated in response to events or conditions of lesser severity. In January 2010, SPPRE_URE3 did not activate its Plan during a SCADA outage. No evacuation of the Control Center took place because SPPRE_URE3 determined it was quicker to restart SCADA than to evacuate and re-establish operations at the Backup Control Center. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Not activating the plan for less than severe circumstances could result in an extended recovery time. Though the Plan was not activated, SPPRE_URE3’s system administrators and other support staff immediately began recovering the failed systems using previously documented procedures separate from its CIP-009 Plan. The system outage was not unnecessarily prolonged by reliance upon the recovery steps actually utilized. | To mitigate this issue, SPPRE_URE3: 1) revised the Plan Activation section of its Plan to include: a. an additional provision for Plan activation by the Chief Information Officer on an as-needed basis. This additional provision allows for activation of the Plan for a wide variety of circumstances of varying duration and severity, b. Plan activation by Successors to the CIO, and c. additional scenarios whereby the Plan may be activated in full or part by authorized personnel. 2) developed a configuration and process by which the dispatch personnel may remotely utilize the alternative EMS system without leaving the primary control center; thereby allowing an alternative means to perform the BA functions in situations where SPPRE_URE3 staff believe the primary EMS functionality would be recovered in less time than would be required to physically evacuate to the Backup Control Center. 3) key SPPRE_URE3 employees who were involved in the recovery activities resulting from the outage have since attended vendor and general network training. The main Electronics Technician and Senior Network Specialist also familiarized themselves with each other’s duties and equipment. SPP RE has verified the completion of all mitigation activity.
2014-03-31 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 3 (SPPRE_URE3) | NCRXXXXX | SPP2012011404 | CIP-005-1 | R1; R1.5 | During a Compliance Audit, SPP RE determined that SPPRE_URE3 had an issue of noncompliance of CIP-005-1 R1, specifically R1.5. SPPRE_URE3’s log server that monitors access for five Electronic Security Perimeter (ESP) access points had not been identified as an electronic access control and monitoring system, thus SPPRE_URE3 was unable to demonstrate that all of the requirements referenced in CIP-005-1 R1.5 were applied to the log server, including but not limited to: performing compliance vulnerability assessments, implementing security patches, testing before applying patches or significant changes, and being included in SPPRE_URE3’s change control program. | SPPRE_URE3’s issue with CIP-005-1 R1.5 posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although SPPRE_URE3 did not identify the log server as an electronic access control and monitoring system, the log server resided within SPPRE_URE3’s defined Physical Security Perimeter and access was limited to personnel who had undergone background investigations and completed cyber security training. The log server was regularly patched and anti-malware was installed on it. Furthermore, the log server was separated from the defined ESP by the access point firewalls that deny all access from outside the ESP. Log directories on the log server were backed up and retained per policy. Additionally, access logs for the access point firewalls were reviewed in accordance with CIP-005-1 requirements. SPPRE_URE3 Information Technology personnel are trained in incident response roles and responsibilities with respect to information systems, and participate in the annual CIP-008 Incident Response test. Recovery procedures for the log server are included in SPPRE_URE3’s CIP-009 Cyber Asset recovery plan. | To mitigate this issue, SPPRE_URE3: 1) eliminated the functionality of this log server as it pertains to any Cyber Assets or Critical Cyber Assets. The log server that is the subject of this issue is no longer considered an access control and monitoring system for purposes of the NERC Reliability Standards. 2) redirected the logging functionality to an existing server identified by SPPRE_URE3 as a Cyber Asset used in the access control and monitoring of the ESP and protected according to CIP-005 R1.5. SPP RE has verified the completion of all mitigation activities.
2014-03-31 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 4 (SPPRE_URE4) | NCRXXXXX | SPP2013013282 | CIP-002-3 | R2 | SPPRE_URE4 submitted a Self-Report stating that it had an issue of noncompliance with CIP-002-3 R2. Due to an incidental oversight, SPPRE_URE4 did not perform an annual review of its null Critical Assets list in 2012. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SPPRE_URE4 does not own any Critical Assets. Prior to 2012, SPPRE_URE4 has applied its Risk Based Assessment Methodology (RBAM) and has continually determined that it does not own any Critical Assets. Furthermore, the annual reviews of the null Critical Asset lists in 2011 and 2013 demonstrate that SPPRE_URE4’s issue of noncompliance was merely a gap issue. | To mitigate this issue, SPPRE_URE4: 1. Reviewed and updated the 2011 RBAM; 2. Applied the RBAM based on the 2013 SPPRE_URE4 system configuration; 3. Developed a training presentation for affected staff on the RBAM process; 4. Provided the RBAM process training to affected staff involved in reviewing and conducting the Risk Based Assessment; and 5. Set-up calendar reminders for the annual reviews due each year.
2014-03-31 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 4 (SPPRE_URE4) | NCRXXXXX | SPP2013013283 | CIP-002-3 | R3 | SPPRE_URE4 submitted a Self-Report stating that it had an issue of noncompliance with CIP-002-3 R3. Due to an incidental oversight, SPPRE_URE4 did not perform an annual review of its null Critical Cyber Assets list in 2012. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SPPRE_URE4 does not own any Critical Assets and, therefore, does not own any Critical Cyber Assets. Prior to 2012, SPPRE_URE4 has applied its Risk Based Assessment Methodology (RBAM) and has continually determined that it does not own any Critical Assets or Critical Cyber Assets. Furthermore, the annual reviews of the null Critical Cyber Asset list in 2011 and 2013 demonstrate that SPPRE_URE4’s issue of noncompliance was merely a gap issue. | To mitigate this issue, SPPRE_URE4: 1. Reviewed and updated the 2011 RBAM; 2. Applied the RBAM based on the 2013 SPPRE_URE4 system configuration; 3. Developed a training presentation for affected staff on the RBAM process; 4. Provided the RBAM process training to affected staff involved in reviewing and conducting the Risk Based Assessment; and 5. Set-up calendar reminders for the annual reviews due each year.
2014-03-31 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 4 (SPPRE_URE4) | NCRXXXXX | SPP2013013284 | CIP-002-3 | R4 | SPPRE_URE4 submitted a Self-Report stating that it had an issue of noncompliance with CIP-002-3 R4. Due to an incidental oversight, SPPRE_URE4 did not perform an annual review of its Risk Based Assessment Methodology in 2012. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SPPRE_URE4 does not own any Critical Assets. Prior to 2012, SPPRE_URE4 has applied its Risk Based Assessment Methodology and has continually determined that it does not own any Critical Assets. Furthermore, the annual reviews of its Risk Based Assessment Methodology in 2011 and 2013 demonstrate that SPPRE_URE4’s issue of noncompliance was merely a gap issue. | To mitigate this issue, SPPRE_URE4: 1. Reviewed and updated the 2011 RBAM; 2. Applied the RBAM based on the 2013 SPPRE_URE4 system configuration; 3. Developed a training presentation for affected staff on the RBAM process; 4. Provided the RBAM process training to affected staff involved in reviewing and conducting the Risk Based Assessment; and 5. Set-up calendar reminders for the annual reviews due each year.
2014-03-31 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE2013012697 | CIP-004-3a | R4; R4.2 | TRE_URE1 submitted a Self-Report stating it had an issue with CIP-004-3a R4.2. Per R4.2, TRE_URE1 did not revoke physical access to Critical Cyber Assets within seven calendar days for two facilities employees who were transferred to a different area of the company and no longer required such physical access. The first instance involved an employee whose access was revoked eight days after it should have been. The second instance involved an employee whose access was revoked one day after it should have been. Neither employee had cyber access to Critical Cyber Assets. Texas RE determined the issue duration to be approximately two months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The risk is mitigated by the following factors: a) the two employees had physical access but not cyber access to Critical Cyber Assets. Both employees were and are currently in good standing with TRE_URE1; b) both employees had valid Personnel Risk Assessments and Cyber Security training; c) TRE_URE1 stated at the four locations involved, there was defense-in-depth, including visual and electronic monitoring by security staff 24 hours a day, seven days a week; d) TRE_URE1 stated there were redundant systems in place for all systems critical to operations; and e) TRE_URE1 determined post hoc that neither of the two affected employees attempted to gain access to Physical Security Perimeters after their transfer dates. Texas RE considered the compliance history of TRE_URE1 and affiliates and determined, although instances of the same Standard and Requirement occurred, the instant issue was appropriate for FFT treatment due to the minimal risk nature of the issue. | To mitigate this issue, TRE_URE1: 1. held a discussion with the employee who did not enter the transaction in a timely manner to ensure the responsible individual knew and understood the procedures and implications of timely entry; 2. sent an email to all responsible individuals to remind them that Terminations, Transfers, RIFs, and Suspensions must be entered into the system; 3. created a reminder chart for each responsible individual's desk, designed to be a reminder guide to system transactions that need to be entered when an employee’s status changes, was revised to clearly state the same four actions as in the above item; 4. held a staff meeting for the specific purpose of reviewing the system's purpose, transactions, and operational steps. At this time, a “lessons learned” from the missed transaction entry was also developed by the responsible individuals. A TRE_URE1 manager reiterated very clearly the importance of entering transactions correctly and in a timely manner; and 5. now runs a report in the applicant tracking system to identify any transfers to ensure that they are or will be entered into Service Now. The revoke access instructions have been modified in the access removal steps guidance chart used by all responsible personnel to specifically address entering transfers in the system. Texas RE has verified the completion of all mitigation activity.
2014-03-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2013013121 | CIP-004-3 | R4 | WECC_URE1 submitted a Self-Report to WECC stating that it had an issue with CIP-004-3 R4. Specifically, WECC_URE1 failed to complete quarterly reviews of access lists for Q4 2012 and Q1, Q2, and Q3. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Specifically, if someone had attempted to gain unauthorized access to these CCAs, intrusion and motion detection alarms located at the Control Centers and the substation would have alerted WECC_URE1 personnel at the Control Center. The Control Center has operating personnel 24 hours a day 7 days a week and these personnel are positioned to detect and prevent any malicious physical access to CCAs. To detect logical unauthorized access to these CCAs, WECC_URE1 configured Tripwire alerts for these ESPs. In addition, WECC_URE1 configured all SCADA accounts to lock themselves after a certain number of failed logins. | To mitigate this issue, WECC_URE1: 1) assigned staff to manage access review process; 2) revised access review process to clarify roles and responsibilities; 3) created SharePoint workflows to automate access review process; and 4) conducted quarterly reviews for Q4 2013. WECC has verified the completion of all mitigation activity.
2014-02-27 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2013012819 | CIP-004-3a | R4; R4.1 | NPCC_URE1 submitted a Self-Report stating that it had an issue with CIP-004-3a R4. A NPCC_URE1 headquarters employee retired who had authorized physical access to Physical Security Perimeters (PSPs). The Human Resources separation notice for this employee was issued to those who are responsible for updating the list of Human Capital with authorized unescorted physical access to the PSPs. Staff did not immediately recognize the change in status of this former employee and did not remove the former employee from the list of Human Capital with authorized unescorted physical access to the PSPs within the timeframe of the standard. | The issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The employee's physical access badge had been disabled and was subsequently surrendered to corporate Human Resources prior to his departure date. The site access logs show that the employee did not attempt to or access any of the PSPs during the time frame when his authorized unescorted access remained active. In addition, the former employee had a valid seven year personal risk assessment and a valid mandatory CIP training course certification. NPCC also considered NPCC_URE1's cooperation as a mitigating factor in assessing the Find, Fix, Track process. | To mitigate this issue, NPCC_URE1: 1) developed and implemented a new set of internal controls to identify and prevent similar possible violations. The new internal controls are embedded within a new application that provides a single repository for managing all unescorted physical and electronic system access to NPCC_URE1’s critical cyber assets across the enterprise, along with identification of all applicable Critical Infrastructure Protection training records and personnel risk assessments. 2) after reviewing applicable policies and procedures, no changes were deemed necessary.
2014-02-27 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 2 (NPCC_URE2) | NCRXXXXX | NPCC2014013294 | CIP-007-3a | R5; R5.1 | NPCC_URE2 submitted a Self-Report stating that it had an issue with CIP-007-3a R5. NPCC_URE2 ensures that user accounts are implemented as approved by designated personnel by using an electronic system. Two checkboxes are necessary within their system to completely document the authorization. The supervisor only checked one and not both boxes when setting up the user's account which is a failure to ensure that user accounts are implemented as approved by designated personnel. | The issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The user account was approved by designated personnel with the intent to access four non critical cyber assets within the Electronic Security Perimeter (ESP). The account in question was removed within 2 hours and 21 minutes of creation. The account was never accessed by the user. The cyber assets serve to test systems inside the ESP. The individual had a current Personnel Risk Assessment and was up to date in CIP training. Additionally, NPCC_URE2 had logging and alerting systems in place to detect any malicious activity within the ESP. | To mitigate this issue, NPCC_URE2: 1) removed the accounts from all four assets within 2 hours 21 minutes of creation. 2) performed remedial training for the supervisor. 3) performed remedial training for the IT individual who created the account.
2014-02-27 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2013012603 | CIP-004-3 | R2 | On June 21, 2013, RFC_URE1 submitted a Self-Report to ReliabilityFirst that it had an issue with CIP-004-3 R2 (On September 24, 2013, RFC_URE1 submitted a Self-Report to ReliabilityFirst stating that as a BA, GO, GOP, and LSE, it had an additional issue with CIP-004-3 R2, which ReliabilityFirst consolidated into RFC2013012603. Subsequently, ReliabilityFirst determined that the conduct at issue in this Self-Report did not constitute a Possible Violation, and as a result, ReliabilityFirst did not proceed with that Possible Violation) because during an internal review, RFC_URE1 discovered that on March 6, 2013, a supervisor submitted a request for an employee’s unescorted physical access to a Physical Security Perimeter (“PSP”). The individual granting the access mistakenly granted access to the supervisor rather than the employee. The supervisor did not qualify for authorized unescorted physical access to the PSP because the supervisor did not have cybersecurity training, a personnel risk assessment, or authorization for such access. When RFC_URE1 discovered the issue on May 22, 2013, RFC_URE1 revoked the supervisor’s access. During an internal review, RFC_URE1 discovered that an employee’s cybersecurity training qualification expired. On January 10, 2013, the employee requested and received authorized unescorted physical access to a PSP. On May 9, 2013, the employee’s cybersecurity training expired. On May 30, 2013, RFC_URE1 revoked the employee’s access. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. ReliabilityFirst determined that the facts and circumstances of this issue posed a minimal risk to the reliability of the Bulk Power System based on the following two factors. First, regarding the supervisor’s access, the supervisor did not physically access any of the PSPs. Second, regarding the employee whose training expired, the employee was qualified to have access before and after the training expired. ReliabilityFirst considered whether the facts of this issue constitute a repetitive infraction. RFC_URE1 has six previous violations of CIP-004, and one previous violation of CIP-006 R2 that implicated CIP-004 R3. All but one of the previous violations posed a minimal risk to Bulk Power System reliability, and one of the previous violations posed a moderate risk to Bulk Power System reliability. Despite these previous violations, ReliabilityFirst determined that a monetary penalty was not warranted based on the factors listed above, including RFC_URE1’s strengthening of its internal controls to prevent recurrence of CIP-004 noncompliance. In fact, RFC_URE1’s discovery of many of these previous violations led it to take such steps to strengthen its internal controls and prevent further violations. ReliabilityFirst seeks to encourage this comprehensive detection by imposing no monetary penalty and affording FFT treatment. | To mitigate this issue, RFC_URE1 revoked the affected employees’ access. RFC_URE1 committed to conduct an “after action review” to determine the root cause of the violations, review and reinforce the access process by implementing an electronic form. RFC_URE1 committed to conduct quarterly conference calls with the access approvers to discuss potential improvements, questions, or concerns the access approvers have experienced with the process.
2014-02-27 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2013013003 | CIP-004-3 | R4 | On September 24, 2013, RFC_URE1 submitted a Self-Report to ReliabilityFirst that it had an issue with CIP-004-3 R4 because an employee with authorized unescorted physical access to CCAs resigned from RFC_URE1. On June 26, 2013, RFC_URE1 discovered that due to the supervisor failing to complete RFC_URE1’s internal separation process notifying Human Resources of the separation, it had not revoked the physical access rights for this former employee within seven calendar days. RFC_URE1 revoked the former employee’s access on June 26, 2013. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. ReliabilityFirst determined that the facts and circumstances of this issue posed a minimal risk to the reliability of the Bulk Power System based on the following two factors. First, the individual did not have authorized cyber access to CCAs, and as a result, the individual could not have accessed any CCAs even if managing to gain unauthorized physical access to the two plant PSPs. RFC_URE1 determined that the individual did not attempt to gain such access after resigning from RFC_URE1. ReliabilityFirst considered whether the facts of this issue constitute a repetitive infraction. RFC_URE1 has six previous violations of CIP-004, and one previous violation of CIP-006 R2 that implicated CIP-004 R3. All but one of the previous violations posed a minimal risk to Bulk Power System reliability, and one of the previous violations from 2010 posed a moderate risk to Bulk Power System reliability. Despite these previous violations, ReliabilityFirst determined that a monetary penalty was not warranted based on the factors listed above, including RFC_URE1’s strengthening of its internal controls to prevent recurrence of CIP-004 noncompliance. In fact, RFC_URE1’s discovery in 2012 of many of these previous violations led it to take such steps to strengthen its internal controls and prevent further violations. ReliabilityFirst seeks to encourage this comprehensive detection by imposing no monetary penalty and affording FFT treatment. | To mitigate this issue RFC_URE1 revoked the affected employees’ access. RFC_URE1 committed to conduct an “after action review” to determine the root cause of the violations, and review and reinforce the access process by implementing an electronic form. RFC_URE1 committed to conduct quarterly conference calls with the access approvers to discuss potential improvements, questions, or concerns the access approvers have experienced with the process. In addition, RFC_URE1 committed to appoint a business analyst who will implement continuous improvement with RFC_URE1’s access management program by reviewing policies, processes, and procedures for implementing a semi-automated access control program.
2014-02-27 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2013012719 | CIP-003-3 | R5 | During a Compliance Audit, ReliabilityFirst determined that RFC_URE2 had an issue with CIP-003-3 R5. RFC_URE2 failed to maintain a list of designated personnel who are responsible for authorizing logical access to protected information on the LogRythym, Monitor Servers and DMZ2 devices. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. ReliabilityFirst determined that this issue posed a minimal risk to the reliability of the Bulk Power System based on the following five factors. First, although RFC_URE2 did not maintain a list of designated personnel who are responsible for authorizing logical access to protected information on the LogRythym, Monitor Servers and DMZ2 devices, all the devices were protected within a Physical Security Perimeter. Second, the Monitor Servers were also protected within an Electronic Security Perimeter (“ESP”), while the DMZ2 and the LogRythym servers were external to the ESP and served as electronic access control and monitoring devices. Therefore, RFC_URE2 provided each device with the protections of either an ESP or the protections required for electronic access control and monitoring devices. Third, RFC_URE2 confirmed that no inappropriate access was granted for any of the implicated devices. Fourth, access for these systems is denied by default and all access was limited to administrative personnel responsible for monitoring and logging of the systems within ESPs. Fifth and finally, all users had current personnel risk assessments and training for the entire period for which they had access to devices with protection information. ReliabilityFirst considered as a mitigating factor the positive degree and quality of RFC_URE2’s cooperation and remedial action during the Compliance Audit and enforcement processes. RFC_URE2 was cooperative throughout its interaction with ReliabilityFirst in connection with the issues and worked expeditiously to resolve both issues before the conclusion of the Compliance Audit. When assessing this issue, ReliabilityFirst considered whether the facts of this issue constitute a repetitive infraction. RFC_URE2 has a previous violation of CIP-003-1, R5, which contains similar facts as this remediated issue. Therefore, ReliabilityFirst did considerRFC_URE2’s violation history as an aggravating factor during penalty determination. However, this penalty aggravation was outweighed by the mitigating factors and minimal risk discussed above. Therefore, ReliabilityFirst determined that no monetary penalty was necessary and FFT treatment was appropriate. | To mitigate this issue RFC_URE2 named the designated personnel who are responsible for authorizing logical access to protected information on the LogRythym, Monitor Servers and DMZ2 devices and went through an approval cycle for the review of access to the devices. During the Compliance Audit, ReliabilityFirst verified that RFC_URE2 completed these Mitigating Activities.
2014-02-27 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2013012720 | CIP-007-2a | R5 | During a Compliance Audit, ReliabilityFirst determined that RFC_URE2 had an issue with CIP-007-2a R5. RFC_URE2 failed to technically ensure that it meets the password complexity requirements listed in CIP-007-2a R5.3.2 for its Windows Cyber Assets and failed to file a Technical Feasibility Exception (“TFE”) with ReliabilityFirst where such password complexity was not technically feasible. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. ReliabilityFirst determined that this issue posed a minimal risk to the reliability of the Bulk Power System based on the following three factors. First, although Windows based complexity rules cannot enforce NERC CIP password complexity requirements, RFC_URE2 has procedural controls in place which require that all personnel use passwords that meet the complexity requirements of CIP-007 R5.3. Second, RFC_URE2 had technical controls in place that enforce password length and annual password changes for Windows passwords. Third, RFC_URE2 submitted a TFE to ReliabilityFirst to reflect the fact that the Windows password complexity rules, although they contain stringent requirements, do not correspond exactly to the requirements specified in CIP-007 R5.3. ReliabilityFirst considered as a mitigating factor the positive degree and quality of RFC_URE2’s cooperation and remedial action during the Compliance Audit and enforcement processes. RFC_URE2 was cooperative throughout its interaction with ReliabilityFirst in connection with the issues and worked expeditiously to resolve both issues before the conclusion of the Compliance Audit. When assessing this issue, ReliabilityFirst considered whether the facts of this issue constitute a repetitive infraction. RFC_URE2 has a previous violation of CIP-007-1 R5, which contains similar facts as this remediated issue. Therefore, ReliabilityFirst did consider RFC_URE2’s violation history as an aggravating factor during penalty determination. However, this penalty aggravation was outweighed by the mitigating factors and minimal risk discussed above. Therefore, ReliabilityFirst determined that no monetary penalty was necessary and FFT treatment was appropriate. | To mitigate this issue RFC_URE2 filed a TFE with ReliabilityFirst, which ReliabilityFirst accepted and approved. During the Compliance Audit, ReliabilityFirst verified that RFC_URE2 completed this Mitigating Activity.
2014-02-27 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC2013013119 | CIP-006-3c | R1.4 | On October 25, 2013, RFC_URE3 submitted a Self-Report to ReliabilityFirst that it had an issue with CIP-006-3c R1 because on September 17, 2013 at 10:05 AM, two individuals with authorized unescorted access to RFC_URE3’s Telecom Room reported to the Security Operating Center (“SOC”) that they were unable to gain access. Upon investigation, the SOC operator determined that the key card reader had failed. One of the individuals with authorized unescorted access who was attempting to gain access inquired about using the individual’s supervisor’s override key that would manually unlock the door. The SOC operator authorized the individual to try the override key. At 10:11 AM, the SOC operator received an emergency override key switch alarm and a call from the individual confirming entry into the room. The SOC operator recorded who used the key, but after the SOC operator hung up, the SOC operator realized the key was not used by the individual to whom it was issued. Although both individuals had authorized unescorted access and were logged into the secure area by the SOC operator, the individual who used the override key was not the individual to whom the override key was issued. According to RFC_URE3’s physical security plan, it is prohibited to loan access cards, keys, or PIN codes to individuals other than the authorized individual. The reader communication failure immediately reset after the individual used the override key. The SOC operator placed a ticket with the access control vendor who discovered no issues with the reader. RFC_URE3 and the vendor tightened the reader connections, and the reader has not failed since that occurrence. The SOC manager conducted a full review of this occurrence and determined that the SOC operator did not use three-part communication when discussing the reader issue with the individual. The SOC operator did not look up either individual’s records to determine if an override key was assigned to either of them, nor did the SOC operator ask further questions regarding the availability of the supervisor’s override key. RFC_URE3 also determined that the individuals who used the override key and their manager (the authorized owner) were not aware it was prohibited to loan the key. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. ReliabilityFirst determined that this issue posed a minimal risk to the reliability of the Bulk Power System based on the following two factors. First, the two individuals who were attempting access to the asset had authorized unescorted access rights. Second, throughout the course of the issue, the individuals were in contact with the SOC operator who was aware of the access and the use of the override key. ReliabilityFirst considered whether this issue constitutes a repetitive infraction. RFC_URE3 has eight previous violations of CIP-006 R1. Of these eight previous violations, only one previous violation of CIP-006-3c R1 is relevant to the instant issue because of the vast differences among CIP-006-3c R1.1, R1.4 and R1.6. CIP-006-3c R1.1 concerns the six-wall border of a Physical Security Perimeter, R1.4 concerns physical access controls, and R1.6 concerns a visitor control program. The instant issue did not concern a six-wall border issue or a visitor control program issue, and instead concerns a failure to understand and implement the physical access control program. The violation posed a minimal reliability risk and concerned a tailgating issue, which is dissimilar to the instant issue. Despite this previous violation, ReliabilityFirst determined that a monetary penalty was not warranted due to the minimal risk posed by the issue and based on the factors listed above. | To mitigate this issue RFC_URE3: 1) conducted three-part communication training to each employee and contractor who works in the SOC; and 2) conducted training to ensure awareness of override key responsibilities to those issued keys and received confirmation of understanding from such individuals. In addition, RFC_URE3 committed to limit the need for override keys when appropriate by surveying those who have been issued a key to confirm that they still need the key, by collecting all unnecessary keys, and by eliminating the usage of override keys at the Telecom Room.
2014-02-27 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 4 (RFC_URE4) | NCRXXXXX | RFC2014013382 | CIP-007-3a | R2 | On January 24, 2014, RFC_URE4 submitted a Self-Report to ReliabilityFirst that it had an issue with CIP-007-3a R2.1 because on January 10, 2014, RFC_URE4 conducted its monthly ports and services scan of the eight ProWatch Intelligent Controller panels that monitor and log physical access to Physical Security Perimeters and discovered that the scan of one of the eight panels was not consistent with the baseline identified in RFC_URE4’s procedure, “NERC CIP Allowed Ports & Services – ProWatch IC Panels.” The panel is located inside a secured cabinet in the radio building of one of RFC_URE4’s service centers and controls access to its own cabinet and a second cabinet. This inconsistency occurred because a service technician failed to return one switch to the “off” position after completing repair work on that panel on January 5, 2014, as required by RFC_URE4’s procedures. When the switch is in the “on” position, it enables the factory default administrator account and the web interface, both of which are normally disabled. RFC_URE4 returned the switch to the “off” position within approximately one hour of discovering the issue. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. ReliabilityFirst determined that the facts and circumstances posed a minimal risk to the reliability of the Bulk Power System based on the following three factors. First, the two associated card readers were securing equipment cabinets that contained network devices that were pending retirement and no longer in production. Second, if an individual with access to the company network and knowledge of the panel IP address, account name, and password logged into the device and changed its configuration, the individual could not add, modify, or delete any Physical Security Perimeter access privileges and could not unlock a door. Third, while an individual may have been able to take the panel off-line, the doors to the two secured cabinets would have failed in a locked state and the off-line condition would have been reported as an alarm event to the central alarm station for investigation and response. The ProWatch records did not record any outages of the devices confirming that there were no unauthorized configuration changes during this five day period. | To mitigate this issue RFC_URE4: 1) within one hour after discovery of the inconsistent scan results, returned the design configuration to normal; 2) performed another scan of the panels confirming that all eight were in proper configuration; 3) revised its “NERC CIP ProWatch IC Panel Change Management” procedure to strengthen and delineate the process steps to complete while servicing a panel and now includes a verification that the factory default administrator account is disabled before placing the panel back into service and requires completion of a test record for both significant changes to a panel and changes that require enabling the factory default administrator account; 4) provided counseling for the service technician regarding the need to disable the factory default administrator account and web interface prior to placing the panel back into production, to explicitly follow the established procedure, and to have the procedure in hand whenever undertaking future panel service work; and 5) created a latent remedy change record to document completed work on the Cyber Asset at issue consistent with its change management procedure.
2014-02-27 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2013011692 | CIP-004-3 | R4; R4.2 | SPPRE_URE1 submitted a Self Report stating that it had an issue of noncompliance with CIP-004-3 R4. During its quarterly review of its Critical Cyber Asset access lists, SPPRE_URE1 discovered that it did not revoke a contractor’s authorized unescorted physical access to three Physical Security Perimeters (PSPs) containing Critical Cyber Assets within seven calendar days after no longer needing such access. When the contractor’s assignment ended, at which time his badge was collected and secured in a locked area by his manager; however, the process to revoke the contractor’s physical access to the secured areas was not initiated by his manager. SPPRE_URE1 revoked his access a little over 2 months later. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The contractor had an appropriate level of personnel risk assessment, training, and security awareness prior to being granted unescorted physical access to PSPs. Additionally, the contractor was not granted electronic access to any Cyber Assets. Moreover, the contractor did not have physical access to the PSPs after his assignment ended, because his badge was collected before his departure on that date. SPPRE_URE1 reviewed its physical access logs and confirmed that the contractor did not access any of the PSPs after his badge was collected. | To mitigate this issue, SPPRE_URE1: 1) revoked the contractor’s physical access to the secured areas; 2) developed and distributed awareness documents for top level managers on the requirements of CIP-004 and the managers’ responsibilities; 3) developed and distributed awareness documents those who manage CIP employees and contractors on the requirements of CIP-004 and the managers’ responsibilities; 4) developed and conducted training for all affected personnel contractors on CIP-004 and their responsibilities; 5) developed and distributed an awareness document to contractors on CIP-004 and their responsibilities; and 6) verified by documentation that all affected managers, personnel, and contractors, received awareness documents and/or training on CIP-004 and their respective responsibilities. SPP RE has verified the completion of all mitigation activity.
2014-02-27 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPPRE_URE2) | NCRXXXXX | SPP2012010643 | CIP-002-1 | R3 | SPPRE_URE2 submitted a Self-Report stating that it had an issue of noncompliance with CIP-002-1 R3 because it had not accurately maintained its Critical Cyber Asset List. Specifically, SPPRE_URE2: (1) did not properly classify 16 Control Center workstations as Critical Cyber Assets; and (2) did not update its Critical Cyber Asset List after four replacement Critical Cyber Assets, and replacement router switches at the Primary Control Center and the Backup Control Center were placed in service. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Notwithstanding the errors in its Critical Cyber Asset list, the Control Center workstations, four replacement Critical Cyber Assets and the two router switches, were afforded Critical Cyber Asset protection for the duration of the issue. All of the Critical Cyber Assets resided within SPPRE_URE2’s Electronic and Physical Security Perimeters, and access was limited to personnel who had undergone background investigations and completed cyber security training. Additionally, SPPRE_URE2 regularly patched its Cyber Assets, had installed anti-malware, and included its cyber assets in a recovery plan. | To mitigate this issue, SPPRE_URE2: 1) updated the Critical Cyber Asset List to include the 16 Control Center workstations; 2) updated the Critical Cyber Asset List for the four replacement devices and the two server switches; and, 3) revised its process template for changes to cyber assets to include a review of updates to the Critical Cyber Asset List. SPP RE has verified the completion of all mitigation activity.
2014-02-27 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPPRE_URE2) | NCRXXXXX | SPP2012010986 | CIP-002-1 | R3; R3.1 | During a North American Electric Reliability Corporation (NERC) Compliance Investigation, the Compliance Investigation Team determined that SPPRE_URE2 had an issue of noncompliance with CIP-002-1 R3, inclusive of R3.1. SPPRE_URE2 failed to properly identify all its Critical Cyber Assets when it did not include two control center ICCP servers that use routable protocol to communicate outside of the Electronic Security Perimeter on its Critical Cyber Asset list. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The two ICCP servers were located within SPPRE_URE2’s Physical Security Perimeter thereby limiting personnel access. The patches for both servers had been properly updated; malicious software prevention tools were installed on the servers. Spare ICCP servers were available if one of the primary ICCP servers became inoperable and recovery images and data backups were available for the Primary Control Center ICCP server. Personnel Risk Assessments and annual cyber security training were current for personnel with authorized access to the control centers. | To mitigate this issue, SPPRE_URE2: 1) classified the ICCP servers as Critical Cyber Assets on SPPRE_URE2’s Critical Cyber Asset list. SPP RE has verified the completion of all mitigation activity.
2014-02-27 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPPRE_URE2) | NCRXXXXX | SPP2012011086 | CIP-007-2 | R5; R5.3.3 | On September 18, 2012, SPPRE_URE2 submitted a Self-Report stating that it had an issue of noncompliance with CIP-007-2 R5.3.3 because one password on a shared local administrative account for a Critical Cyber Asset was not changed during the 2011 calendar year. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. There were no attempts to log in and use the shared administrative account during the issue time period. The Critical Cyber Asset for the shared administrative account was located inside a SPPRE_URE2 Physical and Electronic Security Perimeter and afforded the protections required by the CIP Reliability Standards. The Critical Cyber Asset has since been decommissioned. | To mitigate this issue, SPPRE_URE2: 1) successfully reset the password; 2) decommissioned the Critical Cyber Asset; 3) implemented a more stringent local account management auditing process to prevent future recurrence. SPP RE has verified the completion of all mitigation activity.
2014-02-27 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPPRE_URE2) | NCRXXXXX | SPP2012011403 | CIP-003-1 | R1.1 | During a Compliance Audit , SPP RE determined that SPPRE_URE2 had an issue of noncompliance with CIP-003-1 R1.1. Specifically, SPPRE_URE2’s cyber security policy did not explicitly address CIP-006-1 R8, which requires SPPRE_URE2 to implement a maintenance and testing program to ensure that all physical security systems under CIP-006-1 R4, R5, and R6 function properly. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. This is a documentation issue. Although the requirements of CIP-006-1 R8 were not explicitly addressed in the cyber security policy, the requirements were included in another SPPRE_URE2 document and in specific SPPRE_URE2 maintenance standards manuals. The required maintenance and testing was performed on the physical security system components and evidence of the maintenance and testing was properly maintained by SPPRE_URE2 and verified on-site by the Audit Team. SPPRE_URE2 updated the cyber security plan to include the CIP-006-1 R8 requirements prior to the conclusion of the Compliance Audit and the Audit Team reviewed the document and found it to be sufficient. | To mitigate this issue, SPPRE_URE2: 1) updated the 2012 cyber security policy to address all of the requirements of CIP-006-1 R8. SPP RE has verified the completion of all mitigation activity.
2014-02-27 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPPRE_URE2) | NCRXXXXX | SPP2012011408 | CIP-005-1 | R4; R4.3 | During a Compliance Audit, SPP RE determined that SPPRE_URE2 had an issue of noncompliance of CIP-005-1 R4.3. SPPRE_URE2’s process to identify ESP access points was incomplete, resulting in the failure to discover one Electronic Security Perimeter (ESP) access point in the 2010 and 2011 Cyber Vulnerability Assessment (CVA). | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although SPPRE_URE2 failed to discover one ESP access point in its 2010 and 2011 CVAs, SPPRE_URE2 did identify the ESP access point in its 2012 CVA. SPPRE_URE2’s electronic access points are configured to only allow network traffic out of the ESP. Because SPPRE_URE2 denies access to devices that attempt to communicate with the ESP from outside the ESP, the possibility of unauthorized access to SPPRE_URE2’s Cyber Assets within the ESP is remote. Furthermore, no Cyber Assets or Critical Cyber Assets within the ESP have internet access. Additionally, SPPRE_URE2 utilizes a Network Intrusion Detection system (System) within its ESP to monitor and alarm for unauthorized access. The System is monitored during office hours by SPPRE_URE2 personnel and is configured to send alarms to authorized personnel on a 24x7 basis. | To mitigate this issue, SPPRE_URE2: 1) added procedures to its CVA process to ensure that all ESP access points are identified and documented; and, 2) conducted its 2012 CVA during which SPPRE_URE2 properly identified the previously undiscovered ESP access point. SPP RE has verified the completion of all mitigation activity.
2014-02-27 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPPRE_URE2) | NCRXXXXX | SPP2012011418 | CIP-007-1 | R8; R8.2, R8.3 | During a Compliance Audit, SPP RE determined that SPPRE_URE2 had an issue of noncompliance with CIP-007-1 R8, inclusive of R8.2 and R8.3. With regard to CIP-007-1 R8 SPPRE_URE2 could not provide evidence that a complete Cyber Vulnerability Assessment (CVA) was performed in 2010 of all Cyber Assets within its Electronic Security Perimeter (ESP). As to CIP-007-1 R8.2, SPPRE_URE2 could not provide evidence that all ports and services required for operation of the Cyber Assets within its ESP were verified in the 2010 CVA. Additionally, there was insufficient evidence in the 2011 CVA to verify that the UDP port assessments were completed. As to CIP-007-1 R8.3, SPPRE_URE2 did not provide evidence that a review of controls for default accounts had been performed in 2010 and 2011. | These issues posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although there were minor issues with SPPRE_URE2’s performance of the 2010 and 2011 CVAs, SPPRE_URE2’s 2012 CVA evidence was found to be sufficient. SPPRE_URE2’s electronic access points are configured to only allow network traffic in one direction, out of the ESP. Because SPPRE_URE2 denies access to devices that attempt to communicate with the ESP from outside the ESP, the probability of unauthorized access to SPPRE_URE2’s Cyber Assets within the ESP is remote. Furthermore, no Cyber Assets or Critical Cyber Assets within the ESP have internet access. Additionally, SPPRE_URE2 utilizes a Network Intrusion Detection system (System) within its ESP to monitor and alarm for unauthorized access. The System is monitored during office hours by SPPRE_URE2 personnel and is configured to send alarms to authorized personnel on a 24x7 basis. | To mitigate this issue, SPPRE_URE2: 1) added procedures to its CVA process, and; 2) trained SPPRE_URE2 staff on the importance of sufficient CVA evidence retention. SPP RE has verified the completion of all mitigation activity.
2014-02-27 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE2013012933 | CIP-007-3a | R5; R5.3.3 | TRE_URE1 submitted a Self-Report during the Self-Certification period stating that it had an issue with CIP-007-3a R5.3.3. TRE_URE1 reported six shared passwords and one individual account password did not undergo the annual password change as required by CIP 007, R5.3.3. Based on a review of the documentation provided by TRE_URE1, Texas RE determined that TRE_URE1 failed to annually change the passwords on seven user accounts. TRE_URE1 has changed the subject account passwords and implemented a password change notification alert on all subject accounts that require password changes. In addition, the account profiles were revised to include a lock out feature for passwords not changed on schedule. Texas RE determined the issue duration period to be for approximately two years and 11 months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. TRE_URE1 failed to perform an annual password change on seven user accounts. A failure to update system passwords increases the risk of harmful and unauthorized intrusions into the SCADA system, compromising the reliability of the BPS. However, the risk is partially offset by the multi layered access authentication structure of the subject accounts and the implementation of the related procedural controls. Before a user is able to log into the subject accounts, each user must first obtain network access through a unique login followed by several independent account logins. The seven accounts at issue only represent one of the many accounts needed to obtain access to the subject accounts. Furthermore, the subject server accounts, which are not remotely accessible, require each user to obtain authorized physical and electronic critical cyber asset access before one could access the subject accounts. Lastly, TRE_URE1 reviews the database access activity reports weekly, and TRE_URE1 noted no adverse activity during the issue period. Texas RE took into account that an affiliate of TRE_URE1 had a previous issue of this Standard and Requirement. Texas RE determined that the instant issue was appropriate for a FFT treatment because the underlying conduct of the two instances was different. | To mitigate this issue, TRE_URE1: 1) changed the passwords on the seven accounts; 2) implemented a new password vault that includes notifications; 3) revised subject server account profiles to include a lock out feature for passwords that are not changed on schedule; and 4) created an automated program that runs daily to check password age of the subject server accounts and notifies the appropriate system team members for shared accounts and individuals for individual accounts. Texas RE has verified the completion of all mitigation activity.
2014-02-27 | TRE_URE1liability Entity (TRE_URE1) | Unidentified Registered Entity 2 (TRE_URE2) | NCRXXXXX | TRE2013012686 | CIP-006-3a | R1; R1.6 | TRE_URE2 submitted a Self-Report stating it had an issue with CIP-006-3a R1. Specifically, TRE_URE2 discovered that it did not have logs documenting entry and exit of for a number of instances per R1.6.1. TRE_URE2’s visitor control program included manual or automatic logging of visitors to and from Physical Security Perimeters (PSPs), including logging of the time of entry to and exit from the PSP, as required in R1.6.1, and the escort name. TRE_URE2 discovered it had 49 omissions in its logs. TRE_URE1 determined the issue duration to be approximately 14 months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The risk is mitigated by the following factors: a) all visitors were escorted by qualified, approved, authorized staff; b) all PSPs had 24 hour video and human monitoring; c) TRE_URE2 trained its employees and contractors in visitor control and monitoring within PSPs; and d) only 1.1% of information from data fields was missing. | To mitigate issue, TRE_URE2: 1) increased the review of PSP Visitor Log sheets to at least once a month; 2) increased awareness of these issues by mentioning proper visitor log procedures at a number of monthly safety meetings as well as in the monthly awareness newsletter; 3) discussed any issues found with the escorts as required; and 4) performed an investigation regarding root causes, with additional recommendations to reduce the likelihood of recurrence. TRE_URE1 has verified all mitigation activity.
2014-02-27 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 3 (TRE_URE3) | NCRXXXXX | TRE2013012856 | CIP-004-3a | R4; R4.1 | TRE_URE3 submitted a Self-Certification stating that it had an issue with CIP-004-3a R4.1. During a quarterly access review, TRE_URE3 discovered there was no record in the Authorized Access List for one individual. The subject individual completed a personnel risk assessment and the required access training, and was granted access to Physical Security Perimeters, but the access permissions were not documented at that time. Specifically, TRE_URE3 failed to create the Authorized Access List record within seven calendar days of the subject individual’s change in access rights as required by CIP-004-3a R4.1. This reported documentation issue is not indicative of a flaw in systems logic, but rather the result of human error. Texas RE determined that TRE_URE3 had an issue with CIP-004-3a R4.1 for approximately 34 days. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The minimal risk was partially mitigated because the subject individual was not included on the authorized unescorted PSP access list for a short period. Additionally, the individual had completed a PRA and the required access training prior to being granted PSP access. Further mitigating this risk is the documentation nature of the issue and the implementation of a documented access control process that has been in place since the Standard’s enforceable date that addresses the maintenance of such access list(s). Texas RE considered the compliance history of TRE_URE3’s affiliates and determined that the instant issue was appropriate for FFT treatment. Although the instances were of the same Standard and Requirement, the underlying conduct of the affiliate instances was different. | To mitigate this issue, TRE_URE3: 1) updated its Authorized Access Records document to include the subject individual’s CCA access rights; 2) created and implemented an Access Request Checklist that requires a separate checklist for each new access request and that checklist will be retained for reference and verification purposes. This checklist will be completed by the individual granting access; 3) evaluated an automated solution to conduct comparisons between configured access within its security access application and the provisioned access listed in the Authorized Access List. This automation would mimic the manual activity performed during the quarterly review but allow TRE_URE3 to recognize errors on a daily or weekly basis. Texas RE has verified the completion of all mitigation activity.
2014-02-27 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 3 (TRE_URE3) | NCRXXXXX | TRE2013012305 | CIP-007-3a | R5; R5.2.1 | TRE_URE3 submitted a Self-Report stating that it had an issue with CIP-007-3a R5.2.1. TRE_URE3's team identified that the passwords for default accounts on three devices had never been changed from the default settings as required by R5.2.1. The three subject devices are non-critical Cyber Assets in the Electronic Security Perimeter (ESP). The support team has always configured the devices directly through the control panel rather than through a remote connection. Therefore, TRE_URE3 elected to disable the remote login capability to the devices on the same day the error was recognized. Texas RE determined that TRE_URE3 had an issue with CIP-007-3a R5.2.1 for 112 days. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The minimal risk was partially mitigated by the subject Cyber Assets residing within its own independent domain within no trust relationships with any other corporate or outside domains hence completely isolating the access control of the devices from all other networks. Further, the functionality of the subject devices are limited and do not control the functionality of any critical operating system equipment. Lastly, TRE_URE3 has an implemented and documented User Account, Authentication and Password Management procedure that has been in place since the Standard’s enforceable date that addresses password management. | To mitigate this issue, TRE_URE3: 1) disabled the remote login capability of the subject remote accounts; 2) modified the Master Asset Inventory list to include columns to track the presence of local accounts on devices; 3) assigned ownership to Process Documents to appropriate Subject Matter Experts (SMEs) which includes responsibility for reviewing the documents annually, updating as necessary and communicating updates to the Support Team; 4) implemented an acknowledgement process for all new or updated Process Documents, which includes proving red-line copy changes and requires written acknowledgement of review and comprehension; 5) conducted an assessment of all existing baselines to validate inclusion of local account information and updated as necessary; 6) modified the Checklist for adding and removing new CCAs, PCAs to its infrastructure to improve the language around default accounts. Previous language only indicated factory default accounts should be deleted and did not specify actions to take if that was not possible. The new language provides guidance related to deletion/disabling of factory default accounts, provisioning of user access to such accounts and validation of default account password changes; and 7) conducted a training session with Support Team members addressing compliance challenges specific to discrete hardware devices with integrated firmware. Texas RE has verified the completion of all mitigation activity.
2014-02-27 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2013012865 | CIP-004-3a | R4 | WECC_URE1 submitted a Self-Report to WECC stating that it had an issue with CIP-004-3a R4. Specifically, WECC_URE1 had recently hired one employee to work within its generation dispatch department and had given the employee physical access to Critical Cyber Assets. Furthermore, after access was granted WECC_URE1 failed to update its Critical Cyber Asset access list within seven days. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Specifically, the Physical Security Perimeter (PSP) in scope has personnel on staff 24 hours a day 7 days a week that would recognize and report any suspicious activity. Additionally, the PSP is monitored with security cameras and only allows personnel that have been granted access via an authorized ID badge. Furthermore, WECC_URE1 implemented detective and corrective controls. Specifically, the devices that are located within the Electronic Security Perimeter (ESP) in scope are password protected and would initiate alerts and lock out the accounts if the threshold of unauthorized attempts occurred. WECC_URE1 also performs periodic audits of its access list to ensure the list is up to date and discovery of the present issue was a result of these audits. Moreover, if WECC_URE1 were to lose visibility of its systems they would initiate its recovery plan within one hour of the incident. Finally, WECC_URE1 implemented compensating controls. Specifically, the individual in scope had Critical Infrastructure Protection (CIP) training, a valid Personnel Risk Assessment and was authorized to access Critical Cyber Assets. | To mitigate this issue, WECC_URE1: 1) updated its Critical Cyber Asset access list; and 2) updated its notification system to alert and identify for CIP setup notifications. WECC has verified the completion of all mitigation activity.
2014-02-27 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2013013132 | CIP-006-3c | R1 | WECC_URE1 submitted a Self-Report to WECC stating that it had an issue with CIP-004-3a R4. Specifically, WECC_URE1 stated that an employee was improperly authorized to have physical access to two Physical Security Perimeters (PSP) containing Critical Cyber Assets. WECC_URE1 initially believed it was appropriate to report the possible issue under CIP-004-3a R4; however, after discussions with WECC, it was determined that this possible issue was more appropriately resolved under NERC Reliability Standard CIP-006-3c R1, specifically R1.4. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Specifically, the individual in scope had a valid Personnel Risk Assessment (PRA) and Critical Infrastructure Protection (CIP) training. Furthermore, the PSPs in scope are monitored with security cameras. Additionally, WECC_URE1 implemented detective and corrective controls to detect and correct the above consequence. Specifically, the devices that are located within the PSPs are monitored by the SCADA Control Center, and alerts would be received if these devices go offline. The devices in scope are also password protected and would initiate alerts and lock out the accounts if the threshold of unauthorized attempts occurred. | To mitigate this issue, WECC_URE1: 1) revoked the employee's access to two PSPs containing Critical Cyber Assets; and 2) updated its notification system to alert and identify for CIP setup notifications. WECC has verified the completion of all mitigation activity.
2014-02-27 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2012010848 | CIP-004-3 | R3 | WECC_URE2 submitted a Self-Report to WECC stating that it had an issue with CIP-004-3 R3. Specifically, WECC_URE2 failed to conduct a personnel risk assessment (PRA) for one employee who was granted access to a Physical Security Perimeter (PSP). The employee’s access was revoked eight days later until WECC_URE2 could conduct a PRA. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. As compensating measures, the employee had physical access only to the PSP and had completed WECC_URE2’s CIP-004 R2 training. Also, access was only granted for 8 days. Additionally, WECC_URE2 had implemented the protections of CIP-003 through CIP-009 at its PSPs, to provide security measures to CCAs, ACMs, and cyber assets. | To mitigate this issue, WECC_URE2: 1) revoked physical access to its PSP for one employee until it could conduct a PRA; and 2) reviewed procedures and work flow diagrams to validate the procedures are still intact and updated internal request, transfer, and termination access forms. WECC has verified the completion of all mitigation activity.
2014-01-30 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2013013134 | CIP-006-3c | R1; R1.6.2 | FRCC_URE1 submitted a Self-Report stating that it had an issue of CIP-006-3c R1.6.2. FRCC_URE1 failed to maintain continuous escorted access within the Physical Security Perimeter (PSP) for a single visitor. FRCC_URE1 had a visitor to the primary control center logged into the visitor log and assigned an escort. The visitor was escorted to a conference room within the PSP and told not to leave the room without an escort. The escort left the visitor unescorted in the conference room. An individual on the next shift discovered the unescorted visitor and the new shift supervisor assigned a new escort to the visitor for the remainder of their time within the PSP. The visitor was left unattended for between one hour and thirty minutes, and one hour and forty-five minutes. The cause of the possible violation was the employee’s failure to follow the documented and distributed procedure which required that escorts remain with visitors at all times while within a PSP. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Critical Cyber Assets (CCAs) located within the defined PSP were located behind an additional layer of doors with additional card reader access required. The visitor did not have physical access to the CCAs. The visitor had previously taken the required training and had a valid personnel risk assessment on file. | To mitigate this violation, FRCC_URE1: 1) assigned a new escort to the visitor for the remainder of their time in the PSP; and 2) advised the original escort of their failure to follow the proper procedures regarding visitor access and the requirement for escorts. FRCC has verified the completion of all mitigation activity.
2014-01-30 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2013011719 | CIP-004-3 | R4; R4.1; R4.2 | MRO_URE1 submitted a Self-Report stating that it had an issue with CIP-004-3 R4 because it did not maintain its list of personnel with authorized cyber or authorized unescorted physical access to Critical Cyber Assets, including specific electronic and physical access rights to Critical Cyber Assets. Two MRO_URE1 employees were improperly granted access to two physical security perimeters containing Critical Cyber Assets. Unauthorized access was granted as a result of an employee who did not follow MRO_URE1's access request procedures. The error was discovered during MRO_URE1's quarterly access review and access was revoked for the employees. The two individuals who had unauthorized access represent less than five percent of authorized personnel with access to Critical Cyber Assets. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). MRO_URE1's two employees who had unauthorized access to two physical security perimeters did not access the physical security perimeters. Further, these two employees were authorized to grant access to Critical Cyber Assets. As a result, actual and potential risk to the BPS was minimal. | To mitigate this issue, MRO_URE1: 1) revoked access for both employees; and 2) retrained the employee who did not follow MRO_URE1's access request procedures. MRO has verified the completion of all mitigation activity.
2014-01-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2013012964 | CIP-004-3 | R4; R4.2 | NPCC_URE1 submitted a self-report to NPCC that it had an issue with CIP-004-3 R4. The contract company did not inform NPCC_URE1 when an on-call contractor with unescorted physical access to a data center containing critical cyber assets (CCAs) voluntarily separated from the contract company. As a result, the company was not aware that the unescorted physical access was no longer needed and did not remove the access within 7 days. | The issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The CCAs which this contractor had unescorted physical access are not used in the real-time operation of the BPS. The contractor only had unescorted physical access to one particular data center. With only physical access and no cyber access, an attack on the CCAs would not impact operation of the BPS, but would limit monitoring and logging of substation data to local substation access. A backup server is located at a sister site in the event of a loss at the primary data center. The contractor would need to be called in by the entity contact if there were repair issues and check in with the network operator upon entering the data center. Review of access logs show that the last access by the contractor matches the date of a known service call. No access attempts were made after that date. The contractor voluntarily separated from the company and had an up-to-date personal risk assessment. | To mitigate this issue, NPCC_URE1: 1) revoked unescorted physical access for the contractor 2) implemented weekly confirmation of vendor/contractor access needs for company IT Physical Security Perimeters until long term solution is in place 3) investigated and evaluated additional vendor/contractor physical access controls for approval by the Vice President of Physical and Cyber Security. The plan is to reduce the number of unescorted contractors in Data Centers to those with a defined business need for a defined period of time. All other contractors (such as on-call service vendors) will have to be escorted while on site. 4) created and implemented a new policy that internally enforce two profiles. The profiles reduce the number of unescorted contractors in Data Centers to those with a defined business need for a defined period of time. All other contractors (such as on-call service vendors) will have to be escorted while on site. The policy requires supervisors to review contract requirements with the contract company manager. The contracts require timely notification when contractor employees with access are terminated. The policy was communicated to staff by email.
2014-01-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 2 (NPCC_URE2) | NCRXXXXX | NPCC2013011740 | CIP-006-1 | R1; R1.8 | NPCC_URE2 submitted a Self-Report stating that it had an issue with CIP-006-1 R1. NPCC_URE2 was notified that a possible noncompliance of CIP-006 R2 was found for a physical security access system which is also used by NPCC_URE2 to ensure compliance with CIP-006. Specifically, the physical security access panels, located within the Critical Asset facility, which authorize and/or log access to the Physical Security Perimeter should be afforded the protective measures specified in CIP-006 R2. | The issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The access panels in question are located within locked cabinets of the PSP. Access to the locked cabinets is restricted to a small group of Corporate Security personnel. Moreover, at all times, the physical access to NPCC_URE2’s facilities is safeguarded by multiple security mechanisms in addition to card reader systems, including security guards and video cameras. In the event of a failure of the Physical Access Control System, it is NPCC_URE2’s policy to physically man the affected PSPs to control and monitor physical access. | To mitigate this issue, NPCC_URE2: 1) created a document used to develop a project to afford the protective measures specified in CIP-006-3 R2 to the local security access panels; 2) created a gap analysis document for the protection of the physical security access panels according to CIP-006-3 R2, R2.1, and R2.2; 3) provided a project status update to NPCC regarding affording the protective measures listed in CIP-006-3 R2 to the local security access panels. To mitigate this violation, NPCC_URE2 will complete the following mitigation activity within 90 days. 1) confirm that the local security access panels have been afforded the protective measures specified in CIP-006-3 R2; 2) complete a gap analysis document for the protection of the physical security access panels according to CIP-006-3 R2, R2.1, and R2.2.
2014-01-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 3 (NPCC_URE3) | NCRXXXXX | NPCC2013013264 | CIP-007-3a | R3; R3.1 | During a Compliance Audit, NPCC determined that NPCC_URE3 had an issue with CIP-007-3a R3. NPCC_URE3 failed to assess security patches and security upgrades for applicability within thirty calendar days of availability of the patches or upgrades. During the period that the patches were released, the person responsible for reviewing those patches was on extended sick leave. NPCC_URE3 did not have sufficient internal controls to ensure that the patches were reviewed. | The issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The security patches were applicable to Cyber Assets running an operating system within the Electronic Security Perimeter. None of the Cyber Assets within the ESP had control functions over critical assets nor were they required for the reliable operation of any Critical Assets. The security patches were evaluated within a few months of availability. NPCC_URE3 restricted physical access to cyber assets due to their location within NPCC_URE3's physical security perimeter. None of the cyber assets could be accessed remotely from the internet. Compensatory measures in place included the blocking of all User Datagram Protocol traffic originating outside of the ESP by the firewall which was the only access point to the ESP. | To mitigate this issue, NPCC_URE3: 1) shared the responsibility to review security patches with other staff; 2) notified the Senior Manager responsible for CIP of periodic patch reviews; 3) added the patch review task to the recurring task scheduling process to ensure that it is completed; and 4) implemented a new security patch management system which generates patch reports weekly and sends to multiple personnel for review.
2014-01-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 4 (NPCC_URE4) | NCRXXXXX | NPCC2013011948 | CIP-006-1 | R1; R1.8 | NPCC_URE4 submitted a Self-Report stating that it had an issue with CIP-006-1 R1. NPCC_URE4 was notified that a possible noncompliance of CIP-006 R2 was found for a physical security access system which is also used by NPCC_URE4 to ensure compliance with CIP-006. Specifically, the physical security access panels, located within the Critical Asset facility, which authorize and/or log access to the Physical Security Perimeter should be afforded the protective measures specified in CIP-006 R2. | The issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The access panels in question are located within locked cabinets of the PSP. Access to the locked cabinets is restricted to a small group of Corporate Security personnel. Moreover, at all times, the physical access to NPCC_URE4’s facilities is safeguarded by multiple security mechanisms in addition to card reader systems, including security guards and video cameras. In the event of a failure of the Physical Access Control System, it is NPCC_URE4’s policy to physically man the affected PSPs to control and monitor physical access. | To mitigate this issue, NPCC_URE4: 1) created a document used to develop a project to afford the protective measures specified in CIP-006-3 R2 to the local security access panels; 2) created a gap analysis document for the protection of the physical security access panels according to CIP-006-3 R2, R2.1, and R2.2; 3) provided a project status update to NPCC regarding affording the protective measures listed in CIP-006-3 R2 to the local security access panels. To mitigate this violation, NPCC_URE4 will complete the following mitigation activity within 90 days. 1) confirm that the local security access panels have been afforded the protective measures specified in CIP-006-3 R2; 2) complete a gap analysis document for the protection of the physical security access panels according to CIP-006-3 R2, R2.1, and R2.2.
2014-01-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 5 (NPCC_URE5) | NCRXXXXX | NPCC2012011628 | CIP-006-1 | R1; R1.8 | Compliance Audit, NPCC determined that NPCC_URE5 had an issue with CIP-006-1 R1. The physical security access panels, located within the Critical Asset facility, which authorize and/or log access to the Physical Security Perimeter (PSP) should be afforded the protective measures specified in CIP-006 R2. | The issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The access panels in question are located within locked cabinets of the PSP. Access to the locked cabinets is restricted to a small group of Corporate Security personnel. Moreover, at all times, the physical access to NPCC_URE5’s facilities is safeguarded by multiple security mechanisms in addition to card reader systems, including security guards and video cameras. In the event of a failure of the Physical Access Control System, it is NPCC_URE5’s policy to physically man the affected PSPs to control and monitor physical access. | To mitigate this issue, NPCC_URE5: 1) created a document used to develop a project to afford the protective measures specified in CIP-006-3 R2 to the local security access panels; 2) created a gap analysis document for the protection of the physical security access panels according to CIP-006-3 R2, R2.1, and R2.2; 3) provided a project status update to NPCC regarding affording the protective measures listed in CIP-006-3 R2 to the local security access panels. To mitigate this violation, NPCC_URE5 will complete the following mitigation activity within 90 days. 1) confirm that the local security access panels have been afforded the protective measures specified in CIP-006-3 R2; 2) complete a gap analysis document for the protection of the physical security access panels according to CIP-006-3 R2, R2.1, and R2.2.
2014-01-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 6 (NPCC_URE6) | NCRXXXXX | NPCC2013011779 | CIP-004-3 | R4; 4.1, 4.2 | NPCC_URE6 submitted a Self-Report stating that it had an issue with CIP-004-3 R4. NPCC_URE6 was notified by the vendor that one of their employees was no longer employed by the vendor. The contractor remained on NPCC_URE6's list that had authorized unescorted access to the facility until he was removed from that list. The need to remove the contractor from the list was not communicated by the vendor prior to this period. NPCC_URE6 did not update the list of that had authorized unescorted access within seven days of the change. | The issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). During this period, the access logs show that the contractor did not attempt to or access the facility's ACS. In addition, the standard practice of this NPCC_URE6 facility is to disable all vendor badges (though not physically collected from the individuals) at the completion of their assigned on-site activities. The vendor employee's badge was disabled by NPCC_URE6's security following his departure from NPCC_URE6's site which was a month prior to his voluntary departure from the vendor. The vendor informed NPCC_URE6 that they took possession of the vendor employee's deactivated NPCC_URE6 ID badge and destroyed it at the time of separation. Logs directly indicated that this individual's badge was disabled and was not re-activated up until the date this was discovered. | To mitigate this issue, NPCC_URE6: 1) contacted all vendors/contractors with employees on NPCC_URE6's authorized list with CCA access to confirm employment status; 2) conducted a review of NPCC_URE6's access control procedures associated with maintaining NPCC_URE6's list with authorized CCA access and modify as needed; 3) provided training to staff responsible for the implementation of NPCC_URE6's access control procedures; 4) formalized the reporting requirement for changes in employee status with existing vendor/contractor service providers who employees require unescorted access to NPCC_URE6's CCAs; and 5) reviewed and revised NPCC_URE6's standard contractual documents.
2014-01-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 6 (NPCC_URE6) | NCRXXXXX | NPCC2013012749 | CIP-006-3c | R4. | NPCC_URE6 submitted a Self-Report stating that it had an issue with CIP-006-3c R4. An employee arrived at the security building and requested a temporary access badge to enter the facility since he had left his assigned access badge at home. The security staff on duty authorized the employees temporary badge with access above the employee's existing authorized Physical Security Perimeter (PSPs) access rights. The Security Supervisor identified the issue and promptly revoked the unauthorized physical access rights. The employee was inadvertently provided a temporary access badge with authorized physical access rights above their authorized physical rights for a short duration. | The issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). During the period in question, the access logs show that the employee did not attempt to or access the any of the facility's PSPs that were above his existing authorized physical access rights. In addition, the involved employee has a valid seven year personal risk assessment and a valid mandatory CIP training course certification. The employee did not have electronic access. | To mitigate this issue, NPCC_URE6: 1) revoked the unauthorized access to the employee; 2) reviewed the applicable NPCC_URE6 procedures and expectations for issuance of access rights to PSPs with the security staff involved; and 3) initiated a disciplinary process for those employees involved in the incident.
2014-01-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 7 (NPCC_URE7) | NCRXXXXX | NPCC2013013055 | CIP-004-3 | R4; R4.2 | During a Compliance Audit, NPCC determined that NPCC_URE7, had an issue of CIP-004-3 R4. The contract company did not inform NPCC_URE7 when an on-call contractor with unescorted physical access to a data center containing critical cyber assets (CCAs) voluntarily separated from the contract company. As a result, the company was not aware that the unescorted physical access was no longer needed and did not remove the access within 7 days. | The issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The CCAs which this contractor had unescorted physical access are not used in the real-time operation of the BPS. The contractor only had unescorted physical access to one particular data center. With only physical access and no cyber access, an attack on the CCAs would not impact operation of the BPS, but would limit monitoring and logging of substation data to local substation access. A backup server is located at a sister site in the event of a loss at the primary data center. The contractor would need to be called in by the entity contact if there were repair issues and check in with the network operator upon entering the data center. Review of access logs show that the last access by the contractor matches the date of a known service call. No access attempts were made after that date. The contractor voluntarily separated from the company and had an up-to-date personal risk assessment. | To mitigate this issue, NPCC_URE7: 1) revoked unescorted physical access for the contractor; 2) implemented weekly confirmation of vendor/contractor access needs for company IT Physical Security Perimeters until long term solution is in place; 3) investigated and evaluated additional vendor/contractor physical access controls for approval by the Vice President of Physical and Cyber Security. The plan is to reduce the number of unescorted contractors in Data Centers to those with a defined business need for a defined period of time. All other contractors (such as on-call service vendors) will have to be escorted while on site; 4) created and implemented a new policy that internally enforce two profiles. The profiles reduce the number of unescorted contractors in Data Centers to those with a defined business need for a defined period of time. All other contractors (such as on-call service vendors) will have to be escorted while on site. The policy requires supervisors to review contract requirements with the contract company manager. The contracts require timely notification when contractor employees with access are terminated. The policy was communicated to staff by email.
2014-01-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 8 (NPCC_URE8) | NCRXXXXX | NPCC2013012965 | CIP-004-3 | R4; R4.2 | NPCC_URE8 submitted a self-report to NPCC that it had an issue with CIP-004-3 R4. The contract company did not inform NPCC_URE8 when an on-call contractor with unescorted physical access to a data center containing critical cyber assets (CCAs) voluntarily separated from the contract company. As a result, the company was not aware that the unescorted physical access was no longer needed and did not remove the access within 7 days. | The issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The CCAs which this contractor had unescorted physical access are not used in the real-time operation of the BPS. The contractor only had unescorted physical access to one particular data center. With only physical access and no cyber access, an attack on the CCAs would not impact operation of the BPS, but would limit monitoring and logging of substation data to local substation access. A backup server is located at a sister site in the event of a loss at the primary data center. The contractor would need to be called in by the entity contact if there were repair issues and check in with the network operator upon entering the data center. Review of access logs show that the last access by the contractor matches the date of a known service call. No access attempts were made after that date. The contractor voluntarily separated from the company and had an up-to-date personal risk assessment. | To mitigate this issue, NPCC_URE8: 1) revoked unescorted physical access for the contractor; 2) implemented weekly confirmation of vendor/contractor access needs for company IT Physical Security Perimeters until long term solution is in place; 3) investigated and evaluated additional vendor/contractor physical access controls for approval by the Vice President of Physical and Cyber Security. The plan is to reduce the number of unescorted contractors in Data Centers to those with a defined business need for a defined period of time. All other contractors (such as on-call service vendors) will have to be escorted while on site; 4) created and implemented a new policy that internally enforce two profiles. The profiles reduce the number of unescorted contractors in Data Centers to those with a defined business need for a defined period of time. All other contractors (such as on-call service vendors) will have to be escorted while on site. The policy requires supervisors to review contract requirements with the contract company manager. The contracts require timely notification when contractor employees with access are terminated. The policy was communicated to staff by email.
2014-01-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 9 (NPCC_URE9) | NCRXXXXX | NPCC2012011590 | CIP-005-3a | R1. | During a Compliance Audit, NPCC determined that NPCC_URE9 had an issue with CIP-005-3a R1. NPCC_URE9 has network switches that are Critical Cyber Assets (CCA). These switches reside within the Control Center ESP. However, their management interfaces are outside the ESP. All traffic from the ESP VLANs to the 102 VLAN must pass through an ESP access point (a firewall). These switches, which are CCAs, do not fully reside within an ESP as required by R1. Additionally, The electronic access monitoring and logging devices were afforded all of the protections required by R1.5 except some of the devices (such as the centralized log server) were not included in the scope of a Cyber Vulnerability Assessment (CVA). | The issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Although the management interfaces on these switches are outside the ESP, these switches do not perform any routing, i.e., they are pure layer two switches. Any traffic traveling to/from the management interface and the switches in the ESP must be routed by the ESP access point, which performs electronic access control as required by CIP-005-3a. Further, the management interface is within a protected segment of NPCC_URE9's network. There is a firewall between this protected segment of the network and NPCC_URE9's corporate network. Also, the network switches require two-factor authentication for all logins and all logins are monitored, and logged. The Primary Control Center and Backup Control Center ESPs have redundant network paths, and NPCC_URE9 could quickly switch over to the Backup Control Center if the Primary Control Center were compromised. The cyber assets that were not included in the CVA are maintained in a separate DMZ network segment which is protected by a firewall and not exposed to the internet. These assets reside in a controlled 6-wall perimeter and require two-factor authentication to gain remote access. Personnel with access to these devices are background checked and complete NERC CIP training. Furthermore, NPCC_URE9's future CVAs includes the cyber assets. NPCC_URE9 removed the cyber assets with the replacement of their SCADA system. | To mitigate this issue NPCC_URE9: 1) replaced their SCADA architecture which eliminates their current configuration 2) added the devices to future CVAs.
2014-01-30 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2011008514 | CIP-006-1 | R3 | During a Compliance Audit conducted from October 17, 2011 through November 4, 2011, SERC determined that SERC_URE1 had an issue with CIP-006 R3 because it failed to implement monitoring and alarming on a single physical access control point to the Physical Security Perimeter (PSP). During the onsite audit, the SERC audit team identified an access point to the PSP that did not alarm and did not provide immediate notification when forced open. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC_URE1 had multiple layers of physical security in place. The site was surrounded by fencing topped by barbed wire or pikes and pedestrian and vehicular access to the site was gated and monitored. The site and the door in question were equipped with closed circuit television and monitored by multiple personnel onsite and offsite twenty-four hours a day, seven days a week. The door in question led to a loading dock area, which was protected by badge readers. | To mitigate this issue, SERC_URE1: 1) Installed parts to enhance alarming on door activity; and 2) Tested to confirm that the door immediately alerts response personnel when opened without badge access. 3) Conducted a comprehensive review of its facilities to ensure that there were no other doors with the same issue.
2014-01-30 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE2013012932 | CIP-006-3c | R2; R2.2 | TRE_URE1 submitted a Self-Report during the Self-Certification period stating that it had an issue with CIP-006-3c R2.2. TRE_URE1 reported that it failed to afford the protective measures specified in CIP-007 R3.1. Specifically, TRE_URE1 did not assess and document security patches for the operating system of its physical security system, primarily due to the loss of several personnel. After a review of the documentation provided by TRE_URE1, Texas RE determined that TRE_URE1 failed to assess and document several security patch assessments within thirty days as required by CIP-007, R3.1 and as outlined in its corresponding procedure. Texas RE determined the issue duration period to be for approximately 10 months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The minimal risk was partially mitigated by the small number of assessments impacted, the subject physical security system has always been provided the required protective measures, and it is an isolated system which resides behind its own firewall. This isolated system is not located in the Electronic Security Perimeter and is not directly connected with any systems influencing BPS reliability. Further, TRE_URE1 has had a documented Security Patch Management Program since the Standard’s enforceable date that addresses the 30 day security patch assessment documentation requirement. Lastly, no issues were revealed and no breaches were reported due to the delayed documentation assessment. | To mitigate this issue, TRE_URE1: 1) reviewed and assessed the security patch applications; 2) started including security patch assessment training as part of its bi-weekly patch assessment meeting for NERC systems; and 3) placed a focus on using its current procedures and training more team members in the patch assessment program. Texas RE has verified the completion of all mitigation activity.
2014-01-30 | TRE_URE1liability Entity (TRE_URE1) | Unidentified Registered Entity 2 (TRE_URE2) | NCRXXXXX | TRE2013012887 | CIP-006-3c | R2; R2.2 | TRE_URE2 submitted a Self-Report during the Self-Certification period stating that it had an issue with CIP-006-3c R2.2. TRE_URE2 reported that it failed to afford the protective measures specified in CIP-007 R3.1. Specifically, TRE_URE2 did not assess and document security patches for the operating system of its physical security system, primarily due to the loss of several personnel. After a review of the documentation provided by TRE_URE2, TRE_URE1 determined that TRE_URE2 failed to assess and document several security patch assessments within thirty days as required by CIP-007, R3.1 and as outlined in its corresponding procedure. TRE_URE1 determined the issue duration period to be for approximately 10 months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The minimal risk was partially mitigated by the small number of assessments impacted, the subject physical security system has always been provided the required protective measures, and it is an isolated system which resides behind its own firewall. This isolated system is not located in the Electronic Security Perimeter and is not directly connected with any systems influencing BPS reliability. Further, TRE_URE2 has had a documented Security Patch Management Program since the Standard’s enforceable date that addresses the 30 day security patch assessment documentation requirement. Lastly, no issues were revealed and no breaches were reported due to the delayed documentation assessment. | To mitigate this issue, TRE_URE2: 1) reviewed and assessed the security patch applications; 2) started including security patch assessment training as part of its bi-weekly patch assessment meeting for NERC systems; and 3) placed a focus on using its current procedures and training more team members in the patch assessment program. TRE_URE1 has verified the completion of all mitigation activity.
2014-01-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2013012290 | CIP-005-1 | R3 | During a Compliance Audit, WECC determined that WECC_URE1 had an issue of CIP-005-1 R3. Specifically, it was determined that seven Electronic Access and Control and Monitoring (EACM) devices did not technically support monitoring and logging access. In addition, WECC_URE1 had failed to file Technical Feasibility Exceptions (TFE) for the seven EACM devices by the due date for submitting TFE Requests. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Specifically, the external interactive access to the devices requires strong authentication. Furthermore, the devices are located within a Physical Security Perimeter (PSP) accessible only by individuals who have received proper training and who are authorized to access Critical Cyber Assets. Moreover, a cyber-vulnerability assessment is conducted annually to verify that ports and services only required for operation are enabled on the devices. Finally, all network traffic is monitored for indications of nefarious activity. The system security logs of these devices are reported to a central security event monitoring system which provides correlation of security data from the various sources and provides ranking and alerting for suspicious activity. | To mitigate this issue, WECC_URE1: 1) submitted TFEs that included the devices in question. TFE# 2013-WECC-TFE02206; TFE# 2013-WECC-TFE02377; TFE#2013-WECC-TFE02378. WECC approved the associated TFEs.
2014-01-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2013012227 | CIP-007-3a | R3 | During a Compliance Audit, WECC determined that WECC_URE1 had an issue of CIP-007-3a R3. Specifically, WECC determined that it was technically infeasible for WECC_URE1 to apply proper security patch management on 12 devices. In addition, WECC_URE1 had failed to file Technical Feasibility Exceptions (TFE) for the 12 devices by the due date for submitting TFE Requests. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Specifically, the external interactive access to the devices requires strong authentication. Furthermore, the devices are located within a Physical Security Perimeter (PSP) accessible only by individuals who have received proper training and who are authorized to access Critical Cyber Assets. Moreover, a cyber-vulnerability assessment is conducted annually to verify that ports and services only required for operation are enabled on the devices. Finally, all network traffic is monitored for indications of nefarious activity. The system security logs of these devices are reported to a central security event monitoring system which provides correlation of security data from the various sources and provides ranking and alerting for suspicious activity. | To mitigate this issue, WECC_URE1: 1) submitted TFEs that included the devices in question. 2013-WECC-TFE02208 WECC approved the associated TFEs.
2014-01-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2013012228 | CIP-007-3a | R4 | During a Compliance Audit, WECC determined that WECC_URE1 had an issue of CIP-007-3a R4. Specifically, WECC determined that it was technically infeasible for WECC_URE1 to implement antivirus and anti-malware software on 31 devices. In addition, WECC_URE1 had failed to file Technical Feasibility Exceptions (TFE) for the 31 devices by the due date for submitting TFE Requests. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Specifically, the external interactive access to the devices requires strong authentication. Furthermore, the devices are located within a Physical Security Perimeter (PSP) accessible only by individuals who have received proper training and who are authorized to access Critical Cyber Assets. Moreover, a cyber-vulnerability assessment is conducted annually to verify that ports and services only required for operation are enabled on the devices. Finally, all network traffic is monitored for indications of nefarious activity 24 hours a day 7 days a week and suspicious activity is analyzed and ranked based on severity and automated alerts are generated the system security logs of these devices are reported to a central security event monitoring system which provides correlation of security data. | To mitigate this issue, WECC_URE1: 1) submitted TFEs that included the devices in question. 2013-WECC-TFE02209; 2013-WECC-TFE02210; 2013-WECC-TFE02211; 2013-WECC-TFE02212; 2013-WECC-TFE02218; 2012-WECC-TFE02151 WECC approved the associated TFEs.
2014-01-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2013012229 | CIP-007-3a | R6 | During a Compliance Audit, WECC determined that WECC_URE1 had an issue of CIP-007-3a R6. Specifically, WECC determined that it was technically infeasible for WECC_URE1 to implement automated tools or organizational process controls to monitor system events related to cyber security on 26 devices. In addition, WECC_URE1 had failed to file Technical Feasibility Exceptions (TFE) for the 26 devices by the due date for submitting TFE Requests. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Specifically, the external interactive access to the devices requires strong authentication. Furthermore, the devices are located within a Physcial Security Perimeter (PSP) accessible only by individuals who have received proper training and who are authorized to access Critical Cyber Assets. Moreover, a cyber-vulnerability assessment is conducted annually to verify that ports and services only required for operation are enabled on the devices. Finally, all network traffic is monitored for indications of nefarious activity 24 hours a day 7 days a week and suspicious activity is analyzed and ranked based on severity and automated alerts are generated the system security logs of these devices are reported to a central security event monitoring system which provides correlation of security data. | To mitigate this issue, WECC_URE1: 1) submitted TFEs that included the devices in question. 2013-WECC-TFE02213; 2013-WECC-TFE02216; 2013-WECC-TFE02215-1; 2013-WECC-TFE02214-1; 2013-WECC-TFE02376; 2013-WECC-TFE02379. WECC approved the associated TFEs.
2014-01-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2013013013 | CIP-007-3a | R3 | WECC_URE2 submitted a Self Report to WECC stating that it had an issue with CIP-007-3a R3. Specifically, WECC_URE2 had failed to properly document mitigating factors for the Remote Terminal Unit (RTU) device that was not capable of having security patches installed as required by the Standard. Furthermore, WECC_URE2 had failed to file quarterly updates for this TFE for the first three quarters of the calendar year. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Specifically, the RTU has the latest anti-virus and malware software, which monitor the device for malicious signatures, new users and services. Also, the RTU is configured to run in kiosk mode so users cannot access the Operating system. Furthermore, all unnecessary TCP/IP ports and services have been disabled. Additionally, WECC_URE2 has multiple backup devices that provide the same functions as the RTU. WECC_URE2 has a control board to control all circuit breakers in the switchyard and an annunciator to annunciate all station alarms. Moreover, WECC_URE2 stated that if the primary RTU was turned off or compromised the energy control center would implement procedures to pull info from the backup. Finally, the RTU device was physically secured, and could only be unlocked with a special key. | To mitigate this issue, WECC_URE2: 1) implemented additional protections and achieved strict compliance; 2) filed its amended TFE and included the RTU device involved
2014-01-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2013012969 | CIP-007-3a | R5 | WECC_URE3 submitted a Self Report to WECC stating that it had an issue with CIP-007-3a R5. Specifically, WECC_URE3 reported that two trainees were permitted to sit at the controls and perform certain duties within WECC_URE3’s secure Electronic Security Perimeter (ESP). WECC_URE3 reported that the two individuals were not authorized to have access to the ESP prior to being allowed access to the ESP. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Specifically, the trainees were not given the password to the shared account in scope, and were only permitted to sit at the controls and perform certain duties within the ESP under the supervision of Operator Maintenance Journeymen. Also, each of the trainees had NERC Critical Infrastructure Protection training and a valid Personnel Risk Assessment, and authorized unescorted physical access to the Physical Security Perimeter (PSP). Furthermore, WECC_URE3 implemented detective and corrective controls. Specifically, the devices in scope are monitored 24 hours a day 7 days a week and are programmed to alert if potential security events occurred. Additionally, each of the devices has anti-malware. These controls would have issued alerts to personnel if the trainees had downloaded or installed malicious content to the devices. Finally, WECC_URE3 has an automated backup and recovery system that would be able to rebuild a hard drive within 2 hours if an issue had occurred. | To mitigate this issue, WECC_URE3: 1) compliance staff intervened and prevented the two trainees from accessing the ESP; 2) conducted additional training to ensure that all employees understand the requirements of CIP-007-3a; and 3) granted the two trainees authorized access to its ESPs.
2014-01-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC2013013103 | CIP-007-3a | R4 | WECC_URE4 submitted a Self Report to WECC stating that it had an issue with CIP-007-3a R1. WECC_URE4 reported that on the first Sunday of every month it received updates for its anti-virus and malware prevention systems. WECC_URE4 reported that after the updates were received, the updates were placed in a test environment and tested to ensure that all updates functioned appropriately. WECC_URE4 stated that after 14 days in the test environment the updates were automatically released into the production environment. WECC_URE4 reported that this process occurred in July; however, WECC_URE4 stated that the individual responsible for overseeing the test phase of the updates was out of town and thus proper tests were not performed on the updates prior to the updates being automatically released into the system. After discussions with WECC_URE4 staff, WECC determined that the possible violation was more appropriately resolved under CIP-007-3a Requirement 4, than the reported CIP-007-3a R1, because the possible issue was more closely related to WECC_URE4’s failure to properly implement its process for testing updates to its anti-virus and malware prevention “signatures.” | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Specifically, all the devices potentially affected by the issue are backed up and are able to be restored per WECC_URE4’s Disaster Recovery Plan. Additionally, the .dat files (signature update files) were from a trusted vendor and WECC_URE4 deploys updates of this nature on a monthly recurring basis. | To mitigate this issue, WECC_URE4: 1) revised its procedures to require its personnel to manually release all .dat files after proper testing had been performed in the test environment.
2014-01-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 5 (WECC_URE5) | NCRXXXXX | WECC2013012936 | CIP-007-3 | R2 | WECC_URE5 submitted a Self Report to WECC stating that it had an issue with CIP-007-3 R2. Specifically, WECC_URE5 failed to file Technical Feasibility Exceptions (TFE) for four devices on which ports and services not required for normal or emergency operations were enabled. On June 30, WECC_URE5 terminated that TFE. Although WECC_URE5 amended an existing TFE, 2011-WECC-TFE01520, to cover some devices originally included in the scope of 2010-WECC-TFE00542, four devices were inadvertently excluded from the amended TFE filing. On July 23, WECC_URE5 submitted a second TFE amendment, 2011-WECC-TFE01520-1, that included the four devices. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Physical and electronic access to the devices was controlled. Each of the four devices was secured within an Electronic Security Perimeter (ESP). Electronic access to the devices was, therefore, controlled, logged and monitored. Unauthorized electronic access attempts would have triggered alarming. The devices were physically secured in a Physical Security Perimeter (PSP). Physical access to the devices was also logged, controlled and monitored on a 24/7 basis. Individuals with physical and/or electronic access to the devices completed Personnel Risk Assessments, and Cyber Security Training. | To mitigate this issue, WECC_URE5: 1)submitted an amended TFE 2011-WECC-TFE01520-1, to include four devices. WECC has approved the amended TFE.
2014-01-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 6 (WECC_URE6) | NCRXXXXX | WECC2013013193 | CIP-004-3a | R3 | WECC_URE6 submitted a Self Report to WECC stating that it had an issue with CIP-004-3a R3. Specifically, WECC_URE6 reported that one employee failed to have a Personnel Risk Assessment (PRA) renewed within seven years as required by the Standard. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Specifically, the employee in scope is a long term employee at WECC_URE2 and had CIP training and a prior PRA. In addition, the Control Center was staffed 24 hours a day 7 days a week by personnel in positions where attempted access to Critical Cyber Assets would be detected. Furthermore, the employee involved had only physical access to Critical Cyber Assets and did not have logical access to these devices. | To mitigate this issue, WECC_URE6: 1) completed a PRA on the employee involved in the issue; and 2) updated its PRA process to clarify roles and responsibilities and centralized the departments managing PRA oversight. WECC has verified the completion of all mitigation activity.
2013-12-30 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2013013035 | CIP-006-3c | R1; R1.7 | During a Compliance Audit, FRCC determined that FRCC_URE1 had an issue of CIP-006-3c R1.7. FRCC_URE1 documentation supplied showed it had failed to update its Physical Security Plan within thirty calendar days of the completion of a physical security system redesign or reconfiguration. The FRCC_URE1 Physical Security Plan document states that the physical security console is located in one facility, however, FRCC_URE1 response to data request states that the physical security console consolidation moved it to another facility. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The risk was reduced because this was a documentation update stating the location that had not been corrected. Furthermore, the accompanying phone number which was cited for the security monitoring desk was correct and continued to work during and after the transition to the new location. | To mitigate this issue, FRCC_URE1 updated and approved the Physical Security Plan to correctly identify the new location of the physical security console. FRCC has verified the completion of all mitigation activity.
2013-12-30 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2013013039 | CIP-006-3c | R5 | During a Compliance Audit, FRCC determined that FRCC_URE1 had an issue of CIP-006-3c R5. FRCC_URE1 documents were insufficient evidence to demonstrate that it monitored physical access at all access points to the Physical Security Perimeter(PSPs) twenty-four hours a day, seven days a week. From the sampled PSP, all doors were tested for door forced open, door held open, and invalid badge swipe with one door failing the test for the door forced open test and door held open test. FRCC_URE1 immediately had the vendor repair the door latch on the same day discovered and provided a copy of the repair bill with successful testing results the next day. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The risk was reduced because the single door with the latch problem was inside a building that was located in a secure facility with armed guards. All other physical access points tested inside the building tested positive. FRCC_URE1 mitigated the problem in the same day by having their vendor repair the door. | To mitigate this issue, FRCC_URE1 had the vendor repair the door latch and retest which verified repair was complete. FRCC has verified the completion of all mitigation activity.
2013-12-30 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 2 (FRCC_URE2) | NCRXXXXX | FRCC2012011556 | CIP-004-3 | R4.1; R4.2 | FRCC_URE2 submitted a Self-Report stating that it had an issue of CIP-004-3 R4.1 and R4.2. FRCC_URE2 failed to remove NERC access for a transferred employee and update the personnel list of access to Critical Cyber Assets (CCAs). The request to remove access was submitted, but due to human error, was not read and processed to remove access and update the personnel list of access to CCAs until after the required date. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The risk was reduced because the employee was a long-term, trusted employee and remains a trusted employee. Additionally, their NERC Cyber training and personnel risk assessment were current. | To mitigate this violation, FRCC_URE2: 1) revoked access; 2) automated notification process for termination and transfer requests; and 3) communicated changes to relevant staff. FRCC has verified the completion of all mitigation activity.
2013-12-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2012010428 | CIP-006-3a | R2; R2.2 | During a Compliance audit, NPCC determined that NPCC_URE1 had an issue of CIP-006-3a R2. At the time of the audit, NPCC_URE1 did not provide evidence that they had performed a cyber vulnerability assessment on Digital Video Recorders (DVRs) and IP addresses for the DVRs were documented incorrectly. | The issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). NPCC_URE1 conducted vulnerability scans of the DVRs prior to their installation. The following year after installation, NPCC_URE1 conducted a vulnerability scan on the front end system which connects to the DVRs. The front end system is the only access point to the DVRs. The incorrect IP address did not affect the operation of the equipment because it was on the same network range. The DVRs are used to store the video logs of the Control Center's physical perimeters for visitor identification for analysis. If the DVRs were compromised, the intruder would have no path to the Critical Cyber Assets that monitor and control the BPS. | To mitigate this issue, NPCC_URE1: 1) corrected the IP Addresses 2) performed vulnerability scans of the actual DVRs 3) identified the DVRs in the list of Electronic Security Perimeter areas and devices scanned for vulnerability assessments. NPCC has verified the completion of all mitigation activity.
2013-12-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2013012415 | CIP-006-3a | R1.1 | On May 1, 2013, RFC_URE1 submitted a Self-Report to ReliabilityFirst stating that it had an issue with CIP-006-3a R1.1. On April 26, 2013, RFC_URE1 discovered an open area above a doorway to one of its PSPs (In November 2010, RFC_URE1 contracted with a construction company to install wire screening above the interior walls of the PSP and received an invoice from the contractor reporting that it had completed the screening in December 2010. RFC_URE1 commenced operation within the PSP under the belief that the construction company completed the fully enclosed six-walled perimeter pursuant to CIP-006-3a R1). Upon discovery of the open area RFC_URE1 conducted an inspection of all its PSPs to ensure each was fully enclosed. During the inspection, RFC_URE1 discovered that a fire damper above the drop ceiling at the same location as the opening above the doorway also did not have the required wire screening. RFC_URE1 completed the inspection of its remaining PSPs on April 30, 2013, and confirmed that no other unidentified access points exist. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following four factors. First, both openings to the PSP were above a drop ceiling and concealed from view. Second, RFC_URE1’s PSP resides within a building to which access is restricted through badges and badge readers with access privileges determined based on business needs and roles. Third, the building which contains the PSP is protected through restricted badge access at the external gates. Fourth, the PSP at issue is staffed twenty-four hours a day, seven days a week. Therefore, it is unlikely that an individual could gain undetected access to the PSP through the two openings above the drop ceiling. RFC_URE1 has two prior Alleged Violations of CIP-006 R1. However, RFC_URE1’s prior Alleged Violations of CIP-006 R1 are distinguishable and ReliabilityFirst therefore did not consider them as an aggravating factor. RFC_URE1’s prior Alleged Violations of CIP-006 R1 involved a failure to properly log the entrance and exit of two visitors into a PSP and a failure to classify and deploy CCAs within a six wall border. Neither prior Alleged Violation of CIP-006 involved unidentified access points to a PSP. | To mitigate this issue, RFC_URE1: 1) installed wire screening on the two openings above the drop ceiling; 2) completed the inspection of all its PSPs; 3) and determined no other unidentified access points exist.
2013-12-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2013012529 | CIP-004-3a | R4.1 | On May 1, 2013, RFC_URE1 submitted a Self-Report to ReliabilityFirst stating that it had an issue with CIP-004-3a R4.1. Effective January 13, 2013, a RFC_URE1 employee at a RFC_URE1 Generation Station retired and therefore no longer required access rights. On January 14, 2013, RFC_URE1 created a physical security change management ticket and a cyber-security change management ticket to revoke the retired employee's access. On January 15, 2013, RFC_URE1 revoked the employee’s physical access rights. RFC_URE1 initiated actions to remove authorized cyber access but upon verifying that the retired employee did not have cyber access through the Control Center Active Directory, the change control ticket was closed with no action taken. On March 11, 2013, during a quarterly review of access rights, RFC_URE1 discovered that the retired employee was still listed as having authorized cyber access to CCAs associated with the Generation Station through the Generation Station Active Directory. On March 11, 2013, RFC_URE1 created a new change management ticket and revoked the retired employee’s cyber access that same day. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the fact that this is solely a documentation issue. It is a documentation issue because the retired employee could not access RFC_URE1 CCAs for the duration of the issue. The retired employee did not have physical access or remote access to the CCAs in the Generation Station despite remaining on the Generation Station Active Directory. Therefore, when RFC_URE1 removed the retired employee’s physical access rights on January 15, 2013, it eliminated any opportunity for the retired employee to access the limited set of CCAs included in the Generation Station Active Directory account. | To mitigate this issue, RFC_URE1 deleted the retired employee’s Generation Station Active Directory account.
2013-12-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2013012948 | CIP-006-3c | R1 | On September 11, 2013, RFC_URE2 submitted two Self-Reports to ReliabilityFirst stating that it had two separate issues with CIP-006-1 R1, which ReliabilityFirst consolidated into one Violation ID Number, RFC2013012948. During ReliabilityFirst’s Compliance Audit of RFC_URE2, ReliabilityFirst discovered an issue with CIP-006-3c R1.1 because ReliabilityFirst discovered an Electronic Security Perimeter (“ESP”) cable that extended outside the Physical Security Perimeter (“PSP”). After performing mitigating actions to address that issue, RFC_URE2 performed a walk-down of the PSP. During the walk-down, RFC_URE2 discovered one ESP where the network data copper cables that run from the server room to the control room were not within the PSP. In September 2012, RFC_URE2 consulted with a vendor to perform an external NERC CIP compliance program assessment, which resulted in a Self-Report to ReliabilityFirst for CIP-006-3c R1. On October 1, 2012, RFC_URE2 implemented a new procedure establishing detailed inspection processes during the annual PSP verification. During the annual PSP verification, RFC_URE2 discovered a physical access point to the PSP that was not documented or remediated. The potential physical access point is an abandoned ventilation duct that penetrates the south concrete block wall of the control room. The 18-inch square gap is approximately 30 inches above the drop ceiling. The duct runs from the control room outside the PSP above the drop ceiling into a general office area. | The facts and circumstances of the cabling issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System based on the following three factors. First, physical access to the cables between the server room and the control room is restricted since the building itself is a controlled access building owned and occupied solely by RFC_URE2. Second, the control room itself is staffed 24 hours a day. Third, RFC_URE2 discovered no additional issues during its walk-down of the PSPs. The facts and circumstances of the six-wall border issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System based on the following two factors. First, the duct is located within RFC_URE2’s service center and physical access to the end of the duct outside the PSP is restricted since the building itself is a controlled access building owned and occupied solely by RFC_URE2. Second, the control room itself is staffed 24 hours a day. ReliabilityFirst determined that a monetary penalty is not warranted for this issue. This is in part based on RFC_URE2’s clear commitment to strengthening its internal controls and preventing recurrence of noncompliance. RFC_URE2 discovered the six-wall border issue as part of a voluntary comprehensive review of its physical security. Strengthening these detective controls increases the likelihood of finding any issues before they result in harm to Bulk Power System reliability. ReliabilityFirst considered whether the facts of this issue constitute a repetitive infraction. RFC_URE2 has two prior violations of CIP-006 R1. One previous violation concerned gaps in the six-wall border similar to the instant issue. The other previous violation, discovered during a Compliance Audit, was similar to and led to RFC_URE2’s discovery of the instant conduit issue. Despite these previous similar violations, ReliabilityFirst determined that a monetary penalty was not warranted based on two factors. First, as stated above, RFC_URE2 strengthened its internal controls to prevent recurrence of CIP-006 R1 noncompliance by voluntarily implementing a walk-down procedure to detect physical security issues. Second, the instant issues posed minimal risk to reliability of the Bulk Power System and essentially constitute extensions of the prior violations rather than repetitive issues. The prior and instant issues, when considered together, pose minimal risk to Bulk Power System reliability, and therefore warrant no monetary penalty and FFT treatment. | To mitigate this issue RFC_URE2 will: 1) install conduit around the cables to address the cabling issue; and 2) update its future drawings of PSPs to include and identify the existence of abandoned-in-place physical systems. RFC_URE2 installed physical barriers to close the potential physical access point.
2013-12-30 | ReliabilityFirst Corporation (ReliabilityFirst), Southwest Power Pool Regional Entity (SPP RE), Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC2013011877; SPP2013011876; TRE2013011889 | CIP-006-3c | R1 | On February 6, 2013, March 19, 2013, and April 29, 2013, RFC_URE3 submitted Self-Reports to the Regions identifying Possible Violations of CIP-006-3c R1. The Regions consolidated their respective Self-Reports into a single Violation ID Number for each region. On at least three occasions from October 31, 2012 through November 2, 2012, a new employee who was not yet approved for unescorted physical access to Physical Security Perimeters (“PSP”) was allowed to travel to locations outside the view of an escort. The escorts at issue misinterpreted the new employee’s possession of a badge to mean that the new employee had unescorted physical access to PSPs. The new employee had most of the applicable credentials, including a bio-badge, but did not possess an identification card at the time due to a software upgrade on the identification card software. On January 8, 2013, a contractor with authorized unescorted physical access to the RFC_URE3 headquarters data center escorted a visitor into the data center. The visitor was an employee of the same contract vendor, but the visitor did not have authorized unescorted physical access to the PSP. The contractor left the visitor three times after logging the visitor into the PSP, each time for under four minutes. The first time, an RFC_URE3 employee with authorized unescorted physical access to the PSP was physically present with the visitor, and the second and third times, the visitor was on a conference call in a conference room within the data center. On January 16, 2013, an unidentified person tailgated into RFC_URE3’s SCADA area. The intruder entered the area as the door was closing following an employee’s exit. The intruder proceeded to another door and attempted to exit, but the door was secured. An employee saw the intruder, conversed with the intruder, and let the intruder out of the area with an understanding that the intruder would proceed to the security desk to sign in. The employee subsequently spoke to the security guard and learned that the intruder did not do so. RFC_URE3 checked applicable logs and determined no abnormal traffic occurred during the ten minutes the intruder was in the PSP. RFC_URE3 later identified the intruder as an individual with a history of trespassing into other companies’ facilities. On April 8, 2013, there were two instances of newly hired contractors being left without a defined escort for a short period of time (less than five minutes) within a PSP. The two contractors had requested access to the PSP and had completed cybersecurity training, but were awaiting their personnel risk assessments to be completed before being granted authorized unescorted physical access. The first instance occurred when the escort visited the restroom, and the second instance occurred when the visitor visited the restroom. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System for several reasons. Regarding the October 31, 2012 incident, RFC_URE3 had authorized this individual to have access to the PSP, but the credentials were not yet in place. The individual could not have gained access to CCAs without intervention from the CCA users because the individual did not have the access information for CCAs. Regarding the January 8, 2013 incident, the escort did not leave for a long period of time, and the escort had properly logged the visitor. The security operations center was aware of the visitor because the SOC noticed the escort leaving the visitor and called to inform the escort to continuously escort the visitor. Regarding the January 16, 2013 incident, the intruder did not approach the area where the CCAs are located and indicated that he was anxious to leave the area. The intruder appeared to be unaware of the functions performed in the protected area. Regarding the April 8, 2013 instances, at no time did the contractors approach any CCAs. The only CCAs in the PSP at issue are continuously manned. Although both visitors were technically without a defined escort for a short period of time, they were not completely alone because there were other authorized personnel present within the PSP. The Regions determined that a monetary penalty was not warranted for the issue. This is in part based on RFC_URE3’s clear commitment to strengthening its internal controls and preventing recurrence of noncompliance. In its Mitigation Plan for the issue, RFC_URE3 committed to strengthening its internal controls by implementing a lanyard program to make visitors more apparent to escorts, developing a job aid for escorts, and physically installing signage outside the PSP (which is in addition to the signage inside the PSP). In addition, RFC_URE3 reconfigured its PSP to reduce the number of doors to the PSP, reducing the amount of monitoring required for PSP access. Further, the internal controls already in place at RFC_URE3 demonstrate RFC_URE3’s clear commitment to preventing and detecting noncompliance. RFC_URE3 detects noncompliance with the escorting aspect of its physical security program through regular and frequent reviews of the queue of open logs on the system. If the physical security team recognizes any discrepancies, they call the escort and discuss the situation, including reminding escorts to properly log and escort the visitors. In addition to the controls related to the escort program, RFC_URE3 performs additional preventive and detective controls related to physical security. For example, RFC_URE3 performs maintenance on physical security systems and includes any applicable vendors in this review and double checks the installation of new physical access points. As a result of the aforementioned internal controls, RFC_URE3 timely detects noncompliances prior to the occurrence of harm, and likely detects instances of noncompliance where similarly situated Registered Entities without such internal controls would not. For example, detecting that a visitor was unescorted while using the restroom demonstrates the granularity of RFC_URE3’s internal controls and the seriousness with which RFC_URE3 addresses its physical security. RFC_URE3 has previous violations of CIP-006 R1. Despite this violation history and in addition to the reasons set forth above, the Regions did not consider RFC_URE3’s violation history as an aggravating factor. The Regions determined that RFC_URE3’s violation history does not demonstrate that RFC_URE3 has a chronic problem with physical security, but that RFC_URE3 has robust internal controls that detect noncompliances related to escorting issues. As a result of the internal controls discussed above, RFC_URE3 timely detects issues prior to the occurrence of harm, and likely detects instances of noncompliance where similarly situated Registered Entities without such internal controls would not. Accordingly, it is more likely that RFC_URE3 would have numerous issues because it has robust detective controls in place, continuously assesses its physical security, and promptly reports any noncompliance. | To mitigate this issue RFC_URE3 will: 1) develop and communicate awareness on escorting best practices and procedures for using a lanyard escorting program in the IT department; 2) add signage to indicate the boundary of the PSP on the inside; 3) communicate with the building owner about the importance of avoiding tailgating incidents in the building in general, distribute a job aid to managers, implement the lanyard escorting program, prepare and publish an awareness article describing the need for employees and contractors to protect against tailgating into facilities; and 4) develop a job aid for managers concerning the physical access process for new hires.
2013-12-30 | ReliabilityFirst Corporation (ReliabilityFirst), Midwest Reliability Organization (MRO) | Unidentified Registered Entity 4 (RFC_URE4) | NCRXXXXX | RFC2013012803; RFC2013012805; RFC2013012806; MRO2013012789 | CIP-004-3 | R2 | On August 14, 2013, the RFC_URE4 submitted Self-Reports to ReliabilityFirst and MRO stating that they had an issue with CIP-004-3 R2. On October 25, 2012, RFC_URE4 revised CIP policies, procedures, and processes became effective. RFC_URE4 failed to update the presentations used to train personnel with the new policies, procedures, and processes. As a result, those with authorized cyber and physical access to CCAs received training with incorrect references to document names and numbers. The training was substantively correct although RFC_URE4 failed to update the cybersecurity training program as necessary. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System based on three factors. First, this administrative oversight was a documentation-only issue where current training material cross-referenced prior policies, procedures, and processes. Second, the presentations used to train individuals from October 25, 2012 were accurate and in accordance with the revised and updated policies, procedures, and processes. Third, the cybersecurity training directed trainees to the location where RFC_URE4 store all CIP reference documents, including the revised documents. Trainees could easily access the revised reference documents by utilizing the version history despite the fact that the documents were mislabeled in the training presentation. Although the RFC_URE4 have previously violated CIP-004 R2, the instant issues do not constitute repetitive conduct. RFC_URE4 previously violated CIP-004 R2 by failing to ensure that a third party joint operating company that has authorized unescorted physical access to certain CCAs had a fully compliant cybersecurity training program. RFC_URE4 also previously violated CIP-004 R2 by failing to train three contractors who had authorized unescorted physical access to CCAs. The first previous violation concerned a joint operating company, and the second previous violation was a failure to conduct training. The instant issue, by contrast, is a failure to update the cybersecurity program when necessary. These issues are factually distinct with separate root causes, and as a result, ReliabilityFirst did not consider RFC_URE4's violation history as an aggravating factor. | To mitigate this issue RFC_URE4: 1) removed all incorrect and outdated information and replaced it with current references within the training material; and 2) removed all specific document numbers to prevent recurrence of this noncompliance if RFC_URE4 change the document numbers again in the future.
2013-12-30 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2013012433 | CIP-006-3c | R4 | SERC_URE1 submitted a Self-Report stating that it had an issue with CIP-006-3c R4 because it failed to manage physical access at two access points to the Physical Security Perimeter (PSP) twenty-four hours a day, seven days a week. Two doors to a PSP experienced card reader communications failures and failed to properly lock. The doors are approximately 20 feet apart and are part of the same PSP. SERC_URE1’s Security Command Center (SCC) console operators received an alarm, which indicated that the door’s card reader was disconnected from its micro-processor. SERC_URE1 stated that the doors were designed to lock by default, and the guards were trained and aware of the default settings. SERC_URE1 reported that the doors were designed to lock in the event of a communications failure. SERC_URE1, therefore, did not immediately dispatch guards to investigate the alarm. 22 minutes later, SERC_URE1 reported that a Security Operations Center (SOC) employee observed the doors’ card readers showing a constant green light, indicating that the doors were unlocked. The SOC employee notified the SCC and verified the security state all other PSP doors, which the individual found to be secure. In addition, the SOC employee secured the malfunctioning doors until security personnel arrived. 11 minutes later, the SCC dispatched a security guard to the malfunctioning doors to control access through manual observation. Although both doors were visible to the guard from one location, the guard taped one of the doors closed to ensure personnel only entered through the other door. The guard verified personnel attempting access to the PSP against a hard copy list generated from the physical access control system. SERC_URE1 repaired and tested both doors approximately four and a half hours after the initial door failure. SERC_URE1 ensured that both doors locked and only unlocked for authorized badges, and that the proper alarms displayed on the SCC’s console. The repair technician determined that the root cause of the malfunctioning doors was a firmware upgrade. The upgrade was applied to only one of the two micro-processors that controlled the badge readers for the two doors that malfunctioned, resulting in a break in the communication between the micro-processor and the two doors’ card readers. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Physical access was not controlled by SERC_URE1 for only 22 minutes. The PSP was protected by additional security controls, such as its location within SERC_URE1’s corporate building which requires a badge for access and cameras located throughout the building to detect unauthorized personnel. SERC_URE1 reviewed surveillance camera footage from the time of the issues and confirmed that only authorized personnel entered the PSP during that time. | To mitigate this issue, SERC_URE1: 1) replaced processor boards and upgraded the firmware for both micro-processors and reset the alarms to return the doors to a locked state; 2) tested the door alarms to ensure proper functioning, especially of "failure mode"; 3) emailed instructions to the console operators and supervisors about the access control alternative measures procedure, which includes controlling access points, monitoring access points, and logging access into PSPs; 4) reviewed the video footage to confirm there was no unauthorized access or access attempts during the time of the outage; and 5) put a procedure in place to review its procedures relating to access controls, monitoring, and logging, clarify them as necessary, and communicate these clarifications to the necessary personnel.
2013-12-30 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2013012088 | CIP-007-3a | R4 | SERC_URE1 submitted a Self-Report stating that it had an issue with CIP-007-3a R4.1 because it failed to document compensating measures applied to mitigate risk exposure where antivirus software and malware prevention tools are not installed. During a monthly Critical Cyber Asset review, SERC_URE1 discovered that two microprocessor relays were scheduled to be installed in two days. SERC_URE1 began gathering the necessary documentation to determine the technical feasibility of using anti-virus software and malware prevention tools on these devices. SERC_URE1 found that the two relays were unable to support the installation of antivirus software and malware prevention tools. Two days later, SERC_URE1 installed the relays within an Electronic Security Perimeter (ESP) prior to documenting the compensating measures applied to mitigate risk exposure Approximately five months later, SERC_URE1 amended an existing Technical Feasibility Exception (TFE) to include the two relays that are not capable of running anti-virus software and other malware prevention tools. This issue was caused because SERC_URE1 personnel responsible for implementing new devices failed to notify SERC_URE1 personnel responsible for evaluating the compliance effects of implementing new devices. Specifically, SERC_URE1’s TFE procedures did not require advance notification to allow SERC_URE1 to evaluate the need for a TFE related to planned devices. SERC_URE1 has since modified its TFE procedures. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The devices were located within an ESP within a Physical Security Perimeter with an alarm that connects to the security console, which is monitored twenty-four hours a day, seven days a week. The devices were not critical to the station operations or the operation of other devices within the substation. SERC_URE1 had an existing TFE for this class of device, and the TFE’s compensating measures were in place prior to and during the issue. | To mitigate this issue, SERC_URE1: 1) prepared and submitted an amendment for an existing TFE to SERC; 2) evaluated the current state of its TFE creation and amendment process; 3) launched new TFE process flow charts and subsequently updated them; 4) assigned a TFE coordinator; and 5) produced and implemented a new TFE escalation process to ensure that TFEs are given proper attention and reduce delays when a TFE or TFE amendment is needed.
2013-12-30 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2013012471 | CIP-007-3a | R8 | SERC_URE1 submitted a Self-Report stating that it had an issue with CIP-007-3a R8 because it failed to perform an annual cyber vulnerability assessment (CVA) on one Critical Cyber Asset (CCA) within the Electronic Security Perimeter (ESP). SERC_URE1 reported that while reviewing the NERC CIP asset report from an internal inventory application it discovered that a CVA was not performed on one station data manager CCA. SERC_URE1 found that the list it generated and utilized to perform the CVA did not include the station data manager device. This was due to an error in the reporting query used to generate the list of devices from its device inventory application. As a result, the station data manager device was omitted from the list and did not receive its annual CVA. SERC_URE1 utilizes the inventory application to maintain a complete list of its assets. SERC_URE1 must perform specific queries to generate a list of devices. In this instance, SERC_URE1 queried the asset type “ESP Network,” and the resulting list failed to include the station data manager device. SERC_URE1 has since developed a new query resulting in a complete list of CIP devices for the location required to undergo a CVA. SERC_URE1 executed the new query, compared the resulting list against its master CCA list, and found that all CCAs were included in both lists. The new query also verified that only the station data manager device had been omitted from the CVA. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The device was located within an ESP and protected by restrictive firewall access control lists and intrusion detection systems. The next year's CVA that did include the station data manager device identified no vulnerabilities requiring action. The issue was limited to only one device. | To mitigate this issue, SERC_URE1: 1) developed a new query using only directly applied fields as the criteria to generate a list of NERC CIP assets; 2) compared the output of the new query against the CCA master list and determined that all CCA’s were included in both lists. SERC_URE1 concluded that only one device was omitted from the CVA; and 3) performed a vulnerability assessment on the CCA station data manager.
2013-12-30 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2013012087 | CIP-007-3a | R6 | SERC_URE1 submitted a Self-Report stating that it had an issue with CIP-007-3a R6 because it deployed two relays within the Electronic Security Perimeter (ESP) that were unable to support monitoring of cyber security events. During a monthly Critical Cyber Asset review, SERC_URE1 discovered that two microprocessor relays were scheduled to be installed in two days. SERC_URE1 began gathering the necessary documents to determine the technical feasibility of implementing automated tools or organizational process controls to monitor system events related to cyber security on those two relays, as required by CIP-007-3a R6. SERC_URE1 found that the two relays would be unable to provide monitoring of cyber security events. Two days later, SERC_URE1 installed the relays within an Electronic Security Perimeter (ESP) prior to filing for a, or amending an existing, Technical Feasibility Exception (TFE) to document the compensating measure applied to the two relays to mitigate risk. Approximately five months later, SERC_URE1 amended an existing TFE to include the two relays that are not capable of logging and reporting cyber security events. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The devices were located within an ESP within a Physical Security Perimeter with an alarm that connects to the security console, which is monitored twenty-four hours a day, seven days a week. The devices were not critical to the station operations or the operation of other devices within the substation. SERC_URE1 had an existing TFE for this class of device, and the TFE’s compensating measures were in place prior to and during the issue. | To mitigate this issue, SERC_URE1: 1) prepared and submitted an amendment for an existing TFE; 2) evaluated the current state of its TFE creation and amendment process; 3) launched new TFE process flow charts and subsequently updated them; 4) assigned a TFE coordinator; and 5) produced and implemented a new TFE escalation process to ensure that TFEs are given proper attention and reduce delays when a TFE or TFE amendment is needed.
2013-12-30 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 2 (SERC_URE2) | NCRXXXXX | SERC2011008284 | CIP-009-1 | R5 | SERC_URE2 submitted a Self-Report stating that it had an issue with CIP-009-1 R5. SERC learned that SERC_URE2 had a recovery plan that included procedures to address the backup and recovery of media containing information critical to the recovery of Critical Cyber Assets (CCA). SERC_URE2 used two media types, a hard drive and a physical tape, to store the same information. After further assessment, SERC learned that SERC_URE2 had tested the hard drive but not the physical tape. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC_URE2 stored its recovery plans on network shared drives, which were backed up daily and monthly. | To mitigate this issue, SERC_URE2: 1) updated the CCA recovery plan procedure with examples of media that should be tested and of recovery scenarios for CCAs; 2) circulated the updated procedure to applicable personnel; and 3) trained personnel involved with back up media testing. SERC has verified the completion of all mitigation activity.
2013-12-30 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 3 (SERC_URE3) | NCRXXXXX | SERC201000511 | CIP-004-1 | R4 | During a compliance Spot Check, SERC determined that SERC_URE3 had an issue with CIP-004-1 R4 because it failed to maintain lists of personnel with authorized cyber or authorized physical access to Critical Cyber Assets (CCAs), including their specific electronic and physical access rights to CCAs. The SERC audit team identified three instances where SERC_URE3 had an issue with CIP-004-1 R4. After further review, SERC determined that only one of the instances identified by the SERC audit team constituted an issue with CIP-004-1 R4. SERC_URE3 could not provide evidence that it had conducted a quarterly review of its lists of personnel and approved vendor personnel with access to CCAs. SERC_URE3 was able to provide emails asking managers to verify whether the individuals on the access lists required such access and evidence that access rights were removed for some individuals, but could not provide emails from the managers demonstrating that they had verified that the access lists were accurate or that some individuals needed to be removed. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC_URE3 provided evidence that user account privileges for its personnel and approved vendor personnel were revoked during the quarter in question, indicating that SERC_URE3 was following internal procedures for revoking CCA access rights. | To mitigate this issue, SERC_URE3: 1) created a task to review its CCA access list quarterly and compare with HR employee records; 2) created quarterly tasks to review and compare its access list to the vendor's access lists; 3) created a new vendor model that denies electronic access to a vendor until SERC_URE3 requires assistance from its vendor. Access is removed when the vendor's task has been completed; and 4) added strong language to vendor contracts insuring timely notification of personnel changes.
2013-12-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2013012344 | CIP-003-3 | R6 | During a Compliance Audit, SPP RE determined that SPPRE_URE1 had an issue with CIP-003-3 R6 because, during one change, i.e. the application of security patches, SPPRE_URE1 did not follow its Change Control and Configuration Management Process. Specifically, the SPPRE_URE1 process indicates that an “open” change ticket shall only be “closed” following completion of the change. In the identified instance, the change was not applied until 31 days after the ticket’s status was changed to closed. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because SPP RE identified only one change ticket that deviated from the documented Change Control and Configuration Management Process. Furthermore, the pending patches were applied within 31 days of the premature ticket closure. | To mitigate this issue, SPPRE_URE1: 1) Altered its Change Control and Configuration Management Process to require administrative approval of changes prior to implementation into production; and 2) Modified its tickets system to require administrator verification of work completion prior to a ticket being closed. SPP RE has verified the completion of all mitigation activity.
2013-12-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2013012350 | CIP-007-3a | R6; R6.1 - R6.5 | During a Compliance Audit, SPP RE determined that SPPRE_URE1 had an issue with CIP-007-3a R6 (R2.2) (issue also implicates versions 1, 2, and 2a of the standard) because a group of Cyber Assets (printers) did not have security monitoring controls in place that would issue automated or manual alerts in response to Cyber Security Incidents per R6.2. Additionally, SPPRE_URE1’s log server was not collecting Cyber Asset logs during reboot, and therefore, logs originating during the reboot timeframe were not subjected to the controls outlined in R6.1 – R6.5. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SPPRE_URE1 was monitoring and logging access at all cyber assets 99.9% of the time. Additionally, SPPRE_URE1 limited the potential routes for malicious access attempts against its cyber assets by allowing only port traffic required for normal operations (where technically feasible). Moreover, the implicated cyber assets reside inside the electronic security perimeter, thereby providing an outer layer of defense against any incoming malicious access attempts. Additionally, while it was not technically feasible for SPPRE_URE1 to establish security monitoring controls to alert on Cyber Security Incidents impacting its printers, SPPRE_URE1 had established security monitoring controls on all other Cyber Assets where technically feasible. | To mitigate this issue, SPPRE_URE1: 1) Configured local logging at its switches; 2) Implemented and documented a manual log review process to be followed anytime its log review server is offline; and 3) Removed the implicated printers from the Electronic Security Perimeter. SPP RE has verified the completion of all mitigation activity.
2013-12-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2013012353 | CIP-007-3a | R1; R1.3 | During a Compliance Audit, SPP RE determined that SPPRE_URE1 had an issue with CIP-007-3a R1 (1.3) (issue also implicates versions 1, 2, and 2a of the standard) because, while SPPRE_URE1 was maintaining change tickets to demonstrate that significant changes were implemented and that they did not adversely affect existing cyber security controls in accordance with its testing process, SPPRE_URE1 did not consistently preserve the test results associated with each change ticket. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SPPRE_URE1’s change control tickets indicated that security control testing had been conducted despite the absence of the supporting testing documents. Furthermore, testing records were available for the majority of change tickets reviewed after February, 2012. Moreover, SPPRE_URE1’s procedures required significant changes to be installed in a testing environment prior to installation on SPPRE_URE1’s production system, thereby providing additional assurance that any adverse impact to existing security controls would have been detected prior to installation on the production system. | To mitigate this issue, SPPRE_URE1: 1) Created a checklist for system administrators detailing the correct security controls evidence to retain for each type of SPPRE_URE1 cyber asset change; and 2) Conducted a training session on the proper retention of security controls testing documents. SPP RE has verified the completion of all mitigation activities.
2013-12-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPPRE_URE2) | NCRXXXXX | SPP2012010959 | CIP-005-1 | R2; R2.1, R2.2, R2.4 | During a Compliance Audit, SPP RE determined that SPPRE_URE2 had an issue with CIP-005-1 R2.1, R2.2, and R2.4 because SPPRE_URE2 had not implemented its organizational processes and technical and procedural mechanisms for controlling electronic access at all electronic access points to its Electronic Security Perimeter (ESP). Regarding CIP-005-1 R2.1, two of SPPRE_URE2’s access point rule sets did not specify explicit access permissions for certain Internet Protocol (IP) addresses. As a result, the access points allowed those Internet Protocol (IP) addresses to communicate with any Cyber Asset/Critical Cyber Asset within the ESP. Regarding CIP-005-1 R2.2, the previously identified access point rule sets were configured to permit access across ports and services that were not required for operations or for monitoring Cyber Assets within the ESP. Regarding CIP-005-1 R2.4, SPPRE_URE2 did not implement strong technical controls to ensure the authenticity of the accessing party for two routers with external interactive access capabilities. Specifically, while virtual access from SPPRE_URE2’s corporate domain to routers located in two SPPRE_URE2 substations required multi-factor authentication (username, password, and an additional means of authentication) for five virtual terminal lines, the remaining eleven virtual terminal lines required only single-factor authentication (username and password). | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Regarding CIP-005-1 R2.1 and R2.2, although the access point configurations did not specify explicit access permissions or restrict access to only those ports and services required for operations or monitoring of Cyber Assets within the ESP for the IP addresses, the rule sets did effectively limit access to the specified IP addresses, which were associated with SPPRE_URE2’s field devices. Additionally, SPPRE_URE2 had an intrusion detection system that scanned the ESP for unauthorized access attempts. The Cyber Assets within the ESP that were technically capable ran antimalware, and access to Cyber Assets located within the ESP was continuously monitored and logged. Regarding CIP-005-1 R2.4, although SPPRE_URE2 did not have strong authentication for the majority of virtual terminal lines between the corporate domain and the two routers, the lines were configured to require single-factor authentication. | To mitigate this issue, SPPRE_URE2: 1) Updated its policy to explicitly indicate that firewalls should deny all access by default, 2) Configured firewall rules to deny by default; 3) Performed a review of permissions to all ESP’s and revised/re-documented as necessary; and 4) Configured the login authentication method for the remaining VTY lines. SPP RE has verified the completion of all mitigation activity.
2013-12-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 3 (SPPRE_URE3) | NCRXXXXX | SPP2013012808 | CIP-006-3c | R2.2 | SPPRE_URE3 self-reported to SPP RE that it had an issue with CIP-006-3c R2.2 because it did not afford the protective measures specified in CIP-007-3. CIP-007-3 R5.1.3 requires SPPRE_URE3 to verify that “access privileges are in accordance with . . . Standard CIP-004-3 Requirement 4.” CIP-004-3 R4.2 requires SPPRE_URE3 to “revoke authorized cyber . . . access to Critical Cyber Assets, including their specific electronic . . . access rights to Critical Cyber Assets.” SPPRE_URE3 did not revoke an employee’s authorized cyber access to a shared account associated with a Physical Access Control System (PACS) device within seven calendar days after his voluntarily termination of employment with SPPRE_URE3. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The only way the former employee could have accessed the PACS device after his departure would have been to have physical or remote access to SPPRE_URE3’s corporate domain. However, because SPPRE_URE3 revoked the former employee’s physical access and all other logical access to its Cyber Assets within seven days of his departure, he was incapable of accessing the PACS device or any other Cyber Asset. Additionally, this was an isolated incident and access to the shared account was revoked 67 days after the former employee’s departure. | To mitigate this issue, SPPRE_URE3: 1) reviewed its provisioning/de-provisioning processes to ensure proper steps are fully documented; 2) retrained all affected staff on the provisioning/de-provisioning processes; and 3) removed all local user accounts where possible, to limit the exposure local user accounts have on Servers.
2013-12-30 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE2013012816 | CIP-002-3 | R2 | TRE_URE1 submitted a Self-Report stating that it had an issue with CIP-002-3 R2. Specifically, TRE_URE1 stated it was not certain that the methodology of its older CIP-002 efforts would meet the requirements of the CIP-002 standards. TRE_URE1 also self-reported that it believed that not having revisited its RBAM or developing its Critical Asset list in one calendar year was a CIP-002 R2 issue. Texas RE determined that TRE_URE1 failed to apply its Risk Based Assessment Methodology (RBAM). Texas RE determined the issue duration period to be approximately 13 and a half months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The risk is mitigated because TRE_URE1 did not have any Critical Assets or Critical Cyber Assets. Additionally, TRE_URE1 performed and approved TRE_URE1's RBAM in the first year and the most recent year and determined a null CA and CCA resulted in both cases. | To mitigate this issue, TRE_URE1: 1) applied its RBAM with resulting null CA and CCA lists, which were approved by the senior manager; and 2) implemented and documented an enhanced RBAM/CA/CCA process to reduce the possibility of reoccurrence. This document is approved by the senior manager. Texas RE has verified the completion of all mitigation activity.
2013-12-30 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE2013012817 | CIP-002-3 | R3 | TRE_URE1 submitted a Self-Report stating that it had an issue with CIP-002-3 R3. Specifically, TRE_URE1 stated it was not certain that the methodology of its older CIP-002 efforts would meet the requirements of the CIP-002 standards. TRE_URE1 also self-reported that it believed that not having revisited its RBAM or developing its Critical Asset list in one calendar year was a CIP-002 R3 issue. Texas RE determined that TRE_URE1 failed to apply its Risk Based Assessment Methodology (RBAM). Texas RE determined the issue duration period to be approximately 13 and a half months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The risk is mitigated because TRE_URE1 did not have any Critical Assets or Critical Cyber Assets. Additionally, TRE_URE1 performed and approved TRE_URE1's RBAM in the first year and the most recent year and determined a null CA and CCA resulted in both cases. | To mitigate this issue, TRE_URE1: 1) applied its RBAM with resulting null CA and CCA lists, which were approved by the senior manager; and 2) implemented and documented an enhanced RBAM/CA/CCA process to reduce the possibility of reoccurrence. This document is approved by the senior manager. Texas RE has verified the completion of all mitigation activity.
2013-12-30 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE2013012818 | CIP-002-3 | R4 | TRE_URE1 submitted a Self-Report stating that it had an issue with CIP-002-3 R4. Specifically, TRE_URE1 stated it was not certain that the methodology of its older CIP-002 efforts would meet the requirements of the CIP-002 standards. Texas RE determined that TRE_URE1 failed to apply and have a senior manager approve its Risk Based Assessment Methodology (RBAM) during one calendar year. Texas RE determined that TRE_URE1 failed to have a senior manager sign the lists of CAs and CCAs, as required by CIP-002-3 R4. The issue duration period was for approximately 13 and a half months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The risk is mitigated because TRE_URE1 did not have any Critical Assets or Critical Cyber Assets. Additionally, TRE_URE1 performed and approved TRE_URE1's RBAM in the first year and the most recent year and determined a null CA and CCA resulted in both cases. | To mitigate this issue, TRE_URE1: 1) applied its RBAM with resulting null CA and CCA lists, which were approved by the senior manager; and 2) implemented and documented an enhanced RBAM/CA/CCA process to reduce the possibility of reoccurrence. This document is approved by the senior manager. Texas RE has verified the completion of all mitigation activity.
2013-12-30 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE2013012855 | CIP-003-1 | R2 | TRE_URE1 submitted a Self-Report stating that it had an issue with CIP-003-1 R2. Specifically, TRE_URE1 stated it was not certain that the methodology of its older CIP-002 efforts would meet the requirements of the CIP-002 standards. Texas RE determined that TRE_URE1 did not assign a senior manager by the date pursuant to the CIP implementation schedule. An entity must assign a senior manager within 12 months of its registration date. Texas RE determined the issue duration period to be approximately two months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The risk is mitigated because the issue duration is short; only approximately two months. Additionally, TRE_URE1 did not have any Critical Assets or Critical Cyber Assets. Additionally, TRE_URE1 performed and approved TRE_URE1's RBAM in the first year and the most recent year and determined a null CA and CCA resulted in both cases. | To mitigate this issue, TRE_URE1: 1) assigned a senior manager; and 2) implemented and documented an enhanced RBAM/CA/CCA process in 2013 to reduce the possibility of reoccurrence. This document is approved by the senior manager. Texas RE has verified the completion of all mitigation activity.
2013-12-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2013012866 | CIP-002-1 | R1 | WECC_URE1 submitted a Self Report to WECC stating that it had an issue with CIP-002-1 R1. Specifically, WECC_URE1 reported it failed to identify and document a risk-based assessment methodology that includes procedures and evaluation criteria. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Specifically, WECC_URE1 did have a methodology process for identifying Critical Cyber Assets. This process was reviewed annually by a WECC_URE1 Engineer and through its annual application of its risk-based methodology; WECC_URE1 identified a null list of Critical Assets and a null list of Critical Cyber Assets. Further, WECC_URE1 submitted an attestation to WECC confirming that its lists of Critical Assets and Critical Cyber Assets are null and reviewed annually. | To mitigate this issue, WECC_URE1: 1) revised its risk-based assessment methodology to include procedures and evaluation criteria for the assets identified in CIP-002-1 R1.2.1 through R1.2.7. WECC has verified the completion of all mitigation activity.
2013-12-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2013013080 | CIP-002-3 | R4 | WECC conducted an off-site audit of WECC_URE2. During the audit it was discovered that WECC_URE2 had an issue with CIP-002-3 R4. Specifically, it was determined that WECC_URE2 failed to keep an annual signed and dated record of the senior manager or delegate(s)’s approval of the risk-based assessment methodology (“RBAM”). Although WECC_URE2’s senior manager annually approved the RBAM, lists of Critical Assets, and lists of Critical Cyber Assets, WECC_URE2 failed to keep a signed and dated record of the senior manager’s approval of the RBAM for one calendar year. Therefore, WECC_URE2 failed to keep a signed and dated record of the senior manager’s approval of the RBAM. | This issue posed minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Specifically, WECC_URE2 applied its RBAM to enumerate a null list of Critical Assets and associated Critical Cyber Assets. Further, WECC_URE2 had a signed record of its null lists of Critical Assets and associated Critical Cyber Assets from previous years. In addition, WECC_URE2 kept a record of the approval of the RBAM from previous years. | To mitigate this issue, WECC_URE2 will complete the following mitigation activities within 90 days: 1) sign and record the approval of its RBAM for the current year; 2) adjust its definition of "annual" from every 15 months to every calendar year in its existing process to prevent future occurence.
2013-11-27 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2013012314 | CIP-002-3 | R2 | During a Compliance Audit, NPCC determined that NPCC_URE1, had an issue with CIP-002-3 R2. NPCC_URE1 did not develop a list of its identified Critical Assets or a Null Set as determined through an annual application of the risk-based assessment methodology. NPCC_URE1 did not review this list at least annually and update as necessary. | The issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. NPCC_URE1 does not and has not had critical assets from NERC registration to the present. NPCC_URE1 provided their initial Critical Asset Identification Method with RBAM for prior years. These documents were reviewed and signed by the senior manager. NPCC_URE1 identified no CAs and CCAs. NPCC_URE1 also provided their current, significantly updated and approved RBAM, CA and CCA List documents, signed and dated, determining no CAs and CCAs. | To mitigate this issue, NPCC_URE1: 1) retained a vendor to develop a compliance tracking system for NPCC_URE1. The tracking system will be a comprehensive ‘one-stop’ database for all of NPCC_URE1’s compliance materials, including calendar reminders for compliance filing deadlines, individual responsibilities and reporting capabilities. 2) retained a contractor to perform a comprehensive gap analysis of NPCC_URE1’s compliance program, develop necessary procedures, and improve existing procedures.
2013-11-27 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2013012316 | CIP-002-3 | R3. | During a Compliance Audit, NPCC determined that NPCC_URE1, had an issue with CIP-002-3 R2. NPCC_URE1 did not develop a list of its identified Critical Assets or a Null Set as determined through an annual application of the risk-based assessment methodology. NPCC_URE1 did not review this list at least annually and update as necessary. | The issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. NPCC_URE1 does not and has not had critical assets from NERC registration to the present. NPCC_URE1 provided their initial Critical Asset Identification Method with RBAM for prior years. These documents were reviewed and signed by the senior manager. NPCC_URE1 identified no CAs and CCAs. NPCC_URE1 also provided their current, significantly updated and approved RBAM, CA and CCA List documents, signed and dated, determining no CAs and CCAs. | To mitigate this issue, NPCC_URE1: 1) retained a vendor to develop a compliance tracking system for NPCC_URE1. The tracking system will be a comprehensive ‘one-stop’ database for all of NPCC_URE1’s compliance materials, including calendar reminders for compliance filing deadlines, individual responsibilities and reporting capabilities. 2) retained a contractor to perform a comprehensive gap analysis of NPCC_URE1’s compliance program, develop necessary procedures, and improve existing procedures.
2013-11-27 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 2 (NPCC_URE2) | NCRXXXXX | NPCC2013011739 | CIP-005-1 | R1; R1.5 | NPCC_URE2 submitted a Self-Report stating that it had an issue with CIP-005-1 R1. During an internal review of Cyber Assets , NPCC_URE2 discovered that a server had not been properly patch managed, had not had its security event logs reviewed, and had not had its anti-virus signature updates regularly implemented. The server in question, acts as a Checkpoint Firewall Management Server within the NPCC_URE2 Energy Management System (EMS) Electronic Security Perimeter (ESP). | The issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The device is a Firewall Management console that was used to configure firewalls on the NPCC_URE2 side and collect firewall logs. The Firewall Management console did not perform the real-time, protective functions of the actual firewalls. The Firewall Management console was connected to two ISO firewalls via a stand-alone, dedicated subnet, and was not remotely accessible. Access to the console was only available from within the Physical Security Perimeter. Although the event logs were not reviewed, the firewall logs to the ESP were continually monitored and manually reviewed in accordance with the CIP standards. No incidents were identified. The firewalls, not the Firewall Management console, secured and protected the network. The annual vulnerability assessments provided confirmation that no additional ports, services or user accounts were created or left undocumented on the Firewall Management console during the period in question. After the checkpoint Firewall Management Server device was brought fully into compliance, it was later decommissioned and removed from service with NPCC_URE2's EMS upgrade. | To mitigate this issue NPCC_URE2: 1) brought the device into compliance: a) device was appropriately patch managed b) had all of its Windows Security Event Logs reviewed and no incidents or issues were identified. c) had its Anti-Virus Signatures brought up to date. 2) upgraded their EMS system which will : a) decommission and remove the Firewall Management Server b) centrally manage anti virus signature updates by the AV Management Server 3) enhanced the process to include monthly patch management review meetings for all devices that comprise and reside in the ESP. These meetings will add an oversight function to the patch management process
2013-11-27 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 3 (NPCC_URE3) | NCRXXXXX | NPCC2013012796 | CIP-002-3 | R4 | During an Off-Site Audit of NPCC_URE3, it was discovered that NPCC_URE3 had an issue with CIP-002-3 R4. NPCC_URE3 did not provide an approved, signed and dated copy of their Risk Based Assessment Methodology (RBAM) or Critical Asset/Critical Cyber Asset (CA/CCA) lists. In particular, NPCC_URE3 did have an RBAM and a CA/CCA list (both null) during the audit period, but there was no approval signature or anything presented that would indicate it was reviewed by a Senior Manager. | The issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The facility was in transition to a new owner. The original owner had self certified but there is no evidence to indicate who was the assigned Senior Manager or that the RBAM and CA/CCA lists were approved. The new owner had the required documentation to support compliance which included a signed, dated and approved RBAM and CA/CCA list by an authorized Senior Manager. Once the transition to the new owner was completed the required documentation was established and is currently in compliance with all requirements for CIP-002 R1-R4. | To mitigate this issue, NPCC_URE3: 1) corrected all documentation 2) included methodology for defining the RBAM and actual execution of the RBAM.
2013-11-27 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 3 (NPCC_URE3) | NCRXXXXX | NPCC2013012797 | CIP-002-3 | R2 | During an Off-Site Audit of NPCC_URE3, it was discovered that NPCC_URE3 had an issue with CIP-002-3 R2. NPCC_URE3 did not provide an approved, signed and dated copy of their Risk Based Assessment Methodology (RBAM) or Critical Asset/Critical Cyber Asset (CA/CCA) lists. In particular, NPCC_URE3 did have an RBAM and a CA/CCA list (both null) during the audit period, but there was no approval signature or anything presented that would indicate it was reviewed by a Senior Manager. | The issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The facility was in transition to a new owner. The original owner had self certified but there is no evidence to indicate who was the assigned Senior Manager or that the RBAM and CA/CCA lists were approved. The new owner had the required documentation to support compliance which included a signed, dated and approved RBAM and CA/CCA list by an authorized Senior Manager. Once the transition to the new owner was completed the required documentation was established and is currently in compliance with all requirements for CIP-002 R1-R4. | To mitigate this issue, NPCC_URE3: 1) corrected all documentation 2) included methodology for defining the RBAM and actual execution of the RBAM.
2013-11-27 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 4 (NPCC_URE4) | NCRXXXXX | NPCC2012011592 | CIP-005-3a | R5; R5.1 | During a Compliance Audit, NPCC determined that NPCC_URE4 had an issue with CIP-005-3a R5. NPCC_URE4 exceeded their annual review of their procedure for securing dial-up by one month and the procedure for securing dial-up access to the Electronic Security Perimeter was not updated to reflect NPCC_URE4's current dial up modem configuration. Additionally, the audit team identified labeling errors on diagrams. | The issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although subsequent reviews of the procedure were up to date, NPCC_URE4 had removed their dial up modems prior to the audit which was not reflected within their procedure. Additionally, the diagrams in question are only used by NPCC_URE4 to demonstrate compliance with the CIP standards. They are not used for operational purposes. The inconsistencies were not Critical Cyber Assets and the devices are outside the CIP Electronic Security Perimeter. | To mitigate this issue NPCC_URE4: 1) retired their procedure that addressed specific dial up devices 2) addressed dial up devices within their policy 3) revised and updated the drawings in question.
2013-11-27 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 4 (NPCC_URE4) | NCRXXXXX | NPCC2012011594 | CIP-007-3a | R2; R2.3 | During a Compliance Audit, NPCC determined that NPCC_URE4 had an issue with CIP-007-3a R2. NPCC_URE4 failed to file a TFE for disabling ports on relays. | The issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The relays are embedded systems behind a firewall, inside an Electronic Security Perimeter and Physical Security Perimeter, with restricted access. NPCC_URE4 has only enabled and documented ports and services required for normal and emergency operations.NPCC_URE4 disables any ports and services that are not approved during security testing. The electronic access points deny all traffic and the unneeded ports are not enabled past the firewall. These devices are located within a six wall perimeter which has restricted access to authorized NPCC_URE4 personnel. A potential threat would also need to compromise a physical security perimeter as the secure network is isolated from other networks. The relay devices are capable of sending control to one individual transmission line within the substation. | To mitigate this issue NPCC_URE4: 1) filed a TFE that was approved by NPCC.
2013-11-27 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 4 (NPCC_URE4) | NCRXXXXX | NPCC2012011596 | CIP-009-3 | R4. | During a Compliance Audit NPCC determined that NPCC_URE4 had an issue with CIP-009-3 R4. The audit team determined that NPCC_URE4 lacked the formalized procedures necessary to restore a physical security server. | The issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. These devices are located at data centers physically. The Electronic Access Points deny all traffic, and the unneeded ports are not enabled to pass through the firewall. These devices are located within a six wall perimeter which has restricted access to authorized entity personnel. These devices run anti-malware solutions. NPCC_URE4 utilizes a server cluster configuration where existing server control data/ parameters are mirrored to a newly added sever. Upon server connection to a cluster, all necessary applications are loaded. Dedicated externally connected storage devices are connected to house the database in the event of database corruption of servers. In the event that the aforementioned mitigating measures are compromised, a potential threat would also need to compromise a physical security perimeter as the secure network is isolated from other networks. If both servers are compromised, NPCC_URE4 would staff the Critical Asset locations with physical guards to continue to apply the required physical access controls. | To mitigate this issue NPCC_URE4: 1) developed a written procedure for the recovery of a server and the server cluster. 2) scheduled vendor support to support execution of recovery drill and the testing of backup media. 3) conducted exercises that utilize the recovery procedure to restore a copy of the database stored on external media to a stand alone server and conducted a paper drill of recovering a server cluster.
2013-11-27 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 4 (NPCC_URE4) | NCRXXXXX | NPCC2012011597 | CIP-009-3 | R5. | During a Compliance Audit NPCC determined that NPCC_URE4 had an issue with CIP-009-3 R5. The audit team determined that NPCC_URE4 failed to annually test back-up media necessary to recover the physical security system servers. | The issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. These devices are located at data centers physically. The Electronic Access Points deny all traffic, and the unneeded ports are not enabled to pass through the firewall. These devices are located within a six wall perimeter which has restricted access to authorized entity personnel. These devices run anti-malware solutions. NPCC_URE4 utilizes a server cluster configuration where existing server control data/ parameters are mirrored to a newly added sever. Upon server connection to a cluster, all necessary applications are loaded. Dedicated externally connected storage devices are connected to house the database in the event of database corruption of servers. In the event that the aforementioned mitigating measures are compromised, a potential threat would also need to compromise a physical security perimeter as the secure network is isolated from other networks. If both servers are compromised, NPCC_URE4 would staff the Critical Asset locations with physical guards to continue to apply the required physical access controls. | To mitigate this issue NPCC_URE4: 1) developed a written procedure for the recovery of a server and the server cluster. 2) scheduled vendor support to support execution of recovery drill and the testing of backup media. 3) conducted exercises that utilize the recovery procedure to restore a copy of the database stored on external media to a stand alone server and conducted a paper drill of recovering a server cluster.
2013-11-27 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2013011814 | CIP-004-3 | R4; R4.1 | SERC_URE1 submitted a Self-Certification to SERC stating that, as a Balancing Authority, Transmission Operator, Transmission Service Provider, Transmission Owner, Generator Operator, Generator Owner, Interchange Authority, and Load Serving Entity, it had an issue with CIP-004-3 R4 because it failed to maintain list(s) of personnel with authorized cyber access to Critical Cyber Assets (CCAs), including specific electronic and physical access rights to CCAs. SERC_URE1 allowed 10 employees of a particular customer read-only access to CCAs to view electronic information for distribution purposes. Employees of the customer were able to access the Electronic Security Perimeter (ESP) using an individual account and a token maintained by the customer. Once inside the ESP, employees of the customer used shared accounts to access specific CCAs. One of the customer’s employees with authorized cyber access to SERC_URE1’s CCAs retired. The employee never had or required physical access to CCAs. The employee had an individual user account with a password, managed by SERC_URE1, and an individual authentication token that together granted electronic access to the SERC_URE1 ESP. The employee’s manager took the retiring employee’s token on the employee's last day of work and sent it to the SERC_URE1 system control computer support department. The customer did not inform SERC_URE1 of the change in the retiring employee’s cyber access rights until two months later. After receiving this notification, SERC_URE1 immediately updated its CCA access lists, removed the customer employee’s individual account, and changed the shared account passwords on the CCAs within the ESP. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The customer employee’s token that granted electronic access to the ESP was removed when the employee left the customer’s site, thereby preventing the employee from gaining access to the ESP or the CCAs within the ESP. The customer employee had read-only access to SERC_URE1’s CCAs and did not have physical access to CCAs. The customer employee no longer needed access to CCAs because of retirement and was not terminated for cause. The customer employee had a valid Personal Risk Assessment and security training. | To mitigate this issue, SERC_URE1: 1) removed the large customer employee's electronic access to CCAs; 2) changed the shared password necessary to gain access to the ESP; and 3) held a meeting with the large customer to determine ways to strengthen its internal procedures to ensure the appropriate notifications are made.
2013-11-27 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2013012086 | CIP-006-3c | R6 | SERC_URE1 submitted a Self-Report to SERC stating that, as a Transmission Operator, Transmission Owner, and Transmission Service Provider, it had an issue with CIP-006-3c R6 because it failed to record sufficient information to uniquely identify individuals and the time of access 24 hours a day, 7 days a week. SERC_URE1 maintains an authentication monitoring zone (AMZ) at its data center that consists of electronic access control and monitoring (EACM) devices and physical access control system (PACS) devices that are inside of a secure locked rack. SERC_URE1 has identified the secure rack as a Physical Security Perimeter (PSP). The PSP rack is locked and has a system installed on the rack that allows only one individual to access the PSP rack at one time. This system is not designed to account for multiple individuals who may be accessing the PSP rack simultaneously. Because of this limitation, SERC_URE1 procedurally enforced manual logging every time someone accessed the PSP rack by requiring the individuals accessing the PSP rack to fill out and sign a manual logbook stored within the PSP rack, sign out when done with their work within the PSP rack, and then return the logbook to the PSP rack. A SERC_URE1 employee accessed the secure rack. As called for in the access procedures, the SERC_URE1 employee filled out and signed the manual logbook. This individual failed to follow the access procedures, however, when he left the logbook outside of the PSP rack after completing his work. As a result, the next individual who accessed the PSP rack did not manually sign the logbook. SERC reviewed the access logs SERC_URE1 provided and confirmed that a single SERC_URE1 employee visited the PSP rack on approximately two weeks later and did not sign in. The same employee repeated this action during a second visit several days later. SERC later learned that a third SERC_URE1 employee who did not have access to the PSP rack mistakenly signed the logbook after it was left outside of the PSP rack and did not sign out properly. Although the third employee’s signing of the logbook was not an issue, the fact that the logbook was left outside of the PSP rack was a failure to follow the access procedure and constituted an issue. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The PSP rack had physical access controls that restricted access to screened and trained individuals. A video camera was trained on the PSP rack and provided 24 hour live video monitoring, enabling identification of anyone accessing the PSP rack. SERC_URE1 reviewed its video, electronic, and manual logs and confirmed that there were no unauthorized access attempts to the PSP rack. The PSP rack was located inside of a data center that limited access to IT personnel with some initial screening. | To mitigate this issue, SERC_URE1: 1) reminded all individuals that access the AMZ within the PSP rack that they must login and logout using the logbook provided and that the logbook must be placed back into the PSP rack; 2) secured the logbook to the interior of the PSP rack so that it cannot be removed but can still be used; and 3) audited logbooks on a monthly basis to ensure accuracy and understand logbook usage.
2013-11-27 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP201100636 | CIP-003-1 | R6 | SPPRE_URE1 submitted a Self Report to SPP RE stating that it had an issue with CIP-003-1 R6 because its documented Change Control and Configuration Management process document merely referenced R6 instead of being an established process to protect Critical Cyber Assets as specified in R6. | This issue posed a minimal risk and not a serious or substantial risk to the reliability of the bulk power system. The failure to establish and document a Change Control and Configuration Management process for additions, modifications, replacement, removal, or changes to Critical Cyber Asset hardware or software presented a risk that the associated Critical Cyber Asset(s) could become inoperable and/or vulnerable to a cyber attack. Although SPPRE_URE1 did not have an established documented Change Control and Configuration Management process in place, it did have change control procedures for vendor-related changes to its supervisory control and data acquisition system and Critical Cyber Asset hardware and software. Additionally, SPPRE_URE1’s Critical Cyber Assets are protected by a firewall specifically configured to only allow traffic using specific protocols to enter the network, which helps prevent unsolicited traffic from passing into the ESP. SPPRE_URE1 also uses a network intrusion detection system to analyze network traffic at access points to the ESP for known and suspect malicious activity. Moreover, access to Critical Cyber Assets is limited to only those individuals with authorized physical and/or electronic access rights. SPPRE_URE1 attested that all Critical Cyber Assets remained fully operational and that there were no security alerts or cyber attacks during the violation duration. | To mitigate this issue, SPPRE_URE1: 1) developed and implemented a new change control and configuration management process in accordance with CIP-003 R6; and 2) trained all applicable personnel on the new process. SPP RE has verified the completion of all mitigation activity.
2013-11-27 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP201100641 | CIP-006-1 | R1.1 | SPPRE_URE1 submitted a Self Report to SPP RE stating that it had an issue with CIP-006-1 R1.1 because its Electronic Access Control Systems (EACS) devices did not reside within an identified Physical Security Perimeter (PSP). | This issue posed a minimal risk and not a serious or substantial risk to the reliability of the Bulk Power System. The EACS devices were afforded multiple layers of protection within a secured facility. For instance, the EACS devices are located in the same building as a police department. The ground floor of the building is manned by police personnel twenty-four hours a day, seven days a week. Additionally, the EACS devices were located in a badge-controlled data center on the third floor. Only authorized personnel with proper credentials have unescorted access to the third floor. Other individuals were permitted to access the third floor but only those with a business need and an escort. Any individual escorted into the secured data center was required to check in at the receptionist desk located just inside the data center access door and be continuously escorted. Moreover, SPPRE_URE1 attested that there were no security alerts or incidents during the violation duration. | To mitigate this issue, SPPRE_URE1: 1) relocated the EACS devices to its PSP; 2) updated its PSP documentation to include the EACS devices; 3) and updated its Physical Security Plan to reflect the changes. SPP RE has verified the completion of all mitigation activity.
2013-11-27 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2011008246 | CIP-004-1 | R4 | The SPP RE CIP determined that SPPRE_URE1 had an issue with CIP-004-1 R4 because, although a complete list of personnel with authorized cyber and unescorted physical access to Critical Cyber Assets was maintained, the specific electronic access rights granted to each individual were not were not included on the list. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The failure to designate specific electronic access presented a risk that an individual could gain access to systems beyond what was necessary for that person’s job duties. However, SPPRE_URE1’s list did include the specific access rights for personnel with authorized unescorted physical access to Critical Cyber Assets. Additionally, SPPRE_URE1 did have an implemented access control policy in place, which required that electronic access to Critical Cyber Assets be granted to personnel with management approval, cleared personal risk assessments, and cyber security training. Moreover, SPPRE_URE1 did review its cyber access list on a quarterly basis, revoke cyber access of terminated individuals or those no longer needing such access, and update the access list upon any status changes as specificed in CIP-004-1 R4.1 and R4.2. SPPRE_URE1 attested that there were no cyber security incidents during the violation duration. | To mitigate this issue, SPPRE_URE1: 1) developed and implemented a process for defining and documenting access privileges, roles, and types of access for personnel that require electronic access to Critical Cyber Assets; and 2) updated its cyber access list to include the specific electronic access rights of each individual.
2013-11-27 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2011008251 | CIP-005-1 | R5; R5.2, R5.3 | The SPP RE determined that SPPRE_URE1 had an issue with CIP-005-1 R5.2 and R5.3. SPPRE_URE1 disconnected a server from a firewall but did not update its documentation to reflect the network change within ninety calendar days per by R5.2. Additionally, SPPRE_URE1’s logging server retained logs for approximately twenty-four hours instead of ninety calendar days as required by R5.3. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Not updating the network change within ninety calendar days was a documentation deficiency. In addition, the logging server logs were retained but not for the required ninety calendar days. Thus, the issue involved documentation and retention deficiencies, which posed no immediate risk to the reliability of the BPS. Additionally, the Cyber Assets located within SPPRE_URE1’s Electronic Security Perimeter (ESP) are protected by a firewall specifically configured to only allow traffic using specific protocols to enter the network, which prevents unsolicited traffic from passing into the ESP. SPPRE_URE1 also uses a network intrusion detection system to analyze network traffic at access points to the ESP for known and suspect malicious activity. Moreover, access to Cyber Assets located within the ESP is limited to only those individuals with authorized physical and/or electronic access rights. SPPRE_URE1 attested that there were no security alerts or cyber attacks during the violation duration. | To mitigate this issue, SPPRE_URE1: 1) updated its documentation to reflect the network change; and 2) installed, configured, and enabled event logging software for all Cyber Assets within the ESP, which is capable of producing electronic access and retaining such logs for at least ninety calendar days. SPP RE has verified the completion of all mitigation activity.
2013-11-27 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2011008292 | CIP-007-1 | R4; R4.1 | The SPP RE CIP audit team determined that SPPRE_URE1 had an issue with CIP-007-1 R4 and R4.1. Specifically, SPPRE_URE1 did not request Technical Feasibility Exceptions (TFEs) for Cyber Assets within its Electronic Security Perimeter (ESP) that are not technically capable of implementing anti-virus or other malware prevention tools as required by R4. Additionally, SPPRE_URE1 did not implement any compensating measures to mitigate risk exposure or document an acceptance of risk for such assets per R4.1. | This issue posed a minimal risk and not a serious or substantial risk to the reliability of the bulk power system because the affected Cyber Assets did reside within SPPRE_URE1’s ESP; therefore, access to such assets was limited to only those individuals with authorized physical and/or electronic access rights. Additionally, SPPRE_URE1’s Cyber Assets were protected by an intrusion detection system, which analyzes network traffic for known and suspect malicious activity. Furthermore, anti-virus software and malware prevention tools were installed on all devices within the ESP where technically feasible. Moreover, SPPRE_URE1 attested that there were no security alerts or incidents during the violation duration. | To mitigate this issue, SPPRE_URE1: 1) submitted a TFE request to the SPP RE for all Cyber Assets within the ESP for which it is not technically feasible to install anti-virus and/or anti-malware; and 2) documented compensating measures for all affected Cyber Assets. SPP RE has verified the completion of all mitigation activity.
2013-11-27 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2013011832 | CIP-004-3 | R4; R4.2 | SPPRE_URE1 submitted a Self Report to SPP RE stating that it had an issue with CIP-004-3 R4.2 because it did not revoke a heating, ventilation, and air-conditioning (HVAC) system vendor’s employee’s authorized unescorted physical access to Critical Cyber Assets within seven calendar days after his voluntary termination of employment with the vendor. The vendor did not provide notice of the employee’s resignation to SPPRE_URE1 until thirty-two days after his last date of employment, which prompted an immediate disabling of the former employee’s access badge and full revocation of his physical access rights several days thereafter. As a result, the individual’s access rights were revoked thirty-four calendar days after his resignation instead the seven-day time period prescribed in R4.2. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. A personnel risk assessment (PRA) had been completed on the individual at issue prior to his being granted access to SPPRE_URE1’s Critical Cyber Assets. The PRA was still valid at the time of his resignation. The individual had also completed annual cyber security training. Upon notification of the resignation by the vendor, SPPRE_URE1 immediately disabled his physical access card and completely revoked his access rights several days later, which was only twenty-seven days after SPPRE_URE1 was required to do so. Additionally, SPPRE_URE1 did review its cyber access list on a quarterly basis, revoke cyber access of terminated individuals or those no longer needing such access, and update the access list upon any status changes as specificed in CIP-004-3 R4.1 and R4.2. SPPRE_URE1 attested that there were no cyber security incidents during the violation duration. | To mitigate this issue, SPPRE_URE1: 1) revised its Physical Security Plan quarterly physical security perimeter access review procedure to include the following requirements: a. contact vendors with employees having unescorted physical access to verify continued employment; b. conduct a physical inventory of vendor access cards kept in Systems Operations; c. vendor access cards will: i. remain in System Operations; ii. be issued only to vendor employees with current vendor identification on an as-needed basis; and iii. be revoked immediately after the need has expired; and 2) train all affected personnel on the new physical access procedure. SPP RE has verified the completion of all mitigation activity.
2013-11-27 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPPRE_URE2) | NCRXXXXX | SPP2013012346 | CIP-005-3a | R3; R3.2 | The SPP RE CIP audit team determined that SPPRE_URE2 had an issue with CIP-005-3a R3 (R3.2) (issue also implicates versions 1, 1a, 2, 2a, and 3 of the standard) because SPPRE_URE2 did not implement and document an electronic or manual process for monitoring and logging access at the electronic access points to the SPPRE_URE2 Electronic Security Perimeter (“ESP”), twenty-four hours a day, seven days a week. Specifically, the server used by SPPRE_URE2 to monitor and log access at SPPRE_URE2’s access points did not collect and monitor access logs at the ESP access points during reboots of the server and no logs were locally captured to allow for a manual review of logs as required by R3.2. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SPPRE_URE2 was monitoring and logging access at all access points 99.9% of the time. Additionally, SPPRE_URE2 had hardened the logical ports at its access points to only allow port traffic required for normal operations, thereby limiting the potential routes for malicious access attempts. Moreover, the servers and workstations residing inside the access points had hardened logical ports and local passwords meeting the CIP complexity requirements, thereby reducing the potential for system compromise even if unauthorized access had been obtained at the access point during the reboot timeframe. | To mitigate this issue, SPPRE_URE2: 1) configured local logging at its access points; and 2) implemented and documented a manual log review process to be followed anytime the log review server is offline. SPP RE has verified the completion of all mitigation activity.
2013-11-27 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 3 (SPPRE_URE3) | NCRXXXXX | SPP2013013050 | CIP-008-3 | R1 | The SPP RE CIP audit team determined that SPPRE_URE3 had an issue with CIP-008-3 R1, R1.4 and R1.6. Specifically, SPPRE_URE3 did not update its Cyber Security Incident response plan within 30 calendar days of any changes (lessons learned) as required by R1.4. Additionally, SPPRE_URE3 did not test its Cyber Security Incident response plan for the calendar year of 2012 as required by R1.6. | SPP RE determined that the issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Although SPPRE_URE3 did not update its Cyber Security Incident response plan within 30 days of completing its lessons learned, it updated the changes within 76 days. Furthermore, the lessons learned did not result in SPPRE_URE3 making any substantial material corrections to its plan. Additionally, although SPPRE_URE3 did not test its response plan during the 2012 calendar year, it did test its plan in late 2011 and early 2013, only 14 months apart. Per CAN-0010, the 14 month interval between tests would have met the definition of “annual” had SPPRE_URE3 tested its plan for the calendar year of 2012. | To mitigate the issue, SPPRE_URE3: 1) tested its plan for the calendar year of 2013; 2) incorporated the changes made to its response plan; and 3) implemented an annually reoccurring calendar notice to alert subject matter experts, CIP compliance administrators, and corporate compliance teams about upcoming testing and upcoming deadlines for incorporating any changes to its plan.
2013-11-27 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 3 (SPPRE_URE3) | NCRXXXXX | SPP2013013051 | CIP-009-3 | R2 | The SPP RE CIP audit team determined that SPPRE_URE3 had an issue with CIP-009-3 R2 because it did not exercise its recovery plan at least annually. Specifically, SPPRE_URE3 did not test its recovery plan for the calendar year of 2012. | SPP RE determined that the issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Although SPPRE_URE3 did not test its recovery plan during the 2012 calendar year, it did test its plan in late 2011 and early 2013, only 14 months apart. Per CAN-0010, the 14 month interval between tests would have met the definition of “annual” had SPPRE_URE3 tested its plan for the calendar year of 2012. | To mitigate the issue, SPPRE_URE3: 1) tested its recovery plan for the year of 2013; and 2) implemented an annually reoccurring calendar notice to alert subject matter experts, CIP compliance administrators, and corporate compliance teams about upcoming testing
2013-11-27 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE2013011980 | CIP-005-3a | R1; R1.6 | TRE_URE1 submitted a Self-Report citing an issue with CIP-005-3a R1.6. Specifically, TRE_URE1 failed to maintain documentation for an interconnected Remote Terminal Unit (RTU). TRE_URE1 discovered that a Test RTU (Remote Terminal Unit) device was not connected to a switch in the Quality Assurance System Demilitarized Zone (QAS DMZ) as expected but instead was connected to a switch inside the Electronic Security Perimeter (ESP). TRE_URE1 determined that this issue occurred because the Test RTU device was connected to the switch inside the ESP for temporary testing and not removed after the validation process was completed. As a result, the Test RTU (a non-critical Cyber Asset) was not included in the documentation of non-critical cyber assets within an ESP, as required by CIP-005-3a R1.6. Once TRE_URE1 discovered the issue, the Test RTU was removed from the ESP. Therefore, TRE_URE1 had an issue with CIP-005-3a R1.6 for approximately seven weeks (the date the standard was enforceable until the date the Test RTU was removed from the ESP). | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The minimum risk was partially mitigated because the Test RTU was not connected to any device other than the switch but was isolated. Further, the Test RTU only communicated with the switch via Transmission Control Protocol/Internet Protocol (TCP/IP) and not with any other devices within the ESP. In addition to moving the Test RTU to the appropriate subnet, TRE_URE1 has implemented its Change Control Procedures and has revised its CVA procedures to include a cross reference check between all devices identified during physical walk or the network port/services scan, the Cyber Asset inventory list and the TRE_URE1 system configuration drawing. Lastly, TRE_URE1 completed an additional vulnerability assessment to ensure all applicable Cyber Assets in the ESP were correctly reflected in the required CIP-005 documentation and hosted in the ESP. | To mitigate this issue, TRE_URE1: 1) removed the Test RTU from the ESP; 2) implemented its Change Management Process; 3) modified CVA Process to include a cross-reference check between all devices identified during physical walkthrough or the network port/services scan, the Cyber Asset inventory list and the TRE_URE1 system configuration drawing; and 4) completed secondary CVA to revalidate that all the documentation related to the ESP devices is correct documented. Texas RE has verified the completion of all mitigation activity.
2013-11-27 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE2013011981 | CIP-006-3c | R5 | TRE_URE1 submitted a Self-Report citing an issue with CIP-006-3c R5. Specifically, physical access monitoring was not in place at one access point to a Physical Security Perimeter (PSP) for 36 days due to a micro-tamper switch failure that prevented access alerts from being sent to the designated security personnel. TRE_URE1 utilizes an Access Control System to monitor unauthorized physical access attempts at all access points to the PSP. Alarms are sent through the Access Control System to consoles at its security post. Upon review of alarm response logs maintained, the CIP Program Manager recognized that no micro-tamper alarms were recorded for one of its PSPs despite two documented instances of access by individuals with authorized access. The subject PSP is in a locked cabinet inside a facility room and contains the microcontroller panels that operate the badge readers for four (4) TRE_URE1 facilities. TRE_URE1 conducted mechanism testing of physical security components immediately before its compliance enforcement date. During this testing, a technician shorted the wires for the subject PSP to simulate a micro-tamper action, which confirmed that the switch was configured properly in the Access Control System. However, this test did not detect that the wire to the micro-tamper switch was not terminated properly and therefore not operational. TRE_URE1 intended to complete the installation of badge readers on the subject PSP prior to its enforcement date; however, the manufacturer of the lock that works in conjunction with the badge readers had components on back-order which resulted in an installation delay. Therefore, TRE_URE1 had an issue with CIP-006-3c R5 for approximately 5 weeks (the date the standard was enforceable until the date the Badge Reader was installed on the subject PSP to enforce access control and monitoring 24 hours a day, 7 days a week). | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The minimal risk was partially mitigated by the fact that the two referenced access instances recorded during this period were by personnel with authorized access rights to the CIP area access, TRE_URE1 maintains and regularly reviews a separate PSP access log which it compares with the alarm response logs, which led to its discovery of the subject issue. The building were the PSP is located is monitored by security guards. | To mitigate this issue, TRE_URE1: 1) reviewed alarm response logs to validate that alarms are working and alarm responses are properly documented; 2) installed Badge Reader on the subject PSP to enforce access control and monitoring twenty-four hours a day, seven days a week; 3) developed a PSP validation checklist; and 4) updated the Physical Security Mechanism Testing Process to include instructions for the technician to physically open the door to test the microcontroller rather than shorting the wires to simulate opening the cabinet. Texas RE has verified the completion of all mitigation activity.
2013-11-27 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE2013012166 | CIP-004-3a | R2; R2.1 | TRE_URE1 submitted a Self-Report citing an issue with CIP-004-3a R2.1. During an internal quarterly review, TRE_URE1 discovered two employees who had not completed the mandatory CIP training were configured in the Physical Access Control system with granted access to a designated Physical Security Perimeter (PSP) which contained Critical Cyber Assets. Both employees satisfactorily completed the required Personnel Risk Assessment (PRA) but failed to complete the necessary training. Once the issue was originally discovered, the CIP Program Manager requested the revocation of the untrained two employees and received notification the revocation was complete. However, two months later the revocation was reported to be completed in part, at which time the revocation for both employees was fully completed pursuant to the access modification history report. Therefore, TRE_URE1 had an issue with CIP-004-3a R2.1 for approximately two months. | This issue posed a minimum risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The minimum risk was partially mitigated by the following facts: (1) a successful Personnel Risk Assessment (PRA) was completed for the two untrained employees before the standard became enforceable, (2) based on the CCA access logs the two employees never entered the PSP, (3) access was quickly revoked upon discovery of the subject issue, and (4) the entity’s internal controls discovered the issue. Although the lack of training could have resulted in the two untrained employees using the CCAs in a manner that jeopardized the reliability of the BPS, the actual impact was minimal because the PRA minimized the risk of a possible breach or system failure on the CCA’s due to malice. Texas RE took into account that an affiliate of TRE_URE1 had a previous issue of this Standard. Texas RE determined that the instant issue is appropriate for a FFT treatment because although the previous issue by the affiliate is similar, TRE_URE1 self-reported and mitigated the issue to assist in preventing the likelihood of future occurrences. | To mitigate this issue, TRE_URE1: 1) revoked access to the PSP for both individuals; 2) implemented a reporting system that allows the individual modifying user access rights to validate the changes made as well as allowing the CIP Program Manager to see all changes by individuals who have system privileges to add or remove TRE_URE1 CIP Categories; and 3) provided edit rights to the CIP Program Manager in order to allow modification of all records within its reporting system. Texas RE has verified the completion of all mitigation activity.
2013-11-27 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2013012026 | CIP-007-3a | R8 | WECC_URE1 submitted a Self Certification to WECC stating that it had an issue with CIP-007-3a R8. Specifically, after discussions with WECC_URE1, WECC determined that, for one non-critical cyber asset located within an Electronic Security Perimeter (ESP), WECC_URE1 failed to conduct an annual Cyber Vulnerability Assessment (CVA). | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Specifically, WECC_URE1 performed a CVA on the device two years prior. Additionally, the device is located within an Electronic Security Perimeter (ESP) and Physical Security Perimeter (PSP) where physical and logical access is limited to personnel who have undergone Personnel Risk Assessments and received proper CIP training. Furthermore, the functionality of the device can be quickly and easily disconnected and direct communication can be implemented. | To mitigate this issue, WECC_URE1: 1) performed a CVA on the device involved; and 2) assigned a CIP asset custodian responsibility for the switch to the Energy Management System (EMS) support team.
2013-11-27 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2013012027 | CIP-009-3 | R2 | WECC_URE1 submitted a Self Certification to WECC stating that it had an issue with CIP-009-3 R2. Specifically, WECC determined that WECC_URE1 failed to exercise its Energy Management System (EMS) recovery plan in the prior calendar year. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Specifically, WECC_URE1 performed a fail over procedure to the backup control center in the prior year. This procedure incorporates elements of the backup plan and helped WECC_URE1 to prepare for some potential occurrences. WECC_URE1 exercised the plan two years prior and the current year. | To mitigate this issue, WECC_URE1: 1) excercised its EMS recovery plan; and 2) created an Energy Infrastructure Technology Group annual assessment calendar to track monthly, quarterly and annual obligations. WECC has verified the completion of all mitigation activity.
2013-11-27 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2013012028 | CIP-009-3 | R5 | WECC_URE1 submitted a Self Certification to WECC stating that it had an issue with CIP-009-3 R5. Specifically, WECC_URE1’s Energy Management System (EMS) group did not test backup media for 24 EMS workstations in the prior calendar year. WECC determined that the information on the 24 EMS workstations was essential to recovery and should have been tested on an annual basis. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Specifically, WECC_URE1 performed a fail over exercise to the backup control center. This exercise verifies that all systems function properly including the redundant EMS workstations. Furthermore, within 11 days following the end of the prior calendar year, WECC_URE1 tested all backup media related to the 24 EMS workstations. | To mitigate this issue, WECC_URE1: 1) tested the backup media on all 24 workstations; and 2) created an Energy Infrastructure Technology Group annual assessment calendar to track monthly, quarterly and annual obligations. WECC has verified the completion of all mitigation activity.
2013-11-27 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2013012576 | CIP-007-3a | R6 | WECC_URE1 submitted a Self Report to WECC stating that it had an issue with CIP-007-3a R6. Specifically, WECC_URE1 reported that a Critical Cyber Asset failed to properly maintain security logs. WECC_URE1 reported that a firmware bug caused the Critical Cyber Asset to stop logging security files. WECC_URE1 reported that it failed to record logs for three months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Specifically, WECC_URE1 kept the device in question behind a Physical Security Perimeter and protected the device with a strong non-default password. Furthermore, all individuals with access to the device had undergone a Personnel Risk Assessment and had received CIP training. Finally, the substation is monitored 24 hours a day 7 days a week by WECC_URE1 control center dispatchers. | To mitigate this issue, WECC_URE1: 1) applied the manufacturer's firmware update to fix the bug causing the security log issue; and 2) created an additional procedure to explain how personnel can access the device while retaining logs.
2013-11-27 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2013012655 | CIP-002-3 | R4 | WECC_URE2 submitted a Self Report to WECC stating that it had an issue with CIP-002-3 R4. Specifically, WECC_URE2 could not locate evidence of annual approval by a senior manager or delegate for two lists of Critical Cyber Assets (CCAs). | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The duration of the alleged violation is limited to the calendar year, as the two lists in scope were reviewed and approved the prior year and the year following. Furthermore, WECC_URE2 did not substantively change its CCA lists. | To mitigate this issue, WECC_URE2: 1) provided evidence of signed and dated versions of the CCA lists in question and; 2) enhanced its filing system to better track and maintain documentation required to demonstrate compliance. WECC has verified the completion of all mitigation activity.
2013-11-27 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2013012658 | CIP-007-3a | R5 | WECC_URE2 submitted a Self Report to WECC stating that it had an issue with CIP-007-3a R5. Specifically, WECC_URE2 failed to submit timely Technical Feasibility Exemptions (TFEs) for some devices that do not have the capability to enforce password complexity requirements. WECC_URE2 submitted three late amended TFEs associated with this Standard. WECC_URE2 submitted amendments to 2010-WECC-TFE0966, 2011-WECC-TFE01620 and 2011-WECC-TFE01626 to add devices that do not have the capability to enforce password requirements. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE2 has implemented mitigating measures including layered physical and cyber access controls and centralized logging/alerting tools for cyber events associated with cyber access controls. As a preventative measure, WECC_URE2 has blocked remote write access directly to the relays. In addition, WECC_URE2 has installed anti-virus and malicious software on all devices used to control or monitor the devices in question, and requires compliant passwords to login and connect to the device. | To mitigate this issue, WECC_URE2: 1) submitted TFEs for the technicial infeasibility of its devices that do not have the capability to enforce password complexity requirements. WECC has approved the TFEs.
2013-11-27 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2013012659 | CIP-007-3a | R4 | WECC_URE2 submitted a Self Report to WECC stating that it had an issue with CIP-007-3a R4. Specifically, WECC_URE2 failed to submit a timely Technical Feasibility Exemption (TFE) for nineteen Cyber Assets that do not have the capability to implement anti-virus software and other malicious software prevention tools to Cyber Assets within an Electronic Security Perimeter (ESP). WECC_URE2 submitted three late TFEs associated with this Standard. WECC_URE2 submitted 2013-WECC-TFE02332, stating its devices do not have the capability to implement an anti-virus or malicious software prevention solution. WECC_URE2 submitted 2013-WECC-TFE20333, stating its devices do not have the capability to implement anti-virus or malicious software prevention solutions. In addition, WECC_URE2 submitted 2013-WECC-TFE20334, stating its controller devices do not have the capability to implement an anti-virus or malicious software prevention solution(s). | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE2 has implemented a defense-in-depth architecture of physical and logical Cyber Security controls, including physical security mechanisms with guards, special locks, closed circuit TV, and logical perimeter and internal Cyber Security controls, including firewalls, vulnerability scanning tools, and Intrusion Detection Systems. In addition, WECC_URE2 has implemented a centralized logging and alert tool for cyber events associated with the cyber access controls. | To mitigate this issue, WECC_URE2: 1) submitted TFEs for the technicial infeasibility of Cyber Assets that cannot use anti-virus software and other malicious software prevention tools, to detect, prevent, deter, and mitigate the introduction. WECC has approved the TFEs.
2013-11-27 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2013012660 | CIP-007-3a | R6 | WECC_URE2 submitted a Self Report to WECC stating that it had an issue with CIP-007-3a R6. Specifically, WECC_URE2 failed to submit a timely Technical Feasibility Exemption (TFEs) for Cyber Assets within an Electronic Security Perimeter (ESP) that do not have the capability to implement some of the automated tools or organizational process controls to monitor system events that are related to cyber security. Specifically, the Cyber Assets do not have the capability to monitor, alert, or maintain logs for events related to cyber security. WECC_URE2 submitted a late TFE associated with this Standard. WECC_URE2 submitted TFE 2013-WECC-TFE02335 for its controller devices that do not have the capability to monitor, alert, or maintain logs for events related to cyber security. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE2 has implemented compensating and mitigating measures including layered physical and cyber access controls and centralized logging/alerting tools for cyber events associated with cyber access controls. | To mitigate this issue, WECC_URE2: 1) submitted TFEs for the technicial infeasibility of its Cyber Assets within an ESP that do not have the capability to implement some of the automated tools or organizational process controls to monitor system events that are related to cyber security. WECC has approved the TFEs.
2013-11-27 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2013012309 | CIP-007-1 | R4 | WECC_URE3 submitted a Self Report to WECC stating that it had an issue with CIP-007-1 R4. Specifically, WECC_URE3 failed to submit Technical Feasibility Exceptions (TFE) for 11 devices, where anti-virus software and other malicious prevention tools were not technically feasible. WECC_URE3 failed to submit TFEs when installed to address the assets inability to install anti-virus or other malware software prevention tools. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The devices in scope have no keyboards, CD/DVD drives or USB ports. In addition, the equipment is contained within an environment that is not connected to the internet and network access to the equipment is restricted by the use of access control lists that deny all connections by default. Further, these devices reside within a physical security perimeter and only personnel with CIP training and current Personnel Risk Assessments have access to the equipment. | To mitigate this issue, WECC_URE3: 1) submitted three TFE's for technical infeasibility of the 11 devices to install anti-virus software and other malware prevention tools. WECC has approved the TFE requests.
2013-11-27 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2013012310 | CIP-007-1 | R5 | WECC_URE3 submitted a Self Report to WECC stating that it had an issue with CIP-007-1 R5. Specifically, WECC_URE3 failed to submit a Technical Feasibility Exception (TFE) on 54 devices that were not technically capable of enforcing the six character minimum, combination of alpha, numeric, and special characters, or complexity. Three months after the submission of its Self Report, WECC_URE3 submitted four TFEs (2013-WECC-TFE02395, 2013-WECC- TFE02394, 2013-WECC-TFE-02390, 2013-WECC-TFE-02396) addressing its technical infeasibility to enforce password complexities on the 54 devices. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The devices in scope have no keyboards, CD/DVD drives or USB ports. In addition, the equipment is contained within an environment that is not connected to the internet and the passwords in scope were not associated with an account name. Further, these devices reside within a physical security perimeter and only personnel with CIP training and current Personnel Risk Assessments have access to the devices. | To mitigate this issue, WECC_URE3: 1) submitted four TFE's for technical infeasibility of 54 devices to implement passwords that contain a minimum of six characters that consist of alpha, numeric and special characters. WECC has approved the TFE requests.
2013-10-30 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2012011523 | CIP-006-3c | R4 | MRO_URE1 submitted a Self-Report to MRO stating that it had an issue with CIP-006-3c R4 because it failed to manage its temporary Physical Security Perimeter (PSP) for a period of approximately two minutes. MRO_URE1's procedure for deactivating a temporary Electronic Security Perimeter (ESP) and PSP, which is used during an exercise, required the electric network ports to be verified deactivated prior to the deactivation of the PSP. The process to activate and deactivate the control center used in the exercise required multiple procedures. The order of the deactivation was reserved by mistake. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). The temporary PSP was not managed for approximately two minutes and immediate resolution and prompt mitigation reduced the potential risk to the BPS. Further, the risk was contained to one conference room where MRO_URE1 conducted the exercise to test its control center. | To mitigate this issue, MRO_URE1: 1) reviewed the event with operating staff; 2) amended its procedures to clarify actions to be taken by the real time operator; and 3) conducted training for each member of the operations group.
2013-10-30 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2012011526 | CIP-006-3c | R5 | MRO_URE1 submitted a Self-Report to MRO stating that it had an issue with CIP-006-3c R4 because it failed to monitor or alarm its temporary Physical Security Perimeter (PSP) for a period of approximately two minutes. MRO_URE1's procedure for deactivating a temporary Electronic Security Perimeter (ESP) and PSP, which is used during an exercise, required the electric network ports to be verified deactivated prior to the deactivation of the PSP. The process to activate and deactivate the control center used in the exercise required multiple procedures. The order of the deactivation was reserved by mistake. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). The temporary PSP was not monitored or alarmed for approximately two minutes and immediate resolution and prompt mitigation reduced the potential risk to the BPS. Further, the risk was contained to one conference room where MRO_URE1 conducted the exercise to test its control center. | To mitigate this issue, MRO_URE1: 1) reviewed the event with operating staff; 2) amended its procedures to clarify actions to be taken by the real time operator; and 3) conducted training for each member of the operations group.
2013-10-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2012010119 | CIP-005-1 | R2 | NPCC_URE1 notified NPCC of an issue with CIP-005-3 R2. NPCC_URE1 did not have documentation of the enabled ports and services for its Electronic Security Perimeter (ESP) access points. | The issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. NPCC_URE1 only enabled those ports and services required for operations and for monitoring Cyber Assets within the ESP, but failed to document its configuration. | To mitigate this issue, NPCC_URE1: 1) Created a list of required ports and services for all access points to the ESP to document, individually or by specified grouping, the configuration of those ports and services.
2013-10-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 2 (NPCC_URE2) | NCRXXXXX | NPCC2013012966 | CIP-004-3 | R4 | NPCC_URE2 reported to NPCC thatit had an issue with CIP-004-3 R4. An employee with restricted unescorted physical access priviledges to the Energy Control Center (ECC) transferred positions within NPCC_URE2. Based on the employee's new position, the employee no longer required access to the ECC. However the employee's access was not revoked due to the old sponsor failing to update the access list and an oversight in employee access review due to a name change of the employee. | The issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although the employee had unescorted physical access priviledges, the access was limited and the employee's new position would have allowed the same level of restricted access if it had been granted by the employee's manager. The employee required control center personnel to escort them in and out of the ECC from the armed guard security point. The employee was not provided any card swipe access to any area in the building including the control room or server rooms. Additionally, the employee must be registered for each visist and each of the visits must be approved by the general manager of system operations beforehand. The employee continued to maintain all required training and background check qualifications necessary for ECC access. The employee did not attempt to enter the ECC after they transferred positions. | To mitigation this issue, NPCC_URE2: 1) compared all employees in the ECC's physical access control system to the corporate human resources database to verify that last names were identical. This resulted in no other mismatched names being found. 2) will have future reviews check ECC's access control system by employee number instead of only checking the employee's last name. The employee number stays constant throughout the employee's employment. 3) reminded employee sponsors of the importance of reviewing their list of assigned employees.
2013-10-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 3 (NPCC_URE3) | NCRXXXXX | NPCC2013012794 | CIP-002-3 | R1 | It was discovered that NPCC_URE3 had an issue with CIP-002-3 R1. NPCC_URE3's 2010 Risk Based Assessment Methodology did not contain all the required evaluation criteria to determine if a critical asset (CA) exists and the review of assets in 2010 was incomplete in identifying a CA or a critical cyber asset (CCA). | The issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. NPCC_URE3's 2011 and 2012 RBAMs contained complete evaluation criteria and NPCC_URE3 was determined to not have any Critical Assets and therefore no Critical Cyber Assets during those reviews. | To mitigate this issue, NPCC_URE3: 1) Subsequent RBAMs contained complete evaluation criteria 2) included methodology for defining the RBAM and actual execution of the RBAM.
2013-10-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2012011451 | CIP-005-1 | R3 | On November 13, 2012, RFC_URE1 submitted a Self-Report stating that it had an issue of CIP-005-1 R3. On February 8, 2013, RFC_URE1 submitted a Self-Report to ReliabilityFirst identifying a possible issue of CIP-007-3 R6. During the Compliance Audit, ReliabilityFirst determined that the facts and circumstances of that Self- Report constitute a possible issue of CIP-005-3a R3, consolidated into RFC2012011452. On October 9, 2012, five routers, which are Cyber Assets used in the access control and monitoring of the ESP, did not maintain logs for up to 76 hours. This malfunction occurred because an upgrade was necessary for the appliance. RFC_URE1 therefore failed to implement a process for monitoring and logging access at these access points to the ESP 24 hours a day, as required by CIP-005-3a R3. Since these logs were unavailable during this time, RFC_URE1 failed to review the logs for attempts at or actual unauthorized access, as required by CIP-005-3a R3.2. In addition, RFC_URE1 discovered that for two voltage regulators at the generating station, which are dial-up access points to the ESP, RFC_URE1 did not have evidence of monitoring and logging at access points to the ESP 24 hours a day, as required by CIP-005-3a R3. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The risk posed by the foregoing facts and circumstances was mitigated by the following factors. Regarding the routers, the gaps in logs impacted a minimal number of devices for a short period of time. There were no gaps in the other devices that log access because those devices had individual logging in addition to the appliance. RFC_URE1 was able to manually retrieve local logs for the other devices. In addition, there were no Cybersecurity Incidents during the time period of this issue. Regarding the dial-up devices, pursuant to the dial-up procedure, the phone line is disconnected when not in use. The procedure to allow dial-up access includes an approval process and visual monitoring of the system during the connection. ReliabilityFirst considered certain aspects of RFC_URE1's compliance program as mitigating factors. RFC_URE1 has a NERC Compliance Assurance process in place to ensure that it meets the requirements of the Reliability Standards. In addition, the individuals responsible for compliance have direct relationships with senior executives. RFC_URE1's Transmission and Regulatory Strategies Compliance personnel are responsible for FERC and NERC compliance and report directly to the Vice President. Furthermore, RFC_URE1 periodically conducts internal self-evaluations for compliance with the Reliability Standards. The Chairman of the Executive Management Committee regularly reports compliance status to the RFC_URE1 compliance review committee. ReliabilityFirst considered that it discovered all of the issues except one through timely self reports and applied mitigating credit. ReliabilityFirst did not consider the self report from February 8, 2013 as a self report because RFC_URE1 discovered the issue connected to the Compliance Audit. Effective oversight of the reliability of the bulk power system depends on robust and timely self reporting by Registered Entities. RFC_URE1 promptly identified and reported the issue except one due to the effective execution of its compliance program and the installation of internal controls that yielded identification of the issues prior to the occurrence of any harm. When assessing the penalty for the issue, ReliabilityFirst considered whether the facts of this issue constitute a repetitive infraction. RFC_URE1 has no previous alleged violations of CIP-005 R3. As a result, ReliabilityFirst did not consider RFC_URE1's violation history. | To mitigate the issue RFC_URE1 will complete the following mitigation activities within 90 days: 1) upgrade its software to restore proper function; 2) investigate a backup system to activate in the event of primary system failure; 3) implement a service contract with the vendor to provide support for voltage regulator system devices; and 4) configure devices to allow event logging/reviewing capability or submit Technical Feasibility Exceptions, and create a job aid for adding devices into the ESP.
2013-10-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2012011570 and RFC2012011450 | CIP-004-3 | R4 | On November 13, 2012, RFC_URE1 submitted a Self-Report stating that it had an issue with CIP-004-3 R4 (RFC2012011450). On November 27, 2012, RFC_URE1 submitted a Self-Report to ReliabilityFirst identifying an additional possible issue of CIP-004-3 R4 (RFC2012011570). On February 8, 2013, RFC_URE1 submitted a Self-Report to ReliabilityFirst identifying an additional possible issue of CIP-004-3 R4, which was consolidated into RFC2012011570. Effective August 13, 2012, a RFC_URE1 employee transferred from a position that required authorized cyber access to Critical Cyber Assets to a position that did not require such access. RFC_URE1 failed to revoke the employee’s access within seven calendar days, as required by CIP-004-3 R4.2. RFC_URE1 discovered the issue during its quarterly access review, and on September 25, 2012, RFC_URE1 revoked the employee’s access. In addition, during its quarterly access review, RFC_URE1 discovered that it failed to update the list of those with authorized cyber access to Critical Cyber Assets within seven calendar days of any change of personnel with such access to Critical Cyber Assets. RFC_URE1 failed to remove from that list the names of four individuals who had retired, as required by CIP-004-3 R4.1. On September 26, 2012, RFC_URE1 revised the access list for three of the employees who retired (one retired June 1, 2012 and two retired July 1, 2012), and on October 6, 2012, RFC_URE1 revised the access list for one of the employees who retired July 1, 2012. In addition, during its 2012 fourth quarter review, RFC_URE1 discovered that it failed to update the list of those with authorized cyber access to Critical Cyber Assets within seven calendar days of any change of personnel with such access to Critical Cyber Assets, as required by CIP-004-3 R4.1. RFC_URE1 failed to add the names of eight individuals from that list. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System. The risk posed by the foregoing facts and circumstances was mitigated by the following factors. Regarding the employee whose cyber access RFC_URE1 did not timely revoke, the employee transferred to a position within RFC_URE1 that no longer required authorized cyber access to Critical Cyber Assets. The employee has cybersecurity training and a valid personnel risk assessment and remains a trusted RFC_URE1 employee. In addition, upon review of the logs, RFC_URE1 confirmed that the employee did not access any Critical Cyber Assets after transferring to the new position. Regarding the individuals that RFC_URE1 failed to remove from the list of those with authorized cyber access to Critical Cyber Assets, RFC_URE1 had revoked the individuals’ authorized unescorted physical access and remote access rights to the Critical Asset. In addition, RFC_URE1 had confiscated company laptops. Regarding the individuals that RFC_URE1 failed to add to the access list, the individuals had the required access and were in training during the time period their names were not on the access list. As a result, it was unlikely that these individuals would need to be on the access list to perform reliability functions during the time period of the issue. ReliabilityFirst considered certain aspects of RFC_URE1's compliance program as mitigating factors. RFC_URE1 has a process in place to ensure that it meets the requirements of the Reliability Standards. In addition, the individuals responsible for compliance have direct relationships with senior executives. RFC_URE1's Transmission and Regulatory Strategies Compliance personnel are responsible for FERC and NERC compliance and report directly to the Vice President. Furthermore, RFC_URE1 periodically conducts internal self-evaluations for compliance with the Reliability Standards. The Chairman of the Executive Management Committee regularly reports compliance status to the RFC_URE1 compliance review committee. ReliabilityFirst considered that it discovered all of the issues except one through timely Self-Reports and applied mitigating credit. Effective oversight of the reliability of the Bulk Power System depends on robust and timely self reporting by Registered Entities. RFC_URE1 promptly identified and reported the issue due to the effective execution of its compliance program and the installation of internal controls that yielded identification of the issues prior to the occurrence of any harm. ReliabilityFirst considered whether the facts of this issue constitute a repetitive infraction. At the time this issue occurred, RFC_URE1 had three previous violations of CIP-004 R4. The three prior violations, which each posed lesser risk to the Bulk Power System, concerned RFC_URE1 employees who transferred positions and remained trusted RFC_URE1 employees, and each prior violation lasted relatively short durations prior to RFC_URE1 discovering the issues. ReliabilityFirst determined that the conduct related to the access revocation does not warrant a monetary penalty. Despite the violation history, ReliabilityFirst determined that FFT treatment is appropriate and that a monetary penalty is not warranted. This is based on two factors. First, RFC_URE1 has demonstrated a clear commitment to strengthening its internal controls and preventing reoccurrence of noncompliance with respect to the access revocation issues. In its mitigating actions for this issue, RFC_URE1 strengthened its internal controls by establishing an electronic report for employee transfers that flags employees requiring access revocation. Second, neither a monetary penalty nor a negotiated settlement agreement would incent desired behavior, discourage undesired behavior, or send any important signals to RFC_URE1 or the industry. | To mitigate the issue of timely revoking access RFC_URE1: 1) established an electronic report to summarize all employee transfers and flag those transfers that require access revocation (This report will be available daily for review by a small, specialized group of personnel responsible for verifying that the revocation process occurred); 2) reviewed the “Employee Offboarding Checklist” to incorporate a specific step instructing supervisors to ensure that they notify human resources promptly when an employee leaves RFC_URE1 or transfers within RFC_URE1 and 3) formalized the employee transfer process and developed an associated job aid listing the specific actions required by human resources any time an employee transfers from one position to another within the company. RFC_URE1's Senior Vice President of human resources and shared services issued a letter to all human resources consultants responsible for initiating transfer of employee access revocation discussing the importance of following the transfer notification process. On May 24, 2013, ReliabilityFirst verified RFC_URE1's completion of these mitigating activities. To mitigate the issue of updating the access lists, RFC_URE1: 1) revised the access lists and committed to implement an internal process for a second party review to ensure the Critical Cyber Asset list is updated; and 2) implemented a process with its human resources department to compare weekly employee lists. On June 20 2013, ReliabilityFirst verified RFC_URE1's completion of these mitigating activities.
2013-10-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2012010922 | CIP-006-3c | R1 | On August 8, 2012, RFC_URE2 submitted a Self Report stating that it had an issue of CIP-006-3c R1. For its Physical Security Perimeters, including at a particular NERC CIP facility, RFC_URE2 has in place an electronic badge access control system. RFC_URE2 only permits authorized personnel with a valid personnel risk assessment and cyber security training to have authorized unescorted access to this facility. RFC_URE2 has in place visitor management procedures to ensure that it escorts visitors and completes a visitor log with the date and time of ingress and egress. In addition, RFC_URE2 has signage posted at the entrance of the facility requiring adherence to the NERC CIP Requirements. On June 27, 2012, however, RFC_URE2 failed to implement these policies. On June 27, 2012, two RFC_URE2 employees who did not have authorized unescorted physical access to the NERC CIP facility attempted to gain access to the NERC CIP facility. The employees’ invalid access attempts triggered a security alert to RFC_URE2’s Security Command Center, which pursuant to normal procedure, remotely monitored and recorded the employees’ activities. During the time the employees attempted to gain access, a contractor with authorized unescorted physical access to the site was inside the facility. The contractor opened the door and allowed the two employees to enter. The contractor did not record as the escort in the visitor log, and the contractor left the visitors in the NERC CIP facility momentarily to test the access control system from the outside, believing that the individuals should have access to the facility. The Security Command Center then contacted one of the unauthorized employees and asked that both of the employees exit the facility. The authorized contractor immediately escorted the employees out of the facility. During this incident, RFC_URE2 failed to (a) implement logs to document the entry and exit of the visitors to and from the Physical Security Perimeter as required by CIP-006-3c R1.6.1 and (b) implement continuous escort of visitors within the Physical Security Perimeter, as required by CIP-006-3c R1.6.2. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. ReliabilityFirst determined that this issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk-Power System based on the following factors. RFC_URE2 has a physical security plan in place that includes a visitor control program for visitors to a Physical Security Perimeter, though it failed in part to implement the program in this instance. In addition, these employees had access to the NERC CIP facility at issue prior to the implementation of the CIP Standards. Lastly, although the contractor failed to follow certain RFC_URE2 procedures, the overall security process in place was effective as the unauthorized individuals were promptly detected and removed from within the Physical Security Perimeter. ReliabilityFirst considered certain aspects of RFC_URE2’s compliance program as mitigating factors. RFC_URE2’s internal compliance program is incorporated as part of its parent company’s corporate compliance program, which includes a council that is dedicated to ensuring that all employees under the parent company comply with all applicable laws and regulations, including, but not limited to, the NERC Reliability Standards. The chief NERC officer, reports to an individual who sits on the regulatory council and is empowered to bring compliance matters directly to RFC_URE2’s CEO and the parent company’s Board of Directors. Additionally, the parent company’s internal auditing department has incorporated Reliability Standard compliance and the internal compliance program into its regular audit cycle. Internal training includes NERC Reliability Standards Compliance Training. Management and subject matter experts receive comprehensive compliance information regarding NERC Standards and requisite reference documents. The parent company also has a NERC compliance group within its legal department who are responsible for developing and implementing appropriate procedures and controls to ensure compliance with the Reliability Standards. Furthermore, RFC_URE2’s NERC Compliance Group directs, manages, and tracks RFC_URE2’s compliance activities, provides compliance training and advice to subject matter experts, interfaces with the parent company compliance group, and provides updates to RFC_URE2’s senior management. ReliabilityFirst considered whether the facts of this issue constitute a repetitive infraction. Although RFC_URE2 has prior violations of CIP-006 and CIP-007 (See RFC201000680, RFC201000679, RFC201000332, RFC2012010441, RFC2012001321, RFC2012010440, RFC2012010443, RFC2012010442, RFC2011001125, and RFC2012010102), ReliabilityFirst did not consider the prior violations an indicator of repetitive conduct that represents an increased risk to the Bulk-Power System. RFC_URE2 is an organization with strong internal controls that promptly identifies, corrects, and reports violations of Reliability Standards. In doing so, RFC_URE2 has created a record of prior violations of a Standard. However, this record does not necessarily indicate an increased risk or warrant the imposition or aggravation of a penalty. Here, RFC_URE2’s violations are the result of distinct facts and circumstances that do not evidence or suggest a shared root cause with a prior violation. Specifically, RFC2012010922 and RFC2012010923 are examples of isolated human error that are dissimilar from other isolated human errors that were discovered in prior violations. For example, prior violation RFC2012010418 involved a misidentification of an exit to a Physical Security Perimeter, which was corrected by reviewing and updating Physical Security Perimeter exit names. Therefore, ReliabilityFirst did not consider RFC_URE2’s violation history an aggravating factor. | To mitigate the issue RFC_URE2: 1) reinforced visitor escort requirements with the service provider, removed the specific contractor from their accounts, and updated its company-wide “Standards of Integrity” training to reinforce awareness of required access controls at NERC CIP locations; and 2) reinforced visitor escort requirements with the department utilizing the contract company’s services for the contractors assigned to their account. On March 20, 2013, ReliabilityFirst verified that RFC_URE2 completed the Mitigation Plan.
2013-10-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2012010923 | CIP-003-3 | R6 | On August 8, 2012, RFC_URE2 submitted a Self-Report stating that it had an issue of CIP-003-3 R6. During the application of new anti-virus signatures, on June 14, 2012, a RFC_URE2 system administrator misread the change record and applied an anti-virus signature to two Electronic Access Control and/or Monitoring (“EACM”) systems that were not listed in the change request form. Because anti-virus and patch updates are often applied to the same four EACM systems, the system administrator erroneously applied the anti-virus signature to all four EACM systems, although two EACM systems were not approved to receive that particular anti-virus signature. As a result, the system administrator unintentionally bypassed RFC_URE2’s change management procedure. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. ReliabilityFirst determined that this issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk-Power System based on the following factors. Although RFC_URE2 failed to implement its change management procedure, all other testing procedures were followed for the erroneous application of the anti-virus signature. In addition, the systems to which the anti-virus signature was applied were behind firewalls, continued to operate as expected, and are not associated with controls on the Bulk Electric System. ReliabilityFirst considered certain aspects of RFC_URE2’s compliance program as mitigating factors. RFC_URE2’s internal compliance program is incorporated as part of its parent company’s corporate compliance program, which includes a council that is dedicated to ensuring that all employees under the parent company comply with all applicable laws and regulations, including, but not limited to, the NERC Reliability Standards. The chief NERC officer, reports to an individual who sits on the regulatory council and is empowered to bring compliance matters directly to RFC_URE2’s CEO and the parent company’s Board of Directors. Additionally, the parent company’s internal auditing department has incorporated Reliability Standard compliance and the internal compliance program into its regular audit cycle. Internal training includes NERC Reliability Standards Compliance Training. Management and subject matter experts receive comprehensive compliance information regarding NERC Standards and requisite reference documents. The parent company also has a NERC compliance group within its legal department who are responsible for developing and implementing appropriate procedures and controls to ensure compliance with the Reliability Standards. Furthermore, RFC_URE2’s NERC Compliance Group directs, manages, and tracks RFC_URE2’s compliance activities, provides compliance training and advice to subject matter experts, interfaces with the parent company compliance group, and provides updates to RFC_URE2’s senior management. ReliabilityFirst considered whether the facts of this issue constitute a repetitive infraction. Although RFC_URE2 has prior violations of CIP-006 and CIP-007 (See RFC201000680, RFC201000679, RFC201000332, RFC2012010441, RFC2012001321, RFC2012010440, RFC2012010443, RFC2012010442, RFC2011001125, and RFC2012010102), ReliabilityFirst did not consider the prior violations an indicator of repetitive conduct that represents an increased risk to the Bulk-Power System. RFC_URE2 is an organization with strong internal controls that promptly identifies, corrects, and reports violations of Reliability Standards. In doing so, RFC_URE2 has created a record of prior violations of a Standard. However, this record does not necessarily indicate an increased risk or warrant the imposition or aggravation of a penalty. Here, RFC_URE2’s violations are the result of distinct facts and circumstances that do not evidence or suggest a shared root cause with a prior violation. Specifically, RFC2012010922 and RFC2012010923 are examples of isolated human error that are dissimilar from other isolated human errors that were discovered in prior violations. For example, prior violation RFC2012010418 involved a misidentification of an exit to a Physical Security Perimeter, which was corrected by reviewing and updating Physical Security Perimeter exit names. Therefore, ReliabilityFirst did not consider RFC_URE2’s violation history an aggravating factor. | To mitigate the issue RFC_URE2: 1) conducted refresher training on the CIP Standards and the relevant RFC_URE2 procedures related to anti-virus and patch management; and 2) removed the system administrator’s access to all the systems and restored his access in stages after close supervision of several cycles of anti-virus and patch applications. On May 6, 2013, ReliabilityFirst verified that RFC_URE2 completed the Mitigation Plan.
2013-10-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2013011668 | CIP-007-3 | R5 | On December 31, 2012, RFC_URE2 submitted a Self-Report stating that it had an issue of CIP-007-3 R5. On December 3, 2012, a newly-retained contractor functioning as a Security Command Center operator began training. The operator performed the functions of an operator under the supervision of a senior shift operator/trainer, but RFC_URE2 had not added the contractor to the authorized list of users for the Physical Access Control System (The Physical Access Control System monitors and controls access points to Physical Security Perimeters). The discrepancy was discovered on December 19, 2012 by personnel supporting the Physical Access Control system and the contractor was removed from the operator duties until the formal authorization process was complete five days later. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. ReliabilityFirst determined that this issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk-Power System based on the following factors. The contractor had a completed personnel risk assessment, had received NERC training, and held authorized unescorted physical access privileges. In addition, the contractor’s actions on the Physical Access Control System were supervised during the entirety of the violation. ReliabilityFirst considered certain aspects of RFC_URE2’s compliance program as mitigating factors. RFC_URE2’s internal compliance program is incorporated as part of its parent company’s corporate compliance program, which includes a council that is dedicated to ensuring that all employees under the parent company comply with all applicable laws and regulations, including, but not limited to, the NERC Reliability Standards. The chief NERC officer, reports to an individual who sits on the regulatory council and is empowered to bring compliance matters directly to RFC_URE2’s CEO and the parent company’s Board of Directors. Additionally, the parent company’s internal auditing department has incorporated Reliability Standard compliance and the internal compliance program into its regular audit cycle. Internal training includes NERC Reliability Standards Compliance Training. Management and subject matter experts receive comprehensive compliance information regarding NERC Standards and requisite reference documents. The parent company also has a NERC compliance group within its legal department who are responsible for developing and implementing appropriate procedures and controls to ensure compliance with the Reliability Standards. Furthermore, RFC_URE2’s NERC Compliance Group directs, manages, and tracks RFC_URE2’s compliance activities, provides compliance training and advice to subject matter experts, interfaces with the parent company compliance group, and provides updates to RFC_URE2’s senior management. ReliabilityFirst considered whether the facts of this issue constitute a repetitive infraction. Although RFC_URE2 has prior violations of CIP-006 and CIP-007 (See RFC201000680, RFC201000679, RFC201000332, RFC2012010441, RFC2012001321, RFC2012010440, RFC2012010443, RFC2012010442, RFC2011001125, and RFC2012010102), ReliabilityFirst did not consider the prior violations an indicator of repetitive conduct that represents an increased risk to the Bulk-Power System. RFC_URE2 is an organization with strong internal controls that promptly identifies, corrects, and reports violations of Reliability Standards. In doing so, RFC_URE2 has created a record of prior violations of a Standard. However, this record does not necessarily indicate an increased risk or warrant the imposition or aggravation of a penalty. Here, RFC_URE2’s violations are the result of distinct facts and circumstances that do not evidence or suggest a shared root cause with a prior violation. Although RFC2013011668’s root cause related to an unclear procedure, which also occurred in prior violations, the procedure implicated was unrelated to those procedures that had previously been improved through mitigation, such as prior violation RFC2012010442’s modifications to a procedure to document system changes. Therefore, ReliabilityFirst did not consider RFC_URE2’s violation history an aggravating factor. | To mitigate the issue RFC_URE2 completed the authorization process for the contractor, conducted refresher training on the process for bringing new operators on board, affixed signage in the work station areas reminding operators to use their own credentials on the Physical Access Control System, and clarified the operator on-boarding process to explicitly state that new operators must use their own credentials. On September 25, 2013, ReliabilityFirst verified that RFC_URE2 completed the Mitigation Plan.
2013-10-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC2013012709 | CIP-009-1 | R1 | On June 27, 2013, RFC_URE3 submitted a Self-Report stating that it had an issue of CIP-009-3 R1. During an internal review of its compliance with CIP-009, which was part of a larger review of its CIP compliance, RFC_URE3 discovered an issue with its recovery plan for CCAs. RFC_URE3’s recovery plan for CCAs primarily focused on restoring the loss of RFC_URE3’s entire system operations control center rather than on recovery of the energy management system (EMS) CCAs. As a result, RFC_URE3 failed to adequately create a recovery plan for CCAs. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The risk posed by the foregoing facts and circumstances was mitigated by the following factors. RFC_URE3’s EMS has a quad-redundant system. The EMS features two separate data centers stored at two separate locations. The system has onsite redundancy as well to allow seamless automatic failovers within each site. The site personnel are able to quickly perform a switchover to the second site at the senior system supervisor’s request. As a result, it is less likely that RFC_URE3’s failure to include recovery of individual CCAs in its recovery plan would have caused a reliability issue in the event of a disaster. ReliabilityFirst considered certain aspects of RFC_URE3’s compliance program as mitigating factors. RFC_URE3’s Vice President of Distribution Operations has independent access to the CEO and is designated as the CIP Senior Manager. The manager of NERC CIP Compliance reports to the NERC compliance senior manager, and the NERC compliance office consists of 15 full-time employees. RFC_URE3 conducts internal audits of selected Reliability Standards and encourages its employees to submit any issues they suspect involve compliance with the Reliability Standards. ReliabilityFirst also considered that it discovered the issue through a Self-Report. Effective oversight of the reliability of the Bulk-Power System depends on robust and timely Self-Reporting by Registered Entities. RFC_URE3 promptly identified and reported the issue due to the effective execution of its compliance program and the installation of internal controls that yielded identification of the issue prior to the occurrence of any harm. As a result, ReliabilityFirst seeks to encourage this type of Self-Reporting characterized by spontaneous timely detection and timely correction unconnected to a pending regional compliance monitoring action, by imposing no monetary penalty for the issue. ReliabilityFirst considered whether the facts of this issue constitute a repetitive infraction by analyzing whether it evidenced any (a) repeated or continuing conduct similar to that underlying a prior violation of the same or a closely-related Reliability Standard Requirement; (b) conduct addressed in any previously submitted mitigation plan for a prior violation of the same or a closely-related Reliability Standard Requirement; or (c) multiple violations of the same Standard and Requirement. This is RFC_URE3’s first issue with CIP-009, and as a result, ReliabilityFirst did not consider RFC_URE3’s violation history. | To mitigate the issue RFC_URE3 will complete the following mitigation activities within 90 days: 1) update its recovery plan to include the process for recovering CCAs.
2013-10-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 4 (RFC_URE4) | NCRXXXXX | RFC2012011377 | CIP-007-3a | R3.1 | On October 29, 2012, RFC_URE4 submitted a Self-Report stating that it had an issue of CIP-007-3a R3.1. RFC_URE4 utilizes vendor-provided software packages for management and operational tasks. On May 1, 2012, the vendor issued a software vulnerability advisory with a listing of numerous IBM Java patches available and applicable to its software packages, including patches released in 2011. RFC_URE4 compared the advisory list to all RFC_URE4 previously assessed patches and determined that RFC_URE4 failed to assess two security patch releases for the IBM Java Application within thirty days of the availability of the patches, as required under CIP-007. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System. ReliabilityFirst determined that this issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BulkPower System based on the following factors. RFC_URE4 has a security patch management program in place for tracking, evaluating, testing, and installing applicable cyber security software patches for its Cyber Assets within the Electronic Security Perimeter. Additionally, although RFC_URE4 failed to assess the applicability of two patches within the required thirty-day timeframe, RFC_URE4 did assess both patches at a later date. Additionally, RFC_URE4 assessed patches on critical software within the required thirty-day timeframe. The two missed patches were for the IBM Java application, which is not critical software and the failure to assess patches for this software does not have the same potential impact on the Bulk Electric System as a failure to assess more critical software. ReliabilityFirst favorably considered certain aspects of RFC_URE4’s compliance program. For instance, RFC_URE4’s Director of Reliability and Compliance Assurance has independent access to RFC_URE4’s President and CEO, and has routine communications with RFC_URE4’s President regarding Bulk Power System reliability issues. RFC_URE4’s Electric System Reliability Standards Team and Reliability and Compliance Assurance Unit carry out RFC_URE4’s compliance program. These departments assign each applicable Reliability Standard to an individual for overall responsibility for compliance with that Reliability Standard. The Reliability and Compliance Assurance Unit operates independently from RFC_URE4 business units with responsibility for implementation of the Reliability Standards. ReliabilityFirst considered that it discovered the issue through a RFC_URE4 Self-Report and applied mitigating credit. Effective oversight of the reliability of the Bulk Power System depends on robust and timely self-reporting by Registered Entities. RFC_URE4 identified and reported the issue in this FFT Report due to the effective execution of its compliance program and the installation of internal controls that yielded identification of the issues. As a result, ReliabilityFirst seeks to encourage this type of self-reporting, characterized by timely detection and correction unconnected to a pending regional compliance monitoring action, by imposing no monetary penalty for these remediated issues. ReliabilityFirst considered whether the facts of this issue constitutes repetitive infractions by analyzing whether they evidenced any (a) repeated or continuing conduct similar to that underlying a prior violation of the same or a closely-related Reliability Standard Requirement; (b) conduct addressed in any previously submitted mitigation plan for a prior violation of the same or a closely-related Reliability Standard Requirement; or (c) multiple violations of the same Standard and Requirement. Since this constitutes RFC_URE4’s first issue with this Reliability Standard or a closely-related Reliability Standard, ReliabilityFirst determined that the instant issue was not repetitive. Therefore, ReliabilityFirst did not assign RFC_URE4 with a penalty due to this factor. | To mitigate the issue RFC_URE4 conducted an assessment of the patches, upgraded of the operating system which included RFC_URE4’s replacement of the system with a newer version of Java, and initiated a detailed internal investigation to identify any necessary additional long-term remediation.
2013-10-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 5 (RFC_URE5) | NCRXXXXX | RFC2013012438 | CIP-007-3a | R7 | On April 29, 2013, RFC_URE5 submitted a Self-Report stating that it had an issue of CIP-007-3a R7. While performing its routine disposal and redeployment procedure, RFC_URE5 discovered that one device was missing. On October 24, 2012, RFC_URE5 unplugged the device from the ESP. During the week of November 5, 2012, RFC_URE5 removed the old equipment and set it aside within the Physical Security Perimeter (PSP) as it was installing new equipment. RFC_URE5 retained the old equipment in case it needed the old equipment during installation of the new equipment. The RFC_URE5 technician left the old equipment stored inside the PSP. When RFC_URE5 initiated the disposal process for the old equipment on February 13, 2013, the device was missing, and RFC_URE5 could not locate the device. As a result, RFC_URE5 failed to destroy or erase the data storage media on this device, as required by CIP-007-3a R7.1. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. ReliabilityFirst determined that this issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk-Power System based on the following factors. ReliabilityFirst determined that this issue posed a minimal risk to the reliability of the Bulk Power System based on the following three factors. First, the device does not contain any sensitive data and it is not able to log or record events on the system. There is no information stored directly on the devices, and the device at issue merely converted signals from a serial connection to an internet protocol network as a pass-through device. Second, RFC_URE5 retired all equipment that was associated with this device at the same time as the device, and the device only contained a setting that was unique to its associated equipment. Third, RFC_URE5 changed all passwords in accordance with its annual password change policy, and as a result, the device does not contain the current password used to secure other devices in the ESP. As a result of the foregoing factors, it was less likely that any information on the missing device would have resulted in compromise to the RFC_URE5 system. ReliabilityFirst considered that it discovered the issue through a Self-Report. Effective oversight of the reliability of the Bulk Power System depends on robust and timely self reporting by Registered Entities. RFC_URE5 promptly identified and reported the issue due to the effective execution of its compliance program and the installation of internal controls that yielded identification of the issue prior to the occurrence of any harm. ReliabilityFirst considered the following aspects of RFC_URE5’s internal compliance program. RFC_URE5’s Compliance Officer has independent access to the CEO, Executive Committee, and Board of Directors. In addition, RFC_URE5’s Reliability Compliance Committee is responsible for ensuring implementation and oversight of RFC_URE5’s program to comply with the Reliability Standards. The NERC Compliance Steering Committee works to, inter alia, establish clear, visible, simple, and efficient processes; secure adequate resources for compliance; and assign clear accountability for achieving results associated with compliance activities. RFC_URE5’s compliance program provides an annual schedule of standards to review and internal assessments of compliance by each affected business unit and by independent staff such as Internal Audits and Regulatory Services. RFC_URE5 also utilizes a compliance management software program and has clearly-defined procedures dictating the steps to take when compliance issues arise and mitigating activities are necessary. Furthermore, RFC_URE5’s tools and training enable employees to comply with the Reliability Standards. ReliabilityFirst considered whether this issue constitutes a repetitive infraction. This is RFC_URE5’s first issue with CIP-007-3a R7, and as a result, ReliabilityFirst did not consider RFC_URE5’s violation history. | To mitigate the issue RFC_URE5 changed all RMC30 passwords, committed to evaluate the CIP-007 R7 process for removal and retirement of devices and change if necessary, and develop and deliver updated targeted refresher training regarding the CIP-007 R7 process for removal and retirement for relevant personnel.
2013-10-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 6 (RFC_URE6) | NCRXXXXX | RFC2013012707 | CIP-004-3 | R4.1 | On July 16, 2013, RFC_URE6 submitted a Self-Report stating that it had an issue of CIP-004-3 R4.1. Effective October 1, 2012, a RFC_URE6 employee changed positions, resulting in a change to his CCA access rights from “full access” to “read only.” Although his cyber access rights were changed to “read only” within the required seven day time frame, the access rights change was not reflected in the list of personnel with authorized cyber access to CCAs. In addition, effective April 1, 2013, a RFC_URE6 employee retired. RFC_URE6 removed the employee’s access rights within seven days but failed to remove his name from the list of personnel with authorized cyber access to CCAs. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. ReliabilityFirst determined that this issue posed a minimal risk to the reliability of the Bulk Power and did not pose a serious or substantial risk based on the following three factors. First, the employee who changed positions remained a trusted RFC_URE6 employee with continued read-only access to CCA information, and the employee who retired did not leave RFC_URE6 for cause. Second, RFC_URE6 timely revoked both employees’ cyber access to CCAs and unescorted physical access to CCAs. Third, this was solely a documentation issue because the subject list is a manually maintained Excel spreadsheet and does not actually authorize or remove personnel access to the CCAs. ReliabilityFirst considered that it discovered the issue through a Self-Report. Effective oversight of the reliability of the Bulk Power System depends on robust and timely self reporting by Registered Entities. ReliabilityFirst considered certain aspects of RFC_URE6's compliance program as mitigating factors. RFC_URE6 has a NERC Compliance Assurance process in place to ensure that it meets the requirements of the Reliability Standards. In addition, the individuals responsible for compliance have direct relationships with senior executives. RFC_URE6's Transmission and Regulatory Strategies Compliance personnel are responsible for FERC and NERC compliance and report directly to the Vice President of Energy Supply Operations. Furthermore, RFC_URE6 periodically conducts internal self-evaluations for compliance with the Reliability Standards. The Chairman of the Executive Management Committee regularly reports compliance status to the RFC_URE6 compliance review committee. ReliabilityFirst considered whether the facts of this issue constitute a repetitive infraction. RFC_URE6 has five previous violations of CIP-004 R4. Four of the prior violations and issues concerned RFC_URE6's failure to timely revoke individuals’ access, and are therefore distinguishable from the instant documentation issues. Only one of the prior issues concerned RFC_URE6's failure to update access lists, and ReliabilityFirst considered that prior issue when assessing RFC_URE6's violation history. Specifically, ReliabilityFirst determined that the conduct related to the transferred employee is not repetitive conduct because it occurred before RFC_URE6's implementation of its mitigating actions for the prior issue. ReliabilityFirst determined that the conduct related to the retired employee, although arguably repetitive conduct, does not warrant a monetary penalty for the reasons set forth in the following paragraph. Despite the violation history outlined above, ReliabilityFirst determined that FFT treatment is appropriate and that a monetary penalty is not warranted. This is based on a number of factors. First, RFC_URE6 has demonstrated a clear commitment to strengthening its internal controls and preventing recurrence of noncompliance. In its Mitigation Plan for the issue, RFC_URE6 committed to strengthening its internal controls by including quality control checks for its access list changes, creating job aids, and training relevant personnel on the changes. Second, as this is solely a documentation issue with no bearing on actual physical access to CCAs, it poses a minimal risk to the Bulk Power System. Third, neither a monetary penalty nor a negotiated settlement agreement would incent desired behavior, discourage undesired behavior, or send any important signals to RFC_URE6 or the industry. | To mitigate the issue RFC_URE6 will complete the following mitigation activities within 90 days: 1) revise its process documentation to include quality control checks for access list changes and train applicable personnel on the process. 2) create an associated job aid listing the specific actions required by applicable personnel when making the cyber access list changes and will train applicable personnel on the use of the new job aid.
2013-10-30 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2011008317 | CIP-006-3a | R1, R1.7 | SERC_URE1 submitted a Self-Report stating that it had an issue with CIP-006-3a R1.7 because it failed to update the physical security plan within 30 calendar days of modification to its access points to a Physical Security Perimeter (PSP). This modification constitutes a physical security system redesign or reconfiguration, as described in CIP-006-3a R1.7. SERC_URE1 reported that on February 16, 2011, it completed changes modifying one of its access points to the PSP. Specifically, SERC_URE1 relocated a door and security cameras leading into the transmission room of its control center. SERC_URE1 moved the door and security cameras less than 10 feet to accommodate new control center furniture. These modifications did not change the size or shape of the associated PSP. SERC_URE1 stated that it did document these modifications within its physical security plan within 30 calendar days, but SERC_URE1 did not complete the necessary update of its physical security plan by approving the updates within 30 calendar days. SERC determined that SERC_URE1’s cyber security policy and physical security plan did require updates within 30 calendar days of completion of any physical security system redesign or reconfiguration. SERC_URE1, however, did not implement these provisions in this instance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system bulk power system. SERC_URE1 documented the modifications in question with this issue, despite not formally approving them, and its failure to approve the documented changes did not alter the physical security of the PSP. The door and surveillance cameras continued to function properly throughout this issue. The size and configuration of the PSP in question with this issue did not change, except for the modifications described above. SERC_URE1 had implemented exterior and interior access controls to reduce the risk of unauthorized access to its Critical Cyber Assets, such as logged video surveillance, roving police/security officer patrols 24 hours a day, 7 days a week, and electronic badge access controls at all six access points to PSPs, five of which require a badge for both ingress and egress. | To mitigate this issue, SERC_URE1: 1) Secured formal approval of the updated physical security plan documentation; and 2) Enhanced the monthly compliance report to ensure appropriate documentation is reviewed and approved.
2013-10-30 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2011009001 | CIP-006-1 | R1, R1.1 | A SERC audit team reported that SERC_URE1 had an issue with CIP-006-1 R1.1 because it discovered two openings larger than 96 square inches, in the Physical Security Perimeter (PSP) resulting in Cyber Assets within its Electronic Security Perimeter not residing in a completely enclosed "six-wall" border. The first opening was 42 inches high and ran the entire length of the 40 foot long PSP. This opening could be accessed by climbing through a nine foot tall drop ceiling, which was located in a restricted access area outside of the PSP. Once above the drop ceiling, an individual could access the protected area through the opening. However, the opening was located 21.5 feet above the floor. The protected area was manned 24 hours a day, seven days a week by two individuals. The second opening was a ventilation duct measuring 7.5 inches by 13.5 inches. The ventilation duct lacked a grate to cover the opening. After this opening, the ventilation duct turned 90 degrees upward and terminated seven inches from a concrete ceiling. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system bulk power system. The first opening was above a drop ceiling in a restricted access area which would have required a ladder to access, the opening into the protected area was 21.5 feet above the floor, and the protected area was manned 24 hours a day, seven days a week. The size and configuration of the second opening would have made it nearly impossible for any human to use it as a physical entry point. SERC_URE1 had implemented exterior and interior access controls to reduce the risk of unauthorized access to its Critical Cyber Assets, such as logged video surveillance, roving police/security officer patrols 24 hours a day, 7 days a week, and electronic badge access controls at all six access points to PSPs, five of which require a badge for both ingress and egress. | To mitigate this issue, SERC_URE1: 1) Hired licensed contractors to install drywall around the area that was a concern; 2) Hired licensed contractors to construct an opening that was 96 square inches or less around one of the office's HVAC vents; and 3) Communicated requirements with SERC_URE1 facility services to prevent future issues.
2013-10-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2013012299 | CIP-006-3c | R5 | SPPRE_URE1 submitted a self report to SPP RE stating that it had an issue with CIP-006-3c R5.1, because it failed to monitor physical access points to a substation PSP for unauthorized access attempts twenty-four hours a day, seven days a week. SPPRE_URE1 utilizes primary and secondary (backup) alarm systems to monitor and alarm Security Operations Center (SOC) personnel of any unauthorized physical access to the substation PSP. The secondary alarm device powered down and became inoperable. A ticket to replace the device was submitted to SPPRE_URE1’s access control vendor. Pending replacement of this device, the primary alarm device went off-line and likewise became inoperable. Thus, both alarm devices lost monitoring and alarming capabilities of the substation PSP. Within several minutes of being alerted of the failure of the primary alarm device, the SOC operator confirmed network communication to the primary device. As a result, the SOC operator mistakenly believed that the primary alarm device was operating properly and did not follow the human observation procedures prescribed in SPPRE_URE1’s Physical Security Plan to monitor physical access points at the substation PSP. | SPP RE determined that the issue posed a minimal risk and not a serious or substantial risk to the reliability of the bulk power system. The substation’s primary alarm device became operational and thus capable of monitoring and alerting for unauthorized attempts or access to the substation PSP approximately seven and one-half hours after going off-line. In addition, the substation is secured by a seven foot fence augmented at the top with barbed and concertina (razor) wire. Inside the perimeter fencing is an independent perimeter intrusion detection system that would have detected an intruder entering the perimeter. Additionally, all door windows are secured with steel mesh window screens. Moreover, SPPRE_URE1 attested that after the primary alarm device became operational, SPPRE_URE1 reviewed the site alarm logs and confirmed that the only two designated access points remained locked and that there were no unauthorized attempts or access to the PSP for the duration of the issue. | To mitigate the issue, SPPRE_URE1 counseled all SOC personnel to ensure they understand their responsibilities and the importance of following the CIP outage procedures of the Physical Security Plan. SPP RE has verified the completion of all mitigation activity.
2013-10-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPPRE_URE2) | NCRXXXXX | SPP2013012298 | CIP-006-3c | R1; R1.7 | SPPRE_URE2 submitted a self report to SPP RE stating that it had an issue with CIP-006-3c R1.7 because it did not update a substation physical security perimeter (PSP) drawing, which is required by SPPRE_URE2’s Physical Security Plan, to reflect physical security system reconfiguration (e.g., security enhancement) of three of four existing access points to the substation PSP within thirty calendar days. The reconfiguration of the PSP access points was completed in November of 2012; however, the PSP drawing was not updated until March of 2013. | SPP RE determined that the issue posed a minimal risk and not a serious or substantial risk to the reliability of the bulk power system. The issue was a documentation deficiency, which did not increase the risk of unauthorized access to SPPRE_URE2’s Critical Cyber Assets located inside the PSP. The PSP was previously found to be compliant with CIP-006 R1 during a 2012 compliance audit. The access points to the PSP were reconfigured to enhance the security of the Critical Cyber Assets located inside the PSP. For instance, since the reconfiguration, all four (instead of only one) of the access points to the PSP are secured by a biometric card reader. Additionally, the PSP drawing was updated less than four months after the reconfiguration of the access points was completed. | To mitigate the issue, SPPRE_URE2 updated the substation PSP drawing in accordance with its Physical Security Perimeter. SPP RE has verified the completion of all mitigation activity.
2013-10-30 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE2012011187 | CIP-009-3 | R5 | Unidentified Registered Entity 1 (TRE_URE1) discovered and self-certified an issue with CIP-009-3 R5. Specifically, TRE_URE1 failed to timely perform an annual test of its backup media for certain Critical Cyber Assets. TRE_URE 1's tested its back up media three months after TRE_URE1's policy states it should be tested. TRE_URE1 had an issue for approximately three months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the bulk power system because: a) the duration period was brief – approximately three months, b) the last exercise was performed 17 months prior - well within the required timeframes contained in Compliance Application Notice (CAN) 0010 – Implementation of Annual in Reliability Standards Requirements (Revised), c) after the testing was performed there were no substantive changes to the Critical Cyber Asset backup media, and d) for the applicable backup systems, the media is non-removable (i.e., backed up to multiple servers at different locations) and, therefore, the media is a hard drive. Each applicable system housing backups for restoration in accordance with the recovery plan is in a defined Physical Security Perimeter. | To mitigate this issue, TRE_URE1 performed the testing of the back-up media. Texas RE has verified the completion of all mitigation activity.
2013-10-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2013012852 | CIP-002-3 | R4 | WECC_URE1 submitted its Self Certification to WECC stating that, it was compliant with CIP-002-3 R4. WECC reviewed WECC_URE1 Self Certification and contacted the entity to request WECC_URE1's Risk-Based Assessment Methodology (RBAM), and lists of Critical Assets and Critical Cyber Assets. WECC determined that a WECC_URE1 senior manager or delegate failed to approve the 2012 RBAM. WECC determined that although the senior manager reviewed the 2012 RBAM, the senior manager failed to approve the 2012 RBAM through signature. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE1’s senior manager did review and approve by signature WECC_URE1’s lists of Critical Assets and Critical Cyber Assets. Further, WECC_URE1 provided evidence demonstrating that the senior manager did review the RBAM. WECC determined that although the senior manager did not formally approve the RBAM by signature, the senior manager validated the RBAM informally over email. | To mitigate this issue, WECC_URE1: 1) WECC_URE1's CIP Senior Manager signed and dated the RBAM; 2) and enhanced its filing system to track instances in which documentation is not reviewed and approved per the timetable outlined by NERC Reliability Standards. WECC has verified the completion of all mitigation activity.
2013-10-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2013012821 | CIP-007-3a | R4 | WECC_URE2 submitted a Self Report to WECC stating that it had an issue with CIP-007-3a R4. WECC_URE2 failed to use anti-virus software and other malicious prevention tools, where technically feasible, when implementing certain equipment associated within its CCURE system. Specifically, WECC_URE2 installed 16 control panels without implementing anti-virus or malware as part of an expansion effort to reconfigure its existing control panels at 12 locations. The expansion increased the number of panels from 22 to 38; however, the 16 additional panels do not support installation of anti-virus or malware prevention tools. Related to this Self-Report, WECC_URE2 submitted a Technical Feasibility Exception (TFE) addressing its technical infeasibility to install anti-virus and other malware software on these devices. WECC approved the TFE request. Based on this information, WECC then determined that WECC_URE2 is in violation of CIP-007-3a R4 for failing to include the 16 control panels to the existing WECC-approved TFE prior to being placed in service. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE2's servers are protected by anti-virus and malware prevention tools that block the introduction of malicious code and or virus-infected files. The panels are used to encrypt data communications between itself and the server and will not respond to any other data connections. Also, the equipment is contained within an environment that is not connected to the internet and network access to the equipment is restricted by the use of access control lists that deny all connections by default. | To mitigate this issue, WECC_URE2: 1) submitted a TFE for the technical infeasibility of the control panels to install anti-virus software and other malware prevention tools. WECC approved the TFE.
2013-09-30 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2013011936 | CIP-004-3 | R3; R3.2 | MRO_URE1 submitted a Self-Report stating that it failed to update each personnel risk assessment (PRA) at least every seven years after the initial PRA, as required by CIP-004-3 R3.2. Specifically, MRO_URE1 failed to perform one PRA within seven years of the previous PRA for one employee. MRO_URE1 originally performed a PRA on the employee. However, the PRA date was incorrectly entered into MRO_URE1's tracking system. Therefore, MRO_URE1 was not properly notified by the system to perform the PRA within the required seven year time period. As a result, MRO_URE1 missed the seven year time period by one year and six months. MRO_URE1 performed a comprehensive review of its PRA records and reported that it has over 2,400 PRA records. Of those 2,400 records, MRO_URE1 identified one data entry error which resulted in one PRA missing a renewal by one year and six months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The employee has worked for MRO_URE1 for over 15 years and has maintained appropriate CIP training. Additionally, this was the second PRA conducted for the employee. MRO_URE1 already performed one PRA on the employee. Furthermore, MRO_URE1 confirmed that the data entry error was limited to one renewal PRA out of 2,400 records. | To mitigate this issue, MRO_URE1: 1) performed a PRA on the employee; 2) reviewed all criminal history and identity verification dates; 3) revised criminal history and identity verification data entry procedures to include an additional level review; and 4) trained personnel on revised data entry procedures. MRO has verified the completion of all mitigation activity.
2013-09-30 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 2 (MRO_URE2) | NCRXXXXX | MRO2012010532 | CIP-004-1 | R2; R2.1 | During a Compliance Audit, MRO_URE2determined that MRO_URE2 failed to ensure that all personnel with access to Critical Cyber Assets, including contractors and service vendors, were trained within ninety calendar days of such authorization as required by CIP-004-1 R2.1. Upon discovering the issue, MRO_URE2 performed a comprehensive review of its personnel training records and determined that 22 individuals did not have training in 2008 (approximately 15%), and five individuals did not have training in 2009 (approximately 4%). All employees, contractors and vendors had proper training in 2010, 2011, 2012, and 2013. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. All of the individuals without the required training in 2008 and 2009 were long term MRO_URE2 employees and contractors that knew the systems. Additionally, all of the employees, contractors and vendors had proper training in 2010, 2011, 2012, and 2013. Therefore, this training issue was resolved three and a half years ago. | To mitigate this issue, MRO_URE2: 1) reviewed policies in place that account for CIP-004 R2, including the processes for MRO_URE2 employee, contractor, and vendor training, and reviewed the contractor and vendor procedures for access and revocation; and 2) developed a more focused training program for Electronic Security Perimeters, Physical Security Perimeters, CIP classification, and NERC compliance training.
2013-09-30 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 2 (MRO_URE2) | NCRXXXXX | MRO2012010538 | CIP-005-1 | R2; R2.2 | During a Compliance Audit, MRO_URE2determined that MRO_URE2 failed to document ports and services required for operations and for monitoring Cyber Assets within the Electronic Security Perimeter (ESP) as required by CIP-005-2 R2.2. Specifically, MRO_URE2 failed to document one port that was enabled for monitoring Cyber Assets within the ESP. Although the port was properly enabled, it was not documented. The port is required for operations and monitoring when using a device (VPN) web interface. Access to that interface requires two factor authentication. Upon discovering the documentation issue, MRO_URE2 performed a full review of its ports and services required for operations and for monitoring Cyber Assets within the ESP. Of the ports subject to CIP-005-2 R2.2, MRO_URE2 failed to document one out of 96 ports, or approximately 1%. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because although MRO_URE2 failed to document the port, the port was properly enabled. Additionally, MRO_URE2 did not identify any other documentation issues with its ports and services required for operations and monitoring Cyber Assets within the ESP. It failed to document one out of 96 ports, or approximately one percent. | To mitigate this issue, MRO_URE2: 1) developed additional procedures for assessing ports and services including the creation of baselines and their verification; 2) prepared a capital project for acquiring a tool-based technical solution that would provide advanced protections to Critical Cyber Assets within the ESPs, access points, and monitoring systems; and 3) changed its review process to alternate between third party Cyber Vulnerability Assessments (CVAs) and in-house CVAs. This will address concerns regarding “checks and balances” within MRO_URE2 where the same personnel that completed the work are the only ones equipped to execute the CVA in order to assess the work.
2013-09-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2012009780 | CIP-005-2 | R4; R4.2, R4.3 | NPCC_URE1 submitted to NPCC that it had an issue CIP-005-2 Requirement 4. Upon reviewing the vulnerability assessment, it was discovered that there was no documentation showing proof that a review of the ports and services required for operations at the access points was completed as part of the assessment. There was no documentation showing the discovery of all access points to the Electronic Security Perimeter. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. During the mitigation of the violation, NPCC_URE1's Risk Based Assessment Methodology changed and subsequently removed the critical assets from the critical asset list. The facility in question was not a critical asset and does not need the same protections afforded to critical assets. There was no actual impact as there were no cyber incidents at NPCC_URE1 facilities. | To mitigate this issue, NPCC_URE1: 1) removed the facilities from their critical asset list. NPCC has verified the completion of all mitigation activity.
2013-09-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2012009700 | CIP-005-2 | R4; R4.4 | NPCC_URE1 submitted to NPCC that it had an issue with CIP-005-2 Requirement 4. In a review of NPCC_URE1 vulnerability assessment (VA), it was discovered that the VA did not include evidence of a review of controls for default accounts, passwords, and network management community strings on electronic access points to the Electronic Security Perimeter. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. During the mitigation of the violation, NPCC_URE1's Risk Based Assessment Methodology changed and subsequently removed the critical assets from the critical asset list. The facility in question was not a critical asset and does not need the same protections afforded to critical assets. NPCC_URE1 protects its cyber assets by including firewalls, access authentication, and access monitoring. There was no actual impact as there were no cyber incidents at NPCC_URE1 facilities. | To mitigate this issue, NPCC_URE1: 1) removed the facilities from their critical asset list. NPCC has verified the completion of all mitigation activity.
2013-09-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2013011693 | CIP-006-3c | R1; R1.6.1 | NPCC_URE1 submitted to NPCC that it had an issue with CIP-006-3c Requirement 1. After a review of visitor logs it was identified that there was no exit time on the written log for a visitor. The badge reader system did not log the exit time. The videos from this day were not retrievable for the physical security perimeter. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although the visitor did not have an exit time, he was continually escorted during the duration of his visit. During the mitigation of the violation, NPCC_URE1's Risk Based Assessment Methodology changed and subsequently removed the critical assets from the critical asset list. The facility in question was not a critical asset and does not need the same protections afforded to critical assets. | To mitigate this issue, NPCC_URE1: 1) removed the facilities from their critical asset list. NPCC has verified the completion of all mitigation activity.
2013-09-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2012009781 | CIP-007-2a | R5; R5.1, R5.2, R5.3 | NPCC_URE1 submitted to NPCC that it had an issue with CIP-007-2a Requirement 5. It was discovered that NPCC_URE1 did not have documentation showing an initial review of individual and shared system accounts and authorized access permissions. NPCC_URE1 did not have the proper documentation showing implementation of their procedure for minimizing and managing scope of acceptable use of administrator, shared, and other generic account privileges due to lack of a valid baseline of administrator, shared, and other generic account privileges. NPCC_URE1 did not submit Technical Feasibility Exceptions for all devices that could not technically enforce the standard. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. During the mitigation of the violation, NPCC_URE1's Risk Based Assessment Methodology changed and subsequently removed the critical assets from the critical asset list. The facility in question was not a critical asset and does not need the same protections afforded to critical assets. Access authorization is documented to include physical and cyber access to all employees and access is monitored. | To mitigate this issue, NPCC_URE1: 1) removed the facilities from their critical asset list. NPCC has verified the completion of all mitigation activity.
2013-09-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2012009783 | CIP-007-2a | R8; R8.2, R8.3 | NPCC_URE1 submitted to NPCC that it had an issue with CIP-007-2a Requirement 8. Upon reviewing the vulnerability assessment, it was discovered that there was no documentation showing a review to verify that only ports and services required for operation of the cyber assets within the Electronic Security Perimeter were enabled. There was no documentation showing a review of controls for default accounts. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. During the mitigation of the violation, NPCC_URE1's Risk Based Assessment Methodology changed and subsequently removed the critical assets from the critical asset list. NPCC_URE1 also protects its cyber assets by including firewalls, access authentication, and access point monitoring. The facility in question was not a critical asset and does not need the same protections afforded to critical assets. Also there was no actual impact as there were no cyber incidents at NPCC_URE1 facilities. | To mitigate this issue, NPCC_URE1: 1) removed the facilities from their critical asset list. NPCC has verified the completion of all mitigation activity.
2013-09-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2012009782 | CIP-007-3a | R6; R6.4 | NPCC_URE1 submitted to NPCC that it had an issue with CIP-007-3a Requirement 6. Upon an internal review, NPCC_URE1 discovered that its primary centralized log server had a service outage and did not retain logs for the past 90 days. The backup server was configured to retain logs for only 30 days. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Logging and alerting was still functional through the backup centralized log server during the outage of the main log server. | To mitigate this issue, NPCC_URE1: 1) installed a new centralized log server; 2) ensured the setting for the backup log center is set to retain logs for 90 days; and 3) documented and communicated all updates to staff NPCC has verified the completion of all mitigation activity.
2013-09-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2012009784 | CIP-008-2 | R1; R1.1, R1.2 | NPCC_URE1 submitted to NPCC that it had an issue with CIP-008-2 Requirement 1. It was discovered that the NPCC_URE1 documented cyber security incident response plan did not include procedures to characterize and classify events as reportable cyber security events. Their cyber security incident response plan included roles and responsibilities, but did not include response actions to cyber security incidents. While NPCC_URE1 uses a notification matrix for these types of incidents, there was no reference to the notification matrix in the incident response plan that showed how and when this matrix was triggered or executed. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. During the mitigation of the violation, NPCC_URE1's Risk Based Assessment Methodology changed and subsequently removed the critical assets from the critical asset list. The facility in question was not a critical asset and does not need the same protections afforded to critical assets. Although NPCC_URE1 did not specifically have a reference to the notification matix in their response plan, NPCC_URE1's notification matrix defines whom to contact during times of incident. Also there was no actual impact as there were no cyber incidents at NPCC_URE1 facilities. | To mitigate this issue, NPCC_URE1: 1) removed the facilities from their critical asset list. NPCC has verified the completion of all mitigation activity.
2013-09-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 2 (NPCC_URE2) | NCRXXXXX | NPCC2012011562 | CIP-005-3a | R3; R3.2 | NPCC_URE2 submitted to NPCC that it had an issue with CIP-005-3a R3. NPCC_URE2 had a hardware failure of their Monitoring, Analysis, and Response System (MARS) and was unable to monitor, log, or alert personnel of attempts at unauthorized electronic access. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although NPCC_URE2's MARS was inoperable for 5-11 days, accesss control processes were fully operational. The access control processes authenticate authorized electronic access and prevent unauthorized electronic access to the Electronic Security Perimeter (ESP). Also, NPCC_URE2 is able to monitor and record authorized electronic access to the ESP and authorized users must contact the Shift Supervisor before accessing the ESP. The electronic access point is located on a private corporate network that is protected by a corporate firewall and is not directly accessible from the internet. | To mitigate this issue, NPCC_URE2: 1) Replaced the MARS device; and 2) implemented an automated test to verify the availability and function of the monitoring and alerting process. NPCC has verified the completion of all mitigation activity.
2013-09-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 2 (NPCC_URE2) | NCRXXXXX | NPCC2012011631 | CIP-007-1 | R5; R5.1 | NPCC_URE2 submitted to NPCC that it had an issue with CIP-007-1 R5. During an internal review of the process for monitoring security events, NPCC_URE2 determined that the logging functions of three Cyber Assets located within the Electronic Security Perimeter (ESP) were not generating logs of sufficient detail to create historical audit trails of individual user account access activity. | The issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The three cyber assets provided a communications path between the control room and a programmable logic controller (PLC) that operates two diesel generators used in blackstart situations. The diesel generators are located adjacent to the power plant housing the control center. In the event of failure of the communications path, the plant operators would start the diesel generators from the local control panel. The three cyber assets were included in approved TFEs. They were also located on a subnet that had no routable communications outside the subnet and no devices that were dial up accessible on the subnet. The subnet was entirely located within a defined Physical Security Perimeter (PSP). Physical access to the subnet was required in order to log on to the network switches. The personnel that had authorized access to the switches had personnel risk assessments and annual cyber security training. Physical access controls restricted, logged, and monitored physical access to the PSP where the three cyber assets were located during the period that the three devices lacked sufficient logging of electronic access. | To mitigate this issue, NPCC_URE2: 1) Removed the three switches from the ESP. Due to their location on an isolated subnet, the three network switches could not be configured to communicate with the existing monitoring, analysis, and response system that consolidates logs and generates alerts. 2) Added tasks to annually check all devices within the ESP to verify that logging, monitoring and alerting of security events is properly implemented on all Cyber Assets or that applicable TFEs have been approved. NPCC has verified the completion of all mitigation activity.
2013-09-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 2 (NPCC_URE2) | NCRXXXXX | NPCC2012011632 | CIP-007-1 | R6; R6.1, R6.2, R6.3 | NPCC_URE2 submitted to NPCC that it had an issue with CIP-007-1 R6. During an internal review of the process for monitoring security events, NPCC_URE2 determined that three Cyber Assets located within the Electronic Security Perimeter (ESP) were not configured to monitor and log system events or issue alerts for detected cyber security incidents. Organizational processes and technical and procedural mechanisms for monitoring for security events were not properly implented on three cyber assets. | The issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The three cyber assets provided a communications path between the control room and a programmable logic controller (PLC) that operates two diesel generators used in blackstart situations. The diesel generators are located adjacent to the power plant housing the control center. In the event of failure of the communications path, the plant operators would start the diesel generators from the local control panel. The three cyber assets were included in approved TFEs. They were also located on a subnet that had no routable communications outside the subnet and no devices that were dial up accessible on the subnet. The subnet was entirely located within a defined Physical Security Perimeter (PSP). Physical access to the subnet was required in order to log on to the network switches. The personnel that had authorized access to the switches had personnel risk assessments and annual cyber security training. Physical access controls restricted, logged, and monitored physical access to the PSP where the three cyber assets were located during the period that the three devices did not log system events or issue alerts. | To mitigate this issue, NPCC_URE2: 1) Removed the three switches from the ESP. Due to their location on an isolated subnet, the three network switches could not be configured to communicate with the existing monitoring, analysis, and response system that consolidates logs and generates alerts. 2) Added tasks to annually check all devices within the ESP to verify that logging, monitoring and alerting of security events is properly implemented on all Cyber Assets or that applicable TFEs have been approved. NPCC has verified the completion of all mitigation activity.
2013-09-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 2 (NPCC_URE2) | NCRXXXXX | NPCC2012011563 | CIP-007-3a | R6; R6.2 | NPCC_URE2 submitted to NPCC that it had an issue with CIP-007-3a R6. NPCC_URE2 had a hardware failure of their Monitoring, Analysis, and Response System (MARS) and was unable to issue automated or manual alerts for detected cyber security incidents. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In a review of the event logs maintained on the Cyber Assets, no security events occurred during the 5-11 days in which NPCC_URE2's MARS was inoperable. Access control processes were fully operational. The access control processes authenticate authorized electronic access and prevent unauthorized electronic access to the Electronic Security Perimeter (ESP). Also, NPCC_URE2 is able to monitor and record authorized electronic access to the ESP and authorized users must contact the Shift Supervisor before accessing the ESP. The electronic access point is located on a private corporate network that is protected by a corporate firewall and is not directly accessible from the internet. | To mitigate this issue, NPCC_URE2: 1) Replaced the MARS; and 2) implemented an automated test to verify the availability and function of the monitoring and alerting process. NPCC has verified the completion of all mitigation activity.
2013-09-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 3 (NPCC_URE3) | NCRXXXXX | NPCC2012010785 | CIP-002-1 | R4 | NPCC_URE3 submitted to NPCC that it had an issue with CIP-002-1 Requirement 4. NPCC_URE3, as part of the Risk Based Assessment Methodology (RBAM), determined they had no critical assets, but failed to execute a Null List. | The issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). NPCC_URE3 applied the RBAM and did not have any Critical Assets or Critical Cyber Assets and it is signed by a senior officer. | To mitigate this issue, NPCC_URE3: 1) Updated 2009 and 2010 RBAMs to include Null List; 2) Updated their Computerized Maintenance Management System (CMMS) to include an annual application of the RBAM including a null list if required; 3) Updated CMMS to alert the requirement for completion of the annual RBAM 90 days prior to due date.
2013-09-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 4 (NPCC_URE4) | NCRXXXXX | NPCC2012011242 | CIP-004-3 | R4; R4.2 | NPCC_URE4 submitted to NPCC that it had an issue with CIP-004-3 R4. NPCC_URE4 failed to revoke a vendor's physical access to Critical Cyber Assets within seven calendar days after the vendor voluntarily separated from their company. The revocation of the employee's access was not completed until nine days after his separation from the company. | The issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although NPCC_URE4 did not revoke the vendor's access within seven calendar days, the vendor did not have possession of his access card which must be turned into personnel at the end of each work day. The individual was fully CIP trained and had an up-to-date personal risk assessment. The vendor's access was removed nine days after the vendor voluntarily separated from their company. | To mitigate this issue, NPCC_URE4: 1) Issued a reminder of CIP reporting obligations to all vendors. 2) Developed, published, and rolled-out a lessons learned to all transmission contract administrators and project managers. 3) Established a process to ensure timely communication between the contract company and NPCC_URE4. The process is incoporated into training and contracts associated with new CIP contractors as well as active vendors who have employees with CIP access. NPCC has verified the completion of all mitigation activity.
2013-09-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 5 (NPCC_URE5) | NCRXXXXX | NPCC2013012541 | CIP-006-3c | R1; R1.6.2 | NPCC_URE5 submitted to NPCC that it had an issue with CIP-006-3c R1. There were three events in which the NPCC_URE5 allowed unescorted visitor access within the physical security perimeter. On one occasion, the authorized badge holder that was monitoring the construction crew did not have continuous line of sight of the two visitors in question. The visitors had propped open the door to the training room and were able to access the training room’s cyber assets. On two occasions, visitors were unescorted in the NPCC_URE5's lobby which is within NPCC_URE5’s physical security perimeter (PSP). | The issue posed a moderate risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The issue did not pose a minimal risk because on one occasion, the unescorted visitors had physical access to cyber assets that have the ability to reach production applications. Although NPCC_URE5 did not have continuous escorted access of the visitors within the physical security perimeter, the rooms that were accessible did not contain any critical cyber assets. Access to the training room workstations are controlled by CIP compliant accounts and passwords. Also, an authorized approver must grant authority to a user in order to access production applications. The production applications can only be used to monitor the BPS. Video footage found that the visitors did not attempt to access the workstations. On two separate occasions, visitors were unescorted while waiting in a receptionist area which contains a VOIP telephone that was not accessed by the visitors. The area is separated from the rest of the PSP with the use of a dual factor biometric physical access control. NPCC reviewed NPCC_URE5's internal compliance program and considered it to be a mitigating factor. NPCC_URE5 has an Internal Compliance Program in place that is supported and engaged by Senior Management. NPCC_URE5 employs a full time corporate compliance director who reports to the VP and General Counsel. NPCC_URE5 has a mandatory education and training on compliance responsibilities and risk. NPCC also considered NPCC_URE5's cooperation as a mitigating factor in assessing the Find, Fix, Track process. | To mitigate this issue, NPCC_URE5: 1) Required the authorized badge holder to retake the cyber security test. He was also required to attend a meeting with the NPCC_URE5 IT infrastructure manager, the NPCC_URE5 physical security individual, and the owner of the construction company where it was made clear that vendor personnel fully understood the importance of following NPCC_URE5 policies and procedures. NPCC_URE5 personnel made sure vendor personnel were clear on how to properly escort visitors and that circumventing, disabling, or overriding physical access control in anyway was not permitted. 2) The NPCC_URE5 Compliance Manager sent an email to all NPCC_URE5 staff reminding them that all receptionist areas are a part of their PSPs and all visitor control procedures apply to those areas. The individuals who allowed access to the lobby were made clear what the visitor procedures were. 3) The non-critical cyber assets within the ESP in the lobby were reconfigured to no longer be inside the ESP. The lobby was also removed from the PSP. NPCC has verified the completion of all mitigation activity.
2013-09-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2013012619 | CIP-004-3a | R2.1 | On June 18, 2013, RFC_URE1 submitted a Self-Report stating that it had an issue of CIP-004-3a R2.1 (ReliabilityFirst determined that the facts and circumstances of this possible violation also implicated CIP-004-3a R3. ReliabilityFirst treated the issue under one Violation ID number, however, because the issue arose from the same factual situation of improperly granting access to nine individuals). On Monday, June 10, 2013 at 10:51 a.m., while updating a clearance code for a non-CIP protected door, RFC_URE1 inadvertently added two CIP protected doors, resulting in the provisioning of Critical Cyber Assets to nine individuals' access cards. All nine individuals are employees of the two firms that build and maintain the Physical Access Control and Monitoring ("PACM") system for RFC_URE1. In 2009, RFC_URE1 developed a daily automated report that compares data from the PACM application with another system to identify potential errors in data maintenance and the provisioning of access privileges for these situations. On Tuesday, June 11, 2013 at approximately 10:45 a.m. based on the daily report, the individual responsible for NERC program administration was alerted to the mistake and immediately removed the individuals' access. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The risk posed by the foregoing facts and circumstances was mitigated by the following factors. All nine individuals are employees of the two firms that build and maintain the PACM system for RFC_URE1. The nine individuals were trusted contractors who already had clearance codes for every other non-CIP protected asset in the RFC_URE1 fleet. The contractors’ employer had screened the individuals through an investigation more rigorous than required by CIP-004 R3. During the time that the individuals had the potential to access these assets, none of them attempted to gain access at the readers in question. RFC_URE1 stated that it has no reason to believe the individuals were even aware that they had access to the assets. Because RFC_URE1 previously developed a daily automated report that compares data from the PACM application with another system to identify potential errors in data maintenance and the provisioning of access privileges for just this contingency, RFC_URE1 detected the error and promptly corrected it within approximately 24 hours. ReliabilityFirst considered certain aspects of RFC_URE1's compliance program. RFC_URE1 has an internal compliance program, which consists of the Federal Regulatory Affairs and Policy ("FRAP") group. The FRAP group developed and implemented the Federal Energy Regulatory Compliance Program to assure and demonstrate compliance with the FERC electric regulations including the NERC Reliability Standards. The FRAP group also assists in the development and documentation of the necessary compliance processes and helps educate RFC_URE1 individuals responsible for executing the compliance process. In addition, RFC_URE1 requires all employees to annually certify their review and understanding of corporate policies, including the Code of Business Conduct. The Corporate Compliance Officer, who is the Corporate Secretary and General Counsel, has independent access to the Audit and Oversight Committee of the Board of Directors, as well as to the CEO and Chairman of the Board of RFC_URE1. In addition, senior management approves policies, procedures, self-certifications, and data submittals, and receives quarterly reports on the level of FERC and NERC compliance in their respective areas. ReliabilityFirst also considered that it discovered the issue through self report and applied mitigating credit. Effective oversight of the reliability of the Bulk-Power System depends on robust and timely self reporting by Registered Entities. RFC_URE1 promptly identified and reported the issue due to the effective execution of its compliance program and the installation of internal controls that yielded identification of the issues prior to the occurrence of any harm. Specifically, RFC_URE1’s daily automated report that compares data from the PACM application with another system to identify potential errors in data maintenance and access provisioning is commendable. As a result, ReliabilityFirst seeks to encourage these internal controls and this type of self reporting, characterized by spontaneous timely detection and timely correction unconnected to a pending regional compliance monitoring action. ReliabilityFirst considered whether the facts of this issue constitute a repetitive infraction by analyzing whether they evidenced any (a) repeated or continuing conduct similar to that underlying a prior violation of the same or a closely-related Reliability Standard Requirement; (b) conduct addressed in any previously submitted mitigation plan for a prior violation of the same or a closely¬ related Reliability Standard Requirement; or (c) multiple violations of the same Standard and Requirement. RFC_URE1 has not previously violated CIP-004-3a R2, and as a result, ReliabilityFirst did not consider RFC_URE1's violation history as an aggravating factor. | To mitigate this issue, RFC_URE1 implemented a new naming convention in its PACM system for CIP-protected doors that will preclude the possibility that a CIP-protected door could be retrieved when updating clearance codes for non-CIP physical assets.
2013-09-30 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC201000550 | CIP-003-1 | R1, R1.2 | The SERC spot check team reported that SERC_URE1 had an issue with CIP-003-1 R1 because, a year prior to the audit, some of the policies and procedures supporting the main cyber security policy were in draft form and had not been approved by the SERC_URE1 senior manager. In addition, SERC_URE1 failed to make its cyber security policy readily available to all personnel who had access to, or were responsible for, Critical Cyber Assets (CCAs). SERC later determined SERC_URE1 had an issue with CIP-003-1 R1.2 only because it failed to make its cyber security policy readily available to all personnel who had access to, or were responsible for, CCAs. SERC_URE1’s cyber security policy, which consisted of a two page parent policy that restated the CIP Standards and referenced other supporting documents for each CIP Standard, was made available to SERC_URE1 personnel via email distribution. However, SERC_URE1 only provided the documents referenced in the two page parent policy to personnel on a “need to know” basis after they had been specifically requested. Therefore, SERC_URE1 did not make its full cyber security policy readily available to all personnel who had access to, or were responsible for, CCAs. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because: 1) SERC_URE1 made the primary document of the cyber security policy, which was approved by the senior manager, readily available; 2) The supporting documents for each CIP Standard were listed in the cyber security policy, allowing SERC_URE1 personnel to specifically request those documents; and 3) SERC_URE1 made the supporting documents for each CIP Standard available upon request. | To mitigate this issue, SERC_URE1 posted the cyber security policy with the supporting documents on its corporate intranet where it was readily available to all employees, contractors, and vendors. SERC has verified the completion of all mitigation activity.
2013-09-30 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC201000589 | CIP-004-1 | R3 | SERC_URE1 submitted a Self-Report to SERC stating that it had an issue with CIP-004-1 R3 because it did not conduct a personnel risk assessment (PRA) within 30 days of granting personnel authorized cyber or authorized unescorted physical access to Critical Cyber Assets (CCAs). As a result of an internal review, SERC_URE1 discovered that it had failed to conduct a PRA on an individual within 30 days of granting that individual access to CCAs. SERC_URE1 granted one employee authorized physical access and initiated a PRA for the employee. SERC_URE1’s corporate security staff received the results of the PRA one day past the 30 days allowed by CIP-004-1 R3. The employee used his or her access in the 30 day window while SERC_URE1 conducted the PRA. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because: 1) SERC_URE1 received the PRA results for one employee one day late; and 2) The employee in question had worked for SERC_URE1 for eight years and received cyber security training as required within 90 days of being granted access to CCAs. | To mitigate this issue, SERC_URE1's corporate security department revised its PRA procedure to meet Version 2 of the CIP standards requiring that a PRA be completed prior to authorization of unescorted physical access to CCAs. SERC has verified the completion of all mitigation activity.
2013-09-30 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2011007984 | CIP-003-1 | R5, R5.1 | The SERC audit team reported that SERC_URE1 had an issue with CIP-003-1 R5.1 because it failed to provide historical evidence of a complete list used to designate personnel who are responsible for authorizing logical or physical access to protected Critical Cyber Asset (CCA) information as required. SERC_URE1 had a procedure that detailed how cyber access to CCA information should be managed and who should be responsible for authorizing such access. In the procedure, SERC_URE1 provided a list of personnel responsible for authorizing cyber access to protected CCA information including their name, title, phone number, and the information to which they could authorize access. The SERC audit team found this historic procedure was deficient because it did not include information on who should authorize access to any protected CCA information that was physical in nature. Prior to the audit, SERC_URE1 revised and updated its procedure to clarify the roles of designated personnel for authorizing both cyber and physical access to protected CCA information. SERC determined that the historic SERC_URE1 procedure for protected CCA information access focused on cyber access to protected CCA information, and did not address any physical access to protected CCA information stored in physical formats. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because: 1) SERC_URE1’s protected CCA information was securely stored in existing Physical Security Perimeters and only personnel with authorized physical or cyber access were able to access the information; 2) SERC_URE1 personnel responsible for protected CCA information understood that the logical access specified in the procedures included physical access as well; and 3) SERC_URE1 resolved this issue on its own prior to the audit finding. | To mitigate this issue, SERC_URE1 revised its procedure for granting physical and electronic access to protected CCA information. SERC has verified the completion of all mitigation activity.
2013-09-30 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2011007991 | CIP-007-1 | R5, R5.2.3 | The SERC audit team reported that SERC_URE1 had an issue with CIP-007-1 R5.2.3 because it failed to include provisions for creating an audit trail for use of shared accounts in its shared account management policy for one registered function. SERC_URE1 had one Critical Cyber Asset for one registered function, a terminal server that utilized a single administrative shared account. SERC_URE1 addressed account management and appropriate use of the single shared administrative account in its shared account management policy for the registered function. SERC determined that this policy did not address how SERC_URE1 would track shared account usage. Instead, SERC_URE1 covered account set-up, access authorization, and password requirements in a separate access control procedure. Despite the lack of provisions for creating an audit trail in its shared account management policy, SERC_URE1 was able to provide the auditors an audit trail of the use of the shared account by using log-in data obtained from the two-factor authentication log-in server. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because: 1) This issue was limited to a single shared account; 2) SERC_URE1 was able to produce an audit trail of the shared account usage; and 3) SERC_URE1 was able to explain the process for creating an audit trail for the shared account despite the fact that the process was not formally documented. | To mitigate this issue, SERC_URE1 revised its shared account management policy to more clearly define how audit trails for shared accounts are created. SERC has verified the completion of all mitigation activity.
2013-09-30 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 2 (SERC_URE2) | NCRXXXXX | SERC2013012517 | CIP-006-3c | R4 | SERC_URE2 submitted a Self-Report to SERC stating that it had an issue of CIP-006-3c R4 because it failed to implement operational controls to manage physical access at all access points to the Physical Security Perimeter (PSP) 24 hours a day, 7 days a week. On a Saturday afternoon, SERC_URE2 experienced a fire alarm at the facility which houses the primary energy control center. Due to human safety concerns, the fire alarm disabled the physical security controls by de-energizing the access control locks, providing unrestricted ingress and egress to the PSP during an emergency. SERC_URE2 immediately responded to the fire alarm, briefly investigated, and determined it to be a false alarm. SERC_URE2’s physical access control system sent an automated email to certain personnel notifying them of the false fire alarm and that the access control locks needed to be re-energized. SERC_URE2 limited the distribution list for this email to individuals who did not work on weekends. As a result, SERC_URE2 was unaware of the need to re-energize its access control locks until Monday morning, when SERC_URE2’s telecommunications engineer reviewed the email. A few minutes later, SERC_URE2 re-energized the access control locks and verified the locks on the doors to the PSP were functioning correctly. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The primary control center is manned 24 hours a day, 7 days a week, including throughout the approximately 2 days at issue. The primary control center is located within a larger, secured perimeter that is protected by additional layers of security, including fencing and gates, requiring card access for entry. The exterior perimeter gates and PSP doors remained closed and badge readers remained in-service, allowing SERC_URE2 to monitor access throughout the duration of the issue. If an individual entered one of the unlocked doors during the issue without first using a badge reader, a forced door entry alarm would have alerted SERC_URE2 of this entry. | To mitigate this issue, SERC_URE2: 1) added notification to manned on-site personnel and expanded the email notification group for further detail and follow up; 2) installed a reset switch to handle post-fire alarm security system rearming and established a procedure for fire response personnel; and 3) formalized the on-call administration security schedule by moving from a group-based response to an individually assigned on-call response schedule, in which administrative on-call personnel are responsible for verifying the response and completing the investigation.
2013-09-30 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 3 (SERC_URE3) | NCRXXXXX | SERC2013012140 | CIP-006-3c | R1; R1.7 | SERC_URE3 submitted a Self-Report to SERC stating that it had an issue of CIP-006-3c R1.6 because it failed to continuously escort visitors within the Physical Security Perimeter (PSP). Upon reviewing SERC_URE3's physical security plan, SERC determined that SERC_URE3’s visitor control escorting process outlined in the plan was adequate to meet the requirements of CIP-006-3c R1.6. However, while investigating the R1.6 Self-Report, SERC determined that SERC_URE3 had an issue of CIP-006-3c R1.7. SERC_URE3 implemented a control system upgrade and removed all CIP assets from the communications room. Once the CIP assets were removed, there was no need for a secured Electronic Security Perimeter and therefore, no need to protect the room with a PSP. SERC_URE3 was not aware that the communications room did not have any CIP assets until ten months later and did not update the documentation to reflect removing a PSP within the required 30 days. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. There were no Critical Cyber Assets (CCAs) located within the communications room that could have affected the reliability of the Bulk Power System. The issue was the result of a documentation error in that the physical security plan and the corresponding drawings were not updated to reflect removing a PSP. | To mitigate this issue, SERC_URE3: 1) had a meeting with SERC_URE3 departments to remind staff of their duties as an escort; 2) sent an email to staff that have CIP access to remind them of the requirement of an escort for all visitors at all times in CIP rooms; 3) held mandatory training sessions for all personnel who have CIP access that covered the requirements for visitors; 4) provided a procedure on the visitor control program to all personnel who have CIP access; 5) removed all rooms without CCAs from the PSP; and 6) conducted a PSP and CCA audit to confirm PSP boundaries and CCA locations.
2013-09-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2013011955 | CIP-006-3c | R1; R1.1 | SPPRE_URE1 submitted a self report to SPP RE stating that it had an issue with CIP-006-3c R1.1 because it was unable to ensure that all Cyber Assets within an Electronic Security Perimeter (ESP) resided in a completely enclosed “six-wall” Physical Security Perimeter (PSP). SPPRE_URE1 discovered a 20 x 24 inch heating and air-conditioning ventilation (HVAC) floor vent located in a second floor hallway that was not secured. Had the HVAC vent been removed, it would have exposed the top of the ceiling tiles of a Transmission Dispatch Center, which is located on the first floor and within a PSP. | This issue posed a minimal risk and not a serious or substantial risk to the reliability of the bulk power system. The lack of a secure six-wall border presented a risk of unauthorized access to SPPRE_URE1’s Critical Cyber Assets. The risk was lessened because SPPRE_URE1 had a documented physical security plan in place and multiple layers of external and internal access controls protecting Critical Cyber Assests within the PSP. The facility is secured by a ten foot fence augmented at the top with barbed and concertina (razor) wire. Additionally, the facility is secured by an entrance gate, which can only be opened by individuals with a security card to the facility. Also, the facility has nine exterior security cameras that are continuously monitored on-site by SPPRE_URE1 personnel; therefore, any malicious activity would have been seen and immediately investigated. The building perimeter doors require badge access and are also monitored by the SOC personnel. Therefore, a forced or left open exterior door would have triggered an alarm prompting an immediate investigation by SOC personnel. Once inside the facility, had an intruder removed the HVAC vent and ceiling tiles and discovered the PSP gap, the intruder would be required to jump down approximately ten feet to land on the floor of PSP. Further, the PSP is manned twenty-four hours a day, seven days a week. Thus, an intruder most likely would have been seen by SPPRE_URE1 personnel who would have immediately investigated the incident. Considering all the protective measures SPPRE_URE1 had in place, it was extremely unlikely that an intruder could have accessed its PSP undetected. Moreover, SPPRE_URE1 attested that there have been no security incidents regarding its PSP. | To mitigate the issue, SPPRE_URE1: 1. Updated SOC Supervisor procedures to remind the coordinator to re-inspect the PSP and ensure there is a complete 6-wall during the CIP-006 annual test. 2. Inspected all of SPPRE_URE1’s PSPs to ensure there are no openings in the six-wall border. 3. Hired a contractor to secure the HVAC vent. SPP RE has verified the completion of all mitigation activity.
2013-09-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPPRE_URE2) | NCRXXXXX | SPP2012010958 | CIP-005-1 | R1; R1.1 | During a Compliance Audit, the Southwest Power Pool Regional Entity (SPP RE) determined that SPPRE_URE2 had an issue with CIP-005-1 R1.1 because SPPRE_URE2 did not identify and document all access points to the Electronic Security Perimeter (ESP). Specifically, SPPRE_URE2 did not identify its Front End Processor Terminal Servers as access points to its ESP. The servers were communication end points, serially connected to Remote Terminal Units (RTUs) and to Frame Relay Access Devices (FRADs). Both the RTUs and the FRADs resided in SPPRE_URE2 substations, which were designated as PSPs. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although the serial communications were not identified or documented as access points to the ESP, these communications were non-routable, thereby preventing exploitation of the communication in transit. Additionally, because the termination points were located within PSPs, they were afforded physical access controls, lessening the likelihood that the communication could be physically exploited. | To mitigate this issue, SPPRE_URE2: 1) Moved and configured the terminal servers to reside outside of the ESP; and 2) Updated its ESP diagram. SPP RE has verified the completion of all mitigation activity.
2013-09-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 3 (SPPRE_URE3) | NCRXXXXX | SPP2013011797 | CIP-003-(1-3) | R5; R5.1, R5.1.1, R5.1.2, R5.2, R5.3 | SPPRE_URE3 submitted a Self-Report to SPP RE that it had an issue with CIP-003-1 R5 (5.1-5.3) because it had not documented its program for managing access to Critical Cyber Asset information. SPP RE determined that this violation implicated versions 1-3 of CIP-003 R5 (5.1-5.3). | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SPPRE_URE3 had implemented processes to ensure the protection of Critical Cyber Asset information from unauthorized access, despite the lack of a documented program. For instance, all personnel with physical access to Critical Cyber Asset information are trained in the proper treatment of Critical Cyber Asset information prior to being granted access to such information. Moreover, electronic access to Critical Cyber Asset information in electronic “share” folders is restricted by domain groups that are assigned based on “need-to-know” job functions. Furthermore, SPPRE_URE3 required the identification and marking of Critical Cyber Asset information in its document classification and security procedure, thus ensuring that personnel were on notice of which documents required heightened protection measures. | To mitigate the issue, SPPRE_URE3 documented its program for managing access to protected Critical Cyber Asset Information. SPP RE has verified the completion of all mitigation activity.
2013-09-30 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE2012010033 | CIP-003-1 | R1; R1.1 | During an audit Texas RE conducted of TRE_URE1, Texas RE discovered an issue with CIP-003-1 R1. Texas RE found while TRE_URE1 mentioned Standards CIP-002 through CIP-009 in its cyber security policy, TRE_URE1 failed to specifically address the requirements in each CIP-002 through CIP-009 standard per CIP-003-1 R1.1. TRE_URE1 did not address CIP-002 through CIP-009 in its cyber security policy for approximately three years and three months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the bulk power system. An insufficient cyber security policy could result in personnel not having proper direction and guidance with regards to critical cyber assets. Although not specifically mentioned in the policy, TRE_URE1 did have some documentation of a cyber-security policy that addressed the requirements of CIP-002 through CIP-009, though not in specific detail. | To mitigate this issue, TRE_URE1 addressed CIP-002 through CIP-009 in its cyber security policy. Texas RE has verified the completion of all mitigation activity.
2013-09-30 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE2012010035 | CIP-003-1 | R4 | During an audit Texas RE conducted of TRE_URE1, Texas RE discovered an issue with CIP-003-1 R4. Texas RE determined that TRE_URE1 failed to fully implement its information protection program. Specifically, TRE_URE1’s Information Protection Program Assessment states all CIP documents must be labeled with the CEII Confidential in the footer of the document. Texas RE reviewed several CIP documents that did not have the confidential stamp in the footer of each page within the document. However, some of the reviewed documents did have a “Confidential Document” stamp in the header of the first page of the document. Texas RE determined that TRE_URE1 had an issue with CIP-003-1 R4 for approximately three and half years. | This issue posed a minimal risk and did not pose a serious or substantial risk to the bulk power system because despite failing to consistently implement its policy to include a confidential stamp in the page footer of each CIP document, TRE_URE1 did include a “Confidential Document” header on the first page of most of the reviewed CIP documents. Additionally, all documents are stored within the protected Electronic Security Perimeter and Physical Security Perimeter. | To mitigate this issue, TRE_URE1: 1. Labeled (with the CEII Confidential seal) all documents that we previously noted that were not labeled. 2. Revised its information protection program to add a classification level and described how it is labeling documents that pertain to NERC CIP Standards with the “Confidential, CEII and/or have a cover letter stating the classification of the document. Texas RE has verified the completion of all mitigation activity.
2013-09-30 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE2012010036 | CIP-003-1 | R5; R5.2 | During an audit Texas RE conducted of TRE_URE1, Texas RE discovered an issue with CIP-003 R5. TRE_URE1 did document and implement a program for managing access to protected Critical Cyber Assets (CCAs) and did annually review this program. TRE_URE1’s Critical Asset authorized personnel list shows the name, department, title, contact number, shared accounts, CCA approved access to, non-CCA approved access to and several columns with all the Critical Assets of all personnel. The list, however, does not show specific access privileges for each one of the personnel. Texas RE concluded this lack of specificity regarding the electronic access rights precludes TRE_URE1’s ability to fully review the access rights as required by R5.2. Texas RE determined that TRE_URE1 had an issue with CIP-003-1 R5 for approximately three years and seven months. | This issue posed a minimal risk and did not pose a serious or substantial risk because the evidence shows the entity completed the required task despite the lack of clarity on the documented evidence detailing the specific scope of personnel’s electronic access rights. TRE_URE1 maintains that the reviews were conducted, and there are several documents referencing annual reviews and access privileges; however, the documentation is not complete and does not expressly indicate that the annual review, to confirm that access privileges are correct and correspond with the appropriate roles and responsibilities, of access privileges was conducted. Moreover, the personnel within the scope of the issue had personnel risk assessments. TRE_URE1 also stated its CCAs had updated anti-malware and logging enabled installed. | To mitigate this issue, TRE_URE1 provided a revised document which shows a list of personnel by name, department, title, and the physical and cyber access to Cyber assets. It also describes each one of the personnel’s access privileges. Texas RE has verified the completion of all mitigation activity.
2013-09-30 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE2012010034 | CIP-003-2 | R2; R2.3 | During an audit Texas RE conducted of TRE_URE1, Texas RE discovered an issue with CIP-003-2 R2. Texas RE determined that while TRE_URE1 did appoint delegates, the delegates’ listed specific actions did not include overall responsibility for leading and managing the entity’s implementation of, and adherence to, Standards CIP-002 through CIP-009. The duration period for this issue was approximately for two years and four months. Additionally, Texas RE discovered an issue with R2.3 because TRE_URE1’s delegates were not documented in the same manner as R2.1 and R2.2. Specifically, the delegation information did not include the delegates’ titles. The duration period for the issue with R2.3 was approximately for nine months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the bulk power system because TRE_URE1 did delegate the senior manager and TRE_URE1 did delegate actions to four managers. TRE_URE1 simply failed to specifically state that a delegate was responsible for leading and managing the entity’s implementation of, and adherence to, Standards CIP-002 through CIP-009. | To mitigate this issue, TRE_URE1 updated its documentation to reflect the titles of the delegates. TRE_URE1 also updated its documentation to include overall responsibility for leading and managing the entity’s implementation of, and adherence to, Standards CIP-002 through CIP-009. Texas RE has verified the completion of all mitigation activity.
2013-09-30 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE2012010038 | CIP-004-1 | R4 | During an audit Texas RE conducted of TRE_URE1, Texas RE discovered an issue with CIP-004-1 R4. The subject Requirement requires the Responsible Entity to maintain a list(s) of personnel with authorized cyber access rights to Critical Cyber Assets (“CCA”) and to include specific physical and electronic access rights on the list(s). TRE_URE1 does maintain a list of personnel with authorized cyber or authorized unescorted physical access to CCAs, however the list submitted as evidence does not provide specific detail on whether the user’s electronic access is full or limited. In addition, this list did not include the vendors and contractors. The list only addressed specific physical access rights and broad electronic access rights. From this list it was not clear if users were intended to have full or limited electronic access rights. Texas RE determined that TRE_URE1 had an issue with CIP-003-1 R5 for approximately three years and seven months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because TRE_URE1 did not specify the scope of electronic access personnel have to Critical Cyber Assets. The noted lack of specificity regarding if a personnel’s access was full or limited could have resulted in harmful intrusions into the network, jeopardizing the reliability of the BPS. However, this risk was reduced by the fact that all hired personnel, contractors, and vendors successfully completed a Personnel Risk Assessment (PRA) and were trained before CCA access was granted. | To mitigate this issue, TRE_URE1 more clearly documented access rights to include vendors and contractors to provide greater specificity regarding the scope of access. TRE_URE1 has met with the affected employees to notify them of the changes in the Critical Cyber Asset Authorized Personnel List. Texas RE has verified the completion of all mitigation activity.
2013-09-30 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE2012010039 | CIP-005-1 | R1; R1.6 | During an audit Texas RE conducted of TRE_URE1, Texas RE discovered an issue with CIP-005-1 R1. The subject standard requires the Responsible Entity to identify and document all access points to the ESP and to maintain ESP documentation. TRE_URE1 provided its network topology to evidence compliance with the subject standard however this topology failed to clearly identify all the access points identified in the Vulnerability Assessment Baseline document. Specifically, TRE_URE1 did not identify all access points to the electronic security perimeter (ESP). TRE_URE1 attempted to correct this issue, but the network topology labeled the clouds as access points, rather than the firewalls, as illustrated in the supporting baseline document. Texas RE determined that TRE_URE1 did not correctly identify its access points to the ESP for approximately two years and nine months. | This issue posed a minimal risk and did not pose a serious or substantial risk because the Entity inadvertently referred to the clouds as access points only for illustrative purposes, but had well identified all Access Points in the ESP through its CVA and afforded the Access Points all the protective measures as specified by the Standards CIP-003-3; Standard CIP-004-3 Requirement R3; Standard CIP-005-3 Requirements R2 and R3; Standard CIP-006-3 Requirement R3; Standard CIP-007-3 Requirements R1 and R3 through R9; Standard CIP-008-3; and Standard CIP-009-3. The risk is further mitigated in part by the security system protection TRE_URE1 has in place for all CCAs and its ports that reside inside the ESP including firewalls, intrusion protection systems, and antivirus software. | To mitigate this issue, TRE_URE1 corrected its topology diagram to clearly show all access points to the Electronic Security Perimeter(s). Texas RE has verified the completion of all mitigation activity.
2013-09-30 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE2012010046 | CIP-007-1 | R5; R5.1.3 | During an audit Texas RE conducted of TRE_URE1, Texas RE discovered an issue with CIP-007-1 R5. Sub-requirement 5.1.3 requires the Registered Entity to annually review user accounts to verify access privileges are in accordance with standard CIP-003 R5 and Standard CIP-004 R4. TRE_URE1 provided evidence of documented and procedural controls that enforce system access authentication of and accountability for all user activity that is reviewed annually. However, no evidence was provided to demonstrate the annual review was conducted in accordance with CIP-003 R5 and CIP-004 R4. TRE_URE1’s Critical-Cyber Asset Authorized Personnel List, which show user activity and is used to verify access privileges, failed to demonstrate that access privileges are correct and correspond with the Responsible Entity’s needs and appropriate personnel roles and responsibilities. This is due to the list lacking specificity about the scope of electronic access. Without this material specificity, Texas RE concluded the required review was incomplete. Texas RE determined that TRE_URE1 had an issue with CIP-007-1 R5.1.3 for approximately three years and seven months. | This issue posed a minimal risk and did not pose a serious or substantial risk because, despite the lack of documented specificity to help verify the depth of the review required per the standard, TRE_URE1 demonstrated consistent annual reviews were conducted. TRE_URE1’s user access analysis addresses more than electronic access and no issues were identified with TRE_URE1’s depth of review for the remaining required categories. The minimum impact is further mitigated by the fact that all hired personnel, contractors, and vendors successfully completed a Personnel Risk Assessment (PRA) and trained. The PRA and training minimizes the risk of a possible breach or system failure on the protected systems due to malice and/or human error. | To mitigate this issue, TRE_URE1: 1. Included an Access Verification detail section in its accounts management procedure for easy verification of access privileges for user accounts. 2. Confirmed that its procedures regarding user accounts and verifying access privileges implemented under CIP-007 R5 and CIP-005 R3 clearly cross-reference each other Texas RE has verified the completion of all mitigation activity.
2013-09-30 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE2012010047 | CIP-007-1 | R7 | During an audit Texas RE conducted of TRE_URE1, Texas RE discovered an issue with CIP-007-1 R7. Specifically, TRE_URE1 did not have formal methods, processes, and procedures for disposal or redeployment of Cyber Assets within and Electronic Security Perimeter for approximately one year. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). As compensating measure, TRE_URE1 had controls in place to log and monitor access to all Cyber Assets within the ESP. Physical and electronic alerts coming from these controls are reviewed 24 hours a day. In addition, only authorized personnel are granted access to these devices. | To mitigate this issue, TRE_URE1 added a procedure for removal and/or disposing of Critical Cyber assets. Texas RE has verified the completion of all mitigation activity.
2013-09-30 | TRE_URE1liability Entity (TRE_URE1) | Unidentified Registered Entity 2 (TRE_URE2) | NCRXXXXX | TRE2012011185 | CIP-007-1 | R3; R3.1 | TRE_URE2 submitted a self-certification citing an issue with CIP-007-1 R 3. TRE_URE2 reported that it had failed to assess security patches and security upgrades for applicability within thirty calendar days of availability of the patches, thus failing to document the assessment per R3.1. Specifically, TRE_URE2 failed to assess 145 patches within thirty calendar days. This comprised 4% of the total patches. TRE_URE2 had an issue with CIP-007-1 R3 for approximately three and a half years. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failing to conduct assessments of security patches could result in TRE_URE2 missing critical patches that would prevent TRE_URE2’s system from being compromised. The risk was reduced because TRE_URE2 only failed to assess 4% of the total security patches. The risk is further mitigated because TRE_URE2 restricts administrative access to the covered devices with Access Control Lists (ACLs) and does not allow connections with indiscriminate and unknown internet hosts and devices. TRE_URE2 segregates similar Cyber Assets within an ESP from other Cyber Assets within the same ESP by employing unique firewall rules for dissimilar Cyber Assets in order to minimize unknown potential cyber risk. TRE_URE2’s defense in depth and least privilege posture contributes to minimizing attack vectors. TRE_URE2 has defense at enclave boundaries and at the computing environment and maintains a robust physical and personnel security program with authenticated access controls and auditing. | To mitigate this issue, TRE_URE2: 1) created a new work process for security patch management; 2) instituted a procedure whereby team members meet every other week (Wednesdays for Network Operations and Thursdays for the Server Operations team) to assess security patches, assign patch management tasks and track them to completion. By meeting every other week, two cycles will be completed in 28 days. Thus, TRE_URE2’s process is conservative in that a potential patch assessment oversight will have another opportunity to be caught within 30 days; 3) hired one FTE in the Network Operations group; 4) created an IT Quality Assurance/Quality Checking function to review IT compliance evidence for completeness and accuracy; 5) established an IT Compliance Group (embedded in the IT Operations Division) to oversee process implementation and validate execution of IT processes; and 6) hired five contractors to augment vacant positions in the Network Operations group. TRE_URE1 has verified the completion of all mitigation activity.
2013-09-30 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 3 (TRE_URE3) | NCRXXXXX | TRE2012010664 | CIP-002-3 | R4 | TRE_URE3 submitted a self-report citing an issue with CIP-002-3 R4. TRE_URE3 reported that there is no signed and dated record of the senior manager’s approval of the risk-based assessment methodology (RBAM) during one calendar year. This issue began on the date by which TRE_URE3 should have annually approved its RBAM. This date is based on TRE_URE3's definition of annual, which, in accordance with Compliance Application Notice – 0010, is within a calendar year. TRE_URE3 corrected this issue the following year on the date the TRE_URE3 designated senior manager signed the RBAM. | This issue posed a minimal risk and did not pose a serious or substantial risk to the bulk power system because from the time the senior manager originally signed the documents until the time the senior manager signed the next RBAM, the TRE_URE3's RBAM did not change. Moreover, TRE_URE3 did not previously have any CCAs and does not currently identify any CCAs. Other mitigating factors include: the designated senior manager for TRE_URE3 authorized the CA and CCA lists for the missed year based on the approved originally signed RBAM and there were no significant changes to the plant, the RBAM, or the applicable standards since the originally signed RBAM. | To mitigate this issue, TRE_URE3 designated senior manager signed the RBAM. Texas RE has verified the completion of all mitigation activity.
2013-09-30 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 4 (TRE_URE4) | NCRXXXXX | TRE2012010178 | CIP-002-3 | R2 | During an audit Texas RE conducted of TRE_URE4, Texas RE discovered an issue with CIP-002-3 R2. TRE_URE4 failed to consider criterion #6 in its Risk Based Assessment Methodology (RBAM) while developing its list of its identified Critical Assets. Criterion #6 stated “Generation capacity which has been deemed by the regional ISO to be critical to the reliability of the Bulk Electric System and has a net capacity factor greater than 5%.” TRE_URE4 did not consider criterion #6 for approximately eighteen months. The duration period was from the enforcement date of the standard (based on the CIP Implementation table) to the date TRE_URE4 correctly applied its RBAM. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The physical capabilities of the individual units preclude TRE_URE4 from being affected by the criterion it failed to consider. Therefore, even if TRE_URE4 had considered the criterion, it would not have changed the result of the Critical Asset Identification. Additionally, TRE_URE4 attested that it does not meet the criteria for Critical Assets, and that the regional ISO has not provided notice that TRE_URE4 was considered critical to reliability. | To mitigate this issue, TRE_URE4 amended its RBAM document state criterion #6 as “6.Generation capacity which has been deemed by the regional ISO to be critical to the reliability of the Bulk Electric System”. Texas RE has verified the completion of all mitigation activity.
2013-09-30 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 5 (TRE_URE5) | NCRXXXXX | TRE2012010179 | CIP-002-3 | R2 | During an audit Texas RE conducted of TRE_URE5, Texas RE discovered an issue with CIP-002-3 R2. TRE_URE5 failed to consider criterion #6 in its Risk Based Assessment Methodology (RBAM) while developing its list of its identified Critical Assets. Criterion #6 stated “Generation capacity which has been deemed by the regional ISO to be critical to the reliability of the Bulk Electric System and has a net capacity factor greater than 5%.” TRE_URE5 did not consider criterion #6 for approximately thirteen months. The duration period was from the enforcement date of the standard (based on the CIP Implementation table) to the date TRE_URE5 correctly applied its RBAM. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The physical capabilities of the individual units preclude TRE_URE5 from being affected by the criterion it failed to consider. Therefore, even if TRE_URE5 had considered the criterion, it would not have changed the result of the Critical Asset Identification. Additionally, TRE_URE5 attested that it does not meet the criteria for Critical Assets, and that the regional ISO has not provided notice that TRE_URE5 was considered critical to reliability. | To mitigate this issue, TRE_URE5 amended its RBAM document state criterion #6 as “6.Generation capacity which has been deemed by the regional ISO to be critical to the reliability of the Bulk Electric System”. Texas RE has verified the completion of all mitigation activity.
2013-09-30 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 6 (TRE_URE6) | NCRXXXXX | TRE2012011133 | CIP-004-3 | R4.1;R4.2 | TRE_URE6 submitted a self-report to Texas RE stating it had an issue with CIP-004-3 R4.1 and R4.2. First, Employee A transferred to an affiliated company that no longer required CIP physical access rights. TRE_URE6 failed to revoke Employee A’s access within seven days and did not update its list of personnel who have physical access within seven calendar days. Specifically, TRE_URE6 had an issue with CIP-004-3 R4.1 and R4.2 for Employee A for approximately one week. Furthermore, TRE_URE6 self-reported two additional issues with CIP-004-3 R4. Specifically, TRE_URE6 failed to revoke logical access for Employee B and Employee C within seven days of the employees’ retirement dates. Additionally, the access list was not updated for Employee B and C within seven days of the employees’ retirement dates. Employee B’s logical access was not revoked until twenty-seven days after the Employee B retired, and the access list was not updated until eighty-seven days after the employee retired. Employee C’s logical access was not revoked until thirty-five days after the employee retired, and the access list was not updated until twenty-eight days after the employee retired. | This issue did not pose a serious or substantial risk to the bulk power system and had a minimal risk because the three employees had current PRAs and CIP training. While correction of the lists of those with logical access took longer than the standard allows, the amount of time that the employees improperly had access was brief. First, Employee A surrendered the access badge before the employee transferred. Additionally, the employee never had logical access to CIP facilities. Employee A’s physical access was not revoked until seven days after the required date. TRE_URE6’s CIP training of the employee’s supervisor contributed to the short time frame (seven days). Second, revocation of physical access for Employees B and C occurred prior to both retirement dates, and neither had remote access to the CIP facilities. The logical access of the two employees was canceled twenty and thirty days after the required date. The company’s quarterly review of access lists led to the discovery of the two issues. Texas Re took into account that an affiliate of TRE_URE6 had a previous violation of this Standard. Texas RE determined that the instant issue is appropriate for a FFT treatment because although a previous affiliate violation was similar, TRE_URE6 self-reported and mitigated the issues to assist in preventing the likelihood of future occurrences. | To mitigate this issue, TRE_URE6: 1) revised the email notification system; 2) trained the supervisor on the revised email notification system; 3) combined the physical and logical access lists into one document to maintain and review; and 4) modified the access revocation and review process to include a logical and physical access cross-check by two employees. Texas RE has verified the completion of all mitigation activity.
2013-09-30 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 7 (TRE_URE7) | NCRXXXXX | TRE2012011004 | CIP-003-3 | R2.3 | TRE_URE7 submitted a self-report citing an issue an issue with CIP-003-3, R2. Specifically, TRE_URE7 could not demonstrate its delegation document was approved by the senior manager as required by the standard. TRE_URE7 provided its CIP-003-3, R2 delegation document in effect at the time of its registration. The document designated both senior manager and delegate by name, title, and date of designation. The document implied that both senior manager and delegate had overall responsibility for Standards CIP-002-3 through CIP-009-3. However, the document was not signed, and TRE_URE7 could not provide documentation that the senior manager approved the delegation. TRE_URE7 revised its delegation document to include approval by the senior manager to address the requirements of CIP-003-3, R2.3. Thus, TRE_URE7 had an issue with CIP-003-3 R2.3 for approximately sixteen months. (TRE_URE7's registration date through the date TRE_URE7’s revised delegation document was signed.) | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). TRE_URE7 is a small source of generation with less than 50 MW. A large percentage of the MWh generated is consumed within the TRE_URE7’s Private Use Network. The failure of this generator would not cause a significant impact on the BPS due to the low amount of power supplied. In addition, TRE_URE7 stated it has not identified any Critical Assets. | To mitigate this issue, TRE_URE7 revised its delegation document, adding an approval by the senior manager. Texas RE has verified the completion of all mitigation activity.
2013-09-30 | Texas Reliability Entity (Texas RE), ReliabilityFirst (RF), Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 8 (TRE_URE8, RFC_URE8, SPP_URE8) (Collectively, URE_8) | NCRXXXXX | TRE2012011255 RFC2012011194 SPP2012011172 | CIP-007-3a | R5; R5.3.3 | URE_8 self-reported an issue with CIP-007-3a R5. Additionally, URE_8 submitted a self-report to ReliabilityFirst and SPP RE for the same issue. URE_8 stated that it failed to change passwords on several accounts annually per R5.3.3. Texas RE, on behalf of itself, ReliabilityFirst, and SPP RE, determined that URE_8 had an issue for approximately 7 1/2 months. URE_8 submitted an additional self-report to ReliabilityFirst identifying an additional instance of the issue of CIP-007-3 R5 where a password for a backup meter had been reset to the factory default password. An URE_8 employee who was remotely logged into the backup meter inadvertently reset the password to the factory default password. The duration for the additional instance was approximately 1 ½ months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because IDs were expired per policy and the other IDs were several process IDs and one built-in administrator account. Additionally, a coordinated attack of the bulk electric system exploiting these local accounts is unlikely due to the multiple layers of physical and electronic access controls in place. For the second issue that only occurred in the ReliabilityFirst region, the issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because the backup meter is not capable of controlling any device in the generating station, and the password was set to the factory default setting for a short period of time, reducing the likelihood of unauthorized access to this account. | To mitigate the first issue, URE_8 did the following: 1. URE_8 changed the passwords. URE_8 either changed or deleted the user ID passwords. 2. Account passwords that have expired following 90 days since last change (“stale” passwords) are now flagged in the change request system and reported to designated personnel responsible for overseeing the remediation of such passwords. 3. Required actions are effectuated with evidence of remedial actions collected and documented. 4. If necessary changes to the program are identified, tasks are updated in the change control program and system. Texas RE has verified the completion of mitigation activity for the issue that occurred in Texas RE, ReliabilityFirst, and SPP RE. To mitigate the second issue that only occurred in the ReliabilityFirst region, URE_8 committed to reset the password on the backup meter, review internal processes and procedural controls and propose improvement procedures, communicate lessons learned, and implement proposed improvement procedures. Upon completion, ReliabilityFirst will verify URE_8’s completion of these mitigating activities.
2013-09-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2013012382 | CIP-004-3 | R2 | WECC performed a Compliance Audit of WECC_URE1’s compliance with, among other Reliability Standards, CIP-004-3 R2. Prior to WECC's arrival, WECC_URE1 submitted a Self Report to WECC stating that it had an issue with CIP-004-3 R2. Although WECC_URE1 self-reported this violation, because WECC_URE1 self-reported during the Self-Certification submission period, the discovery method for this violation is classified as Self-Certification. Specifically, WECC_URE1 reported that two employees who had authorized unescorted physical access to a Physical Security Perimeter (PSP) did not receive annual cyber security training. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE1 reported that the Critical Cyber Assets were located within a PSP and that the PSP is manned 24 hours a day 7 days a week by authorized personnel. Furthermore, the individuals involved had received cyber security training in past years and had undergone background checks. Finally, the issue is limited to missed annual training for three individuals in good standing at WECC_URE1. | To mitigate this issue, WECC_URE1 revoked access to the Critical Assets for each of the three employees involved.
2013-09-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2013012258 | CIP-004-3a | R4 | WECC_URE1 submitted a Self Report to WECC stating that it had an issue CIP-004-3a R4. WECC_URE1 reported that it had one employee voluntarily leave employment at WECC_URE1. WECC_URE1 reported that this individual was included on its Critical Cyber Asset personnel access list because the individual had unescorted physical access to a Physical Security Perimeter (PSP). WECC_URE1 reported that it did not update its personnel list for Critical Cyber Assets until three months after the employees voluntary termination. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Specifically, WECC_URE1 confiscated and disabled the employee’s access card and ID badge on the last day of the individual’s employment at WECC_URE1. Additionally, all additional personnel with access to the PSP were notified that the individual no longer had authorization to access the PSP. | To mitigate this issue, WECC_URE1 updated its Critical Cyber Asset personnel access list and removed the individual involved in this incident.
2013-09-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2013012200 | CIP-006-3a | R1 | WECC performed a Compliance Audit of WECC_URE1’s compliance with, among other Reliability Standards, CIP-006-3a R1. The Audit Team determined that WECC_URE1 had a possible issue with CIP-006-3a R1, specifically R1.6. Specifically, the Audit Team determined that WECC_URE1 did not have a proper visitor control program for visitors to its Physical Security Perimeters (PSP). | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Specifically, WECC_URE1 required visitors to the PSP to log the date and time of the first entry and the last exit from the PSP, therefore, WECC_URE1 is aware of the individuals who access the PSP. Additionally, while in the PSP, all visitors are physically escorted at all times. | To mitigate this issue, WECC_URE1 implemented a new Physical Security Procedure including appropriate measures to ensure that all PSPs are properly monitored.
2013-09-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2013012225 | CIP-008-3 | R1 | WECC performed a Compliance Audit of WECC_URE1’s compliance with, among other Reliability Standards, CIP-008-3 R1. The Audit Team determined that WECC_URE1 had a possible issue with CIP-008-3 R1, specifically R1.4. Specifically, the Audit Team determined that WECC_URE1’s Cyber Security Incident Response Plan did not have a process for updating within thirty calendar days of any changes. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Specifically, WECC_URE1 reviews its Cyber Security Incident Response Plan annually. Additionally, the Plan is revised regularly and is tested at least once a year with documented lessons learned. Finally, during the pendency of the issue, WECC_URE1 did not experience any reportable cyber security incident. | To mitigate this issue, WECC_URE1 will update its Cyber Security Incident Response Plan to include a process for updating it within thrity calendar days of any changes. WECC_URE1 has not completed all mitigating activities associated with this remediated issue. WECC_URE1 must fully mitigate the remediated issue within 90 days from the date this FFT is filed or posted on the NERC website.
2013-09-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2013011684 | CIP-003-3 | R5 | WECC_URE2 submitted a Self Report to WECC stating that it had an issue with CIP-003-3 R5. Specifically, WECC_URE2 reported that it failed to manage access to Critical Cyber Asset information. WECC_URE2 reported that seven (7) individuals were granted access to file shares containing Critical Cyber Asset information without first receiving requisite approvals required by WECC_URE2’s Information Protection Program (IPP). | This issue posed a minimal risk and did not pose a serious risk or substantial risk to the reliability of the bulk power system. The scope of the compliance issue is limited to four file shares to which thirty-seven individuals were granted access without first receiving requisite approvals. Each of the individuals in scope completed Cyber Security Training before being granted access to Critical Cyber Asset information. Each of the individuals in scope also completed Personnel Risk Assessments including a criminal background check before being granted access to information. The individuals in scope of the issue are employed by WECC_URE2 and remain in good standing. | To mitigate this issue, WECC_URE2 revoked all access to Critical Cyber Asset information for thirty-seven individuals. In addition, WECC_URE2 implemented monthly reviews of IPP access grants to prevent future compliance issues.
2013-09-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2013012476 | CIP-004-3a | R4 | WECC_URE3 submitted a Self-Report to WECC stating that it had an issue with CIP-004-3a R4. WECC_URE3 reported that it had an employee retire. WECC_URE3 reported that the employee had authorized unescorted physical and logical access to Critical Cyber Assets. WECC_URE3 reported that two months after the employee had retired, WECC_URE3 had revoked the employee’s physical access but had failed to revoke the employee’s logical access to its Critical Cyber Assets. Additionally, WECC_URE3 discovered two months later that it had failed to update its Critical Cyber Asset access list to reflect the employee’s departure. | This issue posed a minimal risk and did not pose a serious risk or substantial risk to the reliability of the bulk power system. Specifically, the facility in scope has a security guard at the entrance and the remote terminal unit (RTU) cannot be operated remotely. Also, the RTU is located inside a locked cabinet within a room that is inside a PSP that is staffed 24 hours a day 7 days a week. This would allow personnel to immediately detect and respond to any unauthorized attempts to gain physical or logical access to the RTU thereby preventing the manipulation of the breakers and therefore preventing the loss of 550 MW of generation. Furthermore, WECC_URE3 implemented detective controls to detect the above consequence. Specifically, WECC_URE3 has a centralized system that performs automated logging and monitoring of the access points to the RTU and the RTU itself. Also, the control center operators would receive alarms if any suspicious activity were to occur. Moreover, WECC_URE3 revoked the individual’s physical access on the date of departure, and the individual in scope did not have a key to the cabinet where the device was located. | To mitigate this issue, WECC_URE3 revoked the employee's logical access to Critical Cyber Assets. In addition, WECC_URE3 updated its Critical Cyber Asset access list and removed the employee in question.
2013-09-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC2013012602 | CIP-006-3c | R1 | WECC_URE4 submitted a Self-Report to WECC stating that it had an issue with CIP-006-3c Requirement 1, specifically R1.6. Specifically, WECC_URE4 had begun repair work on certain Computer Room Air Conditioning units (CRACs) located within its Physical Security Perimeters (PSP). WECC_URE4 reported that at its CTC Dispatch PSP, as a part of the repair process, it was required to prop open an access doorway. WECC_URE4 stated that it began work on the CRACs located within the CTC Dispatch PSP and that, while work was being performed, security guards WECC_URE4 had hired to protect the PSP were stationed within the PSP. WECC_URE4 reported that the security guards did not have unauthorized physical access to the PSP and were not being escorted while in the PSP. Additionally, WECC_URE4 stated that the two contractors hired to perform the repair work within the CTC Dispatch PSP were not escorted at all times, specifically, on at least one occasion, the two contractors were not escorted by an authorized WECC_URE4 employee. Furthermore, WECC_URE4 reported that on seven different occasions, either the contractors or the security guards did not log entrance or exit to the PSP. | This issue posed a minimal risk and did not pose a serious risk or substantial risk to the reliability of the bulk power system. WECC_URE4 implemented strong detective and preventive controls to prevent the possible unauthorized logical access described above. Specifically, WECC_URE4 implemented 24 hours a day 7 days a week logging and monitoring of logical access to these systems. Additionally, WECC_URE4 system operators were within the PSP throughout the duration of the issue, these system operators would have likely detected and prevented any unauthorized access or access attempts to the energy management system (EMS) or ACM devices in that area. Also, all Critical Cyber Assets (CCAs) inside the PSP are within eye sight of the operators who would immediately know if any unauthorized person attempted to tamper with or login to the devices thereby preventing any access whatsoever. Additionally, all failed logon attempts to these CCAs are logged and alerted to control system engineers to evaluate and immediately respond to the incident. The facility can be remotely viewed via PSP cameras or responded to in person within 20 minutes by security personnel. Finally, if any of the above activities were detected, based on WECC_URE4’s corrective controls, WECC_URE4 is positioned to respond and correct a negative condition. Specifically, WECC_URE4 implemented redundancy of the EMS servers and workstations at a separate facility which would allow WECC_URE4 to recover if the systems were physically tampered with or disabled. Also, WECC_URE4 would know immediately if any login failures or suspicious EMS activity was occurring and invoke its incident response and recovery procedures if necessary and could immediately send system operators or security personnel to respond. | To mitigate this issue, WECC_URE4 removed the individuals involved from the PSP. WECC has verified the completion of all mitigation activity.
2013-09-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 5 (WECC_URE5) | NCRXXXXX | WECC2013012531 | CIP-004-3a | R2 | WECC_URE5 submitted a Self-Report to WECC stating that it had an issue with CIP-004-3a R2. Specifically, for granting one individual unescorted access to one Physical Security Perimeter (PSP) that contained three Critical Cyber Assets and three Non-Critical Cyber Assets, prior to the individual completing the NERC CIP-004 R2 training. | This issue posed a minimal risk and did not pose a serious risk or substantial risk to the reliability of the bulk power system. WECC_URE5 stated that the new employee had received a PRA, had completed the Employee Code of Business Conduct training, and the Information and Physical Security Policy and Information Security Procedures training. WECC_URE5 also stated that the new employee did not have credentials to log in to the six devices, and two of the three Critical Cyber Assets are manned by operators 24 hours a day 7 days a week. In addition, the devices have antivirus software and are monitored with ArcSight, WECC_URE5’s security intelligence platform, which would have alerted them to any anomalies. | To mitigate this issue, WECC_URE5 immediately revoked unescorted physical access until the new employee had completed the cyber security training program required.
2013-09-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 6 (WECC_URE6) | NCRXXXXX | WECC2013011902 | CIP-007-1 | R7 | WECC_URE6 submitted a Self-Report to it had an issue with CIP-007-1 R7. Specifically, WECC_URE6 reported it failed to erase the data storage media on one Critical Cyber Asset prior to redeployment. In addition, WECC_URE6 failed to maintain records that assets were disposed of in accordance with documented procedures. | This issue posed a minimal risk and did not pose a serious risk or substantial risk to the reliability of the bulk power system. WECC_URE6 did remove the IP address disconnecting the printer incoming data from the network and associated devices. In addition, WECC_URE6 failed to fill out data destruction forms prior to the disposal of 16 Critical Cyber Assets. The devices in scope were thin clients used to gain remote access to WECC_URE6’s control center and workstations that were used to review information at WECC_URE6’s control centers, and a Human Machine Interface that was used to view information for a pollution control device. WECC_URE6 has since improved and streamlined this process by utilizing only one form to document both the disposal/redeployment and data destruction. Further, WECC_URE6 stated that all Critical Cyber Asset information was removed from all devices prior to the device being returned to the manufacturer. | To mitigate this issue, WECC_URE6 implemented a new disposal and redeployment process that requires all documentation to be reviewed from a quality assurance perspective by the WECC_URE6 NERC CIP Compliance team. Further, WECC_URE6 created a single template form for the disposal and redeployment of cyber assets.
2013-09-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 7 (WECC_URE7) | NCRXXXXX | WECC2013012031 | CIP-003-3 | R4 | WECC_URE7 submitted a Self-Certification to WECC stating that it had an issue with CIP-003-3 R4. WECC_URE7 reported that it failed to properly identify recovery and incident response plans associated with Critical Cyber Assets as restricted documents. | This issue posed a minimal risk and did not pose a serious risk or substantial risk to the reliability of the bulk power system. Specifically, the documents were always protected and classified per WECC_URE7’s Critical Cyber Asset (CCA) Information procedures with the exception of the specific “NERC CIP Restricted” note at the bottom of each page. The documents were located in physically and logically protected zones where only approved individuals that were vetted and trained per WECC_URE7’s Critical Cyber Asset procedures were allowed. | To mitigate this issue, WECC_URE7 will designate current CIP-008 and CIP-009 procedures as "NERC CIP Restricted." WECC_URE7 will then update its information protection procedure to better identify, classify and protect CCA information. The updated procedure will have specific steps to identify all information related to CCAs as “NERC CIP Restricted.” WECC_URE7 has not completed all mitigating activities associated with this remediated issue. WECC_URE7 must fully mitigate the remediated issue within 90 days from the date this FFT is filed or posted on the NERC website.
2013-08-30 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC201100423 | CIP-004-3 | R4.1 R4.2 | FRCC_URE1 submitted a Self-Report stating that it had an issue of CIP-004-3 R4.1 and R4.2 because it failed to update the access list within seven calendar days of a change after a person transferred to a different business unit other than CIP access records indicated. A person had transferred out of the control center and should have had access removed and the list updated. Access was immediately revoked upon discovery and the access list was updated. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failure to revoke access and update an access list can allow an individuals access to be inappropriately retained or reinstated by an unknowing administrator leaving potential devices unprotected and vulnerable to a cyber threat. This risk was reduced because the person's access was immediately revoked when discovered, they had not accessed nor attempted to access any CIP areas after transferring out of the business unit requiring CIP access, and their subsequent job required continued CIP access. | To mitigate this issue FRCC_URE1: 1) revoked Critical Cyber Asset (CCA) access; 2) verified transmission and substation CCA access; 3) verified FRCC_URE1s other business units CCA access; 4) conducted a review of all current processes, procedures, and training in support of CIP-004 R4 to identify improvements reducing the probability of reoccurrence; 5) revised CIP-004 processes as needed; 6) investigated and implemented a local solution that incorporated automatic notification escalation of pending revocation requests; and 7) trained impacted supervisors on updated processes. FRCC has verified the completion of all mitigation activity.
2013-08-30 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2011008545 | CIP-006-1 | R1.7 | During a Spot Check, FRCC determined that FRCC_URE1 had an issue of CIP-006-1 R1.7 because evidence was insufficient to demonstrate that FRCC_URE1 updated its Physical Security Plan within the required calendar days (90 days for first two instances and 30 days for last three instances) of the completion of all physical security system redesign or reconfiguration as required. There were several instances of adding new physical security perimeters (PSPs) in which the Physical Security Plan was updated between 60 and 90 days after the required interval. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failure to update the required documentation within the specific time period could result in inadequate controls being applied and leave devices unprotected and vulnerable to a cyber or physical threat. The risk was reduced because all other required controls were implemented and effective. The required documentation did not contain any specifics that would require updating with the addition of new PSPs. This was only a delay in updating documentation history with a recorded entry to indicate that no changes were required. | To mitigate this issue, FRCC_URE1: 1) conducted an extent of condition analysis of physical security perimeters at designated Critical Assets to determine whether there are other instances in which the Physical Security Plan was not updated within 30 days following a reconfiguration or redesign change; 2) reviewed results of extent of condition analysis, if additional instances are identified in which the Physical Security Plan was not updated following a reconfiguration or redesign change, add all necessary updates to the next revision of the Physical Security Plan; 3) collected all applicable physical security drawings related to physical security perimeters for designated Critical Assets from each of the respective business areas; notify business areas that corporate security will assume custodianship and retention responsibilities of the physical security drawings going forward to include within the updated Physical Security Plan; 4) updated Physical Security Plan to include language stating that the Physical Security Plan will be updated and signed by the management of corporate security, as the Senior Manager delegate for CIP-006, to incorporate any physical security redesign or reconfiguration changes (including, but not limited to additional or removal of access points through the physical security perimeter, physical access controls or monitoring/logging controls) within 30 days. The updates to the Physical Security Plan also specified that it is corporate security’s responsibility to be the custodian of all applicable the physical security drawings related to physical security perimeters for designated Critical Assets which will be included within the Physical Security Plan; 5) updated corporate security’s workflow documentation for CIP-006 R1.7 to include a notification to the management of corporate security, as a checkpoint when a physical security configuration change ticket is closed out for any physical security reconfiguration or redesign of physical security perimeters at designated Critical Assets; 6) communicated to corporate security personnel the updated workflow for CIP-006 R1.7; and 7) communicated and conducted training to the applicable business areas regarding the changes to the enterprise Physical Security Plan implemented by this Mitigation Plan. FRCC has verified the completion of all mitigation activity.
2013-08-30 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2012010620 | CIP-004-3 | R4.1 | FRCC_URE1 submitted a Self-Report stating that it had an issue of CIP-004-3 R4.1 because it failed to maintain a complete list of personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets (CCAs). FRCC_URE1's list also could not demonstrate that it had been updated within seven days for all granted access as required. Furthermore, the list showed inaccurate dates for last personnel risk assessment (PRA) completion as well as inaccurate dates for when access was authorized and granted. Eight individuals maintained on the list were identified as being incorrectly documented. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failure to maintain the list of authorized personnel with cyber and unescorted physical access to CCAs could allow unauthorized access to remain after it was no longer required and leave devices unprotected and vulnerable to a cyber or physical threat. The risk was reduced as all access was approved prior to being granted as required by the CIP standards, all PRAs were current, and only authorized personnel had authorized cyber or authorized unescorted physical access to the CCAs. The specific instances of incorrect documentation for this Self-Report resulted from manually transcribing the data from the supporting documentation to the summarized list and were corrected. Furthermore, individual documentation related to access authorization or access revocations discrepancies did exist. | To mitigate this issue, FRCC_URE1: 1) validated the list used to track personnel; 2) reviewed current processes in the maintenance of the lists; 3) reviewed procesed and procedures for identified improvements; and 4) performed training on new processes and procedures. FRCC has verified the completion of all mitigation activity.
2013-08-30 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2012010622 | CIP-007-1 | R3 | FRCC_URE1 submitted a Self-Report stating that it had an issue of CIP-007-1 R3, R3.1, and R3.2 because it failed to provide evidence of a documented security patch management process for several third party non-Critical Cyber Assets within the Electronic Security Perimeter (ESP). | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failure to document all Cyber Assets included in FRCC_URE1's patch management program could result in cyber security software patches not being applied to those Cyber Assets and leave them vulnerable to a cyber threat. The risk was reduced because FRCC_URE1 provided evidence to demonstrate that it tracked, evaluated, tested, and installed all applicable cyber security software patches for all Cyber Assets within the ESPs, including the Cyber Assets included within in the scope of this Self Report. The ESP had limited external interactive access with two-factor authentication, and these Cyber Assets reside within a physical security perimeter (PSP). Furthermore, all personnel had valid PRA and current cyber training. | To mitigate this issue, FRCC_URE1: 1) performed a review of current patch management procedures; 2) conducted an analysis of all applicable Cyber Assets and categorized applicable security patches; 3) performed an analysis to determine what OS, software, applications, and firmware were not currently included in the procedure(s) for formal tracking; 4) updated distribution control center's associated patch management procedures for gaps determined in the first three milestones. 5) updated and released new versions of all applicable patch management programs; and 6) conducted training. FRCC has verified the completion of all mitigation activity.
2013-08-30 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2012010623 | CIP-007-1 | R4 R4.1 | FRCC_URE1 submitted a Self-Report stating that it had an issue of CIP-001-1 R4.1 because they did not use antivirus software and other malicious software (malware) prevention tools on several Critical Cyber Assets (CCAs) and non-CCAs that reside within the Electronic Security Perimeter (ESP) as required, and had not requested and obtained approval for a Technical Feasibility Exception (TFE) for the Cyber Assets. The Cyber Assets were in service prior to the requirement to comply with the CIP standards. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failure to request and receive approval for a Technical Feasibility Exception could have resulted in compensating and mitigating controls not being applied for the protection of the Cyber Assets. The risk was reduced because FRCC_URE1 had the mitigating and compensating controls in place for the Cyber Assets ultimately specified in the TFE. The Cyber Assets reside within an ESP with limited external interactive access with two-factor authentication, and these Cyber Assets reside within a physical security perimeter (PSP). Furthermore, all personnel had valid PRA and current cyber training. This was simply a failure to follow the process to submit an appropriate TFE. | To mitigate this issue, FRCC_URE1: 1) submitted appropriate technical feasibility exceptions (TFEs); 2) performed an inventory of Cyber Assets related to the distribution control center; 3) completed TFEs for any Cyber Assets identified in milestone two as needed; 4) reviewed current process and identified any potential gaps in evaluating the need for a TFE; and 5) updated policies and procedures, and trained personnel. FRCC has verified the completion of all mitigation activity.
2013-08-30 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2012010624 | CIP-007-1 | R5.3.2 R5.3.3 | FRCC_URE1 submitted a Self-Report stating that it had an issue of CIP-007-1 R5.3 because it failed to require and use passwords with the R5.3 specified characteristics for serveral Critical Cyber Assets within the Electronic Security Perimeter (ESP), and had only requested and obtained approval for a technical feasibility exception (TFE) on a couple of the Cyber Assets. In addition, it failed to change account passwords at least annually as required by R5.3.3 on several Cyber Assets. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Failure to require and use passwords with the R5.3 specified characteristics could leave the Cyber Assets unprotected and vulnerable to a cyber threat. The risk was reduced because the Cyber Assets are within a defined ESP with restricted two-factor interactive access, and within a physical security perimeter (PSP). While the account passwords had not been changed within the required timeframe, they were expired and as such would be required to change at the next login attempt. These Cyber Assets also require authentication and access was limited to authorized personnel with with proper cyber training and current personnel risk assessments. Furthermore, FRCC_URE1 does have an approved TFE with FRCC for two other similar Cyber Assets identified and this was simply a failure to update the TFE with the additional devices. | To mitigate this violation, FRCC_URE1: 1) completed the TFE documentation and submit them; 2) performed a review of account(s) for CIP assets and ensured that passwords have been changed within the annual requirement; 3) reviewed remaining accounts for annual password changes; 4) completed a review of current processes and controls to identify gaps; 5) completed and submitted TFEs for any assets identified in previous milestones as needed; and 6) updated the processes and controls as identified, and completed training of personnel. FRCC has verified the completion of all mitigation activity.
2013-08-30 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2013011782 | CIP-003-2 | R2; R2.1 | MRO_URE1 submitted a Self-Report stating that it failed to document a senior manager's name, title and date of designation, as required by CIP-003-2 R2.1. Although MRO_URE1 had a senior manager with authority for managing implementation of Standards CIP-002-2 through CIP-009-2 since 2008, it failed to document such authority in accordance with the Requirement. CIP-003-1 R2 only applied to Registered Entities with Critical Cyber Assets. However, CIP-003-2 R2 applied to Registered Entities regardless of whether they had Critical Cyber Assets. Since MRO_URE1 did not have any Critical Cyber Assets at the time of hiring its senior manager responsible for CIP compliance, it did not document the hire. When the version changed to CIP-003-2, MRO_URE1 did not document the individual as required. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. MRO_URE1 had a senior manager with authority for managing implementation of Standards CIP-002 through CIP-009 since 2008. Additionally, the senior manager responsible for managing compliance as required by CIP-003-2 did not change upon documenting the individual as required by the Standard. Therefore, this was a documentation deficiency. Furthermore, MRO_URE1 does not have any Critical Assets or Critical Cyber Assets. | To mitigate this issue, MRO_URE1: 1) hired a consultant to review and revise its compliance program; 2) created an internal compliance plan; 3) developed a CIP-003 policy guideline and procedure designating a senior manager of cyber security; 4) assigned additional staff to assist with its compliance program; 5) established an internal compliance committee to oversee compliance; and 6) hired a consultant to perform a mock audit of its compliance program. MRO has verified the completion of all mitigation activity.
2013-08-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2012009282 | CIP-002-2 | R1; R1.2 | NPCC_URE1 submitted a Self-Certification to NPCC stating that it had an issue with CIP-002-2 R1. As part of an internal review, NPCC_URE1 had not included evaluation criterion in its documented risk based assessment methodology (RBAM) used to identify critical assets. | The issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although NPCC_URE1 did not address the evaluation criterion within their RBAM, the absence of the documented criterion did not preclude NPCC_URE1 from using such evaluations in verbal discussions and reviews of engineering studies. NPCC_URE1's critical asset list did not change with the updated documentation. | To mitigate this issue, NPCC_URE1: 1) documented their evaluation criterion; 2) updated their RBAM; and 3) notified staff of the changes to the RBAM
2013-08-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 2 (NPCC_URE2) | NCRXXXXX | NPCC2013011738 | CIP-005-1 | R1 | NPCC_URE2 submitted a Self-Report to NPCC stating that it had an issue with CIP-005-1 R1. NPCC_URE2 failed to identify an access point to its electronic security perimeter (ESP). NPCC_URE2 determined that the console server must be considered an access point because it is connected to a switch within the ESP. The console server is used to remotely monitor and reset corporate network equipment such as routers and switches. | The issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The loss of the switch would result in the loss of remote access to the downstream equipment and loss of daily data transmission to a central server from the downstream equipment. The switch is monitored and is able to be reset without the loss of any data if an intrusion were detected. The console server does not connect to cyber assets used in the operation or monitoring of the BPS. If the console server were used to compromise the switch inside the ESP, the substation automation equipment connected to the switch would continue to operate, causing minimal impact to the BPS. | To mitigate this issue, NPCC_URE2: 1) updated drawings, procedures, and other documents to reflect the console device as access points to the ESP; 2) included the console in a review of user access; and 3) submitted technical feasibility applications applicable to the devices
2013-08-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 3 (NPCC_URE3) | NCRXXXXX | NPCC2013011737 | CIP-005-1 | R1 | NPCC_URE3 submitted a Self-Report to NPCC stating that it had an issue with CIP-005-1 R1. NPCC_URE3 failed to identify an access point to its electronic security perimeter (ESP). NPCC_URE3 determined that the console server must be considered an access point because it is connected to a switch within the ESP. The console server is used to remotely monitor and reset corporate network equipment such as routers and switches. | The issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The loss of the switch would result in the loss of remote access to the downstream equipment and loss of daily data transmission to a central server from the downstream equipment. The switch is monitored and is able to be reset without the loss of any data if an intrusion were detected. The console server does not connect to cyber assets used in the operation or monitoring of the BPS. If the console server were used to compromise the switch inside the ESP, the substation automation equipment connected to the switch would continue to operate, causing minimal impact to the BPS. | To mitigate this issue, NPCC_URE3: 1) updated drawings, procedures, and other documents to reflect the console device as access points to the ESP; 2) Included the console in a review of user access; and 3) submitted Technical Feasibility Exception applications applicable to the devices
2013-08-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 4 (NPCC_URE4) | NCRXXXXX | NPCC2011009010 | CIP-006-2 | R2 | NPCC_URE4 submitted a Self-Report to NPCC stating that it had an issue with CIP-006-2 R2.2. NPCC_URE4 did not consider the access control panel associated with the physical security system located at its substation Physical Security Perimeters to be within the scope of NERC CIP standards. The appropriate Technical Feasibility Exception's were filed to mitigate this issue. | The issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system The inclusion of these assets in the NERC CIP program will not result in any change in existing controls. | To mitigate this issue, NPCC_URE4 has filed two TFEs that were approved by NPCC.
2013-08-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2012011565 | CIP-003-3 | R1; R1.3 | RFC_URE1 submitted a Self-Report to RF, stating that it had an issue with CIP-003-3 R1.3. RFC_URE1 had not performed and documented a review of its cybersecurity policy since October 2010. As a result, URE1 did not have evidence demonstrating that it performed an annual review and obtained annual approval of its cybersecurity policy, as required by CIP-003-3 R1.3. RFC_URE1 initially discovered this issue in May 2012, but RFC_URE1 did not recognize the failure to document its annual review and approval of its cybersecurity policy as a reportable issue until Fall 2012, when RFC_URE1 was finalizing a revised cybersecurity policy. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. RFC_URE1 provided evidence that it performed informal reviews of its cybersecurity policy in preparation for its Compliance Audit. RFC_URE1 provided an email in which its senior manager, who would have provided formal approval of the cybersecurity policy had a formal review taken place, indicated that he had reviewed that policy annually. | To mitigate this issue, RFC_URE1: 1) performed a formal annual review of its cybersecurity policy; and 2) generated the required senior manager approval on October 31, 2012.
2013-08-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2012011567 | CIP-003-3 | R4; R4.3 | RFC_URE1 submitted a Self-Report to RF, stating that it had an issue with CIP-003-3 R4. RFC_URE1 had not assessed adherence to its Critical Cyber Asset information protection program, documented the assessment results, and implemented an action plan to remediate deficiencies identified during the assessment, as required by CIP-003-3 R4.3. Specifically, in October 2012, RFC_URE1 discovered that it had last conducted a formal review of its program on December 22, 2010. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. RFC_URE1 informally reviewed its Critical Cyber Asset information protection program in the course of preparing for its Compliance Audit. While RFC_URE1 had informally reviewed its Critical Cyber Asset information protection program, it failed to document the results and any remediation plans; however, RFC_URE1 did assess five elements of its Critical Cyber Asset information protection program and determined that none of those elements presented deficiencies requiring remediation. | To mitigate this issue, RFC_URE1 performed a formal annual assessment of its Critical Cyber Asset information protection program and documented the results of that assessment on December 28, 2012.
2013-08-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2011001226 | CIP-005-1 | R2; R2.2 | RF conducted a Compliance Audit. RF determined that RFC_URE1had an issue with CIP-005-1 R2.2. RFC_URE1 did not enable only ports and services required for operations and for monitoring Cyber Assets within the Electronic Security Perimeter. RFC-URE1 presented documentation showing that six ports were required for normal operations, but RFC_URE1 provided no justification regarding the necessity of these ports being open. Additionally, RFC_URE1 provided the results of a scan conducted on November 17, 2010 showing that seven ports were open, as compared to the six listed ports in its documentation. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. RFC_URE1 was aware of all open ports and services at all times. Specifically, RFC_URE1 verifies its open ports and services during installations, upgrades, firewall rule reviews, and during vulnerability assessments. With respect to the discrepancy between its scan results and its documented ports and services, this discrepancy arose due to the interaction of its scanning software and certain of Linux-based systems, and only six ports were open, despite the inaccurate evidence produced by the scan. | To mitigate this issue, RFC-URE1 compiled a list of its open ports and services and developed a detailed justification for the necessity of each being open.
2013-08-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2011001227 | CIP-005-1 | R4; R4.2, R4.4 | RF conducted a Compliance Audit. RF determined that RFC_URE1, had an issue with R4. Specifically, RF reviewed documentation of RFC_URE1's annual performance of cyber vulnerability assessments (CVAs) of electronic access points to Electronic Security Perimeters (ESPs) as required by CIP-005-1 R4. In the course of this review, RF discovered that RFC_URE1 had not verified that only those ports and services required for operations at access points to ESP were enabled, as required by CIP-005-1 R4.2. Additionally, RF determined that RFC_URE1 had not reviewed controls for default accounts, passwords, and network management community strings, as required by CIP-005-1 R4.4. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. With respect to the aspect of this issue implicating CIP-005-1 R4.2, RFC_URE1 provided a description of its CVAs of access points to ESPs and of the resulting report. Although this report does not evidence RFC_URE1's determination that only necessary ports and services were open, it does demonstrate RFC_URE1's assessment of all open ports and services and any associated vulnerabilities. With respect to the aspect of this issue implicating CIP-005-1 R4.4, RFC_URE1 provided a letter from the vendor responsible for reviewing RFC_URE1's controls for default accounts, passwords, and network management community strings. The vendor explained that its review did address those required elements. RFC_URE1 further explained that its CVA report only documented identified problems discovered through the performance of a CVA and committed to provide more details regarding the activities undertaken during a CVA. | To mitigate this issue, RFC_URE1: 1) compiled a list of its open ports and services and developed a detailed justification for the necessity of each being open; 2) committed to performing, on an ongoing basis, CVAs by comparing open ports and services to this list; 3) committed to including, on an ongoing basis, a statement of all things reviewed pursuant to its CVAs.
2013-08-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2011001231 | CIP-007-1 | R2 | RF conducted a Compliance Audit. RF determined that RFC_URE1, had an issue with CIP-007-1 R2. RFC_URE1 was not able to demonstrate that only those ports and services required for normal and emergency operations were enabled. In addition, RF discovered that RFC_URE1 had devices with unused ports and services that could not be disabled due to technical limitations and RFC_URE1 had failed to submit a Technical Feasibility Exception (TFE) request as required by CIP-007-1 R2.3. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. RFC_URE1 investigated the discrepancies discovered during the Compliance Audit and determined that they were a result of one particular service that operates within a range of ports, and therefore not indicative of programmatic issues. Furthermore, RFC_URE1 subsequently determined that certain of the devices related to the failure to submit TFE requests were able to be re-classified as non-critical and, therefore, able to be removed from the Electronic Security Perimeter (ESP). | To mitigate this issue, RFC_URE1: 1) corrected its baseline list of ports and services to account for the identified discrepancies, and implemented an automated tracking application to monitor its open ports and services. This tracking application alarms for discrepancies between an identified baseline and actual open ports and services; 2) reclassified the devices for which it had not submitted TFE requests as non-critical and removed them from the ESP; and 3) revised its testing procedures to include a review of the criticality of any new Cyber Assets within an ESP.
2013-08-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2011001232 | CIP-007-1 | R3 | RF conducted a Compliance Audit. RF determined that RFC_URE1, had an issue with CIP-007-1 R3. During the Audit, RF reviewed a RFC_URE1 tracking spreadsheet showing available updates for Cyber Assets. In reviewing this spreadsheet, RF determined that, for several months in 2010, RFC_URE1 had failed to review vendor websites for applicable security updates, as required by RFC_URE1’s security patch management program. RF also determined that, although the spreadsheet had been updated, RFC_URE1 failed to review this spreadsheet in April 2011. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. For the duration of the issue, RFC_URE1 did have a process in place requiring the assessment of security patches. RFC_URE1's failure to implement this process were isolated incidents, and therefore not indicative of any programmatic issues. RF also observed, during the Compliance Audit, that RFC_URE1 had already undertaken steps to improve this process. Furthermore, no applicable patches were available during the months identified at the Compliance Audit. | To mitigate this issue, RFC_URE1: 1) reviewed its patch management procedures, particularly with respect to field devices, and revised its patch management procedures to cure the issues identified during such audit. The new patch management procedure requires RFC_URE1 to assess patches for field devices twice per month, schedule implementation of patches, and ensure timely assessment of patches. The individual that assesses and schedules these patches is required to perform a sign-off; and 2) established an automated reminder system to notify the applicable supervisor to review these assessments twice per month to ensure that the patches are being assessed timely and correctly. All of these steps ensure that patches are assessed and scheduled, as appropriate.
2013-08-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2011001234 | CIP-007-1 | R5; R5.1.2; R5.3 | RF conducted a Compliance Audit. RF determined that RFC_URE1, had an issue with CIP-007-1 R5. RF determined that RFC_URE1 failed to maintain logs of sufficient detail to create historical audit trails of individual user account access for a minimum of ninety days, as required by CIP-007-1 R5.1.2. Specifically, RFC_URE1 maintained logs showing activity that occurred on specific shared assets, but RFC_URE1's logs did not provide detail sufficient to show an individual's specific activities with respect to those shared assets. RF also determined that RFC_URE1 failed to implement password security controls as required by CIP-007-1 R5.3 or submit a Technical Feasibility Exception (TFE) request. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although RFC_URE1's logs did not provide sufficient information to create historical audit trails of individual user account activity, RFC_URE1 did maintain logs of shared account activities. Furthermore, RFC_URE1 filed TFE requests for the devices implicated in the issue with CIP-007-1 R5.3, and RF subsequently approved them. | To mitigate this issue, RFC_URE1: 1) implemented software that ensures that every device deployed by RFC_URE1 is configured to log activities in accordance with CIP-007 R5.1.2; and 2) submitted TFE requests for the devices implicated by the issue with CIP-007-1 R5.3 which were subsequently approved by RF.
2013-08-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2011001235 | CIP-007-1 | R6 | RF conducted a Compliance Audit. RF determined that RFC_URE1, had an issue with CIP-007-1 R6. From January 1, 2010 to June 26, 2011, RFC_URE1 relied on an informal checkout process performed each day by the individual responsible for monitoring activity on RFC_URE1's supervisory control and data acquisition system. The results of this process were communicated during daily meetings, but the results were not formally documented. RF determined that this lack of documentation constituted non-compliance with CIP-007-1 R6. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. RFC_URE1 had an informal checkout process in place for the duration of the issue. Implementation of the informal checkout process and communication of the results of this process daily would have enabled RFC_URE1 to quickly discover and address security events on Cyber Assets within the Electronic Security Perimeter. Furthermore, RFC_URE1 mitigated this issue by formalizing this previously informal process. | To mitigate this issue, RFC_URE1 implemented a formal supervisory control and data acquisition system On Call Checkout Procedure. This document formalizes RFC_URE1's checkout procedures that were previously informal. RF has verified the completion of all mitigating activity.
2013-08-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2011001236 | CIP-007-1 | R7 | RF conducted a Compliance Audit. RF determined that RFC_URE1, had an issue with CIP-007-1 R7. RFC_URE1 could not produce evidence that it implemented its methods, processes, and procedures for one Cyber Asset, located in a RFC_URE1 substation and listed as decommissioned. In fact, this device had been deactivated by RFC_URE1 but had not yet been identified for disposal or redeployment. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The device in question had been removed from RFC_URE1's network, and was physically and logically disconnected from the Electronic Security Perimeter (ESP) in which it had been located. Furthermore, the device in question remained secured in a Physical Security Perimeter. | To mitigate this issue, RFC_URE1 strengthened its asset management procedures to provide visibility regarding the status of Cyber Assets with ESPs throughout the lifecycle of such devices. RFC_URE1 now has the ability to precisely identify the status of Cyber Assets, including Cyber Assets that have been disconnected from RFC_URE1's networks.
2013-08-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2011001239 | CIP-009-1 | R1 | RF conducted a Compliance Audit. RF determined that RFC_URE1, had an issue with CIP-009-1 R1. RF determined that RFC_URE1's recovery plan did not specify the required actions in in response to events or conditions of varying duration and severity that would activate the recovery plans, as required by CIP-009-1 R1.1. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. RFC_URE1 had recovery plans in place, and its responsible personnel were well versed in these plans and trained on an annual basis. RFC_URE1's recovery plans did describe certain events that would necessitate their use, and they contained references to procedures to be used in recovering assets. | To mitigate this issue, RFC_URE1 added detail to its recovery plans specifying events and conditions of varying duration and severity and the required actions in each circumstance. RF has verified the completion of all mitigating activity.
2013-08-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2011001240 | CIP-009-1 | R2 | RF conducted a Compliance Audit. RF determined that RFC_URE1, had an issue with CIP-009-1 R2. RFC_URE1 provided evidence of device failover testing and other situations requiring immediate attention as evidence that it exercised its recovery plan. RF determined that this evidence could not be correlated to specific provisions of RFC_URE1's recovery plan. Therefore, RF determined that RFC_URE1 failed to show that it had annually exercised its recovery plan. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The evidence provided by RFC_URE1 demonstrates that activities occurred pursuant to a recovery plan, which constitute exercises of RFC_URE1's recovery plan. | To mitigate this issue, RFC_URE1: 1) deployed a new software tool to automate notification and tracking of recovery plan exercises; and 2) revised its recovery plan documentation to provide procedures for the backup and storage of information required to successfully restore all Critical Cyber Assets and tested this revised recovery plan. RF has verified the completion of all mitigating activity.
2013-08-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2011001241 | CIP-009-1 | R4 | RF conducted a Compliance Audit. RF determined that RFC_URE1, had an issue with CIP-009-1 R4. RF reviewed RFC_URE1's processes and procedures for the backup and storage of information required to successfully restore Critical Cyber Assets, required pursuant to CIP-009-1 R4. RFC_URE1 provided statements of its policy to backup information as required. RFC_URE1 also provided statements regarding the servers and other types of equipment requiring backup. RFC_URE1, however, did not provide specific processes and procedures for the backup of information, nor did RFC_URE1 provide information about the use of those backups to successfully restore Critical Cyber Assets (CCAs). | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. RFC_URE1's evidence showed that it maintained a policy of using tapes to backup all required information. RFC_URE1's processes and procedures relating to backup information had been tested. RFC_URE1 would have been able to successfully restore CCAs using this information. | To mitigate this issue, RFC_URE1 revised its recovery plans to require documentation of the specific provisions of the recovery plan exercised pursuant to CIP-007 R2. RF has verified the completion of all mitigating activity.
2013-08-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2013012208 | CIP-004-3a | R2 | RFC_URE2 submitted a Self-Report to RF stating that it had an issue with CIP-004-3a R2. RFC_URE2 failed to adequately ensure that all personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets had the appropriate level of personnel risk assessment, training, and security awareness. | The issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The individual to whom access privileges were assigned and the individual for whom access was requested had identical surnames and worked for the same organization, so the error is not likely to recur. The individual to whom access privileges were granted was unaware of the granted access. A review of access records was immediately conducted upon discovery of the issue, and this review determined that the privileges were not used to access any NERC Physical Security Perimeter. | To mitigate this issue, RFC_URE2: 1) revoked the access privileges assigned to the wrong person and assigned access privileges to the correct person; and 2) reinforced the correct procedures for assigning access privileges and for checking individual’s name for a match as well as for the badging and access control administrator. RF has verified the completion of all mitigating activity.
2013-08-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC2013012419 | CIP-003-1 | R2 | RFC_URE3 submitted a Self-Report to RF stating that it had an issue with CIP-003-1 R2. Within its Self-Report, RFC_URE3 stated that it cannot locate a specific document that identifies the assignment of senior manager by name, title, and date of designation, as required by CIP-003-1, R2.1, for the time period from July 1, 2008 to January 18, 2010. Additionally, RFC_URE3’s January 18, 2010 document stating the assignment of senior manager did not identify the senior manager’s delegate by name and URE3’s May 9, 2012 version of this document did not identify the senior manager by title, as required by CIP-003-1, R2.1. Finally, URE3 made a change to the senior manager on May 9, 2012, but failed to document the change within 30 calendar days of the effective date, as required by CIP-003, R2.2. Instead URE3 named a change of senior manager 56 calendar days after the effective date of the change, which is 26 days longer than the 30 calendar day requirement. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because this issue was a documentation issue only; URE3 had an individual in charge of leading and managing URE3’s implementation of, and adherence to, Standards CIP-002 through CIP-009 at all times. Specifically, the Chief Executive Officer and the Management Committee Representative of RFC_URE3, was the senior manager with responsibility and authority for leading and managing RFC_URE3’s CIP-002 through CIP-009 compliance from the start date of compliance through March 16, 2012. Effective March 16, 2012, a new Chief Executive Officer and Managing Committee Representative was named. On May 9, 2012, 56 calendar days after the Chief Executive Officer and the Management Committee Representative’s departure, the senior manager role was assigned to the RFC_URE3 Plant Manager. Furthermore, the limited documentation related nature of the issue was also evidenced by the fact that the RFC_URE3’s senior manager implemented all CIP-related responsibilities, including an annual review of RFC_URE3’s CIP procedures and Risk Based Assessment Methodology. RF favorably considered that it discovered the issue through a Self-Report, which resulted from shared lessons learned. Effective oversight of the reliability of the Bulk Power System depends on robust and timely self-reporting by Registered Entities. RFC_URE3 promptly identified and reported the issue due to the effective execution of internal controls that yielded identification of the issue prior to the occurrence of any harm. | To mitigate this issue, RFC_URE3: 1) conducted a review of its procedure for ensuring compliance with the CIP Reliability Standards. 2) revised for clarity and now maintains a current and accurate Designation of Senior Manager letter, which it stores in its electronic document management program for document retention; and 3) created a task activity in the Electronic Data Tracking System, which generates an annual reminder to review the Senior Management assignments; and 4) established a managerial transition checklist guideline for its use during changes in senior management and will be utilized within 30 days to ensure a timely assignment of a new senior manager.
2013-08-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 4 (RFC_URE4) | NCRXXXXX | RFC2013012128 | CIP-007-1 | R3 | RFC_URE4 submitted a Self-Report to RF stating that it had an issue with CIP-007-1, R3 because RFC_URE4 failed to implement its security patch management program for tracking, evaluating, testing, and installing applicable cyber security software patches for all Cyber Assets within the Electronic Security Perimeter(s). Specifically, for its Cisco networking devices within RFC_URE’s Electronic Security Perimeters and Cisco firewalls that serve as Electronic Security Perimeter access points, RFC_URE4 failed to document the assessment of security patches and security upgrades for applicability within thirty calendar days of availability of the patches and upgrades and failed to document the implementation of security patches. RFC_URE4 utilized a vendor to monitor and assess its security patch management, but discovered that the vendor did not conduct assessments and implementation of security patches for Cisco devices and firewalls in the manner required by CIP-007-1, R3. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Due to the minimal feature set RFC_URE4 had enabled on the Cisco devices in its environment, RFC_URE4 was susceptible only to minimal denial of service vulnerabilities and was not subject to more critical vulnerabilities. Additionally, RFC_URE4 was still able to retain local control of the system and was able to operate normally during the time period of the issue. RF favorably considered that RFC_URE4 discovered the issue through self-report. Effective oversight of the reliability of the Bulk Power System depends on robust and timely self-reporting by Registered Entities. RFC_URE4 promptly identified and reported the issue due to the effective execution of internal controls that yielded identification of the issue prior to the occurrence of any harm. When assessing the issue, RF considered whether the facts of this issue constitute repetitive infractions by analyzing whether they evidenced any (a) repeated or continuing conduct similar to that underlying a prior violation of the same or a closely-related Reliability Standard Requirement; (b) conduct addressed in any previously submitted Mitigation Plan for a prior violation of the same or closely-related Reliability Standard Requirement; or (c) multiple violations of the same Standard and Requirement. | To mitigate this issue, RFC_URE4: 1) will perform a software upgrade to RFC_URE4’s SCADA/EMS systems, which will bring the missed equipment up to current software versions and ensure timely patch management on an ongoing basis.
2013-08-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 5 (RFC_URE5) | NCRXXXXX | RFC2013012585 | CIP-007-2a | R1 | RF conducted a Compliance Audit. RF determined that RFC_URE5, had an issue with CIP-007-2a R1. RFC_URE5 failed to provide sufficient evidence demonstrating it implemented its cyber security test procedure. Additionally, RFC_URE5 failed to ensure that significant changes to existing Cyber Assets within the Electronic Security Perimeter do not adversely affect existing cyber security controls. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because RFC_URE has documented procedures for testing cyber security controls, even though it failed to strictly comply with the requirements listed within these procedures. Additionally, RFC_URE5 was able to provide documentation evidencing its testing of significant changes related to enabled ports and services, even though it failed to evidence its testing of all cyber security controls pursuant to the RFC_URE5 Cyber Security Test Procedures. | To mitigate this issue, RFC_URE5: 1) modified its cyber security test procedures to ensure that new Cyber Assets and significant changes to existing Cyber Assets within the Electronic Security Perimeter do not adversely affect existing cyber security controls; and 2) implemented a new tool to test for security controls. RF verified RFC_URE5's completion of all mitigating activity.
2013-08-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 5 (RFC_URE5) | NCRXXXXX | RFC2013012586 | CIP-007-2a | R3 | RF conducted a Compliance Audit. RF determined that RFC_URE5 had an issue with CIP-007-2a R3. RFC_URE5 failed to assess four patches within thirty calendar days of availability. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because although RFC_URE5 failed to assess the applicability of four patches within the required thirty-day timeframe, RFC_URE5 did assess all four patches at a later date. Additionally, RFC_URE5 assessed patches on critical software within the required thirty-day timeframe. The software at issue is not critical software and the failure to assess patches for this software does not have the same potential impact on the Bulk Electric System that as a failure to assess more critical software. | To mitigate this issue, RFC_URE5: 1) discussed the issue with the third party patch assessment vendor to ensure that forthcoming patches would not be missed. RF verified RFC_URE5's completion of all mitigating activity.
2013-08-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 5 (RFC_URE5) | NCRXXXXX | RFC2013012587 | CIP-007-2a | R5 | RF conducted a Compliance Audit. RF determined that RFC_URE5 had an issue with CIP-007-2a R5. RFC_URE5 failed to maintain an audit trail of shared account use for one shared account. Specifically, RFC_URE5 has four individuals with access to this shared account but failed to maintain an audit trail of account use for this shared account, as required by CIP-007-2, R5.2.3. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because RFC_URE5 has only one shared account for which it failed to maintain an audit trail of account use. The primary user of the shared account is the SCADA Lead Engineer, a trusted employee, who received the required cyber security training, as well as a personnel risk assessment that identified no issues. Finally, the remaining three employees with access to this shared account also received the required cyber security training and personnel risk assessment that identified no issues. | To mitigate this issue, RFC_URE5 began maintaining and will continue to maintain an audit trail of access to the shared account. RF verified RFC_URE5's completion of all mitigating activity.
2013-08-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 6 (RFC_URE6) | NCRXXXXX | RFC2012010408 | CIP-007-3a | R5 | RFC_URE6 submitted a Self-Certification to RF stating that it had an issue with CIP-007-3a R5. RFC_URE6 determined that it could not technically enforce the complexity requirements of CIP-007-3a R5 or its passwords nor had RFC_URE6 submitted a TFE for this issue of non-compliance. Windows XP, which RFC_URE6 uses as the operating system for its computers, does not enforce the same password complexity as that required by CIP-007-3a R5. Therefore, RFC_URE6 could not demonstrate compliance with CIP-007-3a R5. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because although RFC_URE6 could not enforce its password criteria due to software limitations, it could enforce that each password contain a minimum of six characters. RFC_URE6 required the use of passwords with the specific criteria included in its electronic access control process during the duration of the alleged violation. Specifically, RFC_URE6’s policy is that passwords require at least 3 of the following four elements: 1) Upper case letters, 2) Numbers, 3) Lower case letters, and 4) Special characters. RF considers certain aspects of RFC_URE6’s compliance program as mitigating factors. RFC_URE6 distributes its compliance program to employees who have direct or indirect responsibility for compliance. RFC_URE6’s employees and corporate team members regularly attend NERC and regional workshops and conferences. RFC_URE6 conducts internal audits of its internal compliance program semi-annually. When assessing the issue, RF considered whether RFC_URE6 evidenced repetitive infractions by considering whether there was any (a) repeated or continuing conduct similar to that underlying the prior violation of the same or a closely-related Reliability Standard Requirement; (b) conduct addressed in any previously submitted mitigation plan for a prior violation of the same or a closely-related Reliability Standard Requirement; or (c) multiple violations of the same Standard and Requirement. RF determined that RFC_URE6 does not have prior alleged violations of the same Standards included in this Agreement. However, RF considered RFC_URE6’s affiliated Registered Entity’s prior alleged violation of CIP-007-2 R5.2 as an aggravating factor. A RFC_URE6 affiliate Registered Entity discovered a network switch with previously unknown functionality. The affiliated Registered Entity determined it had not adjusted the default accounts to meet the password requirements of CIP-007 R5.3. Unlike the alleged violation described in this FFT Report, the affiliated Registered Entity’s alleged violation did not involve a technical limitation to an operating system, but rather a network switch on which the affiliated Registered Entity could enforce CIP-007 R5.3’s password complexity requirements. Therefore, RF determined the alleged violations are sufficiently different to warrant FFT treatment of RFC_URE6’s alleged violation. | To mitigate this issue, RFC_URE6: 1) revised the password character length requirement from six to eight characters; and 2) submitted a TFE request, which RF accepted and approved. RF verified RFC_URE6's completion of all mitigating activity.
2013-08-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 7 (RFC_URE7) | NCRXXXXX | RFC2012010108 | CIP-007-3a | R5 | RF conducted a Compliance Audit. RF determined that RFC_URE7, had an issue with CIP-007-3a R5. RFC_URE7 failed to provide evidence that it enforced the complexity requirements pursuant to CIP-007-3a R5 on its passwords nor did RFC_URE7 submit a TFE for this issue of non-compliance. Windows XP, which RFC_URE7 uses as the operating system for it computers, does not enforce the same password complexity as that required by CIP-007-3a R5. Therefore, RFC_URE7 could not demonstrate compliance with CIP-007-3a R5. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because although RFC_URE7 could not enforce its password criteria due to software limitations, it could enforce that each password contain a minimum of six characters. RFC_URE7 required the use of passwords with the specific criteria included in its electronic access control process during the duration of the alleged violation. Specifically, RFC_URE7’s policy was that passwords required at least 3 of the following four elements: 1) Upper case letters, 2) Numbers, 3) Lower case letters, and 4) Special characters. RF considers certain aspects of RFC_URE7’s compliance program as mitigating factors. RFC_URE7 distributes its compliance program to employees who have direct or indirect responsibility for compliance. RFC_URE7’s employees and corporate team members regularly attend NERC and regional workshops and conferences. RFC_URE7 conducts internal audits of its internal compliance program semi-annually. When assessing the issue RF considered whether RFC_URE7 evidenced repetitive infractions by considering whether there was any (a) repeated or continuing conduct similar to that underlying the prior violation of the same or a closely-related Reliability Standard Requirement; (b) conduct addressed in any previously submitted mitigation plan for a prior violation of the same or a closely-related Reliability Standard Requirement; or (c) multiple violations of the same Standard and Requirement. RF determined that RFC_URE7 does not have prior alleged violations of the same Standards included in this Agreement. However, RF considered RFC_URE7’s affiliated Registered Entity’s prior alleged violation as an aggravating factor. A RFC_URE7 affiliate Registered Entity discovered a network switch with previously unknown functionality. The affiliated Registered Entity determined it had not adjusted the default accounts to meet the password requirements of CIP-007 R5.3. Unlike the alleged violation described in this FFT Report, the affiliated Registered Entity’s alleged violation did not involve a technical limitation to an operating system, but rather a network switch on which the affiliated Registered Entity could enforce CIP-007 R5.3’s password complexity requirements. Therefore, RF determined the alleged violations are sufficiently different to warrant FFT treatment of RFC_URE7’s alleged violation). | To mitigate this issue, RFC_URE7 : 1) revised the password character length requirement from six to eight characters; and 2) submitted a TFE request, which RF accepted and approved. RF verified RFC_URE7's completion of all mitigating activity.
2013-08-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2012011413 | CIP-007-3a | R4; R4.2 | During a Compliance Audit, the Southwest Power Pool Regional Entity (SPP RE) determined that Unidentified Registered Entity 1 (SPPRE_URE1) had an issue with CIP-007-3a R4.2. SPP RE determined that SPPRE_URE1 did not implement its malware prevention process as required by CIP-007-3a R4.2 when applying anti-virus signatures to two operator consoles. During a specific date, anti-virus signatures were automatically pushed to the consoles without first undergoing pre-installation testing as required by the SPPRE_URE1 process because the two consoles were configured to seek automatic signature updates when they were turned on after being shut down for more than 30 days. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The anti-virus signatures originated from a trusted anti-virus vendor and therefore presented a minimal risk of being malicious. Furthermore, the signatures were applied to two individual operator consoles, and therefore did not pose a risk to the security controls residing on SPPRE_URE1’s Energy Management Server. Moreover, the operator consoles resided within a back-up control center, thereby limiting any potential loss of functionality or security control compromises to the primary control center that might have resulted from the automatic installation. | To mitigate this issue, SPPRE_URE1 made the determination to keep the workstations at the back-up control center continuously powered on, thereby preventing the automatic installation of anti-virus signatures following a restart of the consoles after a 30 day period.
2013-08-30 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE2012010666 | CIP-002-3 | R4 | TRE_URE1 submitted a self-report citing an issue with CIP-002-3 R4. TRE_URE1 reported that there is no signed and dated record of the senior manager’s approval of the risk-based assessment methodology (RBAM) during one calendar year. This issue began on the date by which TRE_URE1 should have annually approved its RBAM. This date is based on TRE_URE1's definition of annual, which, in accordance with Compliance Application Notice – 0010, is within a calendar year. TRE_URE1 corrected this issue the following year on the date the TRE_URE1 designated senior manager signed the RBAM. | This issue posed a minimal risk and did not pose a serious or substantial risk to the bulk power system because from the time the senior manager originally signed the documents until the time the senior manager signed the next RBAM, the TRE_URE1's RBAM did not change. Moreover, TRE_URE1 did not previously have any CCAs and does not currently have any CCAs. Other mitigating factors include: the designated senior manager for TRE_URE1 authorized the CA and CCA lists for the missed year based on the approved originally signed RBAM and there were no significant changes to the plant, the RBAM, or the applicable standards since the originally signed RBAM. | To mitigate this issue, a TRE_URE1 designated senior manager signed the RBAM. Texas RE has verified the completion of all mitigation activity.
2013-08-30 | TRE_URE1liability Entity (TRE_URE1) | Unidentified Registered Entity 2 (TRE_URE2) | NCRXXXXX | TRE2012010904 | CIP-003-3 | R2 | During an audit TRE_URE1 conducted of TRE_URE2, TRE_URE1 discovered an issue with CIP-003-3 R2. In accordance with the CIP Implementation plan, TRE_URE2 is required to have an assigned and documented CIP Senior Manager 12 months following TRE_URE2’s registration. On that date, TRE_URE2 should have had an assigned and documented CIP senior Manager. TRE_URE2 was unable to provide evidence that it had officially assigned a CIP Senior Manager until approximately one year later. Thus, the duration of the issue is from the 12 months following TRE_URE2’s registration date a through the date TRE_URE2 officially assigned a CIP Senior Manager. | This issue posed a minimal risk and did not pose a serious or substantial risk to the bulk power system because, both before and after a CIP Senior Manager was assigned, TRE_URE2 did not identify any CAs or CCAs. Additionally, the amount of distribution TRE_URE2 provides at peak demand represents a relatively small risk to the whole of the BES. | To mitigate this issue, TRE_URE2 designated a CIP Senior Manager. TRE_URE1 has verified the completion of all mitigation activity.
2013-08-30 | Texas Reliability Entity (Texas RE), ReliabilityFirst (RF), Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 3 (TRE_URE3, RFC_URE3, SPP_URE3) (Collectively, URE_3) | NCRXXXXX | TRE2013011976 RFC2013012069 SPP2013011831 | CIP-003-3 | R4 | URE_3 submitted a self-report to Texas RE citing it had an issue with CIP-003-3 R4. Additionally, URE_3 submitted a self-report to ReliabilityFirst and a self-certification to SPP RE for the same issue. URE_3 stated in its self-report that it did not classify a draft Critical Asset List according to its Information Protection Program. Specifically, URE_3 mistakenly uploaded its draft Critical Asset list on its SharePoint site which some employees who had access to the site were not authorized to access such protected information. URE_3 later discovered this document was not supposed to be on the SharePoint site and removed the document, placing it in the correct location where only those personnel authorized to have access to the protected information could access the document. Additionally, URE_3's draft Critical Asset list was not marked confidential per URE_3's Information Protection Program. URE_3 has since marked the document with the confidential stamp. Texas RE, on behalf of itself, ReliabilityFirst, and SPP RE, determined that URE_3 had an issue with CIP-003-3 R4 because, by uploading the draft CA list to the wrong SharePoint site, URE_3 failed to implement its Information Protection Program correctly in accordance with CIP-003-3 R4. | This issue posed a minimal risk and did not pose a serious or substantial risk to the bulk power system. The document was uploaded to the wrong location for only 22 days. Additionally, URE_3 explained that during the time period of the issue, 79 individuals had access to the SharePoint site. Of those 79 individuals, 28 were not authorized to view URE_3's draft Critical Asset list, none of which actually viewed the document. | To mitigate this issue, URE_3: 1) Removed the document from the SharePoint site 2) Developed communication on proper storage location of documents 3) Developed communication on URE_3's information classification CIP standard 4) Conducted an awareness meeting with the department and staff involved Texas RE has verified the completion of all mitigation activity.
2013-08-30 | Texas Reliability Entity (Texas RE), ReliabilityFirst (RF), Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 3 (TRE_URE3, RFC_URE3, SPP_URE3) (Collectively, URE_3) | NCRXXXXX | TRE2013011888 RFC2013011789 SPP2013011833 | CIP-007-3a | R9 | URE_3 submitted a self-report to Texas RE stating it had an issue with CIP-007-3 R9. Additionally, URE_3 submitted a self-report to ReliabilityFirst and SPP RE for the same issue. Specifically, URE_3 failed to document a change resulting from modifications to the system used for security management within 30 calendar days of the change being completed. URE_3 did not update its Disposal and Redeployment documentation per CIP-007-3 R7 to reflect a new change and asset management tool. URE_3 updated its Disposal and Redeployment documentation to reflect the new change and asset management tool approximately two months after URE_3 implemented the new tool, which is used for Asset and Change Management. Texas RE, on behalf of itself, ReliabilityFirst, and SPP RE, determined that URE_3 had an issue with CIP-007-3 R9 for two months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the bulk power system because the basic processes for asset and change management did not change even though the entity failed to update its documentation within 30 calendar days after the change to the system was completed. URE_3 attested that no adverse consequences arose from the oversight. | To mitigate this issue, URE_3 reviewed and updated its documentation regarding Disposal and Redeployment to reflect a change to the new system for its change and asset management tool. Texas RE has verified the completion of all mitigation activity.
2013-08-30 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 4 (TRE_URE4) | NCRXXXXX | TRE2013011977 | CIP-003-3 | R4 | TRE_URE4 submitted a self-report to Texas RE citing it had an issue with CIP-003-3 R4. TRE_URE4 stated in its self-report that it did not classify a draft Critical Asset List according to its Information Protection Program. Specifically, TRE_URE4 mistakenly uploaded its draft Critical Asset list on its SharePoint site which some employees who had access to the site were not authorized to access such protected information. TRE_URE4 later discovered this document was not supposed to be on the SharePoint site and removed the document, placing it in the correct location where only those personnel authorized to have access to the protected information could access the document. Additionally, TRE_URE4's draft Critical Asset list was not marked confidential per TRE_URE4's Information Protection Program. TRE_URE4 has since marked the document with the confidential stamp. Texas RE determined that TRE_URE4 had an issue with CIP-003-3 R4 because, by uploading the draft CA list to the wrong SharePoint site, TRE_URE4 failed to implement its Information Protection Program correctly in accordance with CIP-003-3 R4. | This issue posed a minimal risk and did not pose a serious or substantial risk to the bulk power system. The document was uploaded to the wrong location for only 22 days. Additionally, TRE_URE4 explained that during the time period of the issue, 79 individuals had access to the SharePoint site. Of those 79 individuals, 28 were not authorized to view TRE_URE4's draft Critical Asset list, none of which actually viewed the document. | To mitigate this issue, TRE_URE4 1) Removed the document from the SharePoint site 2) Developed communication on proper storage location of documents 3) Developed communication on TRE_URE4's information classification CIP standard 4) Conducted an awareness meeting with the department and staff involved Texas RE has verified the completion of all mitigation activity.
2013-08-30 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 4 (TRE_URE4) | NCRXXXXX | TRE2013011887 | CIP-007-3a | R9 | TRE_URE4 submitted a self-report for an issue with CIP-007-3 R9. TRE_URE4 failed to document a change resulting from modifications to the system within 30 calendar days of the change being completed. Specifically, TRE_URE4 did not update its Disposal and Redeployment documentation per CIP-007-3 R9 to reflect a new change and asset management tool. The prior tool remained in place for read-only purposes and for completion of in-flight change requests. TRE_URE4 updated its Disposal and Redeployment documentation three months after implementing the new tool, which is used for Asset and Change Management. | This issue posed a minimal risk and did not pose a serious or substantial risk to the bulk power system because the basic processes for asset and change management did not change even if the entity failed to update its documentation within 30 calendar days. No adverse consequences arose from the oversight. | To mitigate this issue, TRE_URE4 reviewed and updated its documentation regarding Disposal and Redeployment to reflect a change to the new system for its change and asset management tool. Texas RE has verified the completion of all mitigation activity.
2013-08-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2013012015 | CIP-002-3 | R4 | WECC_URE1 submitted a Self Certification to WECC stating that it had an issue with CIP-002-3 R4. Specifically, WECC_URE1 reported it failed to approve annually the risk-based assessment methodology, the list of Critical Assets, and the list of Critical Cyber Assets for calendar years 2011 and 2012. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although WECC_URE1 failed to have sufficient signed and dated records of these approvals, a WECC_URE1 Engineer had reviewed these documents on an annual basis during the period of noncompliance, and the lists were null. | WECC_URE1 has not completed all mitigating activities associated with this remediated issue. WECC_URE1 must fully mitigate the remediated issue within 90 days from the date this FFT is filed or posted on the NERC website.
2013-08-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2013012064 | CIP-002-3 | R4 | WECC_URE2 submitted a Self Certification to WECC stating that it had an issue with CIP-002-3 R4. Specifically, WECC_URE2 reported it failed to approve annually the risk-based assessment methodology, its list of Critical Assets, and its list of Critical Cyber Assets for calendar year 2012. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although WECC_URE2 failed to have sufficient signed and dated records of these approvals, WECC_URE2 had reviewed these documents in 2010 and 2011 and the lists were null. In addition, WECC_URE2 implemented an automated notification reminder that will alert personnel mid-year to complete its annual CIP-002 R4 approvals. | To mitigate this issue, WECC_URE2’s senior manager reviewed and approved WECC_URE2’s risk-based assessment methodology, its null list of Critical Assets, and its null list of Critical Cyber Assets.
2013-08-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2013012065 | CIP-003-2 | R2 | WECC_URE2 submitted a Self Certification to WECC stating that it had an issue with CIP-003-2 R2. Specifically, WECC_URE2 reported it failed to assign a single manager with overall responsibility and authority for leading and managing its implementation of, and adherence to Standards CIP-002 through CIP-009 as required by CIP-003-2 R2. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although WECC_URE2 failed to document a senior manager, WECC_URE2 did have an identified technical compliance employee that was tasked with ensuring compliance to all CIP related standards. In addition, WECC_URE2 applied its risk-based assessment methodology and determined that it does not have any Critical Assets or Critical Cyber Assets. | To mitigate this issue, WECC_URE2 assigned a single senior manager with overall responsibility and authority for leading and managing the implementation of, and adherence to, CIP-002-2 though CIP-009-2, as required by CIP-003-2 R2.
2013-08-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2013012259 | CIP-006-3c | R4 | WECC_URE3 submitted a Self-Report to WECC stating that it had an issue with CIP-006-3c R4. Specifically, WECC_URE3 reported it failed to implement the operational and procedural controls to manage physical access at one access point to a Physical Security Perimeter (PSP) twenty-four hours a day, seven days a week. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although the card reader was not managing access to the continuous emission monitoring system (CEMS) PSP for 16 hours, the PSP is surrounded by fencing that is secured with a card reader and video monitoring twenty-four hours a day, seven days a week. WECC_URE3 security checked the surveillance footage after the incident and confirmed the fence was active and monitoring during the duration of the violation and no suspicious or malicious activity occurred. The CEMS PSP contains six devices, two Critical Cyber Assets (sensor controller PLC, server) that track and maintain the analysis data for the air permit, and four non-Critical Cyber Assets (3 analyzers, 1 recorder) that are for analyzing carbon monoxide, ammonia, and nitrous oxide. If an attacker was to gain access to these devices, the server is password protected and the remaining five devices do not have a user interface. Further, if the password controls were bypassed, the attacker would not have access to the Peaker network. Additionally, if an attacker was to compromise these devices, the devices would stop analyzing particulate matter and the WECC_URE3 Corporate Security would receive immediate alerts and alarms. | To mitigate this issue, WECC_URE3 distributed an email requiring all employees, whom access WECC_URE3's PSPs, to review WECC_URE3 Division Order once again. The Division Order details the procedure for compliance with CIP-006 R4, and includes Section G, End of Shift Final Inspection, which is the procedure for ensuring all doors are locked, secured, and armed prior to leaving the site.
2013-08-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC2013012284 | CIP-007-3a | R2 | WECC_URE4 submitted a Self-Report to WECC stating that it had an issue with CIP-007-3a R2. Specifically, WECC_URE4 reported that its affliate completed a port scan associated with the vulnerability assessment of WECC_URE4’s ports and services. After reviewing the results of the scan, the affliate identified an open port that was not needed for normal and emergency operations, and therefore should have been disabled. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE4 confirmed that the Cyber Asset in question was located in an identified Physical Security Perimeter (PSP) and protected from unauthorized physical access by a card key access control system that is configured to only allow personnel who are trained, vetted, and authorized for such access to restricted areas. Additionally, all devices reside in an identified Electronic Security Perimeter (ESP), where all logical access is restricted, logged, and monitored by restrictive boundary devices. WECC_URE4 further stated it does a complete vulnerability and configuration port/service scan every quarter on the ESP subnets to detect any unnecessary ports/services running. In addition, the port was open in error for 10 days or less. | To mitigate this issue, WECC_URE4 remediated this issue when it disabled the device and conducted a port scan, to ensure the port was correctly disabled.
2013-08-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 5 (WECC_URE5) | NCRXXXXX | WECC2013012300 | CIP-009-3 | R4 | WECC conducted an on-site compliance audit of WECC_URE5. During the course of the audit, the WECC Audit Team determined that WECC_URE5 had an issue with CIP-009-3 R4. Although WECC_URE5 has backups required to successfully restore Critical Cyber Assets, WECC_URE5 failed to provide process or procedures explaining and where backups are created and stored as part of its recovery plans for Critical Cyber Assets associated with two (2) Critical Assets. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although WECC_URE5 recovery plans for these two facilities did not include specific processes, WECC_URE5 maintained general processes for backup and information storage. WECC_URE5 provided evidence demonstrating that is has backups required to successfully restore Critical Cyber Assets at both locations. | To mitigate this issue, WECC_URE5 updated recovery plans to include processes used to backup and store information required for the restoration of Critical Cyber Assets.
2013-08-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 6 (WECC_URE6) | NCRXXXXX | WECC2012010754 | CIP-002-3 | R4 | WECC_URE6 submitted a Self-Report to WECC stating that it had an issue with CIP-002-3 R4. WECC_URE6 submitted its Self-Certification reporting the same issue. Although WECC_URE6 self-reported this violation, because WECC_URE6 self-reported during the Self-Certification submission period, the discovery method for this violation is classified as Self-Certification. Specifically, WECC_URE6 failed to annually review and approve one of two of its Critical Cyber Asset Lists for its Energy Management System (EMS) and Distribution Control System (DCS). WECC_URE6 had created the lists, but they were not always included in the annual review cycle of CIP documents required for sign-off by senior management. Both lists were reviewed and signed in 2010; the list for EMS equipment was reviewed and signed in 2011; but the list for DCS equipment had not been reviewed and signed in 2011. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE6 did apply a risk-based assessment methodology to identify Critical Assets and create an associated list of Critical Cyber Assets. As additional compensating measures, WECC_URE6 affirms that all CCAs reside within an identified ESP and PSP; have active monitoring and logging; and implement AV/Malware Prevention tools. Further, WECC_URE6’s senior manager reviewed and approved the list in 2010 and in 2012. In addition, all individuals with access to the devices have updated personal risk assessments and training. | To mitigate this issue, WECC_URE6 submitted a 2012 Critical Cyber Asset List signed by its senior management. WECC has verified the completion of all mitigation activity.
2013-07-31 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2013012145 | CIP-002-1 | R1; R.1.1 | During a Compliance Audit, MRO discovered MRO_URE1 failed to adequately document its risk-based assessment methodology (RBAM) for assessment of criticality of Bulk Electric System assets. MRO_URE1 provided several studies as evidence of an assessment, but did not document a methodology. In its RBAM, MRO_URE1 described why its assets were not critical, but did not include a defined set of evaluation criteria defining the assessment process pursuant to CIP-002-1 R1.1. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. MRO_URE1's failure to comply with CIP-002-1 R1 was related to a lack of clear documentation and was unrelated to performance. After separating the methodology, which is the RBAM, from the assessment, which is the excercise of the RBAM, and creating two distinct documents, MRO_URE1 still had no critical assets. | To mitigate this issue, MRO_URE1 created two distinct documents separating the methodology from the assessment. MRO_URE1 now has a separate, independent, and repeatable process to assess assets for criticality in place pursuant to CIP-002-1 R1. Under its new process, MRO_URE1 concluded it continued to have no critical assets.
2013-07-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2012011571 | CIP-006-3c | R4 | RFC_URE1 submitted a Self-Report to RF that, it had an issue with CIP-006-3c R4 because RFC_URE1 failed to implement operational and procedural controls to manage physical access at an access point to the Physical Security Perimeter. At its generating facility, RFC_URE1 undertook a construction project that included permanently bricking up certain windows. RFC_URE1 unlocked a padlocked window to a conference room and broke off the device that permanently sealed the window, creating an access point to the Physical Security Perimeter. While the project manager committed to provide access control, there were times throughout the day when the project manager was not controlling access through this access point, as required by CIP-006-3c R4. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Multiple employees were working outside of the conference room where the window was open. Anyone attempting to gain access through this window would have walked past these employees to access any Cyber Assets. RFC_URE1 uses the Cyber Assets within the accessible portion of the building to monitor the Supervisory Control and Data Acquisition system, and all workstations are locked down when employees are not using them. In addition, the employees working outside the conference room all had authorized unescorted physical access to the Physical Security Perimeter. Access to any part of the facility requires authorization through an identification badge. The facility has closed circuit cameras monitored by security personnel. In addition to card readers that authorize access into the building, some specific areas of the facility have additional card readers to prevent unauthorized access. | To mitigate this issue, RFC_URE1: 1) closed the opening in the Physical Security Perimeter; 2) modified its procedures to incorporate additional examples of access points that it may need to monitor; and 3) trained all relevant management personnel on physical security changes and modifications awareness. RF has verified the completion of all mitigation activity.
2013-07-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2012011572 | CIP-006-3c | R5 | RFC_URE1 submitted a Self-Report to RF that, it had an issue with CIP-006-3c R5 because RFC_URE1 failed to implement technical and procedural controls for monitoring physical access at an access point to the Physical Security Perimeter. At its generating facility, RFC_URE1 undertook a construction project that included permanently bricking up certain windows. RFC_URE1 unlocked a padlocked window to a conference room and broke off the device that permanently sealed the window, creating an access point to the Physical Security Perimeter. While the project manager committed to provide access control, there were times throughout the day when the project manager was not monitoring access through this access point, as required by CIP-006-3c R5. RFC_URE1 submitted a Self-Report to RF identifying an additional issue of CIP-006-3c R5. Due to a planned power outage, a security officer was monitoring an access point to the Physical Security Perimeter. After testing two other access points, the security officer thought the electronic monitoring of the access point was functioning, so the security officer stopped monitoring that access point. RFC_URE1 later determined that access point was not functioning. As a result, RFC_URE1 failed to monitor an access point to the Physical Security Perimeter for one hour and 18 minutes. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Regarding the issue related to the construction project multiple employees were working outside of the conference room where the window was open. Anyone attempting to gain access through this window would have walked past these employees to access any Cyber Assets. RFC_URE1 uses the Cyber Assets within the accessible portion of the building to monitor the Supervisory Control and Data Acquisition system, and all workstations are locked down when employees are not using them. In addition, the employees working outside the conference room all had authorized unescorted physical access to the Physical Security Perimeter. Access to any part of the facility requires authorization through an identification badge. The facility has closed circuit cameras monitored by security personnel. In addition to card readers that authorize access into the building, some specific areas of the facility have additional card readers to prevent unauthorized access. Regarding the issue related to the planned poweroutage, when the system loses power, the card reader is programmed to “fail safe,” meaning the only way the access point is only accessible by using an emergency key. RFC_URE1 issues the emergency keys in accordance with its key control policy and its corporate security procedures. | To mitigate this issue, RFC_URE1: 1) closed the opening in the Physical Security Perimeter; 2) modified its procedures to incorporate additional examples of access points that it may need to monitor; and 3) trained all relevant management personnel on physical security changes and modifications awareness. RF has verified the completion of all mitigation activity. To mitigate the issue related to RFC_URE1's failure to monitor the Physical Security Perimeter. RFC_URE1: 1) closed the opening in the Physical Security Perimeter; and 2) revised procedures for human monitoring of physical access points during testing. The security officers at issue reviewed the procedure.
2013-07-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2012011573 | CIP-006-3c | R6 | RFC_URE1 a Self-Report to RF that, it had an issue with CIP-006-3c R6 because RFC_URE1 failed to log physical entry at this access point, as required by CIP-006-3c R6. At its generating facility, RFC_URE1 undertook a construction project that included permanently bricking up certain windows. RFC_URE1 unlocked a padlocked window to a conference room and broke off the device that permanently sealed the window, creating an access point to the Physical Security Perimeter. While the project manager committed to provide access control, there were times throughout the day when the project manager was not logging physical entry at this access point, as required by CIP-006-3c R6. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Multiple employees were working outside of the conference room where the window was open. Anyone attempting to gain access through this window would have walked past these employees to access any Cyber Assets. RFC_URE1 uses the Cyber Assets within the accessible portion of the building to monitor the Supervisory Control and Data Acquisition system, and all workstations are locked down when employees are not using them. In addition, the employees working outside the conference room all had authorized unescorted physical access to the Physical Security Perimeter. Access to any part of the facility requires authorization through an identification badge. The facility has closed circuit cameras monitored by security personnel. In addition to card readers that authorize access into the building, some specific areas of the facility have additional card readers to prevent unauthorized access. | To mitigate this issue, RFC_URE1: 1) closed the opening in the Physical Security Perimeter; 2) modified its procedures to incorporate additional examples of access points that it may need to monitor; and 3) trained all relevant management personnel on physical security changes and modifications awareness. RF has verified the completion of all mitigation activity.
2013-07-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2013012115 | CIP-009-1 | R1 | RF conducted a compliance audit of RFC_URE1. During this Compliance Audit, RF discovered that RFC_URE1 had an issue with CIP-009-3 R1 because RFC_URE1 failed to have a recovery plan in place that specifies the required actions in response to events or conditions of varying duration and severity that would activate the recovery plan and defines the roles and responsibilities of responders. For two years, RFC_URE1 had in place a recovery plan for Critical Cyber Assets at its generating plant that minimally addressed the requirements of CIP-009-1. That plan, however, did not constitute a complete recovery plan. For example, the recovery plan did not specify how to recover specific Critical Cyber Asset device types. Although the recovery plan discussed system backups, system restoration, and configuration management, RFC_URE1 failed to address in detail how those areas were part of the recovery plan. In addition, the recovery plan contained a section referring to maintenance of spare parts but did not address how RFC_URE1 would utilize these spare parts in the recovery. In addition, the recovery plan addressed certain events where RFC_URE1 would use the recovery plan but did not address the severity or duration required to trigger its implementation. As a result, the recovery plan did not adequately specify required actions in response to events or conditions of varying duration and severity that would activate the recovery plan, as required by CIP-009-3 R1.1. The recovery plan had a short section regarding roles and responsibilities that addressed roles but not those individuals that would be responsible for those roles, and as a result, it did not adequately define the roles and responsibilities of responders, as required by CIP-009-3 R1.2. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. During the Compliance Audit interviews, RF determined that RFC_URE1 personnel had the knowledge and expertise to have properly recovered the generating plant Critical Cyber Assets during an incident. | To mitigate this issue, RFC_URE1 revised recovery plans for the Critical Cyber Assets. RF has verified the completion of all mitigation activity.
2013-07-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2012011212 | CIP-002-3 | R2 | RFC_URE2 submitted a Self-Report to RF (RFC_URE2 submitted this self-report within 90 days of a previously scheduled compliance audit. However, RF determined that without this self-report, the issue would have likely been missed during the compliance audit) that, it had an issue with CIP-002-3 R2 because RFC_URE2 discovered that had not applied its RBAM for a particular year to determine if two generating units located outside RFC_URE2's parent company's transmission footprint. RFC_URE2 determined that the RBAM that emerged from the consolidation of RFC_URE2's separate CIP programs into a single consolidated CIP Program did not require the assessment of RFC_URE2's parent company-owned generating units outside RFC_URE2's parent company's transmission footprint. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. This issue is a documentation issue. It is a documentation issue because the generating units at issue are non-Critical Assets. Further, application of RFC_URE2’s RBAM from the year prior to the RBAM from the year at issue, which RFC_URE2 conducted prior to the issue and considered the two affected generating units, determined the units are not Critical Assets. Additionally, following the discovery of the issue, RFC_URE2 subjected the generating units to its RBAM for the affected year and confirmed that the generating units are non-Critical Assets. Finally, the generating units do not participate in system restoration. | To mitigate this issue, RFC_URE2 : 1) evaluated the two affected generating units consistent with its 2012 RBAM and determined they are non-Critical Assets; and 2) committed to change its RBAM to include all RFC_URE2 owned generation outside the RFC_URE2's parent company's transmission system footprint.
2013-07-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2012011258 | CIP-002-3 | R4 | RF conducted a compliance audit of RFC_URE2. During this Compliance Audit, RF discovered that RFC_URE2 had an issue with CIP-002-3 R4 because it could not provide evidence of approval by a senior manager or delegate of its RBAM for a specific year. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. This issue is a documentation issue. It is a documentation issue because RFC_URE2 presented evidence that a senior manager had reviewed and approved the RBAM for the year at issue, but neglected sign and date it following that review. This evidence RFC_URE2 provided included RFC_URE2’s approved Critical Asset and CCA list for the following year, both of which are based on the RBAM. RFC_URE2 also provided evidence that the senior manager approved the RBAMs, Critical Asset lists and CCA lists for all other RFC_URE2 affiliated Registered Entities for the following year. | To mitigate this issue, RFC_URE2: 1) consolidated its individual CIP procedures into a single CIP program. RFC_URE2’s consolidated CIP program includes a new process to help ensure senior manager approves the RBAM at least annually; and 2) provided evidence that its CIP senior manager approved its RBAM the year following the one at issue.
2013-07-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC2013012504 | CIP-005-2 | R1 | RF conducted a Compliance Audit of RFC_URE3. During this Compliance Audit, RF discovered that RFC_URE3 had an issue with CIP-005-2 R1 because it failed to adequately maintain documentation of all Cyber Assets deployed for the access control and monitoring of access points to the Electronic Security Perimeter. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. This was solely a documentation issue. Although the onsite Compliance Audit revealed that RFC_URE3 provided the multi-factor authentication appliance with the required security controls that are needed for electronic access and log and monitoring devices, RFC_URE3 did not document as such within its Cyber Asset Lists and/or network diagrams. | To mitigate this issue, RFC_URE3: 1) updated the diagrams for its control centers to document the multi-factor authentication appliances as devices engaged in the access control and monitoring of access points to the Electronic Security Perimeter; and 2) updated its Cyber Asset Lists for its control centers to include the missing devices.
2013-07-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC2013012506 | CIP-006-2a | R1; and R1.6 | RF conducted a compliance audit of RFC_URE3. During this Compliance Audit, RF discovered that RFC_URE3 had an issue with CIP-006-2a R1 because it failed to adequately document, implement, and maintain a physical security plan that addresses the inclusion of the Electronic Security Perimeter’s Cyber Assets within an identified Physical Security Perimeter and the proper maintenance of the visitor control program. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. RFC_URE3 has defense in depth in place at both the PCC and the BCC which layers various defense mechanisms in a way that discourages or prevents cyber intrusion. Specifically, RFC_URE3 has a guard stationed during business hours at the entrance to each location and visitors must sign in and be escorted in order to gain access to each building. All RFC_URE3 Physical Security Perimeters are located exclusively within RFC_URE3 buildings, rather than other commercial real estate locations containing other businesses and non-RFC_URE3 personnel. RFC_URE3’s Physical Security Perimeters are each locked and enclosed in six-wall borders. Furthermore, RFC_URE3 requires the use of access badges to access the elevators and stairs leading to RFC_URE3’s control centers. In addition to the mitigating evidence regarding RFC_URE3’s defense in depth, RF considered the fact that the issue of CIP-006-2a R1.6 was solely a documentation error related to missing exit times and dates in the visitor logs. | To mitigate this issue, RFC_URE3 commissioned contractors and internal staff to remediate all breaches in the Control Center and to enclose the implicated Supervisory Control and Data Acquisition ("SCADA”) cables within conduit. RFC_URE3 presented pictures of the repairs to the Compliance Audit team to evidence its completion of the remediation efforts.
2013-07-31 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP201100646 | CIP-009-1 | R3 | SPPRE_URE1 self-reported to SPP RE an issue with CIP-009-1 R3 because it did not update its recovery plan to reflect changes or lessons learned as a result of an exercise of the plan, nor had it communicated these updates to personnel responsible for activating and implementing the recovery plan. Specifically, SPPRE_URE1 performed a disaster planning table top exercise, and recorded a list of possible changes as a result of this exercise; however, it did not update its recovery plan to include the changes noted from the disaster recovery tabletop exercise, nor did it communicate the changes to appropriate personnel within 90 days. | SPP RE determined that the issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SPPRE_URE1 had a recovery plan in place at the time of this issue that was well-defined. Furthermore, SPPRE_URE1 acknowledged that the changes stemming from the exercise were to stream-lining the recovery process rather than material corrections to the process. Finally, SPPRE_URE1 conducted a subsequent disaster recovery exercise, in which SPPRE_URE1 did not have any new changes to make to its recovery plan. | To mitigate this issue, SPPRE_URE1 developed and implemented new procedures to document lessons learned and track and communicate updates and changes to the recovery plan as a result of any lessons learned. SPP RE has verified the completion of all mitigation activity.
2013-07-31 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2011008245 | CIP-003-1 | R4; R4.2, R4.3 | SPPRE_URE1 self-reported to SPP RE that it had an issue with CIP-003-1 R4.3 because it could not demonstrate that it had annually assessed adherence to its critical cyber asset information protection program, documented any assessment results, or implemented action plans to remediate deficiencies identified during any assessments for two years. During a subsequent audit, SPP RE discovered an issue with CIP-003-3 R4.2. because some of SPPRE_URE1’s documents associated with critical cyber assets were not classified in accordance with its critical cyber asset information protection program. Because the self-report and audit findings were closely related and implicate the same Standard and Requirement, SPP RE consolidated the two findings. | SPP RE determined that the issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SPPRE_URE1 had implemented a documented program to identify, classify, and protect information associated with critical cyber assets. Although some confidential documents associated with critical cyber assets were not properly classified, SPPRE_URE1 attested that at no time was there any misuse of the documents. Furthermore, the documents which were incorrectly classified were provided proper protection in accordance with SPPRE_URE1’s critical cyber asset information protection program. Hard copies were secured in locked file cabinets within SPPRE_URE1’s Physical Security Perimeter and electronic copies were stored on restricted access drives. | To mitigate this issue, SPPRE_URE1: 1) Reassessed and modified its critical cyber asset information protection program and documentation to ensure compliance with all the requirements specified in CIP-003-1 R4; and 2) Correctly classified the documents that had been mislabeled or unlabeled. SPP RE has verified the completion of all mitigation activity.
2013-07-31 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPPRE_URE2) | NCRXXXXX | SPP2013012352 | CIP-006-3c | R5 | During an SPP RE CIP Compliance audit of SPP_URE2, SPP RE discovered a possible issue with CIP-006-3c R5 because SPP_URE2 disabled controls for monitoring physical access at two physical access points to its Physical Security Perimeter (PSP), and thus physical access to the PSP could not be monitored twenty-four hours a day, seven days a week per CIP-006-3c R5. | SPP RE determined that this issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although alarming would not occur for forced or held open doors at two physical access points to SPP_URE2’s PSP, normal entering and exiting the PSP was still logged by the Physical Access Control System. In addition, the PSP is manned twenty-four hours a day, seven days a week. Therefore, if an intruder had gained access to the secured area, an operator in the PSP most likely would have observed the intruder. Furthermore, the PSP was within a building that had controlled access points, reducing the risk of unauthorized personnel gaining access to SPP_URE2’s PSP. Finally, the duration of this issue was four months, and SPP_URE2 reviewed its physical access logs and confirmed that no unauthorized attempts occurred during that time. | To mitigate this issue, SPP_URE2: 1) Re-enabled the alarms to the affected access points; and 2) Updated its Physical Security Plan to require testing of all impacted equipment following any maintenance actions. SPP RE has verified the completion of all mitigation activity.
2013-07-31 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 3 (SPPRE_URE3) | NCRXXXXX | SPP2013012461 | CIP-002-3 | R4 | During an SPP RE CIP audit of SPP_URE3, the SPP RE audit team identified an issue with CIP-002-3 R4. Specifically, the audit team determined that SPP_URE3’s Senior Manager had not signed, nor dated, an annual approval of SPP_URE3's risk-based assessment methodology (RBAM). | SPP RE determined that the issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although the RBAM was not approved by SPP_URE3’s Senior Manager or documented delegate(s), it was approved by an officer of the company. The Senior Manager did, however, approve the Critical Asset and the Critical Cyber Asset lists in accordance with CIP-003-2 R2 and R3, both of which are null because SPP_URE3 does not own any such assets. Additionally, the audit team determined that SPP_URE3 had a CIP-002-3-compliant RBAM. | To mitigate this issue, SPP_URE3: 1) Provided its senior manager’s review of its RBAM; and 2) Revised its CIP-002-3 procedure to include language for senior manager’s annual review and sign off of SPP_URE3's RBAM. SPP RE has verified the completion of all mitigation activity.
2013-07-31 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 4 (SPPRE_URE4) | NCRXXXXX | SPP2012009974 | CIP-007-1 | R2; R2.1 | SPP_URE4 submitted a self report to SPP RE stating that it had an issue with CIP-007-1 R2.1 because it was unable to ensure that only those ports required for normal and emergency operations were enabled. Although SPP_URE4 had a documented ports and services process in place, its ports and services baseline did not identify ephemeral port ranges for enabled services needed for normal and emergency operations. Without port ranges, SPP_URE4 was unable to identify all ports that could be associated with each enabled service. As a result, SPP_URE4 was unable to ensure that each enabled port associated with a particular enabled service identified in its periodic ports and services scans was the necessary port to run the associated service. | The issue posed a minimal and not a serious or substantial risk to the reliability of the Bulk Power System (BPS). The risk to the BPS was mitigated because SPP_URE4 had CIP-007 systems security management policies and procedures in place. For instance, before and after installing new cyber assets and significant changes to existing cyber assets within the ESP, SPP_URE4 tested the affected cyber assets by running ports and services scans to ensure they did not adversely affect existing cyber security controls. In doing so, SPP_URE4 compared the scans with its ports and services baseline, assessed and tested any inconsistencies for legitimacy, and maintained a “library” of approved ports for specific services. Thus, although SPP_URE4 was unable to ensure that these approved enabled ports were the only ports required to enable the associated services due to the lack of port ranges in its baseline, it did routinely assess and test enabled ports and services and verify that cyber security controls were effective in minimizing the risk of malicious threats to the cyber assets located within its ESP. SPP_URE4 also uses a network intrusion detection and prevention system to analyze network traffic for known and suspect malicious activity, which includes potential threats affecting ports and services. Moreover, SPP_URE4’s ESP firewalls are specifically configured to only allow traffic using specific protocols to enter the network, which prevents unsolicited traffic from passing into the ESP. SPP_URE4 attested that there were no security alerts or cyber attacks during the violation duration. | To mitigate this issue and to prevent reoccurrence, SPP_URE4 implemented a new ports and services program. The program supplements the pre-existing ports and services procedure and clearly defines each affected personnel’s roles and responsibilities for compliance with the applicable standard. The program also requires port ranges to be included in SPP_URE4’s ports and services baseline. SPP_URE4 revised its ports and services baseline to include port ranges. SPP_URE4 now is able to compare its periodic ports and services scans and ensure that only those ports and services required for normal and emergency operations are enabled. SPP RE has verified the completion of all mitigation activity. SPP RE has verified the completion of all mitigation activity.
2013-07-31 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 4 (SPPRE_URE4) | NCRXXXXX | SPP2012010283 | CIP-005-1 | R2; R2.2 | During a compliance audit, SPP RE determined that SPP_URE4 had an issue with CIP-005-1 R2.2 because one electronic access control system (EACS) firewall, serving as an access point to the ESP, enabled ports and services that were not documented in SPP_URE4’s ports and services baseline. As a result, SPP_URE4 was unable to ensure that only ports and services required for operations and for monitoring cyber assets within its Electronic Security Perimeter (ESP) were enabled. | SPP RE has determined that SPP_URE4’s issue of noncompliance posed a minimal and not a serious or substantial risk to the reliability of the Bulk Power System (BPS). The risk to the BPS was mitigated because SPP_URE4 had CIP-005 cyber security policies and procedures in place, including maintaining the EACS firewall and protecting it with implemented electronic monitoring and assess controls. Additionally, SPP_URE4 uses a network intrusion detection and prevention system to analyze network traffic for known and suspect malicious activity, which includes potential threats affecting ports and services. Moreover, SPP_URE4’s ESP firewalls are specifically configured to only allow traffic using specific protocols to enter the network, which prevents unsolicited traffic from passing into the ESP. SPP_URE4 attested that there were no security alerts or cyber attacks during the violation duration. | To mitigate its violation of CIP-006-1 R2 and to prevent reoccurrence, SPP_URE4: 1) Developed and implemented a Ports and Services Program, which provides guidance to affected staff in managing and complying with the ports and services requirements in the NERC CIP Standard CIP-005 R2.2 and CIP-007 R2; and 2) Updated its ports and services baseline document to include the port (or range of ports), associated service, and the business justification for the open port and service. SPP RE has verified this mitigation as completed.
2013-07-31 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE2012010931 | CIP-002-1 | R4 | During a Compliance Audit, Texas RE concluded that TRE_URE1 had an issue with CIP-002-1 R4 because TRE_URE1 did not include a signed “null” Critical Cyber Asset list based on its “null” Critical Asset list developed in R2. Specifically, Texas RE determined that TRE_URE1 developed a Risk Based Assessment Methodology (RBAM) and a list of Critical Assets (CAs) identified through application of its RBAM, but failed to provide evidence that it developed a corresponding list of Critical Cyber Assets (CCAs). As a result, TRE_URE1 had an issue with CIP-002-1 R4 from the date the requirement became enforceable for TRE_URE1 to the date TRE_URE1 developed its null list of CCAs. | Texas RE determined the issue posed a minimal risk and not a serious or substantial risk to the bulk power system because no CA/CCAs were identified. Because TRE_URE1’s list of CAs was null throughout the duration period, TRE_URE1 would also have developed a null list of CCAs. Following the Audit, TRE_URE1 determined that it does not currently and did not previously have any CCAs, confirming that these lists are also null. | To mitigate this issue, TRE_URE1: 1) re-performed its RBAM; 2) developed a null list of both CAs and CCAs; and 3) retroactively identified null lists of CCAs for the previous years where documentation was lacking. To prevent re-occurrence, TRE_URE1 hired a new Manager of Reliability Compliance to oversee the development and maintenance of the CIP program. TRE_URE1 contracted with a third-party consultant to improve its existing CIP program. TRE_URE1 instituted new policies to ensure that the RBAM and CA/CCA lists are reviewed. TRE_URE1 purchased new software to help track, alert, and archive these documents. TRE has verified the completion of all mitigation activity.
2013-07-31 | TRE_URE1liability Entity (TRE_URE1) | Unidentified Registered Entity 2 (TRE_URE2) | NCRXXXXX | TRE2012010660 | CIP-002-2 | R2 | During a Compliance Audit, TRE_URE1 determined that TRE_URE2 had an issue with CIP-002-1 R2. Specifically, TRE_URE2 was unable to provide evidence that it developed its CA/CCA list through an annual application of its Risk Based Assessment Methodology (RBAM). TRE_URE2 provided documentation of application of its RBAM for the prior year. TRE_URE2 did have its list of Critical Assets, however, TRE_URE2 could not demonstrate that it had developed the list by applying its RBAM. TRE_URE2 had an issue with CIP-002-2 R2 for approximately one year. | This issue posed a minimal risk and did not pose a serious or substantial risk to the bulk power system because TRE_URE2 did have an active RBAM in place, and had developed null CA/CCA lists. TRE_URE2 has attested that the CA/CCA lists were developed through application of this RBAM, but were unable to provide documentation of this process. Furthermore, in both the prior RBAM and when the RBAM was performed the following year, the processes were properly documented and the CA/CCA lists remained null. This indicates that before, throughout, and after the duration period, TRE_URE2 was operating with correct (null) CA/CCA lists. | To mitigate this issue, TRE_URE2: 1) Created a new Risk Based Assessment Methodology 2) Provided evidence that its CA/CCA lists were developed through application of this RBAM TRE_URE1 has verified the completion of all mitigation activity.
2013-07-31 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 3 (TRE_URE3) | NCRXXXXX | TRE2012011154 | CIP-004-3 | R4.1 | TRE_URE3 submitted a self-certification to Texas RE stating it had an issue with CIP-004-3 R4.1. Specifically, TRE_URE3 revoked authorized cyber access to certain Critical Cyber Assets (CCAs) for three employees, but did not timely update its personnel list including specific electronic and physical access rights to CCAs within seven calendar days. TRE_URE3 had an issue with CIP-004-3 R4.1 from the seventh day following access revocation until the date TRE_URE3 when the personnel list was updated. | This issue posed a minimal risk and did not pose a serious or substantial risk to the bulk power system because: a) authorized cyber access was revoked and the three individuals did not have physical access to the CCAs, thus no access was possible, b) the duration period was – one month, c) no adverse consequences were experienced, and d) the issue affected a small percentage of employees. Three of 155 employees with authorized access to cyber assets within the ESP were impacted, representing 1.9% of the total. | To mitigate this issue, TRE_URE3 updated the personnel list to reflect revocation of access rights for the three employees. Texas RE has verified the completion of all mitigation activity.
2013-07-31 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 3 (TRE_URE3) | NCRXXXXX | TRE2012011186 | CIP-009-3 | R2 | TRE_URE3 submitted a self-certification to Texas RE stating it had an issue with CIP-009-3 R2. Specifically, TRE_URE3 failed to timely perform an annual exercise of its Critical Cyber Asset recovery plan. TRE_URE3 had an issue with CIP-009-3 R2 from the day after the deadline for performing an annual exercise until the date when TRE_URE3 performed the annual exercise. | This issue posed a minimal risk and did not pose a serious or substantial risk to the bulk power system because: a) the duration period was brief – approximately three months, b) the last exercise was performed 17 months prior, which is well within the nearly two year maximum timeframe limit contained in Compliance Application Notice (CAN) 0010 – Implementation of Annual in Reliability Standards Requirements (Revised), c) there were no substantive changes to the Critical Cyber Asset recovery plan, and d) affected personnel were aware of and familiar with the recovery procedures. | To mitigate this issue, TRE_URE3 exercised its recovery plan. Texas RE has verified the completion of all mitigation activity.
2013-07-31 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 4 (TRE_URE4) | NCRXXXXX | TRE2012011002 | CIP-004-3 | R4.2 | TRE_URE4 submitted a self-report to Texas RE stating that it had an issue with CIP-004-3 R4.2. Specifically, an IT Service Desk contractor's NERC CIP access was not revoked within the required seven days following a voluntary termination. Seventeen days after the contractor’s last day, the IT Business Management team discovered that the contractor was still showing as active and initiated the process to have access revoked. TRE_URE4 had an issue with CIP-004-3 R4.2 from the seventh day after the contractor’s last day of employment until the day TRE_URE4 revoked access. | This issue posed a minimal risk and did not pose a serious or substantial risk to reliability of the bulk power system (BPS). The risk was mitigated by the following factors: a) TRE_URE4 discovered this issue due to its internal controls when it performed its routine quarterly reviews of employees and contract employees, b) TRE_URE4 revoked access almost immediately after discovering it had not revoked access, c) TRE_URE4 discovered the issue less than two weeks after access revocation was required, d) the contractor was not terminated for cause and resigned, and e) the contractor no longer had their physical access badge, reducing the likelihood that he could have gained access to the Physical Security Perimeter. | To mitigate the issue, TRE_URE4: 1) revoked the individual's access rights; 2) identified, developed, and made available awareness and training for managers who have NERC CIP contractors or employees; 3) sent a letter to managers summarizing termination responsibilities; 4) developed a pending revocation report to show all outstanding electronic access revocation requests; and 5) made appropriate clarifications on the form utilized to begin the process of terminating an individual’s electronic access. Texas RE has verified the completion of all mitigation activity.
2013-07-31 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 4 (TRE_URE4) | NCRXXXXX | TRE2012010780 | CIP-006-1 | R1 | TRE_URE4 submitted a self-report to Texas RE stating that it had an issue with CIP-006-1 R1. Specifically, TRE_URE4 was unable to provide evidence that the physical security plan of TRE_URE4’s parent company had been approved by TRE_URE4’s CIP senior manager for the period that the requirement became enforceable for TRE_URE4 through the date that TRE_URE4 management reviewed and approved the parent company’s physical security plan. TRE_URE4 was also unable to provide evidence that it had reviewed and approved the physical security plan the following year through the date that TRE_URE4’s management reviewed and approved the following revision of its parent company’s physical security plan. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because the issue related to the failure to obtain the required signature and did not change the development or implementation of the physical security plan. Throughout the duration period, the parent company implemented TRE_URE4’s NERC compliance. The physical security plans that were in place were reviewed and approved by the parent company’s management, and the failure to approve by TRE_URE4’s management was due to an oversight. This implies that the physical security plans that were in place have been acceptable throughout the duration period. TRE_URE4 has not noted any problems or effects due to the lack of approval by the senior manager. | To mitigate this issue, TRE_URE4: 1) in both instances, had the senior manager review and approve the most current version of its parent company’s physical security plan at the time; and 2) as of the more recent instance, created a new workflow that ensures that TRE_URE4’s management reviews and approves the parent company’s CIP-related documents. Texas RE has verified the completion of all mitigation activity.
2013-07-31 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 5 (TRE_URE5) | NCRXXXXX | TRE2012010416 | CIP-004-3 | R3.3 | TRE_URE5 submitted a self-report citing an issue with CIP-004-3 R3.3. Specifically, TRE_URE5 failed to retain evidence that background checks were completed on four (4) employees prior to employment. Once the issue was discovered, TRE_URE5 requested its service provider perform new background checks on the four (4) employees. TRE_URE5 had an issue with CIP-004-3 R3.3 from the date the requirement became enforceable for TRE_URE5 until the date TRE_URE5 received the results of the new background checks. | Texas RE determined the issue posed a minimal risk and did not pose a serious or substantial risk to the bulk power system. Although, TRE_URE5 did not retain the results of four background checks for its current employees, TRE_URE5 did in fact have documents on file to substantiate its policy that new employees must pass a background check prior to employment. All missing background checks were obtained the same month the missing documents were discovered. TRE_URE5 provided an attestation stating that full criminal background checks were completed on the four individuals in accordance with its Background Checks and Employment Eligibility Policy. In addition, all four individuals successfully passed the background checks. | To mitigate this issue, TRE_URE5: 1) completed new background checks on the four employees; and 2) reviewed its Human Resources procedures to ensure that the appropriate evidence will be maintained on all future background checks. Additionally, the procedures were updated to state that all background checks shall be renewed at least once every seven years. Texas RE has verified the completion of all mitigation activity.
2013-07-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2013012330 | CIP-005-3a | R1.5 | WECC_URE1 submitted a Self-Certification to WECC stating that had an issue with CIP-009-3 R5. Specifically, WECC_URE1 reported that it failed to perform annual testing of backup media associated with Cyber Assets that are used in the access control and/or monitoring of the Electronic Security Perimeter (“ESP”), Cyber Assets that authorize and/ or log access to the Physical Security Perimeter (“PSP”), and Critical Cyber Assets. Since the Self-Certification included Cyber Assets that are used in the access control and/or monitoring of the ESP, WECC determined CIP-009 did not apply, but that these devices are within the scope of CIP-005-3a R1.5. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE1 had a number of compensating measures in place to secure the device against misuse or malicious attack. Specifically, all Critical Cyber Assets reside within an identified PSP and are protected from un-authorized access through the use of a card key access control system configured to restrict access to personnel who are trained, vetted, and authorized for such access. Additionally all devices are logically protected from unauthorized access by residing within an identified ESP where all logical access is restricted, logged, and monitored by restrictive boundary devices. Specifically, the Critical Assets that this Critical Cyber Asset is associated with has a manual capability that could be activated if Critical Cyber Assets are unable to be recovered. | To mitigate this issue, WECC_URE1 tested its backup media in calendar year 2013.
2013-07-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2013012331 | CIP-006-3c | R2.2 | WECC_URE1 submitted a Self-Certification to WECC stating that WECC_URE1 had an issue with CIP-009-3 R5. WECC_URE1 reported that it failed to perform annual testing of backup media because WECC_URE1 reassigned personnel to this task, and that led to a miscommunication which resulted in missing the deadline. Specifically, WECC_URE1 reported that it failed to perform annual testing of backup media associated with Cyber Assets that are used in the access control and/or monitoring of the ESP, Cyber Assets that authorize and/ or log access to the PSP, and Critical Cyber Assets. Since the Self-Certification included Cyber Assets that authorize and/ or log access to the PSP, a WECC determined CIP-009 did not apply, but that these devices are within the scope of CIP-006-3c R2.2. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE1 had a number of compensating measures in place to secure the devices against misuse or malicious attack. Specifically, all Critical Cyber Assets reside within an identified PSP and are protected from un-authorized access through the use of a card key access control system configured to restrict access to personnel who are trained, vetted, and authorized for such access. Additionally all devices are logically protected from unauthorized access by residing within an identified ESP where all logical access is restricted, logged, and monitored by restrictive boundary devices. Specifically, the Critical Assets that these Critical Cyber Assets were associated with have a manual capability that could be activated if Critical Cyber Assets are unable to be recovered. | To mitigate this issue, WECC_URE1 tested its backup media in calendar year 2013.
2013-07-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2013012057 | CIP-009-3 | R5 | WECC_URE1 submitted a Self-Certification to WECC stating that WECC_URE1 had an issue with CIP-009-3 R5. Specifically, WECC_URE1 reported that it failed to perform annual testing of backup media because WECC_URE1 had reassigned personnel to this task, and that led to a miscommunication which resulted in missing the deadline. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE1 had a number of compensating measures in place to secure the devices against misuse or malicious attack. Specifically, all Critical Cyber Assets reside within an identified PSP and are protected from un-authorized access through the use of a card key access control system configured to restrict access to personnel who are trained, vetted, and authorized for such access. Additionally all devices are logically protected from unauthorized access by residing within an identified ESP where all logical access is restricted, logged, and monitored by restrictive boundary devices. Additionally, the Critical Assets that these Critical Cyber Assets were associated with have a manual capability that could be activated if Critical Cyber Assets are unable to be recovered. | To mitigate this issue, WECC_URE1 tested its backup media in calendar year 2013.
2013-07-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2013011810 | CIP-004-3 | R2 | WECC_URE2 submitted a Self-Report to WECC stating that it had an issue with CIP-004-3 R2. Specifically, WECC_URE2 reported that an employee was granted physical access to Critical Cyber Assets prior to completing cyber security training as required by CIP-004-3 R2.1. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although WECC_URE2 inadvertently granted physical access to one Physical Security Perimeter (PSP), the employee in scope did not have logical access to the workstations. Without logical access to the assets, the employee could not log onto or access the workstations. Because the PSP is monitored (video and security) twenty four hours a day, seven days a week, any suspicious or malicious activity inside the PSP or a potential security compromise to the assets would be noticed and stopped immediately. Further, the employee has been employed with WECC_URE2 for over two years. This employee is in good standing and has computer and operational training completed for WECC_URE2's assets. Finally, Corporate Security confirmed that the employee did not access the PSP. | To mitigate this issue, WECC_URE2: 1) immediately revoked access to the one employee and performed an internal review of employee access rights; and 2) enhanced its access controls by implementing a procedure which no longer allows dual membership in the two approval groups for physical and cyber assets.
2013-07-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2013012328 | CIP-005-3a | R1.5 | WECC_URE3 submitted a Self-Certification to WECC stating that WECC_URE3 had an issue with CIP-009-3 R5. Specifically, WECC_URE3 reported that it failed to perform annual testing of backup media associated with Cyber Assets that are used in the access control and/or monitoring of the Electronic Security Perimeter (“ESP”), Cyber Assets that authorize and/ or log access to the Physical Security Perimeter (“PSP”), and Critical Cyber Assets, a WECC SME determined CIP-009 did not apply, but that these devices are within the scope of CIP-005-3a R1.5. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. There were a number of compensating measures in place to secure the devices against misuse or malicious attack. Specifically, all Critical Cyber Assets reside within an identified PSP and are protected from un-authorized access through the use of a card key access control system configured to restrict access to personnel who are trained, vetted, and authorized for such access. Additionally all devices are logically protected from unauthorized access by residing within an identified ESP where all logical access is restricted, logged, and monitored by restrictive boundary devices. Specifically, the Critical Assets that this Critical Cyber Asset is associated with has a manual capability that could be activated if Critical Cyber Assets are unable to be recovered. | To mitigate this issue, WECC_URE3 tested its backup media in calendar year 2013.
2013-07-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2013012329 | CIP-006-3c | R2.2 | WECC_URE3 submitted a Self-Certification to WECC stating that WECC_URE3 had an issue with CIP-009-3 R5. Specifically, WECC_URE3 reported that it failed to perform annual testing of backup media associated with Cyber Assets that are used in the access control and/or monitoring of the ESP, Cyber Assets that authorize and/ or log access to the PSP, and Critical Cyber Assets. Since the Self-Certification included Cyber Assets that authorize and/ or log access to the PSP, a WECC SME determined CIP-009 did not apply, but that these devices are within the scope of CIP-006-3c R2.2. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. There were a number of compensating measures in place to secure the devices against misuse or malicious attack. Specifically, all Critical Cyber Assets reside within an identified PSP and are protected from un-authorized access through the use of a card key access control system configured to restrict access to personnel who are trained, vetted, and authorized for such access. Additionally all devices are logically protected from unauthorized access by residing within an identified ESP where all logical access is restricted, logged, and monitored by restrictive boundary devices. Specifically, the Critical Assets that these Critical Cyber Assets were associated with have a manual capability that could be activated if Critical Cyber Assets are unable to be recovered. | To mitigate this issue, WECC_URE3 tested its backup media in calendar year 2013.
2013-07-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2013012049 | CIP-009-3 | R5 | WECC_URE3 submitted a Self-Certification to WECC stating that WECC_URE3 had an issue with CIP-009-3 R5. Specifically, WECC_URE3 reported that it failed to perform annual testing of backup media because WECC_URE3 reassigned personnel to this task, and that led to a miscommunication which resulted in missing the deadline. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. There were a number of compensating measures in place to secure the devices against misuse or malicious attack. Specifically, all Critical Cyber Assets reside within an identified PSP and are protected from un-authorized access through the use of a card key access control system configured to restrict access to personnel who are trained, vetted, and authorized for such access. Additionally all devices are logically protected from unauthorized access by residing within an identified ESP where all logical access is restricted, logged, and monitored by restrictive boundary devices. Specifically, the Critical Assets that these Critical Cyber Assets were associated with have a manual capability that could be activated if Critical Cyber Assets are unable to be recovered. | To mitigate this issue, WECC_URE3 tested its backup media in calendar year 2013.
2013-07-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC2011008655 | CIP-006-1 | R1 | WECC_URE4 submitted a Self-Report to WECC stating that WECC_URE4 had an issue with CIP-006-1 R1. Specifically, WECC_URE4 reported that it failed to ensure seven Cyber Assets within an Electronic Security Perimeter (“ESP”) were also located in a Physical Security Perimeter (“PSP”) per CIP-006-1 R1. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The devices in scope were not ESP access points and had limited connectivity within the ESP. Further, the 21 devices were physically secured within locked closets that afforded a number of protections. The closets were secured by magnetic/electronic locks that opened using an authorized access badge. The closets resided in a secured facility that was monitored on a 24/7 basis. Access points to the facility were electronically monitored and alarmed. | To mitigate this issue, WECC_URE4 completed the change control and PSP diagrams supporting the devices in scope are within a PSP. WECC has verified the completion of all mitigation activity.
2013-07-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 5 (WECC_URE5) | NCRXXXXX | WECC2013012076 | CIP-006-3c | R1 | WECC_URE5 submitted a Self-Report to WECC stating that WECC_URE5 had an issue with CIP-006-3c R5. Specifically, WECC_URE5 reported that an employee without authorized access to Critical Cyber Assets entered a Physical Security Perimeter ("PSP") without an escort or appropriately using the physical access controls in place at the access point. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although one employee failed to properly follow WECC_URE5's visitor control program for personnel without authorized unescorted access to PSPs, the PSP in scope is monitored twenty-four hours a day and each PSP access point door is configured to generate an alarm for any unauthorized access. WECC_URE5’s procedures for monitoring unauthorized access proved effective as an alarm sounded and corporate security was immediately alerted. In addition, because of WECC_URE5’s controls, WECC_URE5 was aware at all times the employee was in the PSP and monitored that the employee walked to the designated, appropriate meeting room without accessing any Critical Cyber Assets. | To mitigate this issue, WECC_URE5 immediately removed the employee from the PSP then escorted and logged appropriately. WECC_URE5 reprimanded the employee both in email and in person by his manager. WECC has verified completion of mitigating activties.
2013-07-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 6 (WECC_URE6) | NCRXXXXX | WECC2013012265 | CIP-002-3 | R2 | WECC_URE6 submitted a Self-Report to WECC stating that it had an issue with CIP-002-3 R2. Specifically, WECC_URE6 stated that in the previous calendar year it failed to apply its risk based assessment methodology (RBAM) to determine its Critical Assets and Critical Cyber Assets. Additionally, WECC_URE6 reported that because it did not apply its RBAM it did not have a list of Critical Assets or Critical Cyber Assets that were approved by senior management. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE6 had previously applied its RBAM in previous calendar years and had determined that it had no Critical Assets or Critical Cyber Assets. These prior lists were approved by WECC_URE6 senior management. Additionally, when WECC_URE6 applied its RBAM in calendar year 2013 and, as a result, created a null list of Critical Assets and Critical Cyber Assets that was approved by WECC_URE6 senior management. Finally, WECC_URE6 is a small renewable energy resource plant that has minimal impact on the reliability of the BPS. | To mitigate this issue, WECC_URE6 applied its risk based assessment methodology and had senior management approve the list promulgated from the application of the RBAM.
2013-07-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 6 (WECC_URE6) | NCRXXXXX | WECC2013012266 | CIP-002-3 | R3 | WECC_URE6 submitted a Self-Report to WECC stating that it had an issue with CIP-002-3 R3. Specifically, WECC_URE6 stated that in the previous calendar year it failed to apply its risk based assessment methodology (RBAM) to determine its Critical Assets and Critical Cyber Assets. Additionally, WECC_URE6 reported that because it did not apply its RBAM it did not have a list of Critical Assets or Critical Cyber Assets that were approved by senior management. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE6 had previously applied its RBAM in previous calendar years and had determined that it had no Critical Assets or Critical Cyber Assets. These prior lists were approved by WECC_URE6 senior management. Additionally, when WECC_URE6 applied its RBAM in calendar year 2013 and, as a result, created a null list of Critical Assets and Critical Cyber Assets that was approved by WECC_URE6 senior management. Finally, WECC_URE6 is a small renewable energy resource plant that has minimal impact on the reliability of the BPS. | To mitigate this issue, WECC_URE6 applied its risk based assessment methodology and had senior management approve the list promulgated from the application of the RBAM.
2013-07-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 6 (WECC_URE6) | NCRXXXXX | WECC2013012267 | CIP-002-3 | R4 | WECC_URE6 submitted a Self-Report to WECC stating that it had an issue with CIP-002-3 R4. Specifically, WECC_URE6 stated that in the previous calendar year it failed to apply its risk based assessment methodology (RBAM) to determine its Critical Assets and Critical Cyber Assets. Additionally,WECC_URE6 reported that because it did not apply its RBAM it did not have a list of Critical Assets or Critical Cyber Assets that were approved by senior management. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE6 had previously applied its RBAM in previous calendar years and had determined that it had no Critical Assets or Critical Cyber Assets. These prior lists were approved by WECC_URE6 senior management. Additionally, when WECC_URE6 applied its RBAM in calendar year 2013 and, as a result, created a null list of Critical Assets and Critical Cyber Assets that was approved by WECC_URE6 senior management. Finally, WECC_URE6 is a small renewable energy resource plant that has minimal impact on the reliability of the BPS. | To mitigate this issue, WECC_URE6 applied its risk based assessment methodology and had senior management approve the list promulgated from the application of the RBAM.
2013-07-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 7 (WECC_URE7) | NCRXXXXX | WECC2013012053 | CIP-007-1 | R4 | WECC_URE7 submitted a Self-Certification to WECC stating that it had an issue with CIP-007-1 R4. The devices in scope are networking equipment switches, routers, terminal servers, and integrated Ethernet switches used in the support of WECC_URE7's Energy Management System network. WECC_URE7 stated that it is technically infeasible to install antivirus software on the 19 devices in scope, but it failed to file a Technical Feasibility Exception Request (“TFE”) by the due date. Specifically, although WECC_URE7 had filed a TFE for CIP-007-1 R4, the 19 devices discussed herein were not included in the original request therefore WECC_URE7 submitted an expanded TFE. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although the 19 devices did not have the technical capability to implement antivirus or malware prevention software, there were a number of compensating measures in place to secure the devices against misuse or malicious attack. Specifically, all Critical Cyber Assets reside within an identified Physical Security Perimeter (“PSP”) and are protected from un-authorized access through the use of a card key access control system configured to restrict access to personnel who are trained, vetted, and authorized for such access. Additionally all devices are logically protected from unauthorized access by residing within an identified ESP where all logical access is restricted, logged, and monitored by restrictive boundary devices. Lastly, all other devices, where technically feasible, had AV/malware prevention software installed to help reduce the risk of propagation of malware. | To mitigate this issue, WECC_URE7 submitted an update to its TFE, identified as 2010-WECC-TFE00399-1. WECC_URE7 has made amendments to its TFE policy and procedures and created a checklist to address newly deployed Cyber Assets.
2013-07-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 8 (WECC_URE8) | NCRXXXXX | WECC2013012019 | CIP-003-3 | R1 | WECC_URE8 submitted a Self-Certification to WECC stating that it had an issue with CIP-003-3 R1. WECC_URE8 provided its critical infrastructure protection program poliy CIP 003-3. WECC_URE8 also provided its policy for the previous year, which included a revision history reflecting certain revisions made in the previous year, but WECC_URE8 had an issue because the Policy itself had not been signed by a senior manager. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE8’s CIP-Standard-compliant cyber security policy was last reviewed and approved in December, 2011. Also, the policy is readily available to all personnel, and WECC_URE8’s cyber security policy is part of the annual CIP-004 R2 training program. In addition, WECC_URE8 provided evidence that its cyber security plan had been reviewed in 2012, but it had not documented an approval signature from its senior manager. | To mitigate this issue, WECC_URE8 submitted a copy of its Cyber Security Policy for Securing Critical Cyber Assets CIP-003-3 R1, signed and dated by its Compliance Executive and CIP Senior Manager. WECC has verified the completion of all mitigation activity.
2013-07-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 8 (WECC_URE8) | NCRXXXXX | WECC2012009394 | CIP-004-3 | R2 | WECC_URE8 submitted a Self-Certification to WECC stating that it had an issue with CIP-004-3 R2. WECC_URE8 failed to provide CIP training to three of its employees before granting physical access to Critical Cyber Assets (“CCAs”). Access was granted for 6 days and then revoked for two employees; and access was granted for 14 days and then revoked for the third employee; without first verifying in each case that NERC CIP Training had been completed. Access to the Physical Security Perimeters (“PSPs”) was revoked as described above, immediately following the discoveries. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE8 stated that one of the three employees had a PRA prior to being granted access to the CCAs; one did not, and the third did not need NERC CIP PSP access for his/her job function and access was not required. In addition, WECC_URE8’s procedures include a checklist, and there is a visual reminder on the screen of the tool used when granting NERC CIP PSP access. WECC_URE8’s control center was staffed, monitored and secured twenty-four hours a day during this period. Although WECC_URE8 overlooked training for three employees of the nearly 1000 employees that have NERC CIP PSP access at WECC_URE8, the longest period of non-compliance for any one employee was 14 days and WECC_URE8 security verified that only one of the three employees in scope accessed a NERC CIP PSP during the time period and this employee had appropriate access. Specifically, the employee accessed the NERC CIP PSP in a distribution system operations area that is continually staffed and monitored, and the employee had appropriate job function training to further mitigate the risk. | To mitigate this issue, WECC_URE8 provided evidence its Security Services senior management has reviewed its procedures and checklists, confirming that training and PRA requirements are included; and that all Security Operations Center staff ensure that NERC CIP training and PRAs are current and that asset owners have approved access before granting NERC CIP PSP access. In addition, WECC_URE8 restricted the authority to grant NERC CIP PSP access to only day shift Security Operations Staff to limit the number of employees with this authority, and limit risk of mistakes. WECC has verified the completion of all mitigation activity.
2013-07-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 8 (WECC_URE8) | NCRXXXXX | WECC2012009395 | CIP-004-3 | R3 | WECC_URE8 submitted a Self-Certification to WECC stating that it had an issue with CIP-004-3 R3. WECC_URE8 failed to conduct a PRA for one of its employees, prior to granting physical access to its CCAs, WECC_URE8 granted physical access to CCAs for 6 days, revoking access immediately following the discovery. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The CCAs in scope are EMS workstations located in the control center. As compensating measures, WECC_URE8 stated that upon discovery on July 25, 2011, access was revoked for the person and a PRA was conducted prior to restoring access. The access was revoked immediately when the issue was discovered and WECC_URE8 security verified that the employee did not access a NERC CIP PSP during the time period that inappropriate access was granted. In addition, WECC_URE8's weekly and quarterly reviews the lists of nearly 1000 employees that have NERC CIP PSP access. Finally, WECC_URE8 stated that the control center was staffed, monitored, and secured twenty-four hours a day. | To mitigate this issue, WECC_URE8 provided evidence its Security Services senior management has reviewed its procedures and checklists, confirming that training and PRA requirements are included; and that all Security Operations Center staff ensure that NERC CIP training and PRAs are current and that asset owners have approved access before granting NERC CIP PSP access. In addition, WECC_URE8 restricted the authority to grant NERC CIP PSP access to only day shift Security Operations Staff to limit the number of employees with this authority, and limit risk of mistakes. WECC has verified the completion of all mitigation activity.
2013-07-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 8 (WECC_URE8) | NCRXXXXX | WECC2012011485 | CIP-006-3c | R1 | WECC_URE8 submitted a Self-Report to WECC stating that it had an issue with CIP-006-3c R1. During a routine periodic internal review, WECC_URE8 discovered that four employees were granted access to a NERC CIP Physical Security Perimeter, without verifying such access approval with the clearance level owner. WECC_URE8 verified PRA dates and CIP training dates for all employees. WECC_URE8 revoked NERC CIP PSP physical access for three of the four employees involved. Such access was restored following verification of access approval from the clearance level owner. WECC_URE8 did not revoke access for the fourth employee, because access approval from the clearance level owner was verified. WECC determined that WECC_URE8 maintains its CIP-004 R4 access list for physical access in the system. Since the system maintains the list of personnel with physical access to CCAs, when the four individuals in scope were added, the list no longer accurately reflected those with authorized access permissions to CCAs. Therefore, WECC discovered a possible violaion of CIP-004-3 R4. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although the four employees in question were granted unauthorized access for seven days, WECC_URE8 Security Operations verified that only one of these four employees actually accessed a NERC CIP PSP during the time period of unauthorized access approval. In all four cases PRA dates and CIP training dates had been properly verified prior to granting physical access to WECC_URE8’s PSPs. In addition, WECC_URE8 performs both weekly and quarterly reviews of the WECC_URE8 list of nearly 1000 employees that have NERC CIP PSP access to further check that procedures are followed. In addition, WECC_URE8 stated that all four individuals had current CIP training, PRAs, and were authorized for cyber access to the CCAs inside the PSPs in scope. Also, the PSPs in scope have 24 x 7 logging and monitoring of physical and cyber access. In addition, the EMS workstations in scope are staffed 24 x 7 and video cameras monitor access at all the access points to the PSPs. | To mitigate this issue, WECC_URE8 provided evidence its Security Services senior management has reviewed its procedures and checklists, confirming that training and PRA requirements are included; and that all Security Operations Center staff ensure that NERC CIP training and PRAs are current and that asset owners have approved access before granting NERC CIP PSP access. In addition, WECC_URE8 restricted the authority to grant NERC CIP PSP access to only day shift Security Operations Staff to limit the number of employees with this authority, and limit risk of mistakes.
2013-07-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 9 (WECC_URE9) | NCRXXXXX | WECC200902110 | CIP-003-1 | R1 | WECC_URE9 submitted a Self-Report to WECC stating that it had an issue with CIP-003-1 R1. WECC_URE9 self-reported that it failed to document and implement a cyber security policy that represents management’s commitment and ability to secure its Critical Cyber Assets. However, WECC_URE9 did have a compensating document whose purpose was to classify, identify, and protect information associated with Critical Cyber Assets, regardless of media type, and to provide procedures for managing access to protected Critical Cyber Asset Information. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE9 is subject to security regulations. Specific to the requirements of CIP-003-1 R1, WECC_URE9 provided a document to WECC for review designed to classify, identify, and protect information associated with Critical Cyber Assets, regardless of media type; and a statement showing WECC_URE9’s management’s commitment to compliance with the reliability standards. | To mitigate this issue, WECC_URE9 submitted WECC_URE9 documented and implemented a cyber security policy. WECC has verified the completion of all mitigation activity.
2013-07-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 9 (WECC_URE9) | NCRXXXXX | WECC200902112 | CIP-003-1 | R4 | WECC_URE9 submitted a Self-Report to WECC stating that it had an issue with CIP-003-1 R4. WECC_URE9 self-reported that it failed to implement and document a program to identify, classify, and protect information associated with Critical Cyber Assets, WECC_URE9 subsequently provided a document with the purpose to classify, identify, and protect information associated with Critical Cyber Assets. The document also provided procedures for managing access to protected Critical Cyber Asset Information. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE9 provided its system information protection and access control document, for WECC’s review. This document was designed to classify, identify, and protect information associated with Critical Cyber Assets, and was in effect before the effective date of the Standard. | To mitigate this issue, WECC_URE9 implemented and documented a program to identify, classify, and protect information associated with Critical Cyber Assets. WECC has verified the completion of all mitigation activity.
2013-07-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 9 (WECC_URE9) | NCRXXXXX | WECC200902117 | CIP-003-1 | R5 | WECC_URE9 submitted a Self-Report to WECC stating that it had an issue with CIP-003-1 R5. WECC_URE9 self-reported that it failed to document and implement a program for managing access to protected Critical Cyber Asset information. Specific to CIP-003-1 R5, WECC_URE9 adheres to an Information Assurance policy, which applies to information systems processing and information protection and addresses access control and requires information systems to employ features to ensure that only authorized users who require access may access the information and/or resources when required. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE9 has a variety of compensating documents and policies in place, including guidelines and policies addressing access control that requires information systems to employ features to ensure that only authorized users who require access may access the information and/or resources when required. | To mitigate this issue, WECC_URE9 documented and implemented a program for managing access to protected Critical Cyber Asset informationWECC has verified the completion of all mitigation activity.
2013-07-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 9 (WECC_URE9) | NCRXXXXX | WECC200902118 | CIP-003-1 | R6 | WECC_URE9 submitted a Self-Report to WECC stating that it had an issue with CIP-003-1 R6. WECC_URE9 self-reported that it failed to establish and document a CIP-Standard-compliant process of change control and configuration management for adding, modifying, replacing, or removing Critical Cyber Asset hardware or software, and implement supporting configuration management activities to identify, control and document all entity or vendor related changes to hardware and software components of Critical Cyber Assets pursuant to the change control process. However, in its data responses, WECC_URE9 provided two signed documents, these documents contain many elements of the Standard related to change control and configuration management. Nonetheless, WECC determined WECC_URE9 did not establish and document a process of change control and configuration management in accordance with the requirement. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE9 did provide a high level framework for the security of its cyber systems, including high level direction with respect to security controls. Specifically, WECC_URE9’s policies contained many of the elements of the Standard, and were in effect before the effective date of the Standard. | To mitigate this issue, WECC_URE9 established and documented a CIP-Standard-compliant process of change control. WECC has verified the completion of all mitigation activity.
2013-07-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 9 (WECC_URE9) | NCRXXXXX | WECC200902131 | CIP-004-1 | R3 | WECC_URE9 submitted a Self-Report to WECC stating that it had an issue with CIP-004-1 R3. WECC_URE9 self-reported that it failed to document and implement a program for personnel risk assessment program, WECC_URE9 provided an Attestation of the WECC_URE9's management, affirming that WECC_URE9 adheres governance policies closely related to risk assessments for personnel. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE9 has a variety of compensating documents and policies in place, including requiring checks within three working days. One compensating document requires WECC_URE9 to periodically reinvestigate its personnel every 5 years. The compensating document exceeds the requirement in CIP-004-1 R3.2 that directs WECC_URE9 to update each personnel risk assessment at least every seven years after the initial personnel risk assessment or for cause. | To mitigate this issue, WECC_URE9 documented and implemented a program for personnel risk assessment program. WECC has verified the completion of all mitigation activity.
2013-07-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 9 (WECC_URE9) | NCRXXXXX | WECC200902147 | CIP-007-1 | R7 | WECC_URE9 submitted a Self-Report to WECC stating that it had an issue with CIP-007-1 R7. WECC_URE9 self-reported that it failed to establish formal methods, processes, and procedures for disposal or redeployment of Cyber Assets within the ESP(s), WECC reviewed WECC_URE9’s submitted document. The purpose of this document is to establish formal methods, processes and procedures for disposal or redeployment of cyber assets within the ESP, and lists the specific procedures to be performed when any equipment used within the defined NERC-CIP ESP is decommissioned or redeployed. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE9 mitigated risks associated with this issue, and showed that it had established a compensating program for disposal or redeployment of Cyber Assets within its ESPs, by providing the document containing instructions for disposal or redeployment of cyber assets within the electronic security perimeters. Although the document was not compliant with this requirement, this document showed that WECC_URE9 had established formal methods, processes and procedures for disposal or redeployment of WECC_URE9’s Cyber Assets within the ESP, and listed the specific procedures to be performed when any equipment used within the defined ESP was decommissioned or redeployed. | To mitigate this issue, WECC_URE9 established formal methods, processes, and procedures for disposal or redeployment of Cyber Assets within the ESP(s).
2013-07-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 9 (WECC_URE9) | NCRXXXXX | WECC200902143 | CIP-009-1 | R3 | WECC_URE9 submitted a Self-Report to WECC stating that it had an issue with CIP-009-1 R3, R4, R5. WECC_URE9 self-reported that its main policy meets all requirements of this Standard, but not all systems designated as Critical Cyber Assets are tested, configured or documented per the requirements of the Standard. WECC reviewed WECC_URE9’s system recovery plan (“The Plan”). Although not CIP-Standard-compliant, The Plan document contains procedures for change control and provisions to update the recovery plan to reflect any changes or lessons learned as a result of an exercise or the recovery from an actual incident (R3). The Plan also contains provisions for backup and restoration, to ensure that backups are running successfully (R4); and provisions for testing backup media (R5). | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE9 generating plants with SCADA have sufficient resources to continue operations. WECC_URE9 has compensating controls and documentation, standard operating procedures and processes compliant with regulations. The recovery plan contains provisions to exercise the plan itself; it contains maintenance and change control procedures; backup and restoration procedures; and instructions for testing backup media. | To mitigate this issue, WECC_URE9 submitted (1) WECC_URE9 recovery plan for Critical Cyber Assets, (2) Evidence showing WECC_URE9 has tested its recovery plan, (3) Email showing the new recovery plan was distributed to appropriate personnel; (4) Evidence of WECC_URE9’s backups; (5) Evidence the backup media was tested. WECC has verified the completion of all mitigation activity.
2013-07-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 9 (WECC_URE9) | NCRXXXXX | WECC200902144 | CIP-009-1 | R4 | WECC_URE9 submitted a Self-Report to WECC stating that it had an issue with CIP-009-1 R3, R4, R5. WECC_URE9 self-reported that its main policy meets all requirements of this Standard, but not all systems designated as Critical Cyber Assets are tested, configured or documented per the requirements of the Standard. WECC reviewed WECC_URE9’s system recovery plan (“The Plan”). Although not CIP-Standard-compliant, The Plan document contains procedures for change control and provisions to update the recovery plan to reflect any changes or lessons learned as a result of an exercise or the recovery from an actual incident (R3). The Plan also contains provisions for backup and restoration, to ensure that backups are running successfully (R4); and provisions for testing backup media (R5). | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE9 generating plants with SCADA have sufficient resources to continue operations. WECC_URE9 has compensating controls and documentation, standard operating procedures and processes compliant with regulations. The recovery plan contains provisions to exercise the plan itself; it contains maintenance and change control procedures; backup and restoration procedures; and instructions for testing backup media. | To mitigate this issue, WECC_URE9 submitted (1) WECC_URE9 recovery plan for Critical Cyber Assets, (2) Evidence showing WECC_URE9 has tested its recovery plan, (3) Email showing the new recovery plan was distributed to appropriate personnel; (4) Evidence of WECC_URE9’s backups; (5) Evidence the backup media was tested. WECC has verified the completion of all mitigation activity.
2013-07-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 9 (WECC_URE9) | NCRXXXXX | WECC200902145 | CIP-009-1 | R5 | WECC_URE9 submitted a Self-Report to WECC stating that it had an issue with CIP-009-1 R3, R4, R5. WECC_URE9 self-reported that its main policy meets all requirements of this Standard, but not all systems designated as Critical Cyber Assets are tested, configured or documented per the requirements of the Standard. WECC reviewed WECC_URE9’s system recovery plan (“The Plan”). Although not CIP-Standard-compliant, The Plan document contains procedures for change control and provisions to update the recovery plan to reflect any changes or lessons learned as a result of an exercise or the recovery from an actual incident (R3). The Plan also contains provisions for backup and restoration, to ensure that backups are running successfully (R4); and provisions for testing backup media (R5). | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE9 generating plants with SCADA have sufficient resources to continue operations. WECC_URE9 has compensating controls and documentation, standard operating procedures and processes compliant with regulations. The recovery plan contains provisions to exercise the plan itself; it contains maintenance and change control procedures; backup and restoration procedures; and instructions for testing backup media. | To mitigate this issue, WECC_URE9 submitted (1) WECC_URE9 recovery plan for Critical Cyber Assets, (2) Evidence showing WECC_URE9 has tested its recovery plan, (3) Email showing the new recovery plan was distributed to appropriate personnel; (4) Evidence of WECC_URE9’s backups; (5) Evidence the backup media was tested. WECC has verified the completion of all mitigation activity.
2013-06-27 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2012009680 | CIP-007-1 | R2; R2.1 | During an on-site Compliance Audit, FRCC determined that FRCC_URE1 had an issue with CIP-007-1 R2.1. FRCC_URE1 could not provide evidence to demonstrate that only ports required for normal and emergency operations were enabled for all of its Critical Cyber Assets. For the identified Cyber Assets, scans demonstrated that one port was open which was not documented as a port required for normal and emergency operations. Although a different port was documented in the list of authorized ports for the Cyber Assets, vendor documentation did not support the need for this port and it would vary each time the application was restarted. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk was reduced because the open port varied each time the application was restarted, requiring a new port scan on the system to find the port. The Cyber Asset is located within an Electronic Security Perimeter (ESP) and Physical Security Perimeter. Furthermore, access to the range of unauthorized open ports is closed at the ESP access point firewall preventing access to the Cyber Asset from outside the ESP. | To mitigate this issue, FRCC_URE1: 1) updated its authorized ports and services by asset class - application servers document, to remove the unneeded port and associated service from the list of authorized ports and services; 2) submitted a technical feasibility exception (TFE) to document implementation of the windows firewall to block the unauthorized ports that are not required for operation and cannot be disabled by the vendor supplied application; and 3) verified the TFE mitigating and compensating protections are only allowing the authorized services to listen for connections on authorized ports. FRCC has verified the completion of all mitigation activity.
2013-06-27 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2013011736 | CIP-005-3a | R3; R3.2 | FRCC_URE1 self-reported that it had an issue with CIP-005-3a R3.2. For approximately one minute, FRCC_URE1's backup logging monitoring and alerting Cyber Asset was unable to detect and alert for attempts at or actual unauthorized accesses when it had to switch from the primary to backup monitoring Cyber Asset during a scheduled maintenance update of the primary logging Cyber Asset. FRCC_URE1 did not timely submit a Technical Feasibility Exception (TFE) for the Cyber Asset. It did, however, have a manual process in place to detect and alert for attempts at or actual unauthorized accesses although not clearly documented. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk to the BPS was reduced because FRCC_URE1 had a manual procedure (although not clearly documented) in place for the backup monitoring and logging Cyber Asset to detect and alert (manually) for attempts at or unauthorized accesses. Furthermore, the duration of the issue was short, one minute, and the issue was a result of an administrative oversight in not submitting the TFE. | To mitigate this issue, FRCC_URE1: 1) submitted a TFE for the Cyber Asset's inability to detect and alert; and 2) updated documentation to sufficiently articulate manual review process. FRCC has verified the completion of all mitigation activity.
2013-06-27 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2012011475 | CIP-002-1 | R1; R1.2.2; R1.2.3 | During a Compliance Audit, MRO discovered that MRO_URE1 failed to have a risk-based assessment methodology (RBAM) which considered the following assets: 1) transmission substations that support the reliable operation of the bulk electric system (BES), in accordance with CIP-002-1 R1.2.2; and 2) generation resources that support the reliable operation of the BES, in accordance with CIP-002-1 R1.2.3. Specifically, MRO_URE1 failed to include criteria in order to determine criticality of substations below 230 kV, generators below 100 MW, and transmission and generation assets required for system restoration. Instead of developing criteria, MRO_URE1 relied upon a statement from its subject matter expert (SME). MRO_URE1 also relied upon a similar statement for generators under 100 MW. While engineering judgment is permissible in an RBAM, MRO determined that further documentation of this assertion was necessary. Furthermore, during mitigation, MRO discovered that preliminary asset lists, used to exercise the RBAM, had some discrepancies. However, those discrepancies were found to be assets which were not owned by MRO_URE1, and were erroneously included in its asset list. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Although MRO_URE1’s documentation was insufficient for its justification of excluding these assets from its assessment, MRO_URE1 asserted that its SMEs have sufficient engineering experience with other system studies in this area to make such determinations. MRO_URE1 failed to properly document its SME experience which qualified them to make such determinations. Additionally, the documentation issue with the preliminary asset lists did not impact MRO_URE1’s overall Critical Asset list. The revisions did not result in any additions to MRO_URE1’s actual list of Critical Assets. Therefore, MRO determined that this issue posed a minimal risk to the BPS. | To mitigate this issue, MRO_URE1 revised its RBAM to include more detail regarding the engineering assessment process to achieve the following: 1) clarify the criteria for including or excluding BPS assets from further detailed analysis during the application of the RBAM; 2) provide additional documentation specific to the assessment of restoration resources; and 3) clarify the assessment method for assets that are owned by other registered entities but operated by MRO_URE1.
2013-06-27 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 2 (MRO_URE2) | NCRXXXXX | MRO2012010128 | CIP-002-1 | R1 | During a Compliance Audit, MRO_URE2discovered that MRO_URE2 failed to adequately document evaluation criteria used to assess its Critical Assets to determine the impact on the Bulk Electric System (BES). CIP-002-1 R.1.1 requires the Responsible Entity to maintain documentation describing its risk-based assessment methodology (RBAM) that includes procedures and evaluation criteria. MRO_URE2 included its procedures used to categorize assets in its RBAM, but did not include evaluation criteria. MRO_URE2's RBAM contained impacts to the BES that were conclusory and did not identify how its conclusions were derived for classifying its Critical Assets. For example, MRO_URE2's control center was identified as having a low probability of an event and minimal impact on the BES, but did not state how those conclusions were determined. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). MRO_URE2 does not operate generation or transmission facilities. As a result, its control center is used as a "view-only" tool. Although MRO_URE2 did not include evaluation criteria in its RBAM, MRO_URE2's previous determination regarding its list of Critical Assets remained the same after MRO_URE2 clarified its evaluation criteria. | To mitigate this issue, MRO_URE2 updated its RBAM pursuant to CIP-002 R1, which incorporated bright-line criteria from new CIP versions. Under its current RBAM, MRO_URE2's list of Critical Assets remains the same.
2013-06-27 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 3 (MRO_URE3) | NCRXXXXX | MRO2012010160 | CIP-002-1 | R1; R1.1 | During a Compliance Audit, MRO discovered that MRO_URE3 failed to maintain documentation describing its risk-based assessment methodology (RBAM) that includes procedures and evaluation criteria, in accordance with CIP-002-1 R1.1. MRO_URE3 used a formula for determining criticality. Although MRO_URE3 assigned numbers for both of these scales for each asset, it failed to document how the scale entries were obtained. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Although MRO_URE3’s RBAM lacked clear documentation in the use of the evaluation criteria for determining criticality, MRO_URE3 does not have any Critical Assets. Additionally, MRO_URE3 is a small entity with limited possible impact on the BPS. | To mitigate the issue, MRO_URE3 documented how each rating scale number is determined and how assets fit each rating. MRO has verified the completion of all mitigation activity.
2013-06-27 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2013012125 | CIP-005-3a | R5; R5.2 | RFC_URE1 submitted a Self-Report to ReliabilityFirst stating that it had an issue with CIP-005-3a R5.2. RFC_URE1 changed the way it monitors and logs access at access points to its Electronic Security Perimeters (ESPs) when it replaced a RFC_URE1-owned and managed monitoring and logging appliance with a third-party monitoring and logging service. However, RFC_URE1 failed to update the documentation reflecting the modification of the network and controls within 90 calendar days of this change. RFC_URE1's failure to update documentation following its implementation of a new monitoring and logging service also resulted in RFC_URE1's noncompliance with Reliability Standard CIP-008-3 R1, as described in issue RFC2013012131. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. RFC_URE1's issue was a documentation deficiency related to its reference of a previous version of its monitoring and logging service, rather than the new monitoring and logging service within its CIP-005-3 documentation. RFC_URE1 did not leave its devices unprotected as a result of this documentation error. Rather, in implementing the change from one system to another system, RFC_URE1 did not deactivate its previous monitoring and logging appliance until the new monitoring and logging service was up and running, in order to ensure that there was no interruption in ESP monitoring and logging. In addition, RFC_URE1 personnel responsible for ESP monitoring and logging were directly involved in the transition from the previous monitoring and logging appliance to the new monitoring and logging service, and were therefore familiar with the changes to the monitoring infrastructure. Furthermore, the relevant personnel were continuously able to receive alerts and event data and were knowledgeable about how to customize alerts and access and review log files both during and after the transition to the new monitoring and logging service. The issue was a clerical error that had no impact on its operational capability and which did not interrupt its monitoring or logging of the ESP. | To mitigate this issue, RFC_URE1 modified its change ticket templates for its CIP-003 change control and configuration management process to require change submitter to determine whether, in each instance, RFC_URE1 should update additional documents that might be affected by a change.
2013-06-27 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2013012129 | CIP-007-1 | R4 | RFC_URE1 submitted a Self-Report to ReliabilityFirst stating that it had an issue with CIP-007-1 R4 because it submitted its technical feasibility exception (TFE) request for its monitoring services late due to vendor delays in providing RFC_URE1 the required information. Additionally, RFC_URE1 overlooked the need to file TFEs for two switches, due to the operational functionality of these devices. For all three devices, RFC_URE1 was unable to install anti-virus software and malware prevention tools, but failed to document the compensating measures applied to mitigate risk exposure or acceptance of risk. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. RFC_URE1 provided alternate controls to protect its systems from cybersecurity breaches where anti-virus software and malware prevention tools were technically infeasible. Each implicated system and device is located behind a Physical Security Perimeter (PSP). Additionally, the two switches are located inside an Electronic Security Perimeter (ESP) and utilize a rudimentary proprietary operating system that utilizes magnetic relays to switch between routers and that is not capable of anti-virus or malware installation. RFC_URE1 follows its malware prevention program for all other devices. Furthermore, RFC_URE1 has not experienced any incidents or security breaches during the time frame of this issue. | To mitigate this issue, RFC_URE1 implemented the compensating measures, which included all equipment being inside a six-wall PSP and the switches within the ESP, described in its TFE Part B submittals to mitigate risk exposure.
2013-06-27 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2012010394 | CIP-007-1 | R5; R5.3.2 | RFC_URE1 submitted a Self-Certification and approximately a week later RFC_URE1 submitted a Self-Report to ReliabilityFirst stating that it had an issue with CIP-007-1 R5. RFC_URE1 failed to timely notify ReliabilityFirst of instances related to its operating system where, due to technical infeasibility, RFC_URE1 did not require the use of passwords consisting of a combination of alpha, numeric, and “special” characters. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although RFC_URE1 does not have technical controls regulating password complexity for its operating system, RFC_URE1 had procedural controls in place which require all system users to utilize CIP compliant passwords where possible. RFC_URE1 also submits email reminders to all system users regarding the proper password complexity. RFC_URE1 utilized technical controls to enforce the password complexity to the maximum extent capable by the operating system, which includes, at a minimum, a forced password character length of at least eight characters. Additionally, the equipment that is running the operating system is inside a Physical Security Perimeter and an Electronic Security Perimeter which RFC_URE1 monitors 24 hours a day, seven days a week. | To mitigate this issue, RFC_URE1 submitted a Technical Feasibility Exception to ReliabilityFirst and reminded operators of the CIP-007 R5.3.2 password complexity requirements.
2013-06-27 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2013012130 | CIP-007-1 | R6 | RFC_URE1 submitted a Self-Report to ReliabilityFirst stating that it had an issue with CIP-007-1 R6. For two Cyber Assets within the Electronic Security Perimeter, namely two switches, RFC_URE1 did not ensure that these devices implement automated tools or organizational process controls to monitor system events related to cybersecurity, nor did RFC_URE1 submit a Technical Feasibility Exception (TFE) with ReliabilityFirst to document the technical infeasibility of implementing such controls. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The limited operational functionality of the two switches protects RFC_URE1's system from cybersecurity breaches, since the devices are used only to switch incoming Supervisory Control and Data Acquisition (SCADA) data feeds between a redundant pair of front-end processors. A SCADA and energy management system (EMS) server controls the operation of both switches and will command an “A to B” or “B to A” switchover if it detects a loss of incoming SCADA data. The SCADA/EMS server’s detection of data loss effectively compensates for the fact that the switches themselves have no monitoring capabilities. Furthermore, the SCADA/EMS server has been given the protections as applicable from CIP-002 through CIP-009. Therefore, RFC_URE1 implemented measures to provide protection to its system from cybersecurity events. | To mitigate this issue, RFC_URE1: 1) filed a TFE with ReliabilityFirst related to the switches; and 2) modified its change ticket templates used for CIP-003 change control and configuration management to require change submitters to determine whether one or more TFEs will be required for any new Cyber Asset subject to CIP requirements. If TFE(s) are required, the submitter will be required to enter ReliabilityFirst-assigned TFE identifier(s) before change ticket can be closed out.
2013-06-27 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2012010395 | CIP-007-3 | R9 | RFC_URE1 submitted a Self-Certification to ReliabilityFirst stating that it had an issue with CIP-007-3 R9. RFC_URE1 failed to annually review and update all documentation specified in Standard CIP-007-3. Specifically, RFC_URE1 failed to annually review and update the following CIP-007-3 documentation in 2011: 1) system security management: ports and services procedures; 2) system security management: security patch management; 3) system security management: malicious software prevention; 4) system security management: Cyber Asset disposal or redeployment procedures; and 5) system security management: cyber vulnerability assessments. Instead, within RFC_URE1’s document management system, RFC_URE1 mislabeled the document review frequency label by inserting an incorrect document review due date and thereafter failed to annually review all CIP-007-3 documentation. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The issue was caused by a data entry mistake and was corrected within five months. Only minor updates to the subject document were necessary. Finally, RFC_URE1 performed the necessary reviews and updates for 2012. . | To mitigate this issue, RFC_URE1: 1) labeled documents correctly in its document management system in order to ensure that it conducts future document reviews on an annual basis; 2) created a tool to track document review dates; and 3) reviewed its documentation and added those documents that it had previously not reviewed on an annual basis to its review matrix. ReliabilityFirst has verified the completion of all mitigation activity.
2013-06-27 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2013012131 | CIP-008-3 | R1; R1.4 | RFC_URE1 submitted a Self-Report to ReliabilityFirst stating that it had an issue with CIP-008-3 R1.4. RFC_URE1 changed its system for generating automated Cyber Security Incident alerts, but failed to update its Cyber Security Incident response plan within 30 calendar days of this change. RFC_URE1's failure to update documentation following its implementation of a new monitoring and logging service also resulted in RFC_URE1's noncompliance with Reliability Standard CIP-005-3a R5.2, as described in RFC2013012125. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. RFC_URE1's issue was a documentation deficiency related to its reference of a previous version of its monitoring and logging service, rather than the new monitoring and logging service within its Cyber Security Incident response plan. RFC_URE1 did not leave its devices unprotected as a result of this documentation error. Rather, in implementing the change from one system to another system, RFC_URE1 did not deactivate its previous monitoring and logging appliance until the new monitoring and logging service was up and running, in order to ensure that there was no interruption in Electronic Security Perimeter (ESP) monitoring and logging. In addition, RFC_URE1 personnel responsible for (ESP) monitoring and logging were directly involved in the transition from the previous monitoring and logging appliance to the new monitoring and logging service, and were therefore familiar with the changes to the monitoring infrastructure. Furthermore, the relevant personnel were continuously able to receive alerts and event data and were knowledgeable about how to customize alerts and access and review log files both during and after the transition to the new monitoring and logging service. The issue was a clerical error that had no impact on its operational capability and which did not interrupt its monitoring or logging of the ESP. | To mitigate this issue, RFC_URE1: 1) updated its Cyber Security Incident response plan; and 2) modified its change ticket templates for its CIP-003 change control and configuration management process to require change submitter to determine whether, in each instance, should update additional documents that might be affected by a change.
2013-06-27 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2013012132 | CIP-009-3 | R1 | RFC_URE1 submitted a Self-Report to ReliabilityFirst stating that had an issue with CIP-009-3 R1. RFC_URE1 failed to annually review two documents: 1) the RFC_URE1 IT plan dealing with backup and recovery; and 2) the site replication and failover plan, which are incorporated by reference into RFC_URE1's recovery plan. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. RFC_URE1 conducted an annual review on the remainder of the recovery plan, except the two documents which were incorporated by reference. Additionally, RFC_URE1 determined that the two referenced documents that were not reviewed on an annual basis did not require any updates. | To mitigate this issue, RFC_URE1 added the two missed documents to its annual review matrix and reviewed each document.
2013-06-27 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2013012302 | CIP-003-1 | R2; R2.1 | RFC_URE2 submitted a Self-Report to ReliabilityFirst stating that it had an issue with CIP-003-1 R2. RFC_URE2 could not locate a separate specific document that identified the senior manager by name, title, and date of designation for approximately 28 months. However, the senior manager who approved and signed the CIP-related documents, including the Critical Asset assessment and subsequent lists of Critical Assets and Critical Cyber Assets (CCAs) was the appropriate senior manager during that time period. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). This was a documentation issue only. The senior manager that approved and signed the CIP-related documents was the appropriate senior manager during that time period and is now retired. RFC_URE2 has no Critical Assets or CCAs, reducing the likelihood that this issue would cause a risk to the reliability of the BPS. | To mitigate this issue, RFC_URE2: 1) conducted a review of its CIP procedure; 2) revised its designation of senior manager letter and stored it in the electronic document management program for document retention. In addition, the electronic data tracking system will generate an annual reminder to review senior manager assignments; and 3) created a managerial transition checklist as a reminder to validate the senior manager assignment within 30 days of senior manager assignment.
2013-06-27 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC2013012420 | CIP-003-2 | R1 | ReliabilityFirst conducted a Compliance Audit and determined that RFC_URE3 had an issue with CIP-003-2 R1. RFC_URE3 failed to ensure that its cybersecurity policy addresses all of the requirements in Standards CIP-002 through CIP-009. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. RFC_URE3's policy generally addressed the NERC CIP Standards, even though it did not specifically address each Requirement. RFC_URE3 implemented its cybersecurity policy with limited deficiencies not attributed to the policy document. | To mitigate this issue, RFC_URE3 revised its cybersecurity policy to address the requirements of Standards CIP-002 through CIP-009.
2013-06-27 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC2013012427 | CIP-005-1 | R4; R4.2, R4.3, R4.4 | ReliabilityFirst conducted a Compliance Audit. ReliabilityFirst identified that RFC_URE3 had an issue with CIP-005-1 R4. RFC_URE3's cyber vulnerability assessment (CVA) of electronic access points did not identify all access points, such as WAN routers and gas server room modems. As a result, RFC_URE3 failed to conduct a complete review that only ports and services required for operations at access points are enabled (R4.2) and failed to discover all access points to the Electronic Security Perimeter (R4.3). RFC_URE3 conducts an automatic and a manual review of controls for default accounts, passwords, and network management community strings but, in its CVA failed to include the gas server room modems in the manual review (R4.4). | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. RFC_URE3 performed CVAs for its electronic access points, although it did not document the consideration of R4.2, R4.3, and R4.4. In addition, for the access points that RFC_URE3 did not discover, RFC_URE3 classified the access points it failed to discover as Critical Cyber Assets (CCAs) and afforded them the protective measures of CCAs. | To mitigate this issue, RFC_URE3 revised its documented process for CVAs of access points to the Electronic Security Perimeter.
2013-06-27 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC2013012428 | CIP-006-1 | R1 | ReliabilityFirst conducted a Compliance Audit. ReliabilityFirst identified that RFC_URE3 had an issue with CIP-006-1 R.1. ReliabilityFirst discovered an Electronic Security Perimeter cable that extended outside the Physical Security Perimeter (PSP). In addition, ReliabilityFirst discovered that RFC_URE3 failed to identify an emergency exit door as an access point on its PSP drawing. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The cabling is located under a raised floor for a short distance on the floor of the corporate office, which has limited access. The door at issue is an emergency exit only and it is incapable of opening from the outside. If opened from the inside, an alarm activates and security would respond to the alarm. In addition, the door is located inside a building with limited access. | To mitigate this issue, RFC_URE3 installed conduit around the cable at issue and added the emergency exit door to the PSP drawing.
2013-06-27 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 4 (RFC_URE4) | NCRXXXXX | RFC2013011665 | CIP-006-3c | R1 | RFC_URE4 submitted a Self-Report to ReliabilityFirst stating that it had an issue with CIP-006-3c R1. RFC_URE4 decommissioned a Physical Security Perimeter (PSP) at a power plant because it moved two workstations into another PSP at the plant. RFC_URE4 performed a routine physical walk-down of the power plant to validate network documentation. During the walk-down, RFC_URE4 discovered that two Cyber Assets in the decommissioned PSP, one critical and one non-critical, remained connected to the Electronic Security Perimeter (ESP) through the power plant’s main site distribution switch (which was located in an active and protected PSP. As a result, two Cyber Assets remained connected to ESP after RFC_URE4 decommissioned the PSP. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The devices at issue still had the protections of the ESP. In addition to the protections of the ESP, these devices utilize a non-Windows based operating system that is not as susceptible to mainstream viruses. Although lack of physical protection presents an increased risk of access, the decommissioned PSP was wholly contained on a site with restricted access and perimeter security protection, reducing the likelihood of unauthorized access. | To mitigate this issue, RFC_URE4 removed the devices from the ESP and revised its current change control process to ensure it all business units understand the process of decommissioning PSPs. ReliabilityFirst has verified the completion of all mitigation activity.
2013-06-27 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 4 (RFC_URE4) | NCRXXXXX | RFC2013011946 | CIP-005-1 | R1; R1.4 | RFC_URE4 submitted a Self-Report to ReliabilityFirst stating that it had an issue with CIP-005-1 R1. During a physical walk-down of all CIP Physical Security Perimeters (PSPs), RFC_URE4 discovered an undocumented switch residing in the Electronic Security Perimeter (ESP) and PSP at a power plant. The switch was acting as a hub to connect one of RFC_URE4’s paperless chart recorders to a different switch. RFC_URE4 failed to identify and protect this switch as required by CIP-005-3a R1.4. RFC_URE4 removed the switch from the ESP. RFC_URE4 submitted another Self-Report to ReliabilityFirst identifying an additional issue with CIP-005-1 R1.4, consolidated into RFC2013011946. During its annual physical and electronic walk down of the power plant, RFC_URE4 discovered two undocumented non-critical Cyber Assets within the ESP. The devices, a wireless gateway device and a signal converter, were connected to a router in the plant’s ESP. RFC_URE4 failed to identify these devices as required by CIP-005-1 R1.4. RFC_URE4 disconnected the wireless gateway device from the router and RFC_URE4 disconnected the signal converter from the router. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Regarding the undocumented switch, the switch utilized a non-Windows operating system that is not as susceptible to mainstream viruses. The switch resided in a PSP and the paperless chart recorder was the only device to which it was connected. Both the wireless gateway device and the signal converter device were located within an ESP and PSP. Regarding the wireless gateway device, RFC_URE4 never configured it with an IP address and it was therefore unable to communicate or be discovered on the network. In addition, wireless transmission on the device was inactive. Regarding the signal converter, RFC_URE4 utilizes the device to remotely monitor data on the generating unit, which does not affect plant operation. In addition, its monitoring capability was redundant because a primary means of monitoring the asset was in place. As a result, it was less likely that unauthorized access to Critical Cyber Assets could occur through these devices. | To mitigate this issue, RFC_URE4: 1) removed the device from the ESP and PSP; and 2) removed the devices after verifying that their removal would not impact the reliability of the system.
2013-06-27 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 4 (RFC_URE4) | NCRXXXXX | RFC2013012068 | CIP-004-4 | R2 | RFC_URE4 submitted a Self-Report to ReliabilityFirst stating that it had an issue with CIP-004-4 R2. RFC_URE4 added a new contractor to the network engineering security group to enable the contractor to access a non-NERC system. This contractor did not have cybersecurity training. Adding the contractor to this group inadvertently provided the contractor with cyber access to certain routers and switches, which are Critical Cyber Assets (CCAs). During a periodic user access review, RFC_URE4 discovered this access and immediately revoked it. RFC_URE4 submitted a Self-Report to ReliabilityFirst identifying an additional issue with CIP-004-4, consolidated into RFC2013012068. As part of an internal effort to improve its reporting mechanism for physical and electronic access, RFC_URE4 discovered two contract employees and one RFC_URE4 employee that had not completed annual training but retained physical access to one or more Physical Security Perimeters. RFC_URE4’s internal policy requires employees and contractors to renew their annual training once per calendar year, not to exceed 15 months. In each instance, the employee and the supervisor of the employee were notified that the training was set to expire. Upon discovery, RFC_URE4 revoked access for all three individuals. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Regarding the failure to conduct cybersecurity training prior to granting access, the contractor had a current and valid personnel risk assessment (PRA). In addition, when RFC_URE4 reviewed the logs, it determined that the contractor did not access any of the CCAs. It is unlikely that the contractor would have known about the access to such devices as the contractor’s job roles did not include accessing NERC CIP routers or switches. Regarding the failure to complete annual cybersecurity training, the individuals had physical access only, and all three individuals had current and valid PRAs. All three individuals had completed cybersecurity training prior to being granted access. | To mitigate this issue, RFC_URE4: 1) revoked the employees’ access, and implemented a system-generated nightly list of all personnel with electronic and physical access that have qualifications in jeopardy of surpassing the allotted annual review period. This list will be automatically distributed to the NERC compliance organization for review and monitoring; and 2) communicated the importance of timely access revocation to all RFC_URE4 leaders.
2013-06-27 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 5 (RFC_URE5) | NCRXXXXX | RFC2013012099 | CIP-006-3c | R1; R1.6 | RFC_URE5 submitted a Self-Report to ReliabilityFirst stating that it had an issue with CIP-006-3c R1.6. RFC_URE5 did not log the exit and re-entry of five visitors to a physical security perimeter (PSP). Specifically, RFC_URE5 escorted the five visitors from a conference room inside a PSP to a lab area outside the PSP, but within the same facility, to participate in a demonstration. RFC_URE5 then escorted the five visitors back into the PSP to gather equipment, and then escorted them back out of the PSP to participate in the demonstration. At the close of the demonstration, RFC_URE5 escorted the five visitors back to the PSP. When escorting the visitors into and out of the PSP, RFC_URE5 neglected to log the visitors’ exit and re-entry into the PSP pursuant to CIP-006-3c R1.6.1. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The five visitors had an escort for the duration of the issue. Additionally, the RFC_URE5 escort had successfully completed CIP training, had a valid personnel risk assessment and was authorized to have unescorted access to the PSP at issue. Finally, RFC_URE5 logged initial entry and final exit from the PSP of the five individuals, just not the exit and re-entry associated with the lab demonstration. | To mitigate this issue, RFC_URE5: 1) discussed the incident with the CIP escort and reinforced proper logging procedures; and 2) provided all department personnel with re-education on CIP escort responsibilities during a department meeting.
2013-06-27 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 5 (RFC_URE5) | NCRXXXXX | RFC2013012098 | CIP-004-1 | R4 | RFC_URE5 submitted a Self-Report to ReliabilityFirst stating that it had an issue with CIP-004-1 R4. RFC_URE5 discovered that an authentication source was configured to grant a non-CIP directory service group access to Critical Cyber Assets (CCAs). However, RFC_URE5 had not authorized cyber access to two members of the group through its regulatory access authorization database system. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Both members of the group who lacked cyber authorization from RFC_URE5 had valid CIP training and personnel risk assessments for the duration of the issue. The issue with CIP-004-1 R4 did not provide non-CIP personnel with CIP access; rather it provided cyber access to two CIP-qualified individuals without first formally authorizing access. Finally, the two individuals at issue were unaware they had cyber access to the CCAs at issue and at no time attempted to access the CCAs. | To mitigate this issue, RFC_URE5: 1) removed the two individuals from the group; 2) disabled the group’s ability to access CCAs; 3) created and implemented new naming conventions to delineate between CIP and non-CIP directory service groups, reducing the likelihood that RFC_URE5 will inadvertently assign a non-CIP directory service group to a CIP-controlled access list; and 4) reviewed all directory service groups for similar situations and did not discover any additional instances of possible noncompliance.
2013-06-27 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 5 (RFC_URE5) | NCRXXXXX | RFC2013012100 | CIP-006-3c | R5 | RFC_URE5 submitted a Self-Report to ReliabilityFirst stating that it had an issue with CIP-006-3c R5. During a five-day period, RFC_URE5 did not continuously monitor an access point into a physical security perimeter (PSP) with an alarm system or human observation. RFC_URE5 initially configured an access point to a PSP with a portal mantrap and an exterior steel door with a keypad connected to its Physical Access Control System. During a renovation of the access point RFC_URE5 removed the mantrap and with it the alarm for unauthorized access. During this renovation, RFC_URE5 monitored for unauthorized access with human observation 24 hours a day, seven days a week from an office located next to the access point. However, when FE Utilities renovated that office, it relocated the individuals observing the access point for five days. The employee who decided to relocate the individuals from the office for five days incorrectly believed an alarm input was installed on the exterior steel door adjacent to the keypad. RFC_URE5 failed to monitor the access point with an alarm system or human observation during that five-day period. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Access to the PSP was controlled and logged by an exterior steel door with the keypad access system for the duration of the issue. Additionally, access to the building in which the PSP is located was continuously monitored by a guard staff stationed 24 hours a day, seven days a week for the duration of the issue. | To mitigate this issue, RFC_URE5 installed an alarm on the access point of the PSP.
2013-06-27 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 6 (RFC_URE6) | NCRXXXXX | RFC2013012193 | CIP-004-1 | R4 | RFC_URE6 submitted a Self-Report to ReliabilityFirst stating that it had an issue with CIP-004-1 R4. RFC_URE6 discovered that an authentication source was configured to grant a non-CIP directory service group access to Critical Cyber Assets (CCAs). However, RFC_URE6 had not authorized cyber access to two members of the group through its regulatory access authorization database system. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Both members of the group who lacked cyber authorization from RFC_URE6 had valid CIP training and personnel risk assessments for the duration of the issue. The issue with CIP-004-1 R4 did not provide non-CIP personnel with CIP access; rather it provided cyber access to two CIP-qualified individuals without first formally authorizing access. Finally, the two individuals at issue were unaware they had cyber access to the CCAs at issue and at no time attempted to access the CCAs. | To mitigate this issue, RFC_URE6: 1) removed the two individuals from the group; 2) disabled the group’s ability to access CCAs; 3) created and implemented new naming conventions to delineate between CIP and non-CIP directory service groups, reducing the likelihood that RFC_URE6 will inadvertently assign a non-CIP directory service group to a CIP-controlled access list; and 4) reviewed all directory service groups for similar situations and did not discover any additional instances of possible noncompliance.
2013-06-27 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 7 (RFC_URE7) | NCRXXXXX | RFC2012010380 | CIP-008-3 | R1 | RFC_URE7 self-certified to ReliabilityFirst that it had an issue with CIP-008-3 R1. While RFC_URE7 had a procedure for updating their Cyber Response Plans within 30 calendar days of any changes, it did not consistently implement that procedure. RFC_URE7 did not update its Cyber Response Plans within 30 calendar days on four separate occasions. Specifically, RFC_URE7 failed to change referenced procedure versions or designation numbers in its Cyber Response Plans and did not update the Standard and Requirement language within 30 calendar days of the change from version 2 to version 3 of the CIP Reliability Standards. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The issue is a documentation issue. The changes RFC_URE7 failed to update within 30 calendar days included changing referenced procedure versions or designation numbers and the Standard and Requirement wording arising from the transition from version 2 of the CIP Standards to version 3. Additionally, the changes were administrative in nature, rather than substantive changes to the Cyber Response Plan. | To mitigate this issue, RFC_URE7: 1) consolidated several independent procedures that made up its Cyber Response Plan into one Cyber Response Plan. This new Cyber Response Plan corrected any deficient documentation references as well as eliminated the administrative burden of ensuring several Cyber Response Plans were updated to reflect administrative changes to referenced documents; and 2) consolidated its Cyber Response Plan with that of another registered entity following a merger. During the consolidation, RFC_URE7 removed unnecessary document references within the Cyber Response Plan, reducing any future CIP-008-3 R1.4 issues by eliminating the need for RFC_URE7 to update the Cyber Response Plan following minor changes to referenced documents.
2013-06-27 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 8 (RFC_URE8) | NCRXXXXX | RFC2012010381 | CIP-008-3 | R1 | RFC_URE8 self-certified to ReliabilityFirst that it had an issue with CIP-008-3 R1. While RFC_URE8 had a procedure for updating their Cyber Response Plans within 30 calendar days of any changes, it did not consistently implement that procedure. RFC_URE8 did not update its Cyber Response Plans within 30 calendar days on four separate occasions. Specifically, RFC_URE8 failed to change referenced procedure versions or designation numbers in its Cyber Response Plans and did not update the Standard and Requirement language within 30 calendar days of the change from version 2 to version 3 of the CIP Reliability Standards. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The issue is a documentation issue. The changes RFC_URE8 failed to update within 30 calendar days included changing referenced procedure versions or designation numbers and the Standard and Requirement wording arising from the transition from version 2 of the CIP Standards to version 3. Additionally, the changes were administrative in nature, rather than substantive changes to the Cyber Response Plan. | To mitigate this issue, RFC_URE8: 1) consolidated several independent procedures that made up its Cyber Response Plan into one Cyber Response Plan. This new Cyber Response Plan corrected any deficient documentation references as well as eliminated the administrative burden of ensuring several Cyber Response Plans were updated to reflect administrative changes to referenced documents; and 2) consolidated its Cyber Response Plan with that of another registered entity following a merger. During the consolidation, RFC_URE8 removed unnecessary document references within the Cyber Response Plan, reducing any future CIP-008-3 R1.4 issues by eliminating the need for RFC_URE8 to update the Cyber Response Plan following minor changes to referenced documents.
2013-06-27 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 9 (RFC_URE9) | NCRXXXXX | RFC2012010382 | CIP-008-3 | R1 | RFC_URE9 self-certified to ReliabilityFirst that it had an issue with CIP-008-3 R1. While RFC_URE9 had a procedure for updating their Cyber Response Plans within 30 calendar days of any changes, it did not consistently implement that procedure. RFC_URE9 did not update its Cyber Response Plans within 30 calendar days on four separate occasions. Specifically, RFC_URE9 failed to change referenced procedure versions or designation numbers in its Cyber Response Plans and did not update the Standard and Requirement language within 30 calendar days of the change from version 2 to version 3 of the CIP Reliability Standards. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The issue is a documentation issue. The changes RFC_URE9 failed to update within 30 calendar days included changing referenced procedure versions or designation numbers and the Standard and Requirement wording arising from the transition from version 2 of the CIP Standards to version 3. Additionally, the changes were administrative in nature, rather than substantive changes to the Cyber Response Plan. | To mitigate this issue, RFC_URE9: 1) consolidated several independent procedures that made up its Cyber Response Plan into one Cyber Response Plan. This new Cyber Response Plan corrected any deficient documentation references as well as eliminated the administrative burden of ensuring several Cyber Response Plans were updated to reflect administrative changes to referenced documents; and 2) consolidated its Cyber Response Plan with that of another registered entity following a merger. During the consolidation, RFC_URE9 removed unnecessary document references within the Cyber Response Plan, reducing any future CIP-008-3 R1.4 issues by eliminating the need for RFC_URE9 to update the Cyber Response Plan following minor changes to referenced documents.
2013-06-27 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 10 (RFC_URE10) | NCRXXXXX | RFC2012010383 | CIP-008-3 | R1 | RFC_URE10 self-certified to ReliabilityFirst that it had an issue with CIP-008-3 R1. While RFC_URE10 had a procedure for updating their Cyber Response Plans within 30 calendar days of any changes, it did not consistently implement that procedure. RFC_URE10 did not update its Cyber Response Plans within 30 calendar days on four separate occasions. Specifically, RFC_URE10 failed to change referenced procedure versions or designation numbers in its Cyber Response Plans and did not update the Standard and Requirement language within 30 calendar days of the change from version 2 to version 3 of the CIP Reliability Standards. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The issue is a documentation issue. The changes RFC_URE10 failed to update within 30 calendar days included changing referenced procedure versions or designation numbers and the Standard and Requirement wording arising from the transition from version 2 of the CIP Standards to version 3. Additionally, the changes were administrative in nature, rather than substantive changes to the Cyber Response Plan. | To mitigate this issue, RFC_URE10: 1) consolidated several independent procedures that made up its Cyber Response Plan into one Cyber Response Plan. This new Cyber Response Plan corrected any deficient documentation references as well as eliminated the administrative burden of ensuring several Cyber Response Plans were updated to reflect administrative changes to referenced documents; and 2) consolidated its Cyber Response Plan with that of another registered entity following a merger. During the consolidation, RFC_URE10 removed unnecessary document references within the Cyber Response Plan, reducing any future CIP-008-3 R1.4 issues by eliminating the need for RFC_URE10 to update the Cyber Response Plan following minor changes to referenced documents.
2013-06-27 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 11 (RFC_URE11) | NCRXXXXX | RFC2012010384 | CIP-008-3 | R1 | RFC_URE11 self-certified to ReliabilityFirst that it had an issue with CIP-008-3 R1. While RFC_URE11 had a procedure for updating their Cyber Response Plans within 30 calendar days of any changes, it did not consistently implement that procedure. RFC_URE11 did not update its Cyber Response Plans within 30 calendar days on four separate occasions. Specifically, RFC_URE11 failed to change referenced procedure versions or designation numbers in its Cyber Response Plans and did not update the Standard and Requirement language within 30 calendar days of the change from version 2 to version 3 of the CIP Reliability Standards. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The issue is a documentation issue. The changes RFC_URE11 failed to update within 30 calendar days included changing referenced procedure versions or designation numbers and the Standard and Requirement wording arising from the transition from version 2 of the CIP Standards to version 3. Additionally, the changes were administrative in nature, rather than substantive changes to the Cyber Response Plan. | To mitigate this issue, RFC_URE11: 1) consolidated several independent procedures that made up its Cyber Response Plan into one Cyber Response Plan. This new Cyber Response Plan corrected any deficient documentation references as well as eliminated the administrative burden of ensuring several Cyber Response Plans were updated to reflect administrative changes to referenced documents; and 2) consolidated its Cyber Response Plan with that of another registered entity following a merger. During the consolidation, RFC_URE11 removed unnecessary document references within the Cyber Response Plan, reducing any future CIP-008-3 R1.4 issues by eliminating the need for RFC_URE11 to update the Cyber Response Plan following minor changes to referenced documents.
2013-06-27 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 12 (RFC_URE12) | NCRXXXXX | RFC2012011286 | CIP-001-1a | R2 | During a Compliance Audit, ReliabilityFirst discovered that RFC_URE12 had an issue with CIP-001-1a R2. RFC_URE12 failed to have procedures for the communication of information concerning sabotage events to appropriate parties in the Interconnection. RFC_URE12 provided a safety manual procedure for emergency response, but the document’s emergency contact list did not include appropriate contacts for the Interconnection. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk to the BPS was mitigated by the fact that RFC_URE12 had a procedure in place for responding to suspected or actual sabotage events, including a list of contacts for reporting such events, although this list did not include appropriate parties in the Interconnection. The contact list contained names of various people within the RFC_URE12 organization, county sheriff, Federal Bureau of Investigation, local hospital, gas pipeline contacts, environmental agencies, and other state and federal contacts. | To mitigate this issue, RFC_URE12 updated its safety manual procedure to include telephone numbers for contacting the appropriate parties in the Interconnection concerning sabotage events.
2013-06-27 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 12 (RFC_URE12) | NCRXXXXX | RFC2012011287 | CIP-001-1a | R3 | During a Compliance Audit, ReliabilityFirst discovered that RFC_URE12 had an issue with CIP-001-1a R3. Although RFC_URE12 had sabotage response guidelines on file, RFC_URE12 could not provide evidence that changes to the guidelines were made available to operating personnel. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk to the BPS was mitigated by the fact that RFC_URE12 had developed a sabotage response guidelines. In addition, RFC_URE12 held meetings, during which possible sabotage incidents may be discussed, indicating some awareness of these guidelines by personnel. | To mitigate this issue, RFC_URE12 trained plant personnel on changes to its sabotage response procedure, including changes to the contact list for reporting sabotage events.
2013-06-27 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 13 (RFC_URE13) | NCRXXXXX | RFC2012010914 | CIP-006-3c | R2; R2.2 | RFC_URE13 submitted a Self-Report stating it had an issue with CIP-006-3c R2 to ReliabilityFirst. RFC_URE13 granted a contractor authorized cyber access to a Cyber Asset that authorizes and/or logs access to the Physical Security Perimeter (PSP) so that that contractor could restart the system if it froze and required restarting. The access did not include anything beyond restarting the system. RFC_URE13; however, failed to conduct a personnel risk assessment (PRA) for the contractor prior to granting access, as required by CIP-004-3 R3. RFC_URE13 discovered this issue within seven days of granting access and removed access that day. RFC_URE13 submitted a Self-Report to ReliabilityFirst identifying an additional occurrence of an issue with CIP-006-3c R2 related to CIP-004-3 R3. RFC_URE13 granted three contractors authorized cyber access to its physical access control system, which constitutes a Cyber Asset that authorizes and/or logs access to the PSP. RFC_URE13; however, failed to conduct a PRA for the contractors prior to granting access, as required by CIP-004-3 R3. RFC_URE13 discovered this issue within four days of granting access and removed access that day. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Regarding both occurrences, RFC_URE13's internal controls enabled RFC_URE13 to discover and remediate the issues quickly. Regarding the first occurrence, the first contractor only had access to restart the device and could not perform other functions. Had the contractor restarted the device, logging and monitoring would have remained intact. Regarding the second occurrence, the three contractors were unaware of their access rights to the physical access control system. The three contractors had access in order to support databases not related to the physical access control system. RFC_URE13 database administrators with appropriate access controlled the physical access control system and assigned work to the database administrators unrelated to the physical access control system. As a result, it was unlikely that the contractors would gain inappropriate access. | To mitigate this issue, RFC_URE13: 1) removed the restart capability from the contractor’s group, remove all four contractors from that group, allow only the Cyber Security and critical infrastructure support department to access the Cyber Assets that authorize and/or log access to the PSP; and 2) continued the migration access granting to the Cyber Security and critical infrastructure support department which will process all access requests and require training and PRAs for individuals prior to granting access.
2013-06-27 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2013011822 | CIP-003-2 | R2 | SERC_URE1 submitted a Self-Report to SERC stating that it had an issue with CIP-003-3 R2 because it did not document the assignment of a senior manager with overall responsibility for leading and managing implementation of, and adherence to, Standards CIP-002 through CIP-009 (CIP senior manager). SERC_URE1 had a supervisor that had assumed the responsibility of the CIP senior manager. This supervisor annually approved SERC_URE1’s risk-based assessment methodology (RBAM) and resulting null lists of Critical Assets and Critical Cyber Assets (CCAs). Additionally, SERC_URE1’s cybersecurity policy identified the CIP senior manager by title, but failed to identify the individual by name and the date of designation. This is the only evidence that SERC_URE1 could provide in regards to the designation of the CIP senior manager. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although SERC_URE1 did not identify its CIP senior manager by name, title, and date of designation, SERC_URE1’s cybersecurity policy identified its CIP senior manager by title. The supervisor acting as SERC_URE1’s CIP senior manager approved SERC_URE1’s RBAM and resulting null lists for Critical Assets and CCAs. SERC_URE1 does not own or operate any Critical Assets. | To mitigate this issue, SERC_URE1: 1) revised its CIP compliance document to identify the CIP senior manager by name, title, and date of designation; 2) revised its CIP compliance document to require that any changes to the CIP senior manager must be documented within 30 calendar days of the effective date; 3) revised its CIP compliance document to allow the CIP senior manager to delegate authority for specific actions to a named delegate or delegates provided these delegations are documented in the same manner as R2.1 and R2.2, and approved by the CIP senior manager; and 4) revised its CIP compliance document to allow the CIP senior manager or delegate(s) to authorize and document any exception from the requirements of the cybersecurity policy. SERC has verified the completion of all mitigation activity.
2013-06-27 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP201000446 | CIP-002-1 | R3; R3.3 | SPPRE_URE1 submitted a Self-Report to SPP RE stating that it had an issue with CIP-002-1 R3.3 because it did not identify all of its Critical Cyber Assets (CCAs) associated with Critical Assets that support reliable operation of the Bulk Electric System (BES). SPPRE_URE1 instituted a companywide de-commissioning of all dial-up modems and routers with remote connectivity to monitoring and control devices located within its substations. Subsequently, SPPRE_URE1 discovered that three dial-up devices with remote connectivity to relays designated as Critical Assets were overlooked and not disabled. SPPRE_URE1 disabled the three devices in March 2010. The issue period was from the date the Standard became mandatory and enforceable to the date SPPRE_URE1 disabled the devices at issue. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The three dial-up devices were connected to relays for retrieving fault information only and did not control any of the associated relays. Furthermore, these devices were password-protected and located within locked control houses. Finally, the duration of the issue lasted only three months, and during that time, no events occurred that put the BPS at risk. | To mitigate the issue, SPPRE_URE1: 1) disabled the three dial-up devices; and 2) developed a three-step process to ensure that all CCAs associated with Critical Assets that support reliable operation to the BES are identified. SPP RE has verified the completion of all mitigation activity.
2013-06-27 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE2012009764 | CIP-003-1 | R4; R4.3 | During a Compliance Audit, Texas RE determined that TRE_URE1 had an issue with CIP-003-1 R4.3 because TRE_URE1 did not include within its information protection annual review process the assessment of the incidence response plan(s) as required for CIP-003-1 R4.3. Texas RE determined that the incident response plan was part of the Critical Cyber Asset (CCA) information that TRE_URE1 protected but TRE_URE1 did not perform the assessment, document the assessment results, and implement an action plan to remediate deficiencies if any, identified during an assessment of the incidence response plan. Therefore, TRE_URE1 had an issue with CIP-003-1 R4 from the date the requirement became enforceable for TRE_URE1 through the date that all mitigating activity was completed. | This issue posed a minimal risk and did not pose a serious or substantial risk to the bulk power system because TRE_URE1 stated that it performed an annual assessment of its incidence response plan. Although TRE_URE1 failed to specifically list the “incident response plan” in its annual review process document, or provide sufficient evidence of its annual assessment, TRE_URE1 stated that the incident response plan was assessed and it was protected pursuant to the rest of the protected information list. | TRE_URE1 remediated the issue with CIP-003-1 R4 by providing evidence that TRE_URE1’s information protection annual review process has been updated to include the annual assessment of the incident response plan. Texas RE verified completion of all mitigation activity.
2013-06-27 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE2012009768 | CIP-005-1 | R4; R4.4 | During a Compliance Audit, Texas RE determined that TRE_URE1 had an issue with CIP-005-1 R4.4 because TRE_URE1 did not perform a complete cyber vulnerability assessment (CVA) for the electronic access points to the ESP. Specifically, TRE_URE1 failed to demonstrate that it had reviewed and implemented the network management community strings on all identified electronic access points. Therefore, TRE_URE1 had an issue with CIP-005-1 R4.4 from the date the requirement became enforceable for TRE_URE1, through the date that all mitigating activity was completed. | This issue posed a minimal risk and did not pose a serious or substantial risk to the bulk power system (BPS). The risk to reliability of the BPS was mitigated because while TRE_URE1 did not complete a review of controls for network management community strings, TRE_URE1’s infrastructure is protected from penetration by various layers of protection that include: firewalls, group user authentication, shared account reviews, infrastructure reviews, employee training, cyber incidence detection, and electronic security perimeter and physical security perimeter access authentication. Texas RE determined that the instant issue is appropriate for FFT treatment because although TRE_URE1 has prior CIP violations, they were self-reported and occurred concurrently with the instant issue. | To mitigate this issue, TRE_URE1: 1) provided evidence that a complete CVA was performed; 2) offered supporting documentation; and 3) the CVA process was updated to remind the tester to retain all evidence of test results as a part of the CVA documentation. Texas RE has verified completion of all mitigation activity.
2013-06-27 | TRE_URE1liability Entity (TRE_URE1) | Unidentified Registered Entity 2 (TRE_URE2) | NCRXXXXX | TRE2013012122 | CIP-002-2 | R4 | On March 13, 2013, TRE_URE2 submitted a Self-Report to TRE_URE1, stating that it had an issue with CIP-002-2 R4. Specifically, TRE_URE2 did not have a senior manager or delegate sign its risk-based assessment methodology (RBAM), its list of Critical Assets, and its list of null Critical Cyber Assets (CCAs). TRE_URE2 designated one person as the senior manager. TRE_URE2’s plant manager, instead of the designated person, signed TRE_URE2’s RBAM, its list of Critical Assets, and its list of null CCAs. The plant manager had not been designated as a senior manager or delegate. TRE_URE2 designated a third person as the senior manager and the newly designated person signed and approved TRE_URE2’s RBAM, its list of Critical Assets, and its list of null CCAs. TRE_URE2 had an issue with CIP-002-2 R4 from the date the undesignated person signed the documents to the date the newly designated person signed and approved TRE_URE2's RBAM, its list of Critical Assets, and its list of null CCAs. | This issue posed a minimal risk and did not pose a serious or substantial risk to the bulk power system because from the time the plant manager signed the documents until the time the senior manager signed them TRE_URE2’s methodology did not change. Moreover, TRE_URE2 did not previously have any CCAs and does not currently have any CCAs. TRE_URE1 determined that the instant issue is appropriate for FFT treatment because it occurred around the time one TRE_URE2 affiliated company had an issue with CIP-002-1 R4, and thus is not considered a repeat violation. Also, the circumstances of the two instances of noncompliance are different. | To mitigate this issue, TRE_URE2: 1) correctly designated a senior manager; and 2) had the correctly designated senior manager sign the RBAM, its list of Critical Assets, and its list of null CCAs. To prevent re-occurrence, TRE_URE2 assigned compliance responsibility to in-house personnel rather than an outside consultant. TRE_URE2 hired a director of reliability process and compliance to improve its compliance program. TRE_URE2 updated and refined its compliance procedures for the applicable NERC standards and approving the RBAM. TRE_URE1 has verified the completion of all mitigation activity.
2013-06-27 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 3 (TRE_URE3) | NCRXXXXX | TRE2013012083 | CIP-002-2 | R4 | TRE_URE3 submitted a Self-Report to Texas RE stating that it had an issue with CIP-002-2 R4. Specifically, TRE_URE3 did not have a senior manager or delegate sign its risk-based assessment methodology (RBAM), its list of Critical Assets, and its list of null CCAs. TRE_URE3 designated one person as the senior manager. TRE_URE3’s plant manager, instead of the designated person, signed TRE_URE3’s RBAM, its list of Critical Assets, and its list of null CCAs. TRE_URE3’s plant manager had not been designated as a senior manager or delegate. TRE_URE3 designated a third person as the senior manager. TRE_URE3 had an issue with CIP-002-2 R4 from the date the undesignated person signed the documents to when the newly designated person signed and approved TRE_URE3’s RBAM, its list of Critical Assets, and its list of null CCAs. | This issue posed a minimal risk and did not pose a serious or substantial risk to the bulk power system because from the time the plant manager signed the RBAM, until the time the official delegate signed it, TRE_URE3’s methodology did not change. Moreover, TRE_URE3 did not have any CCAs and does not currently have any CCAs. Texas RE determined that the instant issue is appropriate for FFT treatment because it occurred around the time one TRE_URE2 affiliated company had an issue with CIP-002-1 R4, and thus is not considered a repeat violation. Also, the circumstances of the two instances of noncompliance are different. | To mitigate this issue, TRE_URE3: 1) correctly designated a senior manager; and 2) had the correctly designated senior manager sign the RBAM, its list of Critical Assets, and its list of null CCAs. To prevent re-occurrence TRE_URE3 assigned compliance responsibility to in-house personnel rather than an outside consultant, TRE_URE3 a director of reliability process and compliance to improve its compliance program. TRE_URE3 updated and refined its compliance procedures for the applicable NERC standards and approving the RBAM. Texas RE has verified the completion of all mitigation activity.
2013-06-27 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 4 (TRE_URE4) | NCRXXXXX | TRE201100555 | CIP-004-3 | R4; R4.1 | Following a Compliance Audit, Texas RE determined that TRE_URE4 completed quarterly reviews and maintained documentation of personnel with access to Critical Cyber Assets (CCA) and of the associated access rights for each person. However, TRE_URE4 failed to update the CCA list within seven days of any change of personnel with such access to CCA. Specifically, Texas RE determined after a review of the unescorted physical access rights list, the access control procedures, and an internal disable access order, that TRE_URE4 failed to update its CCA physical access list within seven calendar days of a contractor’s CCA access rights being terminated, as required by R4.1. TRE_URE4 had an issue with CIP-004-3 R4.1 for one day, the date the change in the contractor’s physical access rights were recorded, which was eight days after his access rights were terminated. | This issue posed a minimal risk and not a serious or substantial risk to the reliability of the bulk power system. The risk was mitigated by the short violation duration period and TRE_URE4 evidencing that the contractor’s badge was surrendered to management on his last day of employment. PSP access now requires dual authentication; badging and pin number authentication. | To mitigate this issue TRE_URE4 removed the former contractor from its CCA access list. PSP access now requires dual authentication: badging and pin number authentication. Texas RE has verified the completion of all mitigation activity.
2013-06-27 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 5 (TRE_URE5) | NCRXXXXX | TRE2012011442 | CIP-007-3a | R7; R7.2 | TRE_URE5 submitted a Self-Report to Texas RE stating that it had an issue with CIP-007-3a R7.2. Specifically, on TRE_URE5 redeployed a server analyst workstation without erasing the data storage media to prevent unauthorized retrieval of sensitive cyber security or reliability data. Rather than wiping the drive device with the prescribed tool of choice, the device was re-imaged with a standard analyst workstation image. TRE_URE5 duly erased the data storage media. The issue duration is from the date the server was placed into service, through the date the server drive was properly erased. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because: a) the Cyber Asset remained within the Physical Security Perimeter (PSP) at all times; and b) though TRE_URE5 re-imaged the system instead of securely erasing the system as required, sophisticated and difficult forensic tool and techniques would be required to retrieve any potential data left on the machine. Texas RE determined that the instant issue is appropriate for FFT treatment because none of TRE_URE5’s prior CIP-007 violations involved disposal or redeployment of Cyber Assets. | To mitigate this issue, TRE_URE5: 1) purchased software to erase the data storage media; 2) erased the data storage media; and 3) documented the change control. Texas RE has verified the completion of all mitigation activity.
2013-06-27 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2013012408 | CIP-002-3 | R4 | WECC performed a Compliance Audit of WECC_URE1’s compliance with, among other Reliability Standards, CIP-002-3 R4. According to the WECC audit team, WECC_URE1 could not show evidence of compliance with this Standard for one calendar year. During the audit, WECC_URE1 provided copies of null lists of Critical Cyber Assets (CCAs) and Critical Assets, signed and dated by a senior manager. But WECC_URE1’s risk-based assessment methodology (RBAM) had not been signed or dated. WECC_URE1 did provide evidence of compliance with the Standard for the next calendar year and provided a signed RBAM. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE1 had correctly developed null lists of its Critical Assets and CCAs and its senior manager had signed and dated the lists. Based on these actions, WECC_URE1 did not expose any Critical Assets or CCAs to a potential threat. As a compensating measure, WECC_URE1 incorporated an approval signature block for the CIP senior manager as part of its RBAM review and approval process, and for use in future RBAM criteria documentation. | To mitigate this issue, WECC_URE1: 1) provided copies of its RBAM and null lists of Critical Assets and CCAs signed and dated by a senior manager; and 2) incorporated an approval signature block for the CIP senior manager as part of its RBAM review and approval process, and for use in future RBAM criteria documentation.
2013-05-30 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2013011753 | CIP-003-3 | R2.2 | FRCC_URE1 submitted a Self-Report to FRCC stating that it had an issue with CIP-003-3 R2.2 because it failed to document the appointment of a new senior manager within 30 calendar days of the effective date after the resignation and formal removal of the previous senior manager. The issue was discovered during a self-audit by the compliance officer. The new senior manager was designated and the internal control policy document was updated eight days later. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. FRCC_URE1 does not own any Critical Assets or Critical Cyber Assets, and the issue duration was a short period of time. Furthermore, the acting senior manager during the issue period was the compliance officer who had been on staff for three years and was trained on the CIP standards. FRCC_URE1 is also a small entity. | To mitigate this issue FRCC_URE1: 1) assigned the new CIP senior manager; 2) drafted the CIP-003-3 senior manager appointment internal control policy; 3) presented the CIP-003-3 senior manager internal control policy to executives for review; 4) implemented the CIP-003-3 senior manager appointment internal control policy.
2013-05-30 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 2 (FRCC_URE2) | NCRXXXXX | FRCC2011008537 | CIP-006-1 | R1; R1.1 | FRCC conducted a Spot Check and determined that FRCC_URE2 had an issue with CIP-006-1 R1.1. Specifically, FRCC_URE2 failed to ensure that all Cyber Assets were within an identified Physical Security Perimeter (PSP). Specifically, the ethernet wiring that is an integral part of the network and thus a Critical Cyber Asset (CCA) was not protected inside a PSP and appropriate physical access control was not provided. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk to the BPS was reduced because the only exposed portion of the cabling was for a short length on either side as it exited the buildings housing the PSPs. In addition, the affected buildings are within secured facilities for which physical access is controlled by security guards along with video monitoring. | To mitigate this issue, FRCC_URE2 moved the access point for the Electronic Security Perimeter (ESP) from the main building to the safe room. This made the entire ESP and the access point within the same physical cage. FRCC has verified the completion of the mitigation activity.
2013-05-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2012009744 | CIP-004-3 | R2; R2.1 | NPCC_URE1 submitted a Self-Report to NPCC stating that it had an issue with CIP-004-3 R2.1. NPCC_URE1's site security processed a completed physical access request form for a building and grounds employee with access to Critical Cyber Assets (CCAs). The request form provided a training date which was the date the employee took NPCC_URE1’s 2011 NERC Reliability Standards awareness training. The employee had not taken NPCC_URE1's 2011 mandatory cyber security training, which is required prior to granting unescorted physical access to CCAs and is updated and provided annually to individuals with such access. The error in granting access to the Physical Security Perimeter (PSP) that contained CCAs was discovered and the employee's authorized physical access was immediately revoked by site security. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although the employee had not completed the 2011 mandatory cybersecurity training, the employee had completed this training in 2010. Also, the employee was only granted access to a single PSP and review by NPCC_URE1 security confirmed that the employee had not entered the PSP during the eight-day period he was granted access. | To mitigate this issue, NPCC_URE1: 1) conducted a review of all authorized access request forms to ensure no authorized access had been granted to other employees who had not taken the 2011 mandatory cyber security training; based on completion of the 2011 NERC Reliability Standards awareness training, and revoked immediately in such instances; and 2) issued a guidance statement to staff reaffirming the requirements of CIP-004 for applicable training that must be completed for unescorted physical access to CCAs, along with a PowerPoint training program for them to review.
2013-05-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 2 (NPCC_URE2) | NCRXXXXX | NPCC2011008006 | CIP-002-1 | R3 | NPCC_URE2 submitted a Self-Report to NPCC stating that it had an issue with CIP-002-1 R3. NPCC_URE2 did not update its list of Critical Cyber Assets (CCAs) when new devices were added within an Electronic Security Perimeter (ESP). During a four month time span, NPCC_URE2 converted remote network terminal units (NTUs) from serial communication protocol to an internet protocol (IP) routable protocol. During this process, a network switch was also added to the communication path. The NTUs were added to the CCA inventory but the network switches were not added. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The IT engineer who maintains all the network switches treated the devices as if they were all CCAs. In addition, these network switches were behind a firewall appliance that was an electronic access point for the substation ESP. | To mitigate this issue, NPCC_URE2: 1) had cybersecurity team personnel assess and inventory each CCA and validate connection diagrams; 2) moved the Cyber Asset inventory list from the spreadsheet to the change management database; 3) issued an inventory list for senior manager to approve; 4) discussed with cybersecurity team the importance of listing all assets to be connected to an ESP on the change management ticket and to update the inventory of Cyber Assets at the time of installation or connection within the ESP; and 5) validated that the cybersecurity team understood the importance of listing and updating CCAs by repeating the mitigating actions above in January 2012 and requested the security team members sign an attendance sheet listing all dates.
2013-05-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 3 (NPCC_URE3) | NCRXXXXX | NPCC2011008335 | CIP-007-1 | R4 | NPCC_URE3 submitted a Self-Report to NPCC stating that it had an issue with CIP-007-1 R4. Specifically, the operating systems on a number of Cyber Asset devices did not have anti-virus and anti-malware tools installed. NPCC_URE3 failed to submit a Technical Feasibility Exception (TFE) request for the devices. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The devices at issue reside within a Physical Security Perimeter and an Electronic Security Perimeter. In addition, the incident response plan will notify support personnel to take action in the event a device is compromised and the facility IT contact will interface with the corporate cyber incident response team providing assistance with communication and remediation. Furthermore, network isolation prevents exposure of devices to un-trusted networks, including the Internet and business network. | To mitigate this issue, NPCC_URE3 submitted an open-ended TFE which was accepted and approved by NPCC.
2013-05-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 3 (NPCC_URE3) | NCRXXXXX | NPCC2012010460 | CIP-007-1 | R3 | NPCC_URE3 submitted a Self-Report to NPCC stating that it had an issue with CIP-007-1 R3. Specifically, it could not implement a security patch management program for a number of personal computers. NPCC_URE3 failed to submit a Technical Feasibility Exception (TFE) request for the personal computers. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The devices at issue reside within a Physical Security Perimeter and an Electronic Security Perimeter. In addition, the incident response plan will notify support personnel to take action in the event a device is compromised and the facility IT contact will interface with the corporate cyber incident response team providing assistance with communication and remediation. Furthermore, network isolation prevents exposure of devices to untrusted networks, including the Internet and business network. | To mitigate this issue, NPCC_URE3 submitted an open-ended TFE which was accepted and approved by NPCC.
2013-05-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 4 (NPCC_URE4) | NCRXXXXX | NPCC2011008441 | CIP-007-1 | R4 | NPCC_URE4 submitted a Self-Report to NPCC stating that it had an issue with CIP-007-1 R4. Specifically, the operating systems on a number of devices did not have anti-virus and anti-malware tools installed. NPCC_URE4 failed to submit Technical Feasibility Exception (TFE) request for these devices. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The devices at issue reside within a Physical Security Perimeter and an Electronic Security Perimeter. In addition, the incident response plan will notify support personnel to take action in the event a device is compromised and the facility IT contact will interface with the corporate cyber incident response team providing assistance with communication and remediation. Furthermore, network isolation prevents exposure of devices to untrusted networks, including the Internet and business network. | To mitigate this issue, NPCC_URE4 submitted an open-ended TFE which was accepted and approved by NPCC.
2013-05-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 4 (NPCC_URE4) | NCRXXXXX | NPCC2012010425 | CIP-007-1 | R6 | NPCC_URE4 submitted a Self-Report to NPCC stating that it had an issue with CIP-007-1 R6. Specifically, a number of devices were not capable of generating internal logs of system events including security and authentication-related incidents. NPCC_URE4 failed to submit Technical Feasibility Exception (TFE) requests for these devices. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The devices at issue reside within a Physical Security Perimeter and an Electronic Security Perimeter. In addition, the incident response plan will notify support personnel to take action in the event a device is compromised and the facility IT contact will interface with the corporate cyber incident response team providing assistance with communication and remediation. Furthermore, network isolation prevents exposure of devices to untrusted networks, including the Internet and business network. | To mitigate this issue, NPCC_URE4 submitted an open-ended TFE which was accepted and approved by NPCC.
2013-05-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 4 (NPCC_URE4) | NCRXXXXX | NPCC2013012291 | CIP-007-1 | R5; R5.3 | During an on-site Compliance Audit, NPCC discovered that NPCC_URE4 had an issue with CIP-007-1 R5.3. Specifically, a number of devices did not have technical controls for password length, character complexity, or password change frequency. NPCC_URE4 failed to submit Technical Feasibility Exception (TFE) requests for these device. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The devices at issue are protected by the Electronic Security Perimeter and Physical Security Perimeter. Additionally, personnel risk assessments and training ensure that only vetted personnel have access to these devices. Furthermore, proprietary machine language for instructions inhibits plug-in and control by a potential hacker. | To mitigate this issue, NPCC_URE4 submitted an open-ended TFE which was accepted and approved by NPCC.
2013-05-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 5 (NPCC_URE5) | NCRXXXXX | NPCC2012010465 | CIP-007-1 | R6 | NPCC_URE5 submitted a Self-Report to NPCC stating that it had an issue with CIP-007-1 R6. Specifically, a number of devices were not capable of generating internal logs of system events including security and authentication-related incidents. NPCC_URE5 failed to submit Technical Feasibility Exception (TFE) requests for these devices. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The devices at issue reside within a Physical Security Perimeter and an Electronic Security Perimeter. In addition, the incident response plan will notify support personnel to take action in the event a device is compromised and the facility IT contact will interface with the corporate cyber incident response team providing assistance with communication and remediation. Furthermore, network isolation prevents exposure of devices to untrusted networks, including the Internet and business network. | To mitigate this issue, NPCC_URE5 submitted an open-ended TFE which was accepted and approved by NPCC.
2013-05-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 6 (NPCC_URE6) | NCRXXXXX | NPCC2012011601 | CIP-002-3 | R1; R1.1 | NPCC_URE6 submitted a Self-Report to NPCC stating that it had an issue with CIP-002-3 R1. Prior to 2012, IT personnel and previous NERC responsible personnel failed to document its risk-based assessment methodology (RBAM) for Critical Assets. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). NPCC_URE6 conducted the required assessments to determine whether it had Critical Assets since it was registered, but failed to document its findings. Upon realization, NPCC_URE6 completed a documented RBAM. NPCC_URE6 has no Critical Assets and does not own or operate any facilities that would meet any of the Critical Asset criteria set forth in CIP-002-3. | To mitigate this issue, NPCC_URE6 completed and documented a RBAM for Critical Assets.
2013-05-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 6 (NPCC_URE6) | NCRXXXXX | NPCC2012011602 | CIP-002-3 | R2 | NPCC_URE6 submitted a Self-Report to NPCC stating that it had an issue with CIP-002-3 R2. Prior to 2012, IT personnel and previous NERC responsible personnel failed to document its risk-based assessment methodology (RBAM) for Critical Assets. Therefore, NPCC_URE6 did not develop a list of its identified Critical Assets through an annual application of the RBAM as required by CIP-002-3 R2. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). NPCC_URE6 conducted the required assessments to determine whether it had Critical Assets since it was registered, but failed to document its findings. Upon realization, NPCC_URE6 completed a documented RBAM. NPCC_URE6 has no Critical Assets and does not own or operate any facilities that would meet any of the Critical Asset criteria set forth in CIP-002-3. | To mitigate this issue, NPCC_URE6 completed and documented a RBAM for Critical Assets.
2013-05-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 6 (NPCC_URE6) | NCRXXXXX | NPCC2012011604 | CIP-002-3 | R4 | NPCC_URE6 submitted a Self-Report to NPCC stating that it had an issue with CIP-002-3 R1. Prior to 2012, IT personnel and previous NERC responsible personnel failed to document its risk-based assessment methodology (RBAM) for Critical Assets. Therefore, NPCC_URE6 did not have annual approval of the RBAM by senior management or delegate(s) pursuant to CIP-002-3 R4. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). NPCC_URE6 conducted the required assessments to determine whether it had Critical Assets since it was registered, but failed to document its findings. Upon realization, NPCC_URE6 completed a documented RBAM. NPCC_URE6 has no Critical Assets and does not own or operate any facilities that would meet any of the Critical Asset criteria set forth in CIP-002-3. | To mitigate this issue, NPCC_URE6 completed and documented a RBAM for Critical Assets.
2013-05-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 7 (NPCC_URE7) | NCRXXXXX | NPCC2012011605 | CIP-002-3 | R1; R1.1 | NPCC_URE7 submitted a Self-Report to NPCC stating that it had an issue with CIP-002-3 R1. Prior to 2012, IT personnel and previous NERC responsible personnel failed to document its risk-based assessment methodology (RBAM) for Critical Assets. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). NPCC_URE7 conducted the required assessments to determine whether it had Critical Assets since it was registered, but failed to document its findings. Upon realization, NPCC_URE7 completed a documented RBAM. NPCC_URE7 has no Critical Assets and does not own or operate any facilities that would meet any of the Critical Asset criteria set forth in CIP-002-3. | To mitigate this issue, NPCC_URE7 completed and documented a RBAM for Critical Assets.
2013-05-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 7 (NPCC_URE7) | NCRXXXXX | NPCC2012011606 | CIP-002-3 | R2 | NPCC_URE7 submitted a Self-Report to NPCC stating that it had an issue with CIP-002-3 R1. Prior to 2012, IT personnel and previous NERC responsible personnel failed to document its risk-based assessment methodology (RBAM) for Critical Assets. Therefore, NPCC_URE7 did not develop a list of its identified Critical Assets through an annual application of the RBAM as required by CIP-002-3 R2. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). NPCC_URE7 conducted the required assessments to determine whether it had Critical Assets since it was registered, but failed to document its findings. Upon realization, NPCC_URE7 completed a documented RBAM. NPCC_URE7 has no Critical Assets and does not own or operate any facilities that would meet any of the Critical Asset criteria set forth in CIP-002-3. | To mitigate this issue, NPCC_URE7 completed and documented a RBAM for Critical Assets.
2013-05-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 7 (NPCC_URE7) | NCRXXXXX | NPCC2012011608 | CIP-002-3 | R4 | NPCC_URE7 submitted a Self-Report to NPCC stating that it had an issue with CIP-002-3 R1. Prior to 2012, IT personnel and previous NERC responsible personnel failed to document its risk-based assessment methodology (RBAM) for Critical Assets. Therefore, NPCC_URE7 did not have annual approval of the RBAM by senior management or delegate(s) pursuant to CIP-002-3 R4. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). NPCC_URE7 conducted the required assessments to determine whether it had Critical Assets since it was registered, but failed to document its findings. Upon realization, NPCC_URE7 completed a documented RBAM. NPCC_URE7 has no Critical Assets and does not own or operate any facilities that would meet any of the Critical Asset criteria set forth in CIP-002-3. | To mitigate this issue, NPCC_URE7 completed and documented a RBAM for Critical Assets.
2013-05-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 8 (NPCC_URE8) | NCRXXXXX | NPCC2012011609 | CIP-002-3 | R1, R1.1 | NPCC_URE8 submitted a Self-Report to NPCC stating that it had an issue with CIP-002-3 R1. Prior to 2012, IT personnel and previous NERC responsible personnel failed to document its risk-based assessment methodology (RBAM) for Critical Assets. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). NPCC_URE8 conducted the required assessments to determine whether it had Critical Assets since it was registered, but failed to document its findings. Upon realization, NPCC_URE8 completed a documented RBAM. NPCC_URE8 has no Critical Assets and does not own or operate any facilities that would meet any of the Critical Asset criteria set forth in CIP-002-3. | To mitigate this issue, NPCC_URE8 completed and documented a RBAM for Critical Assets.
2013-05-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 8 (NPCC_URE8) | NCRXXXXX | NPCC2012011610 | CIP-002-3 | R2 | NPCC_URE8 submitted a Self-Report to NPCC stating that it had an issue with CIP-002-3 R1. Prior to 2012, IT personnel and previous NERC responsible personnel failed to document its risk-based assessment methodology (RBAM) for Critical Assets. NPCC_URE8 did not develop a list of its identified Critical Assets through an annual application of the RBAM as required by CIP-002-3 R2. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). NPCC_URE8 conducted the required assessments to determine whether it had Critical Assets since it was registered, but failed to document its findings. Upon realization, NPCC_URE8 completed a documented RBAM. NPCC_URE8 has no Critical Assets and does not own or operate any facilities that would meet any of the Critical Asset criteria set forth in CIP-002-3. | To mitigate this issue, NPCC_URE8 completed and documented a RBAM for Critical Assets.
2013-05-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 8 (NPCC_URE8) | NCRXXXXX | NPCC2012011612 | CIP-002-3 | R4 | NPCC_URE8 submitted a Self-Report to NPCC stating that it had an issue with CIP-002-3 R1. Prior to 2012, IT personnel and previous NERC responsible personnel failed to document its risk-based assessment methodology (RBAM) for Critical Assets. Therefore, NPCC_URE8 did not have annual approval of the RBAM by senior management or delegate(s) pursuant to CIP-002-3 R4. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). NPCC_URE8 conducted the required assessments to determine whether it had Critical Assets since it was registered, but failed to document its findings. Upon realization, NPCC_URE8 completed a documented RBAM. NPCC_URE8 has no Critical Assets and does not own or operate any facilities that would meet any of the Critical Asset criteria set forth in CIP-002-3. | To mitigate this issue, NPCC_URE8 completed and documented a RBAM for Critical Assets.
2013-05-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 9 (NPCC_URE9) | NCRXXXXX | NPCC2012011621 | CIP-002-3 | R1, R1.1 | NPCC_URE9 submitted a Self-Report to NPCC stating that it had an issue with CIP-002-3 R1. Prior to 2012, IT personnel and previous NERC responsible personnel failed to document its risk-based assessment methodology (RBAM) for Critical Assets. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). NPCC_URE9 conducted the required assessments to determine whether it had Critical Assets since it was registered, but failed to document its findings. Upon realization, NPCC_URE9 completed a documented RBAM. NPCC_URE9 has no Critical Assets and does not own or operate any facilities that would meet any of the Critical Asset criteria set forth in CIP-002-3. | To mitigate this issue, NPCC_URE9 completed and documented a RBAM for Critical Assets.
2013-05-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 9 (NPCC_URE9) | NCRXXXXX | NPCC2012011622 | CIP-002-3 | R2 | NPCC_URE9 submitted a Self-Report to NPCC stating that it had an issue with CIP-002-3 R1. Prior to 2012, IT personnel and previous NERC responsible personnel failed to document its risk-based assessment methodology (RBAM) for Critical Assets. Therefore, NPCC_URE9 did not develop a list of its identified Critical Assets through an annual application of the RBAM as required by CIP-002-3 R2. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). NPCC_URE9 conducted the required assessments to determine whether it had Critical Assets since it was registered, but failed to document its findings. Upon realization, NPCC_URE9 completed a documented RBAM. NPCC_URE9 has no Critical Assets and does not own or operate any facilities that would meet any of the Critical Asset criteria set forth in CIP-002-3. | To mitigate this issue, NPCC_URE9 completed and documented a RBAM for Critical Assets.
2013-05-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 9 (NPCC_URE9) | NCRXXXXX | NPCC2012011624 | CIP-002-3 | R4 | NPCC_URE9 submitted a Self-Report to NPCC stating that it had an issue with CIP-002-3 R1. Prior to 2012, IT personnel and previous NERC responsible personnel failed to document its risk-based assessment methodology (RBAM) for Critical Assets. Therefore, NPCC_URE9 did not have annual approval of the RBAM by senior management or delegate(s) pursuant to CIP-002-3 R4. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). NPCC_URE9 conducted the required assessments to determine whether it had Critical Assets since it was registered, but failed to document its findings. Upon realization, NPCC_URE9 completed a documented RBAM. NPCC_URE9 has no Critical Assets and does not own or operate any facilities that would meet any of the Critical Asset criteria set forth in CIP-002-3. | To mitigate this issue, NPCC_URE9 completed and documented a RBAM for Critical Assets.
2013-05-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 10 (NPCC_URE10) | NCRXXXXX | NPCC2012011613 | CIP-002-3 | R1; R1.1 | NPCC_URE10 submitted a Self-Report to NPCC stating that it had an issue with CIP-002-3 R1. Prior to 2012, IT personnel and previous NERC responsible personnel failed to document its risk-based assessment methodology (RBAM) for Critical Assets. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). NPCC_URE10 conducted the required assessments to determine whether it had Critical Assets since it was registered, but failed to document its findings. Upon realization, NPCC_URE10 completed a documented RBAM. NPCC_URE10 has no Critical Assets and does not own or operate any facilities that would meet any of the Critical Asset criteria set forth in CIP-002-3. | To mitigate this issue, NPCC_URE10 completed and documented a RBAM for Critical Assets.
2013-05-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 10 (NPCC_URE10) | NCRXXXXX | NPCC2012011614 | CIP-002-3 | R2 | NPCC_URE10 submitted a Self-Report to NPCC stating that it had an issue with CIP-002-3 R1. Prior to 2012, IT personnel and previous NERC responsible personnel failed to document its risk-based assessment methodology (RBAM) for Critical Assets. Therefore, NPCC_URE10 did not develop a list of its identified Critical Assets through an annual application of the RBAM as required by CIP-002-3 R2. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). NPCC_URE10 conducted the required assessments to determine whether it had Critical Assets since it was registered, but failed to document its findings. Upon realization, NPCC_URE10 completed a documented RBAM. NPCC_URE10 has no Critical Assets and does not own or operate any facilities that would meet any of the Critical Asset criteria set forth in CIP-002-3. | To mitigate this issue, NPCC_URE10 completed and documented a RBAM for Critical Assets.
2013-05-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 10 (NPCC_URE10) | NCRXXXXX | NPCC2012011616 | CIP-002-3 | R4 | NPCC_URE10 submitted a Self-Report to NPCC stating that it had an issue with CIP-002-3 R1. Prior to 2012, IT personnel and previous NERC responsible personnel failed to document its risk-based assessment methodology (RBAM) for Critical Assets. Therefore, NPCC_URE10 did not have annual approval of the RBAM by senior management or delegate(s) pursuant to CIP-002-3 R4. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). NPCC_URE10 conducted the required assessments to determine whether it had Critical Assets since it was registered, but failed to document its findings. Upon realization, NPCC_URE10 completed a documented RBAM. NPCC_URE10 has no Critical Assets and does not own or operate any facilities that would meet any of the Critical Asset criteria set forth in CIP-002-3. | To mitigate this issue, NPCC_URE10 completed and documented a RBAM for Critical Assets.
2013-05-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 11 (NPCC_URE11) | NCRXXXXX | NPCC2012011617 | CIP-002-3 | R1, R1.1 | NPCC_URE11 submitted a Self-Report to NPCC stating that it had an issue with CIP-002-3 R1. Prior to 2012, IT personnel and previous NERC responsible personnel failed to document its risk-based assessment methodology (RBAM) for Critical Assets. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). NPCC_URE11 conducted the required assessments to determine whether it had Critical Assets since it was registered, but failed to document its findings. Upon realization, NPCC_URE11 completed a documented RBAM. NPCC_URE11 has no Critical Assets and does not own or operate any facilities that would meet any of the Critical Asset criteria set forth in CIP-002-3. | To mitigate this issue, NPCC_URE11 completed and documented a RBAM for Critical Assets.
2013-05-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 11 (NPCC_URE11) | NCRXXXXX | NPCC2012011618 | CIP-002-3 | R2 | NPCC_URE11 submitted a Self-Report to NPCC stating that it had an issue with CIP-002-3 R1. Prior to 2012, IT personnel and previous NERC responsible personnel failed to document its risk-based assessment methodology (RBAM) for Critical Assets. Therefore, NPCC_URE11 did not develop a list of its identified Critical Assets through an annual application of the RBAM as required by CIP-002-3 R2. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). NPCC_URE11 conducted the required assessments to determine whether it had Critical Assets since it was registered, but failed to document its findings. Upon realization, NPCC_URE11 completed a documented RBAM. NPCC_URE11 has no Critical Assets and does not own or operate any facilities that would meet any of the Critical Asset criteria set forth in CIP-002-3. | To mitigate this issue, NPCC_URE11 completed and documented a RBAM for Critical Assets.
2013-05-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 11 (NPCC_URE11) | NCRXXXXX | NPCC2012011620 | CIP-002-3 | R4 | NPCC_URE11 submitted a Self-Report to NPCC stating that it had an issue with CIP-002-3 R1. Prior to 2012, IT personnel and previous NERC responsible personnel failed to document its risk-based assessment methodology (RBAM) for Critical Assets. Therefore, NPCC_URE11 did not have annual approval of the RBAM by senior management or delegate(s) pursuant to CIP-002-3 R4. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). NPCC_URE11 conducted the required assessments to determine whether it had Critical Assets since it was registered, but failed to document its findings. Upon realization, NPCC_URE11 completed a documented RBAM. NPCC_URE11 has no Critical Assets and does not own or operate any facilities that would meet any of the Critical Asset criteria set forth in CIP-002-3. | To mitigate this issue, NPCC_URE11 completed and documented a RBAM for Critical Assets.
2013-05-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2013012124 | CIP-003-1 | R2; R2.1 | RFC_URE1 submitted a Self-Report to ReliabilityFirst stating that it had an issue with CIP-003-1 R2.1. RFC_URE1 did not have a separate specific document that identified the CIP senior manager by name, title, and date of designation for one year. A RFC_URE1 senior manager was acting as the senior manager delegate in the duration of the issue, and that senior manager approved the Critical Asset assessments and the lists of Critical Assets and Critical Cyber Assets. While the former CIP senior manager is no longer the CIP senior manager, the individual maintains a position with RFC_URE1 as the director of technical operations for an affiliate company. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The issue was limited to documentation, was of a short duration, and concerned an individual that remains a trusted employee of an affiliate company. | To mitigate this issue, RFC_URE1: 1) conducted a review of its CIP procedure; 2) maintains a current and accurate designation of senior manager letter stored in the electronic document management program for document retention; 3) created a task activity in the electronic data tracking system that will generate an annual reminder to review senior manager assignments; and 4) utilizes a managerial transition checklist when a change in senior management occurs within 30 days to assign a new senior manager.
2013-05-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2013011664 | CIP-006-3c | R2.2 | RFC_URE2 submitted a Self-Report to ReliabilityFirst stating that it had an issue with CIP-004-3 R3. ReliabilityFirst subsequently determined that the facts and circumstances of this Self-Report constituted an issue of CIP-006-3c R2.2 because on RFC_URE2 mistakenly granted authorized cyber access to Physical Access Control System servers, Cyber Assets that authorize and/or log access to the Physical Security Perimeter, to the supervisor that approved the access request instead of the employee who required such access. RFC_URE2 discovered the issue through a routine, periodic user access review, and the next day revoked the supervisor’s access. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The individual at issue is a long-time employee. RFC_URE2 provides separate access grants to the operating system, database, and application for its assets. In order to modify, view physical access control data, application configuration, and or database elements, RFC_URE2 must grant either the database level access or application level access. Operating system level access does not afford change/view privilege. RFC_URE2 confirmed that the supervisor had not logged into the servers during the time period of the issue, and the supervisor did not attempt such access. | To mitigate this issue, RFC_URE2: 1) revoked the supervisor’s access and reviewed the security logs from the servers to determine whether the supervisor had accessed the servers; 2) confirmed that the supervisor had not logged into the servers during the time period of the issue, and the supervisor did not attempt such access; and 3) defined and implemented a new access role that is limited to the Physical Access Control System servers and changed the business unit responsible for provisioning access to the servers to the information security – identity and access management group.
2013-05-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC201100872 | CIP-005-1 | R1; R1.4; R1.6 | RFC_URE3 self-certified to ReliabilityFirst that it had an issue with CIP-005-1 R1. RFC_URE3 had not identified or protected several non-critical Cyber Assets located within the Electronic Security Perimeter (ESP) pursuant to CIP-005-1 R1.4. The non-critical Cyber Assets at issue consist of non-essential devices associated with plant monitoring and printers or print servers. RFC_URE3 also did not maintain documentation for certain Critical Cyber Assets (CCAs) and non-critical Cyber Assets pursuant to CIP-005-1 R1.6. First, RFC_URE3 did not document each interconnected CCA and non-critical Cyber Asset located in ESPs on its ESP network diagrams. Second, RFC_URE3 did not timely submit Technical Feasibility Exception (TFE) requests for several assets as required by Appendix 4D to NERC’s Rules of Procedure. The non-critical Cyber Assets and CCAs at issue with CIP-005-1 R1.6 consist of non-critical Cyber Assets associated with plant monitoring CCAs associated with plant monitoring, a GPS clock, and a printer. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. First, firewalls surrounding the non-critical Cyber Assets at issue were programmed to deny general interactive access to the non-critical Cyber Assets. Second, RFC_URE3's parent company's information technology group monitored and alarmed the firewalls surrounding the non-critical Cyber Assets at issue for authorized and unauthorized access attempts. Third, the non-critical Cyber Assets and CCAs at issue are not located within a system control center, but rather within generation plant Physical Security Perimeters (PSPs) accessible only by escorted individuals or those individuals with valid personnel risk assessments and prior CIP training. Fourth, RFC_URE3 afforded the non-critical Cyber Assets the protective measures specified in the applicable requirements of CIP-003, with the exception of R6, CIP-004, CIP-006, and CIP-008. Fifth, the issue with CIP-005-1 R1.6 is a documentation issue. During the duration of the issue, RFC_URE3 provided the required protections to the CCAs and non-critical Cyber Assets that it had not documented on its ESP network diagrams. Additionally, for the duration of the issue, RFC_URE3 provided the CCAs with the protections described in its TFE requests. The TFE requests addressed CIP-007 requirements. The protections described in the TFE requests included: containing the devices within an ESP and a six-wall PSP that are only accessible by personnel trained and subject to background checks; installing anti-virus software, where possible, to protect against malware; two factor authentication; and port mapping. ReliabilityFirst accepted and approved each of the TFE requests for the CCAs at issue. | To mitigate this issue, RFC_URE3: 1) identified and protected all non-critical Cyber Assets located within the ESP pursuant to CIP-005-1, R1.4; and 2) maintained documentation for all CCAs and non-critical CCAs pursuant to CIP-005-1 R1.6. ReliabilityFirst verified that RFC_URE3 completed all necessary mitigating activities.
2013-05-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 4 (RFC_URE4) | NCRXXXXX | RFC2013012070 | CIP-006-3c | R1; R1.4 | RFC_URE4 submitted a Self-Report to ReliabilityFirst stating that it had an issue with CIP-006-3c R1.4. An employee used a key, intended for emergency use only, to enter a physical security perimeter (PSP) for which the employee was not authorized. The employee’s supervisor had directed the employee to enter the PSP to switch a line into service in anticipation of the arrival of a major weather event. By using the key to enter the PSP, the employee bypassed normal access controls and actuated an alarm. Security personnel investigated the alarm and required the employee to leave the PSP when they determined the employee was not authorized to enter the PSP. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The employee at issue was a long time RFC_URE4 parent company employee with a valid personnel risk assessment (PRA) at the time of the issue. Additionally, RFC_URE4's security personnel detected the improper entry into the PSP and escorted the employee out of the PSP within 15 minutes of entry. Finally, the human performance error which caused this issue was precipitated by the impending arrival of the major weather event. In order to expedite RFC_URE4's switching of the line into service prior to the arrival of the weather event, the employee’s supervisor selected the next available individual without validating the employee’s CIP authorization to that specific substation. | To mitigate this issue, RFC_URE4: 1) conducted CIP training and granted access to enter substation PSPs for the employee at issue; and 2) conducted CIP training, completed PRAs and granted access to enter substation PSPs for other employees who perform similar duties as the employee at issue.
2013-05-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 5 (RFC_URE5) | NCRXXXXX | RFC2012010355 | CIP-008-3 | R1 | RFC_URE5 self-certified to ReliabilityFirst that it had an issue with CIP-008-3 R1. While RFC_URE5 had a procedure for updating its Cyber Response Plans within 30 calendar days of any changes, it did not consistently implement that procedure. RFC_URE5 did not update its Cyber Response Plans within 30 calendar days on several occasions. Specifically, RFC_URE5 failed to change referenced procedure versions or designation numbers in their Cyber Response Plans and did not update the Standard and Requirement language within 30 calendar days of the change from version 2 to version 3 of the CIP Reliability Standards. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The issue is a documentation issue. The changes RFC_URE5 failed to update within 30 calendar days included changing referenced procedure versions or designation numbers and the Standard and Requirement wording arising from the transition from version 2 of the CIP Standards to version 3. Additionally, the changes were administrative in nature, rather than substantive changes to the Cyber Response Plan. | To mitigate this issue, RFC_URE5: 1) consolidated several independent procedures that made up its Cyber Response Plan into one Cyber Response Plan. This new Cyber Response Plan corrected any deficient documentation references as well as eliminated the administrative burden of ensuring several Cyber Response Plans were updated to reflect administrative changes to referenced documents; and 2) consolidated RFC_URE5's Cyber Response Plan with that of another registered entity following a merger. During the consolidation, RFC_URE5 removed unnecessary document references within the Cyber Response Plan to reduce any future CIP-008-3 R1.4 issues by eliminating the need for RFC_URE5 to update the Cyber Response Plan following minor changes to referenced documents.
2013-05-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 6 (RFC_URE6) | NCRXXXXX | RFC2013012074 | CIP-004-3a | R3 | RFC_URE6 submitted a Self-Report to ReliabilityFirst stating that it had an issue with CIP-004-3a. RFC_URE6 granted a vendor without a valid personnel risk assessment (PRA) cyber access to a Critical Cyber Asset (CCA). RFC_URE6 held an information and training program for an Electronic Access Control and Monitoring System. An authorized RFC_URE6 employee logged into a shared account and then turned navigation over to the vendor so the vendor could perform a demonstration. The vendor did not have a valid PRA. For one hour, the vendor navigated in the production environment of the security information and event management application, a CCA, through the shared account. As a result, RFC_URE6 granted the vendor authorized cyber access without conducting a PRA. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The individual at issue was an employee from a trusted vendor with whom RFC_URE6 has confidentiality and non-disclosure agreements in place. The demonstration was done for RFC_URE6 employees with authorized cyber access and a business need to know. These employees had appropriate training and valid PRAs. | To mitigate this issue, RFC_URE6: 1) conducted a training session for the management, which included RFC_URE6’s current CIP access and PRA approval process as well as the NERC project 2009-26 Interpretation of CIP-004-3; and 2) performed a review of all vendors’ PRA documentation and non-disclosure agreements.
2013-05-30 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2012011426 | CIP-002-3 | R2 | Five months after receiving an initial notice of a Compliance Audit, SERC_URE1 submitted a Self-Report to SERC stating that it had an issue with CIP-002-3 R2 because it did not have evidence of the annual application of the risked-based assessment methodology (RBAM) to develop a list of its identified Critical Assets for one year. SERC_URE1 had applied its RBAM annually before and after the missed year to develop its list of identified Critical Assets. SERC_URE1 determined that it had no Critical Assets in each of those years. SERC confirmed that SERC_URE1 could not provide evidence it applied its RBAM to develop its list of Critical Assets for one year. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC_URE1 had applied its RBAM annually before and after the missed year and did not identify any Critical Assets. SERC_URE1 has no Critical Assets and does not own or operate any facilities that would meet any of the Critical Asset criteria set forth in CIP-002-4. | To mitigate this issue, SERC_URE1: 1) incorporated the best practice of making an electronic copy of all CIP related submittals and documents and will save the compliance-related records within an electronic document retention program; 2) entered relevant CIP-002 activities into a corporate managed monitoring database, which will automatically send annual reminders to the CIP senior manager or delegate(s) to review, update as necessary, and approve SERC_URE1's RBAM, list of Critical Assets, and list of Critical Cyber Assets; and 3) hired a full time environmental and regulatory compliance manager, responsible for the development, planning, implementation, and maintenance of an effective facility compliance program. SERC has verified the completion of all mitigation activity.
2013-05-30 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2013011923 | CIP-002-3 | R4 | During a scheduled Compliance Audit, the SERC audit team reported that SERC_URE1 had an issue with CIP-002-3 R4 because it failed to annually approve the risk based assessment methodology (RBAM), list of Critical Assets and list of Critical Cyber Assets (CCAs) for one year. After further assessment, SERC determined that SERC_URE1 did not annually approve its RBAM, Critical Asset list, and CCA list for two years. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC_URE1 had applied its RBAM annually before and after the missed year and did not identify any Critical Assets. SERC_URE1 has no Critical Assets and does not own or operate any facilities that would meet any of the Critical Asset criteria set forth in CIP-002-4. | To mitigate this issue, SERC_URE1: 1) incorporated the best practice of making an electronic copy of all CIP related submittals and documents and will save the compliance-related records within an electronic document retention program; 2) entered relevant CIP-002 activities into a corporate managed monitoring database, which will automatically send annual reminders to the CIP senior manager or delegate(s) to review, update as necessary, and approve SERC_URE1's RBAM, list of Critical Assets, and list of Critical Cyber Assets; and 3) hired a full time environmental and regulatory compliance manager, responsible for the development, planning, implementation, and maintenance of an effective facility compliance program. SERC has verified the completion of all mitigation activity.
2013-05-30 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2013011924 | CIP-003-1 | R2 | During a scheduled Compliance Audit, the SERC audit team reported that SERC_URE1 had an issue with CIP-003-3 R2 because it failed to identify the CIP senior manager by name, title and date of designation prior to the enforceable period. SERC_URE1 failed to properly assign a senior manager as of the date the Standard became mandatory and enforceable for SERC_URE1. Instead, SERC_URE1’s parent company delegated power to and authorized SERC_URE1’s manager to sign any documentation required to establish compliance with NERC Reliability Standards. This delegation failed to identify the manager by name and only included the title of the manager and date of delegation. SERC also determined that SERC_URE1 changed the individual authorized to sign documentation required to establish compliance with NERC Reliability Standards but failed to document that change within 30 calendar days, and instead took 43 days to document the change. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC_URE1’s parent company authorized the manager to sign any documentation required to establish compliance with NERC Reliability Standards. SERC_URE1 was 13 days late in documenting the change to the individual authorized to sign documentation required to established compliance with NERC Reliability Standards. SERC_URE1 has no Critical Assets and does not own or operate any facilities that would meet any of the Critical Asset criteria set forth in CIP-002-4. | To mitigate this issue, SERC_URE1: 1) produced a document that properly designates a single CIP senior manager; 2) created a key managerial transition checklist to review in the event that a key manager, including the CIP senior manager, leaves the company, in order to delegate such a manager's duties to other employees as necessary until a suitable replacement can be found; and 3) entered relevant CIP-003 activities into a corporate managed monitoring database, which will automatically send an annual reminder to the CIP senior manager and any delegate(s) to assign a CIP senior manager and identify that individual pursuant to CIP-003, document changes to the CIP senior manager within 30 calendar days, document any delegations of authority, and authorize and document any exceptions to SERC_URE1's cybersecurity policy. SERC has verified the completion of all mitigation activity.
2013-05-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2013012175 | CIP-003-1 | R4 | During a CIP Compliance Audit of SPPRE_URE1, the Audit Team found that SPPRE_URE1 had an issue with CIP-003-1 R4. SPPRE_URE1 had not classified as confidential its recovery plan for its physical access control system, its response plan, and its corporate procedure for all incident reporting and responding, as required by its information protection program. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although SPPRE_URE1 had failed to mark the three documents in accordance with its information protection program, SPPRE_URE1 did closely control access to these documents. The electronic versions of these confidential documents were username and password protected, secured within SPPRE_URE1’s Electronic Security Perimeter, and available to only those with approved access. The hardcopies of these confidential documents were protected behind access-controlled doors. | To mitigate this issue, SPPRE_URE1 marked its physical access control system recovery plan, response plan, and corporate procedure for all incident reporting and responding as confidential. As a preventative measure, SPPRE_URE1 changed its procedures to ensure electronic file names are classified “confidential” if the actual document cannot be marked. SPP RE has verified the completion of all mitigation activity.
2013-05-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2013012183 | CIP-007-3 | R5.3; R5.3.1; R5.3.2; and R5.3.3 | During a CIP Compliance Audit of SPPRE_URE1, the Audit Team found that URE1 had an issue with CIP-007-3 R5.3. SPPRE_URE1’s administrator account for its storage area network (SAN) could not technically enforce the password complexities required in R5.3.1, R5.3.2, and R5.3.3. SPPRE_URE1 did not request a Technical Feasibility Exception (TFE) for the subject account. Additionally, through the course of mitigating this issue, SPPRE_URE1 noted that three other devices, two network switches within its primary energy management system (EMS) and one network switch within its backup EMS, could not technically enforce the password complexities required in R5.3.1, R5.3.2, and R5.3.3. Similarly, SPPRE_URE1 had not requested a TFE for these devices. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. URE1’s SAN administrator account and network switches were accessible only locally, no remote access possible, and used by authorized staff to manage the device. Furthermore, these devices did have password protection despite the fact that they did not have the ability to enforce the required password complexities. Finally, the SAN device and the network switches were protected within a CIP Physical Security Perimeter. | To mitigate this issue, SPPRE_URE1 filed two TFEs to exclude the SAN devices and network switches from enforcing the password complexity requirements. SPPRE_URE1’s TFE’s compensating measures, which have already been implemented, include randomly generating passwords through a program capable of enforcing the password complexities of CIP-007-3 R5.3.1 and R5.3.2, and manually inputting those generated passwords into the excluded devices, and manually changing passwords on affected devices at least annually. SPP RE has verified the completion of all mitigation activity.
2013-05-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2013012179 | CIP-006-1 | R3 | During a CIP Audit of SPPRE_URE1, the Audit Team found that URE1 had an issue with CIP-006-1 R3 because SPPRE_URE1 did not have documented its technical and procedural controls that were implemented for monitoring of physical access at all access points to its Physical Security Perimeters (PSPs). | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although URE1 did not document its technical and procedural controls for monitoring physical access to all access points to its PSP, the SPP RE Audit Team determined that SPPRE_URE1 sufficiently monitored physical access to its PSPs. SPPRE_URE1’s PSPs were afforded the protective measures of CIP-006-1 R3. SPPRE_URE1 had alarm contacts on its doors to alert on forced and held door-related events; alarms on its door controller panel boxes to alert anytime the panel door was opened; and a physical access control system alarm to alert on unauthorized badge access attempts. This issue was documentation-related. | SPPRE_URE1 revised its physical security program to include its implemented procedural controls for monitoring physical access at all access points to its PSPs. SPP RE verified that all mitigating activities were completed.
2013-05-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPPRE_URE2) | NCRXXXXX | SPP2012010239 | CIP-003-3 | R4 | During a CIP Compliance Audit of SPP_URE2, SPP RE found that SPP_URE2 had an issue with CIP-003-3 R4. SPP_URE2 did not protect Critical Cyber Asset (CCA) information in accordance with its documented CIP information protection program (Program). Specifically, SPP_URE2’s Program requires CCA information to be encrypted if transmitted externally. SPP_URE2 transmitted externally 10 hard drives which contained unencrypted CCA information. Because SPP_URE2 did not encrypt the CCA information on the hard drives prior to transmitting it externally, SPP_URE2 did not protect its CCA information in accordance with its Program and CIP-003-3 R4. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SPP_URE2 attested that the host files from all 10 hard drives were deleted prior to transmitting them for destruction. By deleting the host files, had the 10 hard drives been intercepted by a third party, no CIP protected information would have been accessible without the use of special software to recover the information. This was the only occurrence SPP_URE2 used a carrier to transfer hard drives from one facility to another. | To mitigate this issue, SPP_URE2: 1) updated its Program by clarifying language addressing the encryption of CCA information transmitted externally; and 2) acquired degaussers, a process that erases data, to aid in destroying electronic CIP information on hard drives, at its facility. SPP RE has verified the completion of all mitigation activity.
2013-05-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 3 (SPPRE_URE3) | NCRXXXXX | SPP2012011100 | CIP-005-3 | R4; R4.2; R4.3 | During a Compliance Audit of SPP_URE3, SPP RE determined that SPP_URE3 had an issue with CIP-005-1 R4. SPP_URE3’s cyber vulnerability assessment (CVA) was insufficient to ensure the discovery of all access points to the Electronic Security Perimeter (ESP), as required by CIP-005-1 R4.3. Also, the CVA was insufficient to ensure that the ports and services enabled on one asset, an internal network switch, were required for operations in accordance with CIP-005-1 R4.2. Regarding R4.3, the SPP_URE3 networks were scanned from within the ESP and externally from the Internet to discover all access points. However, the CVA team did not perform a secondary physical inspection of network wiring to identify any access points not identified in the network scans. Additionally, SPP_URE3 did not designate one internal network switch as an electronic access point. Regarding R4.2, SPP_URE3 did not verify that the network switch’s enabled ports and services were required for operations. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SPP_URE3’s CVA involved a review of the SPP_URE3 network topology and included network mapping/vulnerability scanning, which identified all externally communicating network access points (gateways), but SPP_URE3 failed to identify one internal network switch access point. The internal network switch resided on an isolated network segment and only served as a connection point for one remote workstation that communicated with the ESP via a virtual private network (VPN) tunnel. A user at the remote workstation is required to supply a physical token, username, and password before a VPN session can be established, and the session can only be established via the remote workstation. The enabled ports and services on the remote workstation were reviewed as part of the CVA and were subsequently determined to be necessary for operations. The port and service hardening of the remote workstation in combination with the requirement to establish a VPN session between the workstation and ESP firewall negated the risk presented by the lack of a review of ports and services on the network switch. Moreover, any communications passing from the remote workstation through the ESP firewall would have been inspected by the SPP_URE3 ESP firewall anti-virus and the ESP intrusion prevention system. | To mitigate this issue, SPP_URE3: 1) conducted a CVA that included a physical inspection of all network equipment and devices within the ESP to ensure the discovery of all access points to the ESP; and 2) decommissioned the isolated workstation that was communicating remotely via the implicated switch, thereby eliminating the switch as an access point. SPP RE has verified the completion of all mitigation activity.
2013-05-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 4 (SPPRE_URE4) | NCRXXXXX | SPP2012010962 | CIP-007-1 | R6; R6.1 | During a CIP Compliance Audit of SPP_URE4, the Audit Team found that SPP_URE4 had an issue with CIP-007-1 R6. SPP_URE4 had not implemented automated tools or organizational process controls to monitor system events that relate to cyber security for all Cyber Assets within its Electronic Security Perimeter (ESP). Specifically, 21.4% of supervisory control and data acquisition (SCADA) network switches, which monitor system events related to cyber security, were not configured to send automated log messages to a SPP_URE4's server. The syslog server is configured to send alerts to operating personnel for emergent security events across SPP_URE4’s ESP. Two of the three switches are located in SPP_URE4’s back-up control center and one switch is located in SPP_URE4’s primary control center. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The three switches involved, which are not Critical Cyber Assets and which are housed within a physical security perimeter, connect a SPP_URE4 control center and back-up control center to switches at SPP_URE4’s primary and back-up control centers (Control Center Switches). The Control Center Switches were properly configured for logging security events in accordance with CIP-007 R6. Therefore, the syslog server still would have alerted operating personnel of any cyber security incidents that occurred on traffic between the three switches and the Control Center Switches. Furthermore, SPP_URE4’s primary control center had one switch, Switch A, which was properly configured to send logs to the syslog server. Finally, SPP_URE4 had an intrusion detection system that monitors the ESP network for malicious activities and produces reports to personnel in a security management station. | To mitigate this issue, SPP_URE4: 1) modified the configurations of the three SCADA network switches so that they will be monitored and have the capability to send automated log messages to the syslog server; and 2) modified its cyber vulnerability assessment procedures to include a review of Cyber Assets to ensure that log messages from the three switches are sent to syslog servers.
2013-05-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 4 (SPPRE_URE4) | NCRXXXXX | SPP2012010878 | CIP-006-3c | R1; R1.6.2 | SPP_URE4 submitted a Self-Report stating that it had an issue with CIP-006-3c R1.6.2 for failing to provide continuous escorted access for two visitors within its Physical Security Perimeter (PSP). The two visitors, which were maintenance personnel, entered a secured conference room within a SPP_URE4 control center PSP without an escort as an SPP_URE4 employee was leaving the conference room. The visitors remained in the secured area for nine minutes while changing the filters on the heating, ventilation, and air conditioning system, and then exited the conference room. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although the conference room is within SPP_URE4’s control center PSP, the room does not have any Critical Cyber Assets (CCAs) and is separated by controlled access, e.g., magnetically locked doors with card key access and automated alarms, from the control center. Had the visitors attempted to access the control center, an alarm would have been sent to SPP_URE4 security personnel to investigate. Additionally, SPP_URE4’s control center is manned by operators twenty-four hours a day, seven days a week. Had the visitors gained access to the control center, control center operators would have observed the unauthorized visitors and immediately escorted them out of the secured area. SPP_URE4 confirmed that the visitors did not attempt to enter the control center. | SPP_URE4 verbally counseled the visitors to ensure their understanding of SPP_URE4’s escorting procedures. Additionally, SPP_URE4 retrained all affected personnel with authorized physical access to CCAs on the escorting procedures. SPP RE verified that all mitigating activities were completed.
2013-05-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 5 (SPPRE_URE5) | NCRXXXXX | SPP2013011796 | CIP-003-1 | R6 | SPPRE_URE5 submitted a Self-Report stating that it had an issue with CIP-003-1 R6. SPPRE_URE5 did not follow its documented change control and configuration management process for adding, modifying, replacing, or removing Critical Cyber Asset (CCA) hardware or software. Specifically, SPPRE_URE5’s change control and configuration management process designated a SPPRE_URE5 director as the approver for changes to CCAs. However in the tracking system for such changes a SPPRE_URE5 senior engineer approved changes made to its CCAs. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although SPPRE_URE5’s senior engineer was not designated to approve changes per SPPRE_URE5’s documented process for change control and configuration management, it was determined that the changes to CCAs approved by the senior engineer would have been approved in the same manner by SPPRE_URE5’s director. | To mitigate this issue, SPPRE_URE5 changed the designated approver in the tracking system to the designated approver in SPPRE_URE5’s documented process for change control and configuration management to ensure that the director was approving all changes to its CCAs. SPP RE has verified the completion of all mitigation activity.
2013-05-30 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE2012009903 | CIP-002-1 | R1.2.1 | Texas RE conducted an Audit of TRE_URE1 and determined that TRE_URE1 had an issue with Reliability Standard CIP-002-1 R1.2.1. TRE_URE1 did not consider and evaluate control centers and backup control centers performing the functions of the entities listed in the Applicability section of this Standard under its risk-based assessment methodology (RBAM). As of the applicability date for CIP-002-1, TRE_URE1’s RBAM did not include consideration for a third-party control center that was performing some of TRE_URE1's day-ahead schedules and real-time communications. The issue period lasted for about two years and two months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the bulk power system. Although TRE_URE1 failed to include a third-party control center in its RBAM, this control center was not considered a Critical Asset. During the issue period, TRE_URE1 had not identified any Critical Assets or Critical Cyber Assets (CCAs) through the application of its RBAM for the remainder of its system. After TRE_URE1 did include this control center in its RBAM, TRE_URE1 re-performed the application of its RBAM, and still did not identify any Critical Assets or CCAs, confirming that this control center was not critical or in need of Critical Asset or CCA status throughout the issue period. The third-party control center is used as a communications medium between the generation unit and other entities and does not perform any of the operations related to the generation unit. | To mitigate this issue, TRE_URE1: 1) submitted its updated RBAM to Texas RE, which included a consideration of TRE_URE1's third-party control center; 2) re-performed its RBAM and did not identify any Critical Assets or CCAs at this generation station or any of its assets; 3) developed a new procedure intended to ensure that all assets are considered and evaluated when performing its RBAM. This measure was developed in order to directly reduce the risk of recurrence of this violation. Texas RE has verified the completion of all mitigation activity.
2013-05-30 | TRE_URE1liability Entity (TRE_URE1) | Unidentified Registered Entity 2 (TRE_URE2) | NCRXXXXX | TRE2012010027 | CIP-002-1 | R2 | TRE_URE1 performed an Audit of TRE_URE2 and determined that TRE_URE2 failed to correctly apply its risk-based assessment methodology (RBAM) in accordance with Reliability Standard CIP-002-1 R2. First, when applying its RBAM, TRE_URE2 failed to consider the control centers and backup control centers of its contractor. Second, TRE_URE2's original Critical Asset list incorrectly identified the plant control room as a Critical Asset. The control room should not have been placed on the list for about two years. | This issue posed a minimal risk and did not pose a serious or substantial risk to the bulk power system. TRE_URE2 later considered the control centers and backup control centers of its contractor and TRE_URE2 determined that it had no additional CAs. TRE_URE2 had properly identified the other CAs on its CA list at the time of the issue. The third-party control center contractor is used as a communications medium between the generation unit and other entities and does not perform any of the operations related to the generation unit. Additionally, TRE_URE2 has only one generating asset that contributes a small amount of generation to the system. | To mitigate this issue, TRE_URE2: 1) correctly considered the third-party contractor the control centers and backup control centers; and 2) correctly applied its RBAM; TRE_URE1 has verified the completion of all mitigation activity.
2013-05-30 | TRE_URE1liability Entity (TRE_URE1) | Unidentified Registered Entity 2 (TRE_URE2) | NCRXXXXX | TRE2012010030 | CIP-002-1 | R3 | TRE_URE1 conducted an Audit of TRE_URE2, and determined that TRE_URE2 did not properly identify its Critical Cyber Assets (CCA) in accordance with Reliability Standard CIP-002-1 R3. For about two years, TRE_URE2 included in its list of CCAs several assets that were critical to the operation of two TRE_URE2 Critical Assets. However, these assets did not use a routable protocol to communicate outside the Electronic Security Perimeter, did not use a routable protocol within a control center, or were not dial-up accessible. Therefore, those assets did not meet the requirements of a CCA to be identified under CIP-002-1 R3, and should not have been included in TRE_URE2’s list of CCAs. | This issue posed a minimal risk and did not pose a serious or substantial risk to the bulk power system because TRE_URE2 did not have any CCAs once TRE_URE2 correctly developed its list. TRE_URE2 had properly identified the other CAs on its CA list at the time of the issue. The third-party control center contractor is used as a communications medium between the generation unit and other entities and does not perform any of the operations related to the generation unit. Additionally, TRE_URE2 is only one generating asset that contributes a small amount of generation to the system. | To mitigate this issue, TRE_URE2 correctly identified that it had no CCAs. TRE_URE1 has verified the completion of all mitigation activity.
2013-05-30 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 3 (TRE_URE3) | NCRXXXXX | TRE2012009737 | CIP-005-3a | R5.3 | On TRE_URE3 submitted a Self-Report to Texas RE, stating that it had an issue with CIP-005-3a R5.3. TRE_URE3 did not retain electronic access logs for 90 calendar days. TRE_URE3's Energy Management System (EMS) administrator discovered that the logging for one firewall in the Electronic Security Perimeter (ESP) for the new control center was incorrectly configured when installed. This resulted in no logs being retained for that device for about one month. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because all systems are behind a firewall that only allows the ports and services that are required for the system to function. All systems inside the ESP were logged for access during the time period of this issue. TRE_URE3 has stated that there were no incidents of unauthorized access attempts. | To mitigate this issue, TRE_URE3 EMS staff corrected the firewall configuration to send logs and installed a new application server at the backup control center, which will significantly reduce the likelihood of logs being lost in the future. Logs for the firewall are now being retained as required. Texas RE has verified the completion of all mitigation activity.
2013-05-30 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 3 (TRE_URE3) | NCRXXXXX | TRE2012011385 | CIP-006-3c | R7 | TRE_URE3 submitted a Self-Report to Texas RE stating that it had an issue with CIP-006-3c R7. TRE_URE3 discovered that the Physical Security Perimeter (PSP) access logs for approximately eight hours for one day were missing. Therefore, the TRE_URE3 failed to retain physical access logs for at least 90 calendar days as required by CIP-006-3c R7. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because TRE_URE3 identified no evidence of a cyber attack or physical intrusion related to the missing logs. Furthermore, access badges continued to work as expected during the pendency of the issue, protecting the security of TRE_URE3 Critical Cyber Assets. | To mitigate this issue, TRE_URE3 installed new software, including an upgraded version of the archival database for the logging system. Texas RE has verified the completion of all mitigation activity.
2013-05-30 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 4 (TRE_URE4) | NCRXXXXX | TRE2012010554 | CIP-005-1 | R1 | During a Compliance Audit of TRE_URE4, Texas RE determined that TRE_URE4 had an issue with CIP-005-1 R. TRE_URE4 misidentified access points to the Electronic Security Perimeter (ESP). For these access points, TRE_URE4 erroneously identified systems having external programmatic access to the ESP which were termed “highlighted cloud bubbles” or “clouds.” The clouds did not go to the perimeter of the ESP. They went to the firewall. Therefore, TRE_URE4 did not identify access points to the perimeter of the ESP. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because although TRE_URE4’s documentation misidentified the access point in one case and did not label the access point in another, TRE_URE4 understood and treated the firewall controlling electronic access to the ESP as the de facto access point. TRE_URE4 treated the de facto access point as the access point, but did not document it as the access point pursuant to CIP-005 R1. | To mitigate this issue, TRE_URE4: 1) revised its process document to appropriately identify the access point; and 2) updated its network diagram, adding an access point label. Texas RE has verified the completion of all mitigation activity.
2013-05-30 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 5 (TRE_URE5) | NCRXXXXX | TRE201100558 | CIP-006-1 | R1 | After an Audit, Texas RE determined that TRE_URE5 created a physical security plan but failed to show approval by the designated senior manager or delegate(s) for its physical security plan Version 2. A review of the evidence shows that neither the senior manager nor the delegate signed the physical plan, representing a failure to approve the plan by the designated CIP senior manager or delegate. Specifically, the plan was reviewed and signed by a TRE_URE5's officer and the delegate’s direct manager, even though neither was the assigned delegate. The issue was resolved when the next year's physical security plan Version 3 was reviewed and approved by the designated authority in the fall. TRE_URE5 had an issue with CIP-006-1 R1 for about one year and eight months. | This issue posed a minimal and not a serious or substantial risk to the reliability of the bulk power system (BPS). TRE_URE5’s physical security plan has been reviewed by the delegated personnel on an annual basis and has been in effect since the Standard became enforceable. The absence of the expected signature was attributed to a misinterpretation of the signature block title, not an indication that the plan was not approved or reviewed. Texas RE determined that the instant issue is appropriate for FFT treatment because TRE_URE5 identified and mitigated the issue before the Audit commenced. | To mitigate this issue, TRE_URE5 provided documentation showing that the delegated signatory signed Version 3 of the physical security plan. Texas RE verified completion of all mitigation activity.
2013-05-30 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 6 (TRE_URE6) | NCRXXXXX | TRE2012010294 | CIP-005-1 | R4.2, R4.3, R4.4 | During an Audit, TRE_URE6 reported that its diagnostic cyber vulnerability assessment (CVA) data was not accessible because the file containing the data was corrupted and not recoverable. Therefore, TRE_URE6, had an issue with CIP-005-1 R4. In response to this information loss, TRE_URE6 provided internal correspondence showing requests for data to validate that the CVA was conducted, responses to those requests, and work orders used to track time associated with acquiring the appropriate data. TRE_URE6 was able to construct a logical picture from internal correspondence showing that its CVA process and resulting documented assessment was systematically acquired and disseminated to the appropriate parties, which enabled TRE_URE6 to reach the conclusions presented in its CVA assessment. The associated process documents defining TRE_URE6’s approach to conducting CVAs were in accordance with CIP-005-1 R4.1, and the results produced from the CVA were also in accordance with CIP-005-1 R4.5. However, TRE_URE6 failed to provide evidence that a review of ports and services required for operations, discovery of all access points to the Electronic Security Perimeter (ESP), and a review of controls for default accounts, passwords, and network management community strings was performed. Therefore, Texas RE determined that TRE_URE6 had an issue with CIP-005-1 R4.2, R4.3, and R4.4 for about one year. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). TRE_URE6 performed its CVA, implemented a layered approach to protecting its Cyber Assets that included firewalls, group user authentication, shared account reviews, infrastructure reviews, employee training, cyber incidence detection, and ESP and Physical Security Perimeter (PSP) access authentication. In addition, TRE_URE6 improved security by adding third-party assessments to facilitate hardening of its protection scheme. TRE_URE6 also provided evidence that missing data from the corrupted CVA assessment was requested and delivered to the appropriate TRE_URE6 parties. A review of evidence shows that TRE_URE6 followed procedures and performed a review resulting in changes to its network to close ports discovered open on oen of its servers. TRE_URE6 supplied the work order generated to correct the network deficiencies discovered from the CVA. This layered protection was partially based on the information collected in response to the lost CVA diagnostic data. | To mitigate this issue, TRE_URE6 hired a third-party vendor to perform CVAs and retain the results for historical access. All future TRE_URE6 CVAs will be performed by this method. Texas RE verified completion of all mitigation activity.
2013-05-30 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 6 (TRE_URE6) | NCRXXXXX | TRE2012010296 | CIP-007-1 | R8.2, R8.3 | During an Audit that concluded on May 11, 2012, TRE_URE6 reported that its diagnostic cyber vulnerability assessment (CVA) data was not accessible because the file containing the data was corrupted and not recoverable. Therefore, TRE_URE6, had an issue with CIP-007-1 R8. In response to this information loss, TRE_URE6 provided internal correspondence showing requests for data to validate that the CVA was conducted, responses to those requests, and work orders used to track time associated with acquiring the appropriate data. TRE_URE6 was able to construct a logical picture from internal correspondence that its CVA process and resulting documented assessment was systematically acquired and disseminated to the appropriate parties, which enabled TRE_URE6 to reach the conclusions presented in its CVA assessment. The associated process documents defining TRE_URE6’s approach to conducting CVAs were in accordance with CIP-007-1 R8.1, and the results produced from the CVA were also in accordance with CIP-007-1 R8.4. However, TRE_URE6 failed to provide evidence that a review of ports and services required for operations of Cyber Assets and a review of controls for default accounts was performed. Therefore, Texas RE determined that TRE_URE6 had an issue with CIP-007-1 R8.2 and R8.3 for a period of one year. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). TRE_URE6 implemented a layered approach to protecting its Cyber Assets that includes firewalls, group user authentication, shared account reviews, infrastructure reviews, employee training, cyber incidence detection, and Electronic Security Perimeter (ESP) and Physical Security Perimeter (PSP) access authentication. In addition, TRE_URE6 has improved security by adding third-party assessments to facilitate hardening of its protection scheme. TRE_URE6 also provided evidence that missing data from the corrupted CVA assessment was requested and delivered to the appropriate TRE_URE6 parties. A review of evidence shows that TRE_URE6 followed procedures and performed a review of the CVA. As a result, TRE_URE6 implemented changes to harden its network through tightening access privileges and ensuring identified vulnerabilities were patched. TRE_URE6 supplied the work order generated to correct the network deficiencies discovered during the CVA. | To mitigate this issue, TRE_URE6 hired a third-party vendor to perform CVAs and retain the results for historical access. All future TRE_URE6 CVAs will be performed by this method. Texas RE verified completion of all mitigation activity.
2013-05-30 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 7 (TRE_URE7) | NCRXXXXX | TRE201100481 | CIP-007-1 | R6; R6.4; R6.5 | TRE_URE7 submitted a Self-Report stating that it did not retain logs for 43 of its Cyber Assets within the Electronic Security Perimeter (ESP) for 90 calendar days as required by CIP-007-1 R6.4. Upon further review, TRE_URE7 also determined that required logs on domain controllers were not retained. Additionally, TRE_URE7 discovered that some of its devices were collecting logs but that those logs failed to contain all events as required by TRE_URE7’s company procedure. TRE_URE7’s investigation showed that the failure to retain logs was caused by (1) a failure of an application process to transmit the logs of system events to the designated repository; (2) lack of accessibility to system event logs for certain devices; and (3) limited storage space available in each affected Cyber Asset to maintain the required logs. In addition, as part of that same self-assessment, TRE_URE7 discovered that for 50 of its devices, it failed to review certain logs of system events and to maintain documentation of all reviews related to cybersecurity as required by CIP-007-1 R6.5. The failure to conduct the review of the logs was caused by a failure to appropriately execute the review process. Therefore, TRE_URE7 had an issue with CIP-007-1 R6 for about two years and a half. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Although logging and documentation of log reviews were not maintained, alerts were being generated by the firewalls and intrusion detection system equipment, and those alerts were investigated. Those alerts were automated and performed in real-time. The results of those investigations were documented. At no time during the pendency of this issue, did TRE_URE7 experience a system event that presented a risk to the BPS. TRE_URE7’s real-time alerting from firewalls and intrusion detection systems supports TRE_URE7’s ability to detect security related events and take corrective action before a 90-day log review is required by the Standard. | TRE_URE7’s investigation found the root cause to be that employees did not have a clear understanding of their responsibilities and accountability for the review of event logs. TRE_URE7 has taken several steps to prevent or minimize the probability of incurring further issues of the same or similar Standard, including adding a director of internal audit to the functional organization responsible for this area, and reorganizing the group responsible for implementation of CIP-007 to provide added focus to the tactical responsibilities of CIP implementation, enhancing the log review procedure to provide clear responsibilities and accountability for event log review, and taking appropriate actions with employees through the performance review process. To mitigate this issue, TRE_URE7: 1) verified log collection for all Cyber Assets within the EPS; 2) performed reviews required by TRE_URE7’s log review procedures; 3) established Mitigation Plan team; 4) reviewed TRE_URE7’s existing applicable procedures; 5) investigated logging capabilities of storage area network devices; 6) conducted compliance procedure refresher training; 7) installed log transmittal alerting that monitors the connection between log collectors and their associated repositories; and 8) implemented new network equipment log collector process. Texas RE verified completion of all mitigation activity.
2013-05-30 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 8 (TRE_URE8) | NCRXXXXX | TRE201100548 | CIP-007-2a | R3 | TRE_URE10 self-certified that it had procedures and personal performance goals in place for conducting a 30-day assessments of security patches, which requires responsible employees to capture evidence. However, the employees responsible did not capture evidence for all of the assessments. Therefore, TRE_URE8 did not have sufficient documented evidence to show all assessments of security patches were performed within 30 days of availability from the vendor(s). This issue lasted about four months and a half. | This issue posed a minimal risk and did not pose a serious or substantial risk to the bulk power system because TRE_URE8 had several layers of mitigating and compensating measures. First, TRE_URE8 performed but did not document the assessments at issue. Second, the systems at issue are non-critical Cyber Assets that do not reside within the same Electronic Security Perimeter as Cyber Assets performing real-time control center functions. Third, several layers of compensating measures were in place including: a) electronic access was controlled via five means, including authentication services; b) physical access was protected via biometric controls; c) automated electronic processes for log monitoring and collection were in place where technically feasible – no issues were noted; d) electronic intrusion detection systems were in place; e) the operating systems were securely configured to protect against unauthorized access; and f) antivirus and antimalware software was installed. | TRE_URE8 assessed and documented evidence to show all assessments of security patches were performed within 30 days of availability. Texas RE has verified the mitigation activities as complete.
2013-05-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2013011962 | CIP-005-3 | R1; R1.5 | WECC issued WECC_URE1 a Notice of Compliance Audit indicating WECC would conduct an onsite Compliance Audit. The WECC Audit Team conducted onsite interviews with WECC_URE1 Subject Matter Experts (SMEs). During the course of one interview WECC_URE1 disclosed that it had failed to ensure one Cyber Asset used in the access control and/or monitoring (ACM) was afforded the protections described in CIP-007-3 R6.2, as required under CIP-005-3 R1.5. Specifically, WECC_URE1 reported that it failed to ensure the device was configured to issue automated or manual alerts for detected cybersecurity incidents. The device was logging events, but the events were not configured to alert appropriate personnel. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The scope of the violation is limited to a single ACM device. The ACM device is a console works log management server used to monitor and log access to an ESP. Although the device did, in fact, log and monitor access, it was not configured to issue automated alerts signaling a cybersecurity incident. WECC_URE1 electronically secured the ESP with other protections in place during the duration of the issue. WECC_URE1 provided 17 out of 18 protections required under R1.5 to the device. WECC_URE1 restricted electronic and physical access to the device. WECC_URE1 located the device within a Physical Security Perimeter (PSP). Individuals with access to the device had completed personnel risk assessments. Individuals with access were listed pursuant to CIP-004-3 R4. WECC_URE1 staff reviewed the access lists on a quarterly basis. WECC_URE1 logged and monitored all electronic access through the device. Unauthorized electronic access attempts would have been detected and triggered alarms. Only ports and services required for operations and for monitoring Cyber Assets within the ESP were enabled. The device was equipped with antivirus software and malicious software prevention tools. WECC_URE1 restricted electronic access to the ESP using passwords. Further, given “layered” security approach adopted by WECC_URE1, cybersecurity events within the ESP would have been detected and triggered alarming by other Cyber Assets within the ESP. | To mitigate this issue WECC_URE1 reconfigured the device to ensure that automated alerts were issued in the event of a cybersecurity incident.
2013-05-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2013012037 | CIP-004-3 | R3; R3.2 | WECC_URE2 submitted s Self-Certification to WECC stating that it had an issue with CIP-004-3 R3. Specifically, WECC_URE2 reported that it failed to update a personnel risk assessment (PRA) for a single employee after the initial PRA performed seven years earlier. The employee’s PRA was updated approximately 18 months after it was due for completion. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The individual previously completed a PRA and is an employee in good standing. The individual was and is up-to-date with cybersecurity training. The individual in scope of the issue maintained physical access to Critical Cyber Assets (CCAs) associated with a single substation. Physical access to the CCAs was monitored on a 24 hours a day, seven days a week basis by security personnel using a live video feed. WECC_URE2 logged physical access was logged through a card reader and associated database. | To mitigate this issue, WECC_URE2: 1) revoked the employee’s access to CCAs; 2) completed a PRA update for the employee before it reinstated the employee’s access privileges to CCAs; 3) updated its business process to ensure that all PRAs are updated within seven years; and 4) trained all WECC_URE2 employees and contractors on the updated business process to ensure that PRAs are updated within seven years.
2013-05-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2012009678 | CIP-007-3a | R6 | WECC_URE3 submitted a Self-Report to WECC stating that it had an issue with CIP-007-3 R6. Specifically, WECC_URE3 reported that it failed to implement protective measures prescribed under R6 where technically feasible, for a single Cyber Asset. WECC determined that WECC_URE3 deployed a Cyber Asset that did not have automated tools or organizational process controls to monitor system events as technically feasible as required under R6. WECC also determined that because implementation of technical measures to facilities monitoring is technically infeasible on this device, this issue stems from WECC_URE3's failure to file a timely technical feasibility exception (TFE) request. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE3 had compensating protective measures in place during the duration of the issue. The scope of the issue is limited to a single Cyber Asset. Although WECC_URE3 failed to file a timely TFE, WECC_URE3 did ensure that the device was located within an Electronic Security Perimeter, pursuant to CIP-005, wherein system events are monitored and electronic access thereto is controlled. Further the device was physically secured within a Physical Security Perimeter and afforded protections that ensure the physical security of the device. | To mitigate this issue, WECC_URE3: 1) created a database audit function for TFEs that compares the device classification, make, and model to the CIP standards and information related to previously submitted TFEs. The audit function will flag devices that should have a TFE, but have not been accounted for in previous TFE amendments; and 2) amended its previous TFE to include the device. WECC approved the TFE.
2013-05-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC2012010115 | CIP-006-1 | R1; R1.8 | WECC_URE4 submitted a Self-Report to WECC stating that it had an issue with CIP-006-1 R1. WECC conducted a Compliance Audit of WECC_URE4’s compliance with, among other Reliability Standards, CIP-006-1 R1. The Audit Team reviewed WECC_URE4’s Self-Report during its Compliance Audit. According to the Audit Team, WECC_URE4 failed to afford its Cyber Assets the protective measures in Reliability Standards CIP-007-1 R5.2.3, as well as CIP-007-1 R5.3 as required by CIP-006-1 R1.8. With respect to CIP-007-1 R5.2.3, WECC_URE4 failed to change shared accounts on its access control software when personnel changes occurred. With respect to CIP-007-1 R5.3, WECC_URE4 failed to implement technical and procedural controls by having passwords to its Physical Access Control Systems (PACS) that were sufficient in complexity, length, and frequency of password changes. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Logical access to the workstations involved and physical access to the Physical Security Perimeter was revoked when personnel changes occurred. In addition, all of WECC_URE4’s passwords are managed by its active directory server, which enforces password complexity rules and expirations. | To mitigate this issue, WECC_URE4 disabled the shared account, implemented individual user accounts, and implemented technical and procedural controls of account and password management. WECC has verified the completion of all mitigation activity.
2013-05-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC2012010267 | CIP-007-3a | R5 | WECC performed an Compliance Audit of WECC_URE4’s compliance with, among other Reliability Standards, CIP-007-3 R5. According to the Audit Team, WECC_URE4 failed to provide evidence that it changed its passwords for its admin/shared/services accounts for one calendar year. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. As compensating measures, the accounts are not accessible outside a Physical Security Perimeter or an Electronic Security Perimeter. Thus, WECC_URE4 monitors and logs access to these accounts and only authorized WECC_URE4 personnel can gain access to the accounts. In action, the accounts are afforded the physical and electronic protections specified in CIP-005 and CIP-006. | To mitigate this issue, WECC_URE4 later produced evidence that it had changed its passwords for the previous calendar year and developed a new process for ensuring that all passwords are changed annually. WECC has verified the completion of all mitigation activity.
2013-05-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 5 (WECC_URE5) | NCRXXXXX | WECC2013011869 | CIP-007-1 | R2; R2.3 | WECC_URE5 submitted a Self-Report to WECC stating that it had an issue with CIP-007-1 R2. Specifically, WECC_URE5 reported that it identified Cyber Assets that could not meet compliance with CIP-007-1 R2.3, but that did not have an associated technical feasibility exception (TFE). WECC_URE5 reported that although it was technically infeasible to disable unused ports or services for these devices, it failed to file a TFE. | There were a number of compensating measures in place to secure the devices against misuse or malicious attack. WECC_URE5 uses a security information and event management (SIEM) appliance to monitor system events and device event logs associated with the Cyber Assets in scope. The SIEM provides automated alerting of potential cybersecurity events associated with these devices as they occur by utilizing a display showing security events in real time. Cyber Assets are monitored 24 hours a day, seven days a week by SIEM. Further, WECC_URE5 utilizes malicious software prevention tools on all Cyber Assets associated with these devices within the Electronic Security Perimeter and Physical Access Control systems where technically feasible. In addition, WECC_URE5 submitted TFEs associated with these Cyber Assets. Although the TFEs were filed late, WECC approved all TFEs. | To mitigate this issue, WECC_URE5 filed TFEs for the devices. WECC approved the TFEs.
2013-05-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 5 (WECC_URE5) | NCRXXXXX | WECC2013011870 | CIP-007-1 | R3; R3.2 | WECC_URE5 submitted a Self-Report to WECC stating that it had an issue with CIP-007-1 R3.2. Specifically, WECC_URE5 reported that it identified Cyber Assets that could not meet compliance with CIP-007-1 R3.2, but that did not have an associated technical feasibility exception (TFE). WECC_URE5 reported that although it was technically infeasible to install security patches for these devices, it failed to file a TFE. | There were a number of compensating measures in place to secure the devices against misuse or malicious attack. WECC_URE5 uses a security information and event management (SIEM) appliance to monitor system events and device event logs associated with the Cyber Assets in scope. The SIEM provides automated alerting of potential cybersecurity events associated with these devices as they occur by utilizing a display showing security events in real time. Cyber Assets are monitored 24 hours a day, seven days a week by SIEM. Further, WECC_URE5 utilizes malicious software prevention tools on all Cyber Assets associated with these devices within the Electronic Security Perimeter and Physical Access Control systems where technically feasible. In addition, WECC_URE5 submitted TFEs associated with these Cyber Assets. Although the TFEs were filed late, WECC approved all TFEs. | To mitigate this issue, WECC_URE5 filed TFEs for the devices. WECC approved the TFEs.
2013-05-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 5 (WECC_URE5) | NCRXXXXX | WECC2013011871 | CIP-007-1 | R4 | WECC_URE5 submitted a Self-Report to WECC stating that it had an issue with CIP-007-1 R2. Specifically, WECC_URE5 reported that it identified Cyber Assets that could not meet compliance with CIP-007-1 R4, but that did not have an associated technical feasibility exception (TFE). WECC_URE5 reported that although it was technically infeasible to implement antivirus and anti malware solutions on the devices, it failed to file a TFE. | There were a number of compensating measures in place to secure the devices against misuse or malicious attack. WECC_URE5 uses a security information and event management (SIEM) appliance to monitor system events and device event logs associated with the Cyber Assets in scope. The SIEM provides automated alerting of potential cybersecurity events associated with these devices as they occur by utilizing a display showing security events in real time. Cyber Assets are monitored 24 hours a day, seven days a week by SIEM. Further, WECC_URE5 utilizes malicious software prevention tools on all Cyber Assets associated with these devices within the Electronic Security Perimeter and Physical Access Control systems where technically feasible. In addition, WECC_URE5 submitted TFEs associated with these Cyber Assets. Although the TFEs were filed late, WECC approved all TFEs. | To mitigate this issue, WECC_URE5 filed TFEs for the devices. WECC approved the TFEs.
2013-05-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 5 (WECC_URE5) | NCRXXXXX | WECC2013011873 | CIP-007-1 | R5; R5.3; R5.3.2; R5.3.3 | WECC_URE5 submitted a Self-Report to WECC stating that it had an issue with CIP-007-1 R5. Specifically, WECC_URE5 reported that it identified Cyber Assets that could not meet compliance with CIP-007-1 R5, but that did not have an associated technical feasibility exception (TFE). WECC_URE5 reported that although it was technically infeasible to enforce the use of strong passwords, it failed to file a TFE. | There were a number of compensating measures in place to secure the devices against misuse or malicious attack. WECC_URE5 uses a security information and event management (SIEM) appliance to monitor system events and device event logs associated with the Cyber Assets in scope. The SIEM provides automated alerting of potential cybersecurity events associated with these devices as they occur by utilizing a display showing security events in real time. Cyber Assets are monitored 24 hours a day, seven days a week by SIEM. Further, WECC_URE5 utilizes malicious software prevention tools on all Cyber Assets associated with these devices within the Electronic Security Perimeter and Physical Access Control systems where technically feasible. In addition, WECC_URE5 submitted TFEs associated with these Cyber Assets. Although the TFEs were filed late, WECC approved all TFEs. | To mitigate this issue, WECC_URE5 filed TFEs for the devices. WECC approved the TFEs.
2013-05-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 5 (WECC_URE5) | NCRXXXXX | WECC2013011874 | CIP-007-1 | R6 | WECC_URE5 submitted a Self-Report to WECC stating that it had an issue with CIP-007-1 R6. Specifically, WECC_URE5 reported that it identified Cyber Assets that could not meet compliance with CIP-007-1 R6, and that did not have an associated Technical Feasibility Exception (TFE). WECC_URE5 reported that although it was technically infeasible to implement automated tools or organizational process controls to monitor system events that are related to cybersecurity, it failed to file a TFE. | There were a number of compensating measures in place to secure the devices against misuse or malicious attack. WECC_URE5 uses a security information and event management (SIEM) appliance to monitor system events and device event logs associated with the Cyber Assets in scope. The SIEM provides automated alerting of potential cybersecurity events associated with these devices as they occur by utilizing a display showing security events in real time. Cyber Assets are monitored 24 hours a day, seven days a week by SIEM. Further, WECC_URE5 utilizes malicious software prevention tools on all Cyber Assets associated with these devices within the Electronic Security Perimeter and Physical Access Control systems where technically feasible. In addition, WECC_URE5 submitted TFEs associated with these Cyber Assets. Although the TFEs were filed late, WECC approved all TFEs. | To mitigate this issue, WECC_URE5 filed TFEs for the devices. WECC approved the TFEs.
2013-04-30 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2012011576 | CIP-002-1 | R4 | During a Compliance Audit, MRO discovered that MRO_URE1 failed to maintain a signed and dated record of the senior manager or delegate's approval of its annual risk-based assessment methodology (RBAM) for a particular year. In accordance with Standard, the RBAM must be approved annually and have a signed and dated record of the approval. MRO_URE1's current RBAM was approved, signed, and dated approximately one and a half years after its previous RBAM. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The RBAM for the year at issue was approved by the senior manager and in effect, but merely lacked the required signature. The senior manager was not authorized to sign the RBAM and therefore did not do so; however, he has since been delegated the authority to sign the RBAM. | MRO_URE1 current RBAM is approved, signed and dated by the senior manager. MRO has verified the completion of all mitigation activity.
2013-04-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2012010235 | CIP-004-3 | R2; R2.3 | NPCC_URE1 self-reported an issue with CIP-004-3 R2.3. The issue was discovered during a recent review by IT Security noting that the vendor had never used his logon-ID. NPCC_URE1 identified one instance where a vendor's annual training had expired and revocation of cyber access was not completed. The vendor was a former employee who was contracted to assist in the resolution of any problems related to NPCC_URE1's energy management system (EMS). | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The issue was caused by an automated email notification system failing to make proper notifications. Prior to this incident the former employee's CIP training and personnel risk assessment (PRA) were valid. The former employee did not have physical access to any Critical Cyber Asset's and had "read only" access to one CIP application. The former employee had never used his remote access capabilities to NPCC_URE1's network or his corporate network logon ID. The former employee's responsibility as a vendor was to assist in any troubleshooting or assessment relating to NPCC_URE1's EMS. | To mitigate this issue, NPCC_URE1: 1) did not renew the former employee's contract; 2) updated its procedure to reflect management responsibilities; 3) revised its NERC CIP access management policy, to emphasize the importance of granting CIP access only to “active” employees or vendors; 4) implemented e-mail notifications from the database to IT security and systems security when required CIP training expires for an employee or a vendor; 5) issued a lessons learned document requiring "read and sign" to management who supervise personnel with unescorted CIP physical access or CIP cyber access; 6) developed a test plan that will exercise all CIP critical automated functions to be executed for any future changes impacting the person information database and the associated interfacing systems; and 7) conducted and completed a review of current IT business processes.
2013-04-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 2 (NPCC_URE2) | NCRXXXXX | NPCC2012009851 | CIP-007-1 | R2; R2.1 | NPCC conducted a Compliance Audit of NPCC_URE2. NPCC found that NPCC_URE2 had an issue with CIP-007-1 R2.1. NPCC_URE2 listed three ports for Supervisory Control and Data Acquisition (SCADA) host as "unknown" and one port was identified as "Remoteanywhere" and was unable to identify if the ports were required for normal or emergency use. It was determined that the ports were necessary for normal operations. | The issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The issue was due to a documentation oversight. The ports were enabled at the time of the Compliance Audit. The NPCC_URE2 SCADA service vendor monitors the ports and services and ensures that only ports and services necessary for normal or emergency operations are enabled. The ports are associated with the SCADA network which is isolated to the outside by a firewall. The ports reside within the Electronic Security Perimeter and can only be accessed by entering the Physical Security Perimeter with proper authorization to Critical Cyber Assets. The information associated with the ports and services contains data only which is processed through a virtual private network router that is completely disconnected under normal operations. There is no dial-up capability or control circuits associated with these ports and services that can affect BPS operations. | To mitigate this issue, NPCC_URE2; 1) identified and labeled the ports and services prior to the completion of the Compliance Audit; 2) discussed and trained the SCADA service vender on the Mitigation Plan; 3) ensured that only ports necessary for normal or emergency operations are enabled and proper identification of ports and services will be used; 4) will ensure the SCADA administrator will checks the ports and services monthly to verify no unexpected ports and services are running; and 5) will review annually the physical status of ports and services through the vulnerability assessment process.
2013-04-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 2 (NPCC_URE2) | NCRXXXXX | NPCC2012010133 | CIP-002-3 | R3 | NPCC conducted a Compliance Audit of NPCC_URE2. NPCC found that NPCC_URE2 had an issue with CIP-002-3 R3. NPCC_URE2 failed to correctly classify and update Critical Cyber Assets (CCA) servers on the approved CCA final listings. The servers provide a conversion from IP-based network traffic to serial-based protocols. | The issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The issue was administrative and due to the entity failing to correctly classify and update CCA's on the approved CCA final listings. These CCAs resided within the Electronic Security Perimeter (ESP) and were also afforded similar protections to those correctly classified CCAs also within the ESP. The servers were not identified on the CCA Summary sheet, but were identified on the NPCC_URE2 CCA assessment list. The servers process system data only and do not contain control circuits that can affect BPS operations. | To mitigate this issue, NPCC_URE2: 1) added both servers to the CCA Summary List; 2) updated the NPCC_URE2 CCA assessment sheet for better readability; and 3) convened the NPCC_URE2 CIP compliance team bi-weekly to address CIP related items and concerns that will help improve its annual vulnerability assessment process.
2013-04-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 3 (NPCC_URE3) | NCRXXXXX | NPCC2013011947 | CIP-004-3a | R2; R2.3 | NPCC_URE3 self-reported an issue with CIP-004-3a R2.3. NPCC_URE3 discovered that a retired employee did not complete his annual CIP training as a contractor. The retired employee was a former control room supervisor who was hired as a contractor responsible for training distribution operators. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The issue was caused when the company's supervisor failed to re-enroll the contractor in the CIP training program prior to the expiration date. As a former employee the contractor had taken the required CIP training several years in a row and had a current personnel risk assessment (PRA) at the time of the incident. As a contractor, he had unescorted physical access to the Physical Security Perimeter containing Critical Cyber Assets (CCA), but no electronic access to the CCAs. The contractor's function did not involve any capability to affect the operation of the BPS. | To mitigate this issue, NPCC_URE3: 1) had the contractor complete the CIP training; 2) sent an email with a follow-up weekly conference call conveying the process for enrolling both contractors and employees in training; 3) will repeat a CIP reminder of the responsibilities at a semi-annual group meeting of NERC Standards subject matter experts. A weekly conference call is part of a standing agenda item in which the subject matter experts are reminded of various CIP requirements. Each reminder is carried on the agenda for two weeks and is repeated two to three times per year; and 4) will incorporate changes as necessary to the current CIP training policy to clarify the responsibilities of the supervisors and managers.
2013-04-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 4 (NPCC_URE4) | NCRXXXXX | NPCC2012010190 | CIP-003-3 | R4.3 | NPCC auditors found that NPCC_URE4 had an issue with CIP-003-3 R4.3 because NPCC_URE4 does not conduct an annual assessment that confirms NPCC's full adherence to NPCC_URE4's cyber security plan in documenting the assessment and implementation of actions taken to correct identified deficiencies as required by the Standard. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. NPCC_URE4 did provide evidence of an annual review and adherence to information classification that documented test questions, results summary and action items to partially satisfy the Standard. | To mitigate this issue, NPCC_URE4: 1) has an information protection plan (IPP) that has been revised to replace the former assessment practices via quizzes with a new annual assessment process that includes; 2) samples documents subject to the IPP; 3) inspects document printing, copying, and scanning locations to ensure that they have signage posted as reminders of information protection and also have proper marking stamps available to mark documents; and 4) documented assessment results.
2013-04-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 4 (NPCC_URE4) | NCRXXXXX | NPCC2012010120 | CIP-004-3 | R4.1 | Prior to the beginning of a Compliance Audit, NPCC_URE4 notified the auditors of an issue with CIP-004-3 R4.1. NPCC_URE4 failed to complete a quarterly review of its list of personnel with authorized cyber or authorized unescorted physical access to Critical Cyber Assets (CCAs) on one occasion during the audit period. The quarterly review was performed three weeks late. | The issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. NPCC_URE4's access control program is to deny access by default; no access is granted without going through the proper steps. First, a request is made by the manager of the individual for access. The request must then be approved by the owner. If approved, actual access (physical or electronic) is then granted. This process mitigated the risk that personnel may have access which they should not have before the review was performed. Updates to the list were made at the review. During the gap before the review was performed, a script was run periodically by the applications support team to assist in validating that the access privileges in active directory and certain critical applications were consistent. NPCC_URE4 performed all subsequent quarterly reports as required. | To mitigate this issue, NPCC_URE4: 1) timely completed the next quarterly review of the lists of personnel with access and for the remainder of the audit period; and 2) created workflow to remind managers and other personnel responsible for granting and managing access to complete each quarterly review. The workflow is set to send reminder emails 30 days in advance of the due date and every Tuesday thereafter until the task is marked as complete. Initial implementation provided notification to individuals with a code enhancement later implemented to enable email reminders when more than one individual was assigned a task.
2013-04-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 4 (NPCC_URE4) | NCRXXXXX | NPCC2012010188 | CIP-007-3 | R2 | Prior to the beginning of a Compliance Audit, NPCC_URE4 notified the auditors of an issue with CIP-007-3 R2. NPCC_URE4 did not have documentation of ports and services for its Cyber Assets, power distribution units, and media converters, as required by the Standard. | The issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although NPCC_URE4 did not have the documentation of ports and services required by CIP-007-3 R2, it had closed unused ports and services as required by R2's sub-requirements. This issue was documentation only, and the technical controls, i.e., ports and services, were not negatively affected. | To mitigate this issue, NPCC_URE4 created a list of required ports and services for PDUs and Lantronix as well as all other cyber assets within the Electronic Security Perimeter(s) to "establish, document and implement a process to ensure that only those ports and services required for normal and emergency operations are enabled."
2013-04-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 4 (NPCC_URE4) | NCRXXXXX | NPCC2012010189 | CIP-007-3 | R5.2 | Prior to the beginning of a Compliance Audit, NPCC_URE4 had notified the auditors of an issue with CIP-007-3 R5.2. NPCC_URE4 did not have an approved, documented policy to minimize and manage the scope and acceptable use of administrator, shared, and other generic account privileges including factory default accounts as required by the Standard. | The issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Although the NPCC_URE4 did not have the policy required, it had implemented the technical controls required by CIP-007-3 R5.2.1, R5.2.2 and R5.2.3. Accordingly, this issue has minimal impact on the security of the NPCC_URE4 Cyber Assets and thus on the reliability of the BPS. | To mitigate this issue, NPCC_URE4 updated the NPCC_URE4 cyber security policy to include a policy to minimize and manage the scope and acceptable use of administrator, shared, and other generic account privileges including factory default accounts.
2013-04-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 4 (NPCC_URE4) | NCRXXXXX | NPCC2012010191 | CIP-008-3 | R1.6 | NPCC auditors found NPCC_URE4 had an issue with CIP-008-3 R1.6 because the NPCC_URE4 cyber security incident response plan did not contain any language stating their process for conducting annual tests of the plan as required by the Standard. | The issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although the NPCC_URE4 did not contain any language stating their process for conducting annual tests of the plan, NPCC_URE4 was performing and documenting annual tests of the NPCC_URE4 cyber security incident response plan. | To mitigate this issue, NPCC_URE4 updated the NPCC_URE4 cyber security incident reporting and response plan to include the process for conducting annual tests of the cyber security incident reporting and response plan.
2013-04-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 5 (NPCC_URE5) | NCRXXXXX | NPCC2012010707 | CIP-002-3 | R4 | NPCC auditors found NPCC_URE5 had an issue with CIP-002-3 R4 because the NPCC_URE5 senior manager signatory approval for both the Critical Assets and Critical Cyber Asset (CCA) listings did not occur within the allotted annual time frame. | The issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The signatory approval was late, however the review of the Critical Asset and CCA list occurred on time. | To mitigate this issue, NPCC_URE5: 1) completed the signatory approval of the NPCC_URE5 Critical Asset and CCA lists; and 2. created workflow to remind CIP senior manager to review, approve, sign, and date the Critical Asset and CCA lists within the annual timeframe.
2013-04-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 6 (NPCC_URE6) | NCRXXXXX | NPCC2012010062 | CIP-006-3c | R1; R1.6 | NPCC_URE6 self-reported an issue with CIP-006-3c R1.6. NPCC_URE6 discovered that an authorized control center employee accompanied by two minor family members entered the energy control center (ECC). The family members were not processed as visitors in accordance with the NPCC_URE6 access control procedure. The visitors' entry and exit were not logged. | The issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The visitors were continuously escorted by a control center employee who had authorized access. At the time of the incident, the authorized control center employee was up to date on all related CIP training and had a current personnel risk assessment. | To mitigate this issue, NPCC_URE6: 1) ECC personnel have participated in a review of current the access control procedure; 2) control center operations and corporate security have installed new security controls at the ECC and alternate control center. These additional controls include a turnstile system that in addition to the existing access controlled doors at the ECC. The turnstiles will be card-access controlled, and will provide an additional layer of physical security, and enhanced capabilities of access monitoring and enforcement; 3) made the necessary updates to its access control procedure, and security plan; 4) trained all relevant personnel on the operation of the new security system and updated procedures; and 5) incorporated the updated plans and procedures into the annual re-training of all employees who have authorized access.
2013-04-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 6 (NPCC_URE6) | NCRXXXXX | NPCC2012010427 | CIP-006-3c | R1, R1.6 | NPCC_URE6 self-reported an issue with CIP-006-3c R1.6. An NPCC_URE6 employee who did not have authorized (unescorted) access to the NPCC_URE6 energy control center (ECC) was granted access to the ECC, but was not processed as a visitor in accordance with the access control procedure. The visitor's entry and exit were not logged accordingly. | The issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The employee was allowed to enter the ECC to conduct company business and was continuously escorted by a control center employee who had authorized access at the time of the incident. | To mitigate this issue, NPCC_URE6: 1) ECC personnel have participated in a review of current the access control procedure; 2) control center operations and corporate security have installed new security controls at the ECC and alternate control center. These additional controls include a turnstile system that in addition to the existing access controlled doors at the ECC. The turnstiles will be card-access controlled, and will provide an additional layer of physical security, and enhanced capabilities of access monitoring and enforcement; 3) made the necessary updates to its access control procedure, and security plan; 4) trained all relevant personnel on the operation of the new security system and updated procedures; and 5) incorporated the updated plans and procedures into the annual re-training of all employees who have authorized access.
2013-04-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 7 (NPCC_URE7) | NCRXXXXX | NPCC2013011949 | CIP-004-3 | R2; R2.1 | NPCC_URE7 self-reported an issue with CIP-004-3 R2.1. NPCC_URE7 discovered that one employee's annual CIP training had lapsed but was still granted physical access to Physical Security Perimeter (PSP). The employee was granted access to NPCC_URE7 PSPs, but his annual training had expired. The employee's access card had been disabled previously due to a medical leave of absence. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The issue was caused when the employee's supervisor requested NPCC_URE7 corporate security to reactivate the access card and reinstate all CIP clearances that the employee previously had. The employee has been employed with NPCC_URE7 for almost 20 years. He completed CIP training annually and has a current personnel risk assessment (PRA) on file. The employee works as a building mechanic and was only granted physical access to Critical Cyber Assets (CCA). | To mitigate this issue, NPCC_URE7 updated its procedure for granting physical access. Specifically, the email from the NPCC_URE7 security agent to the contract guard account manager requesting access must include the PRA and training dates. Upon receipt, the contract security account manager will conduct an independent verification of the training and PRA dates and will send an email confirmation back to the NPCC_URE7 security agent confirming that access has been granted. Training will be provided to security personnel on the revised process. NPCC_URE7 reviewed the lessons learned with Corporate Security personnel who have involvement in granting physical access. NPCC_URE7 conducted a review of all individuals that have physical access to PSPs to ensure training and PRAs are current.
2013-04-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2012011105 | CIP-005-1 | R1; R1.5 | During a Compliance Audit, ReliabilityFirst determined that RFC_URE1 had an issue with CIP-005-3a R1.5. RFC_URE1 has in place security defense appliances (SDA) that constitute Cyber Assets used in the access control and/or monitoring of the electronic security perimeter (ESP). The SDAs allow for only outbound communication from the ESP. A third-party manages the SDAs and receives metadata from a mirrored port within the ESP so it can analyze anomalous patterns to provide an alert to RFC_URE1. While the third-party has full access and control of the SDAs, it is unable to enter or penetrate the ESP. ReliabilityFirst discovered that for these Cyber Assets, RFC_URE1 failed to afford the protective measures of CIP-004-3 R3 and CIP-007-3 R3, R5, and R6. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk to the BPS was mitigated by the following factors. While the third-party has full access and control of the SDAs, it is unable to enter or penetrate the ESP. The third-party could only disable the SDAs which would render them unable to perform its contracted service of providing logging and alerting to RFC_URE1. In addition, RFC_URE1 afforded the SDAs the remaining protective measures in CIP-005-3a R1. | To mitigate this issue, RFC_URE1: 1) gathered additional necessary evidence to demonstrate that the SDAs were afforded the protective measures as specified in CIP-005-3a R1.5; and 2) reviewed procedures regarding SDAs and updated those procedures as necessary.
2013-04-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2012011120 | CIP-007-1 | R2; R2.2; R2.3 | During a Compliance Audit, ReliabilityFirst determined that RFC_URE1 had an issue with CIP-007-3 R2. For some of its servers, RFC_URE1 failed to disable services that are not required for normal and emergency operations, as required by CIP-007-3 R2.2. In addition, while RFC_URE1 appropriately implemented compensating measures for a non-required service that could not be disabled, it failed to file a Technical Feasibility Exception (TFE) for this service, as required by CIP-007-3 R2.3. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk to the BPS was mitigated by the following factors. The services that were not disabled were located within the requisite Physical Security Perimeter and behind two-factor enabled firewalls in the electronic security perimeter (ESP) with robust authorizing, validating, and deprovisioning access control procedures. The services had up-to-date anti-malware technology with security patches that were assessed within the requisite 30 days, cybersecurity tested, and then installed. RFC_URE1 performed cybersecurity vulnerability assessments on the services at least annually as required. RFC_URE1 utilizes a managed security services provider to monitor the services and provide alerts of signature-based intrusion events and potential anomalous traffic crossing into and out of the established ESP using the security defense appliances and a log collection infrastructure. This monitoring and alerting is provided 24 hours a day, seven days a week. Key trained and experienced personnel are notified via pager, email, and/or telephone of any alerts, as warranted by the severity level assigned to the alert. For the non-required service for which RFC_URE1 failed to file a TFE, RFC_URE1 also appropriately implemented the compensating measures described above. | To mitigate this issue, RFC_URE1: 1) utilized a cross-functional team of subject matter experts to review, research, and analyze the existing ports and services; 2) reviewed and enhanced the documented justification for all running ports and services; 3) identified the ports and services not needed for normal and emergency operations and which require specific change of status; and 4) identified the schedule for testing and implementing ports and services.
2013-04-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2012011125 | CIP-004-3 | R4; R4.2 | RFC_URE1 submitted a Self-Report to ReliabilityFirst identifying an issue with CIP-004-3 R4. An employee from RFC_URE1's affiliate, with authorized physical access to RFC_URE1's Critical Cyber Assets (CCAs) transferred positions to another affiliate, at which time his access to RFC_URE1's CCAs should have been revoked. The transferred employee’s supervisor did not promptly enter a security request system ticket to revoke the employee’s access or enter a personnel action notice form for the transfer prior to the employee’s transfer date, as was required by RFC_URE1 procedures. As a result, RFC_URE1 revoked this employee’s access three days later than the seven days required by CIP-004-3 R4.2. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. RFC_URE1 discovered this issue when a compliance specialist reviewed a security request system ticket to remove all access and recognized that the employee transfer date exceeded the seven day requirement by three days. RFC_URE1 revoked access promptly after discovering it had not revoked access. In addition, the employee at issue remained a NERC CIP-cleared individual with cybersecurity training and a valid personnel risk assessment. Furthermore, the employee did not actually enter any of the three Physical Security Perimeters, and remained employed by a RFC_URE1 affiliate. | To mitigate this issue, RFC_URE1: 1) removed the transferred employee’s access; and 2) sent a special email notice from RFC_URE1’s CIP senior manager to RFC_URE1 supervisors to remind them that when an employee or contract worker no longer requires access to a NERC CIP restricted area or asset, the supervisor is responsible for immediately initiating a ticket to remove the applicable accesses.
2013-04-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2012011275 | CIP-005-3a | R1 | RFC_URE1, RFC_URE2 and RFC_URE3 (collectively, the UREs) self-reported an issue with CIP-005-3a R1 to ReliabilityFirst. While conducting an independent verification of the security patches being installed on certain Cyber Assets, the UREs discovered that it inadvertently installed a system management client on five electronic access control system Cyber Assets, which are Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeter (ESP). The Cyber Assets at issue were two-factor authentication servers and firewall policy manager servers that protect physical access control system servers. The UREs installed this client without completing the steps set forth in its change and configuration management control process, as required by CIP-003-3 R6. The UREs did not issue infrastructure change requests for the change associated with deploying the client on those five Cyber Assets due to miscommunications between the personnel responsible for the change. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk to the BPS was mitigated by the following factors. The UREs had tested and installed the client at issue on many other non-CIP protected assets as part of an operating system patching cycle. The UREs observed no adverse consequences resulting from the installation of the client on these assets. The Cyber Assets at issue have numerous protections in place, including being located within a Physical Security Perimeter, up-to-date security patching, monitoring and logging, anti-malware, strong logical access controls, and cyclical cyber vulnerability assessments. | To mitigate this issue, the UREs: 1) uninstalled the client by following the appropriate steps set forth in the change and configuration management control process; 2) counseled the personnel in the responsible workgroup with primary responsibility for servers regarding the importance of following appropriate change management procedures for NERC CIP protected assets and the consequences of not doing so; and 3) conducted a workgroup meeting to reinforce the requirement to document change control and configuration management procedures and processes.
2013-04-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2012011276 | CIP-005-3a | R1 | RFC_URE1, RFC_URE2 and RFC_URE3 (collectively, the UREs) self-reported an issue with CIP-005-3a R1 to ReliabilityFirst. While conducting an independent verification of the security patches being installed on certain Cyber Assets, the UREs discovered that it inadvertently installed a system management client on five electronic access control system Cyber Assets, which are Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeter (ESP). The Cyber Assets at issue were two-factor authentication servers and firewall policy manager servers that protect physical access control system servers. The UREs installed this client without completing the steps set forth in its change and configuration management control process, as required by CIP-003-3 R6. The UREs did not issue infrastructure change requests for the change associated with deploying the client on those five Cyber Assets due to miscommunications between the personnel responsible for the change. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk to the BPS was mitigated by the following factors. The UREs had tested and installed the client at issue on many other non-CIP protected assets as part of an operating system patching cycle. The UREs observed no adverse consequences resulting from the installation of the client on these assets. The Cyber Assets at issue have numerous protections in place, including being located within a Physical Security Perimeter, up-to-date security patching, monitoring and logging, anti-malware, strong logical access controls, and cyclical cyber vulnerability assessments. | To mitigate this issue, the UREs: 1) uninstalled the client by following the appropriate steps set forth in the change and configuration management control process; 2) counseled the personnel in the responsible workgroup with primary responsibility for servers regarding the importance of following appropriate change management procedures for NERC CIP protected assets and the consequences of not doing so; and 3) conducted a workgroup meeting to reinforce the requirement to document change control and configuration management procedures and processes.
2013-04-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC2012011277 | CIP-005-3a | R1 | RFC_URE1, RFC_URE2 and RFC_URE3 (collectively, the UREs) self-reported an issue with CIP-005-3a R1 to ReliabilityFirst. While conducting an independent verification of the security patches being installed on certain Cyber Assets, the UREs discovered that it inadvertently installed a system management client on five electronic access control system Cyber Assets, which are Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeter (ESP). The Cyber Assets at issue were two-factor authentication servers and firewall policy manager servers that protect physical access control system servers. The UREs installed this client without completing the steps set forth in its change and configuration management control process, as required by CIP-003-3 R6. The UREs did not issue infrastructure change requests for the change associated with deploying the client on those five Cyber Assets due to miscommunications between the personnel responsible for the change. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk to the BPS was mitigated by the following factors. The UREs had tested and installed the client at issue on many other non-CIP protected assets as part of an operating system patching cycle. The UREs observed no adverse consequences resulting from the installation of the client on these assets. The Cyber Assets at issue have numerous protections in place, including being located within a Physical Security Perimeter, up-to-date security patching, monitoring and logging, anti-malware, strong logical access controls, and cyclical cyber vulnerability assessments. | To mitigate this issue, the UREs: 1) uninstalled the client by following the appropriate steps set forth in the change and configuration management control process; 2) counseled the personnel in the responsible workgroup with primary responsibility for servers regarding the importance of following appropriate change management procedures for NERC CIP protected assets and the consequences of not doing so; and 3) conducted a workgroup meeting to reinforce the requirement to document change control and configuration management procedures and processes.
2013-04-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC2012011374 | CIP-005-3 | R1; R1.5 | RFC_URE1, RFC_URE2 and RFC_URE3 (collectively, the UREs) self-reported an issue with CIP-005-3 R1 to ReliabilityFirst. While conducting an internal review, the UREs discovered that it failed to change passwords for five shared accounts annually for one Critical Cyber Asset and four Cyber Assets used in the access control and monitoring of the Electronic Security Perimeter (ESP), and Cyber Assets that authorize and/or log access to the physical security perimeter. This conduct implicated assets subject to the requirements of CIP-007-3 R5.3.3 through CIP-005-3 R1.4 and 1.5, CIP-006-3a R2.2, and CIP-007-3 R5.3.3. ReliabilityFirst determined that the UREs only had an issue with CIP-005-3 R1.5 in order to avoid duplicative enforcement actions. These accounts are not intended for human login, and instead these accounts are interface or system accounts required or used for system-to-system interaction. Due to this fact, the UREs inadvertently overlooked the annual requirement to change these passwords. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk to the BPS was mitigated by the following factors. The accounts at issue only affected a small subset of Cyber Assets. During the period of the issue, each account had strong passwords that otherwise complied with the CIP Requirements, and only those individuals who were NERC CIP-cleared with a business need knew the passwords. The UREs protects the Cyber Assets at issue with logical access controls, strong physical and electronic controls, and monitoring, logging, and alerting. | To mitigate this issue, the UREs: 1) changed passwords or decommissioned accounts, where appropriate; 2) held review meetings with personnel who have access and responsibility for password management of these accounts to reinforce their understanding of requirements applicable to these assets; 3) communicated directly and firmly to personnel that documented procedures and CIP controls for password management must be complied with; and 4) reiterated to personnel that noncompliance may result in a disciplinary action.
2013-04-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2012011375 | CIP-005-3 | R1; R1.5 | RFC_URE1, RFC_URE2 and RFC_URE3 (collectively, the UREs) self-reported an issue with CIP-005-3 R1 to ReliabilityFirst. While conducting an internal review, the UREs discovered that it failed to change passwords for five shared accounts annually for one Critical Cyber Asset and four Cyber Assets used in the access control and monitoring of the Electronic Security Perimeter (ESP), and Cyber Assets that authorize and/or log access to the physical security perimeter. This conduct implicated assets subject to the requirements of CIP-007-3 R5.3.3 through CIP-005-3 R1.4 and 1.5, CIP-006-3a R2.2, and CIP-007-3 R5.3.3. ReliabilityFirst determined that the UREs only had an issue with CIP-005-3 R1.5 in order to avoid duplicative enforcement actions. These accounts are not intended for human login, and instead these accounts are interface or system accounts required or used for system-to-system interaction. Due to this fact, the UREs inadvertently overlooked the annual requirement to change these passwords. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk to the BPS was mitigated by the following factors. The accounts at issue only affected a small subset of Cyber Assets. During the period of the issue, each account had strong passwords that otherwise complied with the CIP Requirements, and only those individuals who were NERC CIP-cleared with a business need knew the passwords. The UREs protects the Cyber Assets at issue with logical access controls, strong physical and electronic controls, and monitoring, logging, and alerting. | To mitigate this issue, the UREs: 1) changed passwords or decommissioned accounts, where appropriate; 2) held review meetings with personnel who have access and responsibility for password management of these accounts to reinforce their understanding of requirements applicable to these assets; 3) communicated directly and firmly to personnel that documented procedures and CIP controls for password management must be complied with; and 4) reiterated to personnel that noncompliance may result in a disciplinary action.
2013-04-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2012011376 | CIP-005-3 | R1; R1.5 | RFC_URE1, RFC_URE2 and RFC_URE3 (collectively, the UREs) self-reported an issue with CIP-005-3 R1 to ReliabilityFirst. While conducting an internal review, the UREs discovered that it failed to change passwords for five shared accounts annually for one Critical Cyber Asset and four Cyber Assets used in the access control and monitoring of the Electronic Security Perimeter (ESP), and Cyber Assets that authorize and/or log access to the physical security perimeter. This conduct implicated assets subject to the requirements of CIP-007-3 R5.3.3 through CIP-005-3 R1.4 and 1.5, CIP-006-3a R2.2, and CIP-007-3 R5.3.3. ReliabilityFirst determined that the UREs only had an issue with CIP-005-3 R1.5 in order to avoid duplicative enforcement actions. These accounts are not intended for human login, and instead these accounts are interface or system accounts required or used for system-to-system interaction. Due to this fact, the UREs inadvertently overlooked the annual requirement to change these passwords. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk to the BPS was mitigated by the following factors. The accounts at issue only affected a small subset of Cyber Assets. During the period of the issue, each account had strong passwords that otherwise complied with the CIP Requirements, and only those individuals who were NERC CIP-cleared with a business need knew the passwords. The UREs protects the Cyber Assets at issue with logical access controls, strong physical and electronic controls, and monitoring, logging, and alerting. | To mitigate this issue, the UREs: 1) changed passwords or decommissioned accounts, where appropriate; 2) held review meetings with personnel who have access and responsibility for password management of these accounts to reinforce their understanding of requirements applicable to these assets; 3) communicated directly and firmly to personnel that documented procedures and CIP controls for password management must be complied with; and 4) reiterated to personnel that noncompliance may result in a disciplinary action.
2013-04-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2013011666 | CIP-006-3c | R2; R2.2 | RFC_URE1 self-reported an issue with CIP-006-3c R2 to ReliabilityFirst. RFC_URE1 maintains control panels to control access to Physical Security Perimeters (PSPs), thereby classifying them as Cyber Assets that authorize and/or log access to the PSP. While troubleshooting the installation of a part on the panel, RFC_URE1 installed firmware on a control panel prior to testing that firmware in accordance with its test procedures pursuant to CIP-007-3 R1. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk to the BPS was mitigated by the following factors. RFC_URE1 had installed the firmware on other non-CIP panels and experienced no issues. In addition, RFC_URE1 stored the firmware on the master server used for access control and alarm monitoring. The technician installing the firmware was aware that RFC_URE1 had previously installed this firmware on other panels and that the firmware was stored on the master server. Furthermore, the panels are located behind firewalls with perimeter logging, monitoring, and alerting in place. | To mitigate this issue, RFC_URE1: 1) performed the testing for the firmware and confirmed that the firmware did not contain any malicious code and was authentic; 2) coached the technician on the need to confirm that all requirements are met before implementing any remedial action during installation; and 3) committed to update appropriate procedures to identify work tasks requiring cybersecurity testing.
2013-04-30 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2013011910 | CIP-002-3 | R1 | The SERC CIP audit team reported that SERC_URE1 had an issue with CIP-002-3 R1 because it failed to identify and document a risk-based assessment methodology (RBAM) to use to identify its Critical Assets. SERC_URE1 registered with NERC after purchasing assets from a registered entity in the SERC Region. The assets purchased by SERC_URE1 were included in the previous owner’s CIP program. Due to a misinterpretation of the CIP Standards and the Implementation Plan for Newly Identified Critical Cyber Assets and Newly Registered Entities, SERC_URE1 believed that it had 24 months to identify and document a RBAM to use to identify its Critical Assets. Pursuant to NERC Compliance Process Bulletin #2011-005, SERC determined that SERC_URE1 was required to have identified and documented a RBAM to use to identify its Critical Assets as of its registration date. SERC determined that SERC_URE1 identified and documented a RBAM to use to identify its Critical Assets approximately one year after SERC_URE1’s registration date. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The entity that sold SERC_URE1 its assets provided a letter of attestation that previous versions of its RBAM indicated that there were no Critical Assets or Critical Cyber Assets (CCAs) for the generation assets that SERC_URE1 purchased. In addition, SERC_URE1 created and applied a RBAM and found that it did not have any Critical Assets or CCAs. | To mitigate this issue, SERC_URE1: 1) Developed and applied a RBAM and found that it had no Critical Assets or CCAs; 2) Had its senior manager review and approve the RBAM, Critical Asset list, and CCA list; 3) Developed and approved a procedure covering CIP-002; 4) Developed and approved a preventative maintenance activity to require the RBAM to be applied on an annual basis in order to develop and approve the Critical Asset list and CCA list; and 5) Notified appropriate personnel of this issue and the corrective actions taken to prevent recurrence.
2013-04-30 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2012011497 | CIP-003-3 | R2 | SERC_URE1 submitted a Self-Report to SERC stating that it had an issue with CIP-003-3 R2 because it did not assign a single senior manager with overall responsibility and authority for leading and managing SERC_URE1’s implementation of, and adherence to, the CIP Standards (CIP senior manager). SERC_URE1 registered with NERC after purchasing assets from a registered entity in the SERC Region. The assets purchased by SERC_URE1 were included in the previous owner’s CIP program. Due to a misinterpretation of the CIP Standards and the Implementation Plan for Newly Identified Critical Cyber Assets and Newly Registered Entities, SERC_URE1 believed that it had 12 months to designate a CIP senior manager. Pursuant to NERC Compliance Process Bulletin #2011-005, SERC determined that SERC_URE1 was required to have designated a CIP senior manager as of its registration date of November 22, 2011. SERC determined that SERC_URE1 designated a CIP senior manager approximately one year after SERC_URE1’s registration date. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC_URE1 had an asset manager acting as the CIP senior manager since its registration even though the asset manager was not officially designated as the CIP senior manager. In addition, SERC_URE1 has no Critical Assets and does not own or operate any facilities that would meet any of the Critical Asset criteria set forth in CIP-002-4. | To mitigate this issue, SERC_URE1: 1) Developed and approved a procedure that gives clear detailed guidance on how to comply with CIP-003; 2) Designated in writing a senior manager responsible for CIP activities; 3) Developed and approved a preventive maintenance activity that requires a monthly review of the CIP-003 procedure to ensure that a senior manager is always designated; and 4) Notified appropriate personnel of this issue and the corrective actions taken to prevent recurrence.
2013-04-30 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 2 (SERC_URE2) | NCRXXXXX | SERC2013011914 | CIP-002-3 | R1 | The SERC CIP audit team reported that SERC_URE2 had an issue with CIP-002-3 R1 because it failed to identify and document a risk-based assessment methodology (RBAM) to use to identify its Critical Assets. SERC_URE2 registered with NERC after purchasing assets from a registered entity in the SERC Region. The assets purchased by SERC_URE2 were included in the previous owner’s CIP program. Due to a misinterpretation of the CIP Standards and the Implementation Plan for Newly Identified Critical Cyber Assets and Newly Registered Entities, SERC_URE2 believed that it had 24 months to identify and document a RBAM to use to identify its Critical Assets. Pursuant to NERC Compliance Process Bulletin #2011-005, SERC determined that SERC_URE2 was required to have identified and documented a RBAM to use to identify its Critical Assets as of its registration date. SERC determined that SERC_URE2 identified and documented a RBAM to use to identify its Critical Assets approximately one year after SERC_URE2’s registration date. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The entity that sold SERC_URE2 its assets provided a letter of attestation that previous versions of its RBAM indicated that there were no Critical Assets or Critical Cyber Assets (CCAs) for the generation assets that SERC_URE2 purchased. In addition, SERC_URE2 created and applied a RBAM and found that it did not have any Critical Assets or CCAs. | To mitigate this issue, SERC_URE2: 1) Developed and applied a RBAM and found that it had no Critical Assets or CCAs; 2) Had its senior manager review and approve the RBAM, Critical Asset list, and CCA list; 3) Developed and approved a procedure covering CIP-002; 4) Developed and approved a preventative maintenance activity to require the RBAM to be applied on an annual basis in order to develop and approve the Critical Asset list and CCA list; and 5) Notified appropriate personnel of this issue and the corrective actions taken to prevent recurrence.
2013-04-30 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 2 (SERC_URE2) | NCRXXXXX | SERC2012011496 | CIP-003-3 | R2 | SERC_URE2 submitted a Self-Report to SERC stating that it had an issue with CIP-003-3 R2 because it did not assign a single senior manager with overall responsibility and authority for leading and managing SERC_URE2’s implementation of, and adherence to, the CIP Standards (CIP senior manager). SERC_URE2 registered with NERC after purchasing assets from a registered entity in the SERC Region. The assets purchased by SERC_URE2 were included in the previous owner’s CIP program. Due to a misinterpretation of the CIP Standards and the Implementation Plan for Newly Identified Critical Cyber Assets and Newly Registered Entities, SERC_URE2 believed that it had 12 months to designate a CIP senior manager. Pursuant to NERC Compliance Process Bulletin #2011-005, SERC determined that SERC_URE2 was required to have designated a CIP senior manager as of its registration date of November 22, 2011. SERC determined that SERC_URE2 designated a CIP senior manager approximately one year after SERC_URE2’s registration date. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC_URE2 had an asset manager acting as the CIP senior manager since its registration even though the asset manager was not officially designated as the CIP senior manager. In addition, SERC_URE2 has no Critical Assets and does not own or operate any facilities that would meet any of the Critical Asset criteria set forth in CIP-002-4. | To mitigate this issue, SERC_URE2: 1) Developed and approved a procedure that gives clear detailed guidance on how to comply with CIP-003; 2) Designated in writing a senior manager responsible for CIP activities; 3) Developed and approved a preventive maintenance activity that requires a monthly review of the CIP-003 procedure to ensure that a senior manager is always designated; and 4) Notified appropriate personnel of this issue and the corrective actions taken to prevent recurrence.
2013-04-30 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 3 (SERC_URE3) | NCRXXXXX | SERC2013011772 | CIP-002-1 | R1 | SERC_URE3 submitted a Self-Certification stating that it had an issue with CIP-002-1 R1 because it did not have a documented risk-based assessment methodology (RBAM) that met all of the requirements of CIP-002-1 R1 to use to identify its Critical Assets. SERC_URE3 had a documented RBAM in place prior to the time that the Standard became mandatory and enforceable, but the initial RBAM lacked evaluation criteria and did not consider any of the assets listed in R1.2.1 through R1.2.7. Subsequent revisions of SERC_URE3’s RBAM lacked evaluation criteria and/or failed to consider all of the assets listed in R1.2.1 through R1.2.7. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC_URE3 conducted several assessments to determine whether it had Critical Assets and found none, even though those assessments did not include evaluation criteria and/or all the assets listed in R1.2.1 through R1.2.7, as required by the Standard. In addition, SERC_URE3 has no Critical Assets and does not own or operate any facilities that would meet any of the Critical Asset criteria set forth in CIP-002-4. | To mitigate this issue, SERC_URE3: 1) Revised SERC_URE3's RBAM to specifically address each and every requirement set forth in CIP-002 R1; and 2) Applied the revised RBAM and had the senior manager approve and sign the RBAM and resulting Critical Assets and Critical Cyber Assets list.
2013-04-30 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 3 (SERC_URE3) | NCRXXXXX | SERC2012011642 | CIP-003-1 | R2 | SERC_URE3 submitted a Self-Report to SERC stating that it had an issue with CIP-003-1 R2 because it failed to assign in writing a single senior manager with overall responsibility and authority for leading and managing its implementation of, and adherence to, the CIP Standards. SERC_URE3 discovered the issue during a mock audit that it conducted as part of its internal compliance program. During an internal compliance team meeting, SERC_URE3 had verbally designated its IT supervisor as the single senior manager with overall responsibility and authority for leading SERC_URE3’s CIP program. SERC_URE3 did not document this assignment in writing with the name, title, and date of designation. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC_URE3’s IT supervisor was acting as the CIP senior manager during the period in question even though SERC_URE3 had not formally assigned the senior manager responsibility to the IT supervisor in writing. In addition, SERC_URE3 has no Critical Assets and does not own or operate any facilities that would meet any of the Critical Asset criteria set forth in CIP-002-4. | To mitigate this issue, SERC_URE3: 1) Documented in writing the designation of SERC_URE3's senior manager responsible for implementation of and adherence to Standards CIP-002 through CIP-009; and 2) Adopted a policy requiring an annual review of the written designation to prevent a future issue with CIP-003 R2.
2013-04-30 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 4 (SERC_URE4) | NCRXXXXX | SERC2013011918 | CIP-002-3 | R1 | The SERC CIP audit team reported that SERC_URE4 had an issue with CIP-002-3 R1 because it failed to identify and document a risk-based assessment methodology (RBAM) to use to identify its Critical Assets. SERC_URE4 registered with NERC after purchasing assets from a registered entity in the SERC Region. The assets purchased by SERC_URE4 were included in the previous owner’s CIP program. Due to a misinterpretation of the CIP Standards and the Implementation Plan for Newly Identified Critical Cyber Assets and Newly Registered Entities, SERC_URE4 believed that it had 24 months to identify and document a RBAM to use to identify its Critical Assets. Pursuant to NERC Compliance Process Bulletin #2011-005, SERC determined that SERC_URE4 was required to have identified and documented a RBAM to use to identify its Critical Assets as of its registration date. SERC determined that SERC_URE4 identified and documented a RBAM to use to identify its Critical Assets approximately one year after SERC_URE4’s registration date. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The entity that sold SERC_URE4 its assets provided a letter of attestation that previous versions of its RBAM indicated that there were no Critical Assets or Critical Cyber Assets (CCAs) for the generation assets that SERC_URE4 purchased. In addition, SERC_URE4 created and applied a RBAM and found that it did not have any Critical Assets or CCAs. | To mitigate this issue, SERC_URE4: 1) Developed and applied a RBAM and found that it had no Critical Assets or CCAs; 2) Had its senior manager review and approve the RBAM, Critical Asset list, and CCA list; 3) Developed and approved a procedure covering CIP-002; 4) Developed and approved a preventative maintenance activity to require the RBAM to be applied on an annual basis in order to develop and approve the Critical Asset list and CCA list; and 5) Notified appropriate personnel of this issue and the corrective actions taken to prevent recurrence.
2013-04-30 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 4 (SERC_URE4) | NCRXXXXX | SERC2012011499 | CIP-003-3 | R2 | SERC_URE4 submitted a Self-Report to SERC stating that it had an issue with CIP-003-3 R2 because it did not assign a single senior manager with overall responsibility and authority for leading and managing SERC_URE4’s implementation of, and adherence to, the CIP Standards (CIP senior manager). SERC_URE4 registered with NERC after purchasing assets from a registered entity in the SERC Region. The assets purchased by SERC_URE4 were included in the previous owner’s CIP program. Due to a misinterpretation of the CIP Standards and the Implementation Plan for Newly Identified Critical Cyber Assets and Newly Registered Entities, SERC_URE4 believed that it had 12 months to designate a CIP senior manager. Pursuant to NERC Compliance Process Bulletin #2011-005, SERC determined that SERC_URE4 was required to have designated a CIP senior manager as of its registration date of November 22, 2011. SERC determined that SERC_URE4 designated a CIP senior manager approximately one year after SERC_URE4’s registration date. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC_URE4 had an asset manager acting as the CIP senior manager since its registration even though the asset manager was not officially designated as the CIP senior manager. In addition, SERC_URE4 has no Critical Assets and does not own or operate any facilities that would meet any of the Critical Asset criteria set forth in CIP-002-4. | To mitigate this issue, SERC_URE4: 1) Developed and approved a procedure that gives clear detailed guidance on how to comply with CIP-003; 2) Designated in writing a senior manager responsible for CIP activities; 3) Developed and approved a preventive maintenance activity that requires a monthly review of the CIP-003 procedure to ensure that a senior manager is always designated; and 4) Notified appropriate personnel of this issue and the corrective actions taken to prevent recurrence.
2013-04-30 | Southwest Power Pool Regional Entity (SPP RE), Western Electricity Coordinating Council (WECC), Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (SPPRE_URE1, MRO_URE1, WECC_URE1) (Collectively, URE_1) | NCRXXXXX | SPP2012010005; MRO2012011021; WECC2012009994 | CIP-007-3 | R1; R1.3 | URE_1 submitted respective Self-Reports to SPP RE and WECC, identifying an issue with CIP-007-3 R1.3. The Self-Reports was submitted on behalf of URE_1's affiliated registered entities. Approximately four months later, URE_1 filed a Self-Report for CIP-007-3 R1.3 with MRO, on behalf of another affiliated registered entity. URE_1 self-reported that it did not have documented test results for installation of 29 of 160 patches. Of the 29 patches, 6 pertained to asset installation or replacement, and 23 pertained to installation of software patches. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although URE_1 was unable to provide test results of the 29 patches after their installation, URE_1 did have change orders that noted testing took place and that the patches had been installed. The Energy Management System (EMS) staff member responsible for installing the patch updates noted on the change order that there was no CIP impact to the machines that were updated; therefore, the patch installation did not affect existing cyber security controls to Cyber Assets within the Electronic Security Perimeter (ESP). Additionally, URE_1 provided documentation that it did assess the patches in a simulated production system prior to installation and that the installation of the patches would not adversely affect the operation of an existing Cyber Asset. Further, the Cyber Assets and Critical Cyber Assets within the ESP were only accessible to those with authorized physical and electronic access rights. | To mitigate this issue of noncompliance, URE_1 revised its testing procedures to make the testing documentation requirements clearer to affected EMS personnel. URE_1 trained all affected personnel on the new testing procedures. Additionally, URE_1 instituted a process and schedule for internal auditing every six months to review EMS change records and ensure that the new testing procedures are being followed.
2013-04-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPPRE_URE2) | NCRXXXXX | SPP2012009723 | CIP-006-1 | R1; R1.8 | SPP_URE2 submitted a Self-Report to SPP RE identifying an issue with CIP-006-1 R1.8, which requires that protective measures should be afforded in accordance with certain Standards, including CIP-007-1 R2.1 and R2.2. SPP_URE2 was operating with ports enabled on its badge system that were not required for normal or emergency operations. During a cyber vulnerability assessment (CVA), SPP_URE2 identified one port on its badge system that was not required for normal or emergency operations. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The badge system is guarded by SPP_URE2's electronic access point firewalls and an intrusion prevention system (IPS) residing in series with the firewalls. The firewalls are enabled with anti-virus software and block malicious software accordingly. The IPS reinforces and compliments the firewall by preventing inbound malicious traffic that might successfully cross the firewall, and by preventing malicious outbound traffic from crossing back through the firewall. Furthermore, the badge system is also running anti-virus software, thereby providing another layer of protection beyond the IPS and firewalls. Moreover, SPP_URE2 identified no malicious exploitation of the one erroneously enabled port. | SPP_URE2 disabled the erroneously enabled port.
2013-04-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 3 (SPPRE_URE3) | NCRXXXXX | SPP2011008256 | CIP-007-1 | R8; R8.3 | During a CIP Compliance Audit of SPP_URE3, SPP RE determined that SPP_URE3 had an issue with CIP-007-1 R8.3. SPP_URE3 did not include a review of all of the implemented controls for default accounts in its annual cyber vulnerability assessment (CVA) of all Cyber Assets within the Electronic Security Perimeter. Specifically, SPP_URE3 did not review default account controls that included renaming, disabling, and changing default passwords of default accounts. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The controls of renaming or disabling were implemented and documented but were not reviewed as part of the annual CVA. SPP_URE3 did document other controls for default accounts as part of the annual CVA including reviewing password complexity and password age for all user and default accounts. | SPP_URE3 revised its CVA procedures to include a review of all the implemented controls for default accounts. The performance of the 2012 CVA included such a review.
2013-04-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 4 (SPPRE_URE4) | NCRXXXXX | SPP201100466 | CIP-007-1 | R4 | SPP_URE4 submitted a Self-Report to SPP RE, stating that it had an issue with CIP-007-1 R4 because it failed to submit a timely Technical Feasibility Exception (TFE) request. SPP_URE4 could not install anti-virus software on the communication front-end (CFE) devices of its Energy Management System (EMS) because SPP_URE4’s EMS vendor did not have anti-virus software available for these devices. Also, the vendor did not recommend that anti-virus protection be implemented on these devices. Subsequently, SPP_URE4 submitted a second Self-Report stating that it had failed to request TFEs for additional devices all of which were part of SPP_URE4's EMS and were located within the Electronic Security Perimeter (ESP). SPP RE consolidated these two Self-Reports into one issue. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SPP_URE4 demonstrated that it had implemented compensating measures for all of its EMS devices for the duration of the issue. These compensating measures included prohibiting direct Internet connection or email accounts on the EMS, as well as disabling the auto-run and auto-play features on all EMS windows equipment. Additionally, SPP_URE4 had documented the aforementioned compensating measures for its CFE devices, EMS servers, and EMS workstations. | SPP_URE4 submitted TFE requests for all affected devices, and performed the compensating measures it had documented in the TFEs. These TFEs were approved by SPP RE. Additionally, SPP_URE4 terminated two TFEs because it became technically feasible to perform the required actions. SPP_URE4 also updated its anti-virus policy and procedure documents, and trained personnel on the updates.
2013-04-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 5 (SPPRE_URE5) | NCRXXXXX | SPP2012009704 | CIP-007-3 | R3; R3.1 | SPPRE_URE5 submitted a Self-Report to SPP RE, stating that it had an issue with CIP-007-3 R3.1. SPPRE_URE5 failed to document 6% of its assessments of available security patches and security upgrades within thirty calendar days of availability. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). While 6% of the patch and security upgrade assessments were not documented within thirty calendar days, 100% were documented within sixty calendar days of availability. Furthermore, only one critical security patch was released during this time. That patch was released for a browser on an asset that did not have Internet access, thus limiting the risk to the BPS. Finally, SPPRE_URE5 had other measures to protect the affected assets and devices, including strict firewall rules, electronically reviewing logs, anti-virus prevention tools, and security patches. | SPPRE_URE5 revised its security patch management program to track and evaluate applicable security patches and security upgrades by performing a blanket assessment of all assets approximately every two weeks, regardless whether a new patch or patch upgrade actually is available.
2013-04-30 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE2012010996 | CIP-002-3 | R4 | During a Compliance Audit, Texas RE concluded that TRE_URE1 had an issue with CIP-002-3 R4 because the senior manager did not annually approve its null lists of Critical Assets and Critical Cyber Assets (CCAs). Therefore, TRE_URE1 had an issue with CIP-002-3 R4 for about four months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the bulk power system. Although TRE_URE1 did not annually approve the null lists of Critical Assets and CCAs for a period of about four months, TRE_URE1 did in fact have the documents to demonstrate that it used its risk-based assessment methodology (RBAM) to create these asset lists. The Critical Asset and CCA lists based on the RBAM were null during the pendency of the issue. | To mitigate this issue, TRE_URE1 provided a signed and dated record of the senior manager’s approval of the null list of Critical Assets and the null list of CCAs. Texas RE has verified the completion of all mitigation activities.
2013-04-30 | TRE_URE1liability Entity (TRE_URE1) | Unidentified Registered Entity 2 (TRE_URE2) | NCRXXXXX | TRE2012011041 | CIP-005-3a | R1.6 | TRE_URE2 submitted a Self-Report stating that it had an issue with CIP-005-3a R1. While conducting an annual cyber vulnerability assessment, TRE_URE2 discovered a non-critical Cyber Asset, which was installed for future communications within the Electronic Security Perimeter (ESP). TRE_URE2 determined the non-critical Cyber Asset had not been identified and documented within the asset management system utilized for maintaining documentation of all interconnected non-Critical Cyber Assets within the ESP, as required by CIP-005-3a R1.6. The duration of this issue was for about ten months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The non-critical Cyber Asset at issue was not connected to additional devices in the ESP. In addition, TRE_URE2 afforded the same protections to the non-critical Cyber Asset that are applicable to all access points and devices in the ESP. Furthermore, the non-critical Cyber Asset was located within a Physical Security Perimeter. Finally, TRE_URE2 conducts an annual discovery scan to identify all Cyber Assets within a given ESP. TRE_URE2 compares the results of this scan to a list of known devices, and then identifies any discrepancies. This process led to the discovery of the non-critical Cyber Asset at issue. TRE_URE1 determined that the instant issue is appropriate for FFT treatment because TRE_URE2 discovered the issue during a self-assessment and self-reported the issue. | To mitigate this issue, TRE_URE2: 1) disconnected the non-critical Cyber Asset from the network and powered it down upon discovery; and 2) updated the non-critical Cyber Asset in TRE_URE2’s asset management system. TRE_URE1 has verified the completion of all mitigation activities.
2013-04-30 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 3 (TRE_URE3) | NCRXXXXX | TRE2012009731 | CIP-003-3 | R2; R2.1 | During a Compliance Audit, Texas RE concluded that TRE_URE3 had an issue with CIP-003-3 R2. TRE_URE3 had not assigned a single senior manager, as required by R2. When the senior manager was assigned, he was not identified by name, title and date of designation, as required by R2.1. The TRE_URE3 had an issue with this Standard for about one year. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Texas RE determined that this is was a documentation issue because the same individual who was previously reviewing and approving the risk-based assessment methodology (RBAM) and Critical Asset and Critical Cyber Asset (CCAs) lists was later designated as the CIP senior manager. TRE_URE3 was already ensuring that the RBAM and Critical Asset and CCA lists were reviewed and approved by the person considered to be the CIP senior manager, although it had not documented his designation properly. Furthermore, even after the CIP senior manager was properly designated, there was no change to the Critical Asset and CCA lists. | To mitigate this issue, the TRE_URE3 officially designated a CIP senior manager by name, title, and date of designation. The CIP senior manager has also reviewed and approved the RBAM and Critical Asset and CCA lists. Texas RE has verified the completion of all mitigation activities.
2013-04-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2013011656 | CIP-004-3 | R4 | WECC notified WECC_URE1 that WECC was initiating the Self-Certification process. WECC_URE1 submitted a Self-Report to WECC stating that it had an issue with CIP-004-3 R4. WECC_URE1 reported that it had hired a contractor and granted the contractor unescorted physical access to Critical Cyber Assets (CCAs). WECC_URE1 reported that the contractor was terminated for cause. WECC_URE1 reported that when it terminated the contractor, it revoked the contractor’s physical access to its CCAs but did not remove the contractor from its CCA access list. WECC_URE1 reported that it did not remove the contractor from its CCA access list until five months later when it conducted an internal compliance audit. WECC_URE1 reported that it subsequently updated its CCA access list to reflect the termination. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE1, upon releasing the contractor, immediately revoked his identification and access granting badge which is required to physically access WECC_URE1’s CCAs. Without an identification badge, WECC_URE1 would have required the contractor to have an escort while interacting with its CCAs. Additionally, all the facilities to which the contractor had access, are continuously monitored by video. | To mitigate this issue WECC_URE1 removed the terminated contractor from its CCA access list.
2013-04-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC201102930 | CIP-007-1 | R5 | WECC_URE2 submitted a Self-Report to WECC stating that it had an issue with CIP-007-1 R5. In its Self-Report, WECC_URE2 stated that it performed an incomplete review of individual and shared accounts. WECC_URE2 stated that it failed to implement technical and procedural controls that enforce access authentication of, and accountability for, all user activity that minimizes the risk of unauthorized system access. Specifically, for Cyber Assets located in an Electronic Security Perimeter (ESP), WECC_URE2 failed to implement controls to manage accounts as required by CIP-007-1 R5.1. In addition, for the same Cyber Assets, WECC_URE2 failed to implement a policy to manage use for shared and generic accounts as required by CIP-007-1 R5.2. Finally, for different Cyber Assets located in ESPs, WECC_URE2 failed to change the password at least annually, as required by CIP-007-1 R5.3.3. WECC_URE2 submitted Technical Feasibility Exceptions (TFE(s)) for CIP-007-1 R5. WECC determined that it is technically infeasible for WECC_URE2 to provide adequate password length for the above devices. WECC_URE2 failed to submit TFEs by the due date for submitting TFE Requests. WECC approved the TFEs. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). During the issue period, there were a number of compensating measures in place to secure the devices against misuse or malicious attack. All devices were secured within a Physical Security Perimeter (PSP) and then an ESP with a card access system. All individuals must have an authorized card to access the PSP and ESP. In addition, WECC_URE2 stated that controls are implemented to log and monitor access to all Cyber Assets within the ESP and the physical and electronic alerts are reviewed 24 hours a day. For the devices in which it is technically infeasible to implement security controls, WECC_URE2 has additional measures in place to ensure the reliability of the BPS. For example failure of a device will not disable the control operator’s visibility. Failure to dispatch in normal configuration has minimal impact. On-site electricians would dispatch the unit manually if necessary restoring operations in a matter of hours. | To mitigate this issue, WECC_URE2: 1) created unique device identifiers for each device for ease of tracking in data collection; 2) reviewed and updated individual, shared, and administrator accounts for all devices in scope; 3) updated passwords for all devices in scope; and 4) submitted TFE requests for the devices incapable of providing adequate password length. WECC approved the TFEs.
2013-04-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC201102931 | CIP-007-1 | R6 | WECC_URE2 submitted a Self-Report to WECC stating that it had an issue with CIP-007-1 R6. In its Self-Report, WECC_URE2 stated that it had an inadequate security monitoring and log review in place. WECC_URE2 stated that it failed to implement security controls to monitor cyber security system events. As a result, WECC_URE2 failed to issue alerts for detected cybersecurity incidents, as well as, maintain, retain, and review logs related to security events. The Cyber Assets in scope are used in the access control and monitoring of WECC_URE2’s Physical Security Perimeter. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). During the issue period, there were a number of compensating measures in place to secure the devices against misuse or malicious attack. All devices were secured within a Physical Security Perimeter (PSP) and then an ESP with a card access system. All individuals must have an authorized card to access the PSP and ESP. In addition, WECC_URE2 stated that controls are implemented to log and monitor access to all Cyber Assets within the ESP and the physical and electronic alerts are reviewed 24 hours a day. For the devices in which it is technically infeasible to implement security controls, WECC_URE2 has additional measures in place to ensure the reliability of the BPS. For example, failure of a device will not disable the control operator’s visibility. Failure to dispatch in normal configuration has minimal impact. On-site electricians would dispatch the unit manually if necessary restoring operations in a matter of hours. | To mitigate this issue, WECC_URE2: 1) created unique device identifiers for each device for ease of tracking in data collection; 2) reviewed and maintained logs per CIP-007-1 R6 for all devices in scope; and 3) submitted TFE requests for the two devices. WECC approved the TFEs.
2013-04-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC201102923 | CIP-007-1 | R5 | WECC_URE3 submitted a Self-Report to WECC stating that it had an issue with CIP-007-1 R5. In its Self-Report, WECC_URE3 stated that it performed an incomplete review of individual and shared accounts. WECC_URE3 stated that it failed to implement technical and procedural controls that enforce access authentication of, and accountability for, all user activity that minimizes the risk of unauthorized system access. Specifically, for certain Cyber Assets, WECC_URE3 failed to implement controls to manage accounts. In addition, for the same Cyber Assets, WECC_URE3 failed to implement a policy to manage use for shared and generic accounts. Finally, for the same Cyber Assets and additional Cyber Asset, WECC_URE3 failed to change the password at least annually. The Cyber Assets in scope are located in Electronic Security Perimeters (ESPs). WECC_URE3 submitted Technical Feasibility Exceptions (TFEs) for CIP-007-1 R5. WECC_URE3 failed to submit a TFE by the due date for submitting TFE Requests. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). During the issue period, there were a number of compensating measures in place to secure the devices against misuse or malicious attack. All devices were secured within a Physical Security Perimeter (PSP) and then an ESP with a card access system. All individuals must have an authorized card to access the PSP and ESP. In addition, WECC_URE3 stated that controls are implemented to log and monitor access to all Cyber Assets within the ESP and the physical and electronic alerts are reviewed 24 hours a day. For the devices in which it is technically infeasible to implement security controls, WECC_URE3 has additional measures in place to ensure the reliability of the BPS. For example failure of a device will not disable the control operator’s visibility. Failure to dispatch in normal configuration has minimal impact. On-site electricians would dispatch the unit manually if necessary restoring operations in a matter of hours. | To mitigate this issue, WECC_URE3; 1) created unique device identifiers for each device for ease of tracking in data collection; 2) reviewed and updated individual, shared, and administrator accounts for all devices in scope; 3) updated passwords for all devices in scope; and 4) submitted TFE requests for the devices incapable of providing adequate password length. WECC approved both TFEs.
2013-04-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC201102924 | CIP-007-1 | R6 | WECC_URE3 submitted a Self-Report to WECC stating that it had an issue with CIP-007-1 R6. In its self-report, WECC_URE3 stated that it had an inadequate security monitoring and log review in place. WECC_URE3 stated that for several of its Cyber Assets, it failed to implement security controls to monitor cyber security system events. As a result, WECC_URE3 failed to issue alerts for detected cybersecurity incidents, as well as, maintain, retain, and review logs related to security events. These devices are located in Electronic Security Perimeters (ESPs). | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). During the issue period, there were a number of compensating measures in place to secure the devices against misuse or malicious attack. All devices were secured within a Physical Security Perimeter (PSP) and then an ESP with a card access system. All individuals must have an authorized card to access the PSP and ESP. In addition, WECC_URE3 stated that controls are implemented to log and monitor access to all Cyber Assets within the ESP and the physical and electronic alerts are reviewed 24 hours a day. For the devices in which it is technically infeasible to implement security controls, WECC_URE3 has additional measures in place to ensure the reliability of the BPS. For example failure of a device will not disable the control operator’s visibility. Failure to dispatch in normal configuration has minimal impact. On-site electricians would dispatch the unit manually if necessary restoring operations in a matter of hours. | To mitigate this issue, WECC_URE3; 1) created unique device identifiers for each device for ease of tracking in data collection; 2) reviewed and updated individual, shared, and administrator accounts for all devices in scope; and 4) submitted TFE requests for the devices. WECC approved both TFEs.
2013-04-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC2012009523 | CIP-004-3 | R4 | WECC_URE4 submitted a Self-Certification stating that it had an issue with CIP-004-3 R4. Specifically, WECC_URE4 reported that employees retired who had physical access to Critical Cyber Assets (CCAs) within the Physical Security Perimeters (PSP). WECC_URE4 noted that the individuals in scope were required to have physical access to the PSPs as part of their job duties, but not electronic access to CCAs. At the time these four individuals retired, WECC_URE4 was relocating all of its employees to a new facility. During this time, WECC_URE4 was shifting over to a new physical access control system which was not yet tied in electronically to the configuration management database. WECC_URE4’s revocation process consists of automated revocation of logical perimeter access and an electronic update of the access list upon processing an employee for termination. However, during the relocation, the Human Resource Department manually revoked the individuals' access privileges, but, the automated controls were not available to ensure revocation of physical CCA access and comprehensive updating of lists upon termination. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although the individuals in scope of the issue had physical access, they did not have electronic access to CCAs. Moreover, physical access was monitored by human observation continuously including security video monitoring. Furthermore, although WECC_URE4 did not update its access list, WECC_URE4 did revoke the individuals’ access privileges. Finally, this issue occurred during a construction phase for WECC_URE4, and during this time, WECC_URE4 assigned a dedicated security resource to oversee physical access beyond the typically assigned security. | To mitigate this issue, WECC_URE4: 1) revoked access to four retired employees; 2) updated access list to remove retired individuals; 3) completed logical connection between Human Resource databases; and 4) consolidated database evidence. WECC has verified the completion of all mitigation activity.
2013-04-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 5 (WECC_URE5) | NCRXXXXX | WECC2013011780 | CIP-006-3c | R2.1 | WECC_URE5 submitted a Self-Report to WECC stating that it had an issue with CIP-006-3c R2.1. WECC_URE5 reported that an employee was inadvertently granted physical access rights to Cyber Assets provisioning physical access control (PAC) to Physical Security Perimeters (PSPs). An employee was granted physical access to rooms containing PAC devices. Access was granted when a new ID card was being issued to a WECC_URE5 employee. While activating the card, WECC_URE5 staff inadvertently granted physical access rights using a “drop-down” menu in WECC_URE5’s physical access control system. The employee did not use this access. WECC_URE5 detected the error and revoked the access rights. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The scope of the issue is limited to a single employee who maintained physical access to devices for a period of less than a month. The PACs devices to which the individual was granted access were secured in rooms that logged and monitored all physical access attempts. Although the employee did not attempt to access either rooms during the duration of the issue, if the employee had attempted to gain access, WECC_URE5 had additional protections in place. The devices to which the employee was granted access were electronically secured. The devices were afforded the protections described under CIP-006-3 R2.2. Specifically, electronic access to the devices required a password. Any attempt by the employee to modify settings to the PACs devices would have triggered alarming. The employee did not have electronic access to the devices. | To mitigate this issue, WECC_URE5modified its physical access control system to reduce the likelihood that access would be inadvertently granted in the future and met with all individuals with administrate privileges to review access grant procedures.
2013-04-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 6 (WECC_URE6) | NCRXXXXX | WECC2013012073 | CIP-002-3 | R1 | WECC_URE6 submitted a Self-Certification to WECC stating that it had an issue with CIP-002-3 R1. Specifically, WECC_URE6 reported that it changed its Critical Asset identification methodology from a risk-based assessment methodology to a bright-line criteria methodology. WECC_URE6 reported that it later learned that the change in methodology resulted in an issue of CIP-002-3 R1. Under each methodology applied, WECC_URE6 had a null list of Critical Cyber Assets (CCAs). | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The potential risks to the BPS were minimized due to compensating measures in place during the duration of the issue. Prior to WECC_URE6 accepting the bright-line criteria methodology, WECC_URE6 applied a risk-based assessment methodology and properly identified its Critical Assets. Furthermore, WECC_URE6’s application of its bright-line criteria methodology produced a list of Critical Assets identical to that created by its previous risk-based assessment methodology. Additionally, the bright-line criteria methodology implemented by WECC_URE6 included proper procedures and considered all asset types as required by CIP-002. Finally, WECC_URE6 does not have CCAs associated with its identified Critical Assets. | To mitigate this issue, WECC_URE6 adopted a new risk-based assessment methodology to identify its Critical Assets as required by CIP-002.
2013-04-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 7 (WECC_URE7) | NCRXXXXX | WECC2013012112 | CIP-007-1 | R5 | WECC notified WECC_URE7 that WECC would be conducting an on-site Compliance Audit at WECC_URE7’s office (Audit Notice). After WECC sent the Audit Notice, but prior to WECC’s arrival for the on-site Compliance Audit, WECC_URE7 submitted a Self-Report stating that it had an issue with CIP-007-1 R5. In the Self-Report, WECC_URE7 stated that one of its Critical Cyber Assets (CCAs) was not capable of having a password of more than four characters as required by CIP-007-1 R5.3.1. WECC_URE7 reported that the device had not been included in its previously filed technical feasibility exception (TFE). | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this case, the potential risks associated with the issue were minimized due to WECC_URE7’s compensating measures. The device in scope is located within an Electronic Security Perimeter (ESP) and a Physical Security Perimeter (PSP) that have limited access. Access to the ESP and PSP is only authorized for personnel who have received CCA training and have undergone a personnel risk assessment. Additionally, the password that existed on the devices was a combination of alpha, numeric, and “special” characters and was changed annually. Finally, the network attached to the device is electronically monitored continuously and if suspicious traffic occurs an alert is immediately sent to WECC_URE7 staff. | To mitigate this issue, WECC_URE7 filed a TFE for the device in question and updated its CIP structured query language database.
2013-04-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 8 (WECC_URE8) | NCRXXXXX | WECC2012011330 | CIP-006-3a | R2 | WECC performed a Compliance Audit of WECC_URE8 which included auditing compliance with CIP-006-3a R2. During the course of the Compliance Audit, the Audit Team requested security testing evidence on physical access control systems (PACS) servers. WECC_URE8 made significant changes (upgrades) to the servers used in the access control and monitoring of the Physical Security Perimeters (PSPs), and failed to provide the protection of CIP-007 R1 (security testing) as required by CIP-006 R2.2. Based on WECC_URE8’s insufficient testing evidence, the Audit Team conducted an interview to discuss what cyber security test procedures WECC_URE8 currently had in place. During the interview, WECC_URE8 stated that it performed functional testing (done at the vendor location on a test server) upon making changes or implementing upgrades to the PACS servers; however, cyber security control testing was not addressed. Because WECC_URE8 did not provide security testing prior to installing the upgrades, WECC_URE8 failed to provide the protection of CIP-007 R1 to the servers, as required by CIP-006 R2.2. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although WECC_URE8 failed to perform security testing on the PACS servers, it did perform functional testing prior to installation. Additionally, the PACS servers are located on a protected network with firewall protection and continuous logging and monitoring of cyber access. Also, WECC_URE8 performs annual cyber vulnerability assessments on this protected network, and the PACS servers have antivirus installed. | To mitigate this issue, WECC_URE8: 1) set up a dedicated test server for PACS Cyber Assets to allow functional testing with the vendor and to facilitate testing of the cyber security controls; and 2) updated its test procedures to ensure that the PACS testing are performed consistently on the test system and on the production system. This process includes ensuring that the associated evidence is captured.
2013-04-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 9 (WECC_URE9) | NCRXXXXX | WECC2012011575 | CIP-002-3 | R1 | WECC conducted an on-site Compliance Audit of WECC_URE9's facilities and determined that WECC_URE9 had an issue with CIP-002-3 R1. WECC_URE9's Critical Asset identification procedure failed to include a risk-based assessment component; instead, WECC_URE9 had correlated the loss, compromise or misuse of asset function of each asset type for its bulk power system (BPS) Critical Asset characteristics, using characteristics defined in CIP-002-4, Attachment 1 (Version 4). The application of this Critical Asset identification procedure generated a null list of Critical Assets. As part of its review, the audit team also reviewed a prior version of WECC_URE9's procedure based on Version 3 of the CIP Standards, the version currently in effect. This Critical Asset identification procedure also returned null lists of Critical Assets and associated Critical Cyber Assets (CCAs). WECC determined WECC_URE9 had an issue of CIP-002-3 R1 for its failure to identify and document a risk-based assessment methodology to use to identify its Critical Assets and its CCAs, compliant with Version 3 of the CIP Standards. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. WECC performed site visits at WECC_URE9's facilities and determined that, as a compensating measure, WECC_URE9 employs air-gapped networks for its control systems. In addition, the networks are not connected to any other network, including the Internet, and only allow internal data transmission. Finally, both methodologies returned null lists for Cyber Assets and associated CCAs. | To mitigate this issue, WECC_URE9 revised its risk-based assessment methodology to include a risk-based assessment component. WECC has verified the completion of all mitigation activity.
2013-03-27 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2011008327 | CIP-007-1 | R5.2.1 | FRCC_URE1 self-reported an issue with CIP-007-1 R5.2.1 to FRCC. FRCC_URE1 failed to disable several administrative and user default accounts. FRCC_URE1 also did not change the passwords prior to placing the assets into service. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The risk was reduced because all the affected devices are behind a corporate firewall within a defined Electronic Security Perimeter and a required Physical Security Perimeter. In addition, the accounts are non-interactive or non-user accessible. Furthermore, the accounts are protected by operating system authorization and authentication prior to their use. | To mitigate this issue, FRCC_URE1: 1) changed the energy management system (EMS) provided account passwords using the EMS vendor to provide the services; 2) conducted a review of all Cyber Assets and documented all accounts required for operations; 3) changed other default account passwords for EMS workstations and servers that were not removed, disabled, or renamed, and where the passwords had not been changed; 4) changed default account passwords; 5) documented all system accounts after implementation of a new EMS system and ensured the passwords meet the password length, password age, and password complexity requirements. If any of these conditions were not met due to technical infeasibility, FRCC_URE1 submitted a technical feasibility exception with reference to the Mitigation Plan related to this issue; 6) ensured that accounts discovered during the review that are not required were either disabled or removed on the applicable Cyber Asset. For all other accounts, FRCC_URE1 changed passwords if the accounts were determined to be older than one year; 7) documented and identified all users who have access to shared or generic accounts and the reason why such access is required; 8) modified existing CIP-007 practice to include processes to define account roles, responsibilities, and functions, as well as controls for all accounts; and 9) created a new account management guideline that provides detailed procedural controls for the creation, function, role, governance, and access level for all accounts including the use of shared accounts on the EMS.
2013-03-27 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2011008538 | CIP-005-1 | R1.6 | FRCC conducted a Spot Check of FRCC_URE1. At the Spot Check, FRCC determined that FRCC_URE1 had an issue with CIP-005-1 R1.6. FRCC_URE1 failed to include one electronic access control and monitoring systems (EACMS) device in the documentation as required by CIP-005-1 R1.6. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. While the EACMS device was not included in the required documentation, the EACMS device was afforded all of the following required protective measures of CIP-003, CIP-004 R3, CIP-005 R2, R3, CIP-006 R2, R3, CIP-007 R1, R3, R4, R5, R6, R7, R8, R9, CIP-008 R1, R2, and CIP-009 R1, R2, R3, R5. These protective measures include: documenting and implementing a personnel risk assessment program; implementing and documenting the organizational processes and technical and procedural mechanisms for control of electronic access at all electronic access points to the Electronic Security Perimeter (ESP); implementing and documenting an electronic or manual process for monitoring and logging access at access points to the ESP 24 hours a day, seven days a week; manage physical access at all access points to the Physical Security Perimeter(s) 24 hours a day, seven days a week; monitoring physical access to the Physical Security Perimeters 24 hours a day, seven days a week using alarm systems and/or human observation of access points; ensuring that new Cyber Assets and significant changes to existing Cyber Assets within the ESP do not adversely affect existing cybersecurity controls; establishing and documenting a security patch management program; using anti-virus software and other malicious software prevention tools; establishing, implementing, and documenting technical and procedural controls that enforce access authentication of, and accountability for, all user activity, and that minimize the risk of unauthorized system access; ensuring that all Cyber Assets within the ESP implement automated tools or process controls to monitor system events related to cybersecurity; establishing formal methods, processes, and procedures for disposal or redeployment of Cyber Assets within the ESP; performing annually a cyber vulnerability assessment of all Cyber Assets within the ESP; reviewing and updating the documentation specified in Standard CIP-007 at least annually and documenting changes within 90 calendar days of the change; developing and maintaining a Cyber Security Incident response plan; keeping relevant documentation related to Cyber Security Incidents reportable per CIP-008-1 R1.1 for three calendar year; creating and annually reviewing, exercising and updating recovery plans for Critical Cyber Assets (CCAs); and ensuring information essential to recovery that is stored on backup media is tested at least annually that information is available. | To mitigate this issue, FRCC_URE1 properly identified the missing device as an EACMS device on the CCA list and approved Cyber Asset lists where appropriate.
2013-03-27 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2012010071 | CIP-004-3 | R4.1 | FRCC_URE1 self-reported an issue with CIP-004-3 R4.1. FRCC_URE1 failed to update the electronic Critical Cyber Asset (CCA) access list within seven days to reflect a change in personnel as required by the Standard. FRCC_URE1 had a student intern whose internship ended and no longer required access to the CCAs. While access was removed within 24 hours of this personnel change, the CCA access list was not updated on the list for 33 days. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The intern was not terminated for cause. FRCC_URE1 revoked access a day after the access was no longer needed as required by R4.2, timely collected all security pass cards, and disabled all electronic access passwords. After that time, the intern had no access to FRCC_URE1's energy management system control center or the building which houses the facility, nor did the intern attempt to gain access. This issue was a documentation error only. | To mitigate this issue, FRCC_URE1: 1) fixed the cybersecurity electronic access list to accurately reflect access to CCAs immediately upon discovery of the issue; and 2) trained users in the use and functionality of internal CIP-004 practice to ensure the human error associated with this Self-Report does not happen again.
2013-03-27 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2012011427 | CIP-003-3 | R2; R2.1; R2.2 | MRO_URE1 self-certified noncompliance with CIP-003-3 R.2.2, due to the failure to document a change to its CIP senior manager personnel within the required 30 day timeframe. A new CIP senior manager was assigned, but not formally documented in MRO_URE1's cybersecurity management document. Two individuals were assigned to replace the general manager, who was placed on administrative leave, and MRO_URE1 intended to assign one of those individuals, as CIP senior manager. Ten months later, MRO_URE1 updated its cybersecurity management document to reflect the designation of the CIP senior manager; however, the date of designation was not clear due to a misunderstanding regarding the effective date contained within the document. CIP-003-3 R2.1 requires a date of designation to be identified along with the name and title of the senior manager. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The designated individual assumed the duties of CIP senior manager immediately after the previous CIP senior manager was placed on leave and was known to others as holding that position. MRO_URE1 identified this individual to assume the duties of CIP senior manager, but merely lacked documentation. The issue was an administrative error. Furthermore, MRO_URE1 does not own or operate any Critical Assets or Critical Cyber Assets. | MRO_URE1 revised the its cybersecurity management document to designate the CIP senior manager. After discussions between MRO staff and MRO_URE1, MRO determined that the effective date was meant to serve as the date of designation.
2013-03-27 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2012011174 | CIP-006-3c | R1; R1.1 | RFC_URE1 self-reported an issue with CIP-006-3c R1.1 to ReliabilityFirst. While performing an on-site inspection at its energy control and data center facility, RFC_URE1 discovered that Cyber Assets resided in two rooms, thus identifying these rooms as Electronic Security Perimeters (ESPs) and Physical Security Perimeters (PSPs). These rooms did not have a fully enclosed six-wall border surrounding the Critical Cyber Assets (CCAs). RFC_URE1 discovered that there was an approximately two-foot gap below the raised floor, and an approximately four-foot gap above the drop ceiling. As a result, RFC_URE1 had an issue with CIP-006-3c R1.1 for failing to have an enclosed six-wall border surrounding the CCAs in these two rooms. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. RFC_URE1 has processes, tools, and procedures in place to control and monitor access to its ESPs and PSPs, including security cameras in place in the PSP at issue, 24 hour monitoring of the cameras, and physical or electronic checkpoints prior to entering the rooms. | To mitigate this issue, RFC_URE1: 1) added cameras to the room that already had cameras; and 2) reconfigured the PSP for the second room by installing: a) an air wall, which addresses the need for an enclosed six-wall border; b) a monitoring and access control in the existing cabinets where the CCAs reside; and c) digital door contacts and badge readers to those cabinets.
2013-03-27 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2012011587 | CIP-006-1 | R1; R1.1 | RFC_URE2 self-reported an issue with CIP-006-3c R1.1 to ReliabilityFirst. While conducting an inspection of the engineering room Physical Security Perimeter (PSP) at a generating station, RFC_URE2 discovered that the engineering room, which constitutes an Electronic Security Perimeter and PSP did not have a fully enclosed six-wall border surrounding the engineering work station, which is a Critical Cyber Asset (CCA). RFC_URE2 discovered that there was an eight to ten-inch gap below the raised floor and an approximate four-foot gap above the drop ceiling. As a result, RFC_URE2 had an issue with CIP-006-3c R1 for failing to have a fully enclosed six-wall border surrounding the CCAs in the engineering room. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The engineering room is an office located within the walls of the control room of the affected station, which is a secured facility with a gated entrance and security personnel. The control room is staffed 24 hours a day, and the control room operators have direct line of sight into the engineering room and the entrance to it. The entrance to the engineering room is secured by controlled key access, and the engineering workstation has both physical and electronic access controls. Given the presence of human observation and access control measures, it is unlikely that an unauthorized individual could gain access to the PSP through the gap above the drop ceiling and below the raised floors. | To mitigate this issue, RFC_URE2: 1) relocated the affected CCA (the engineering workstation) into a secure lockable cabinet; 2) updated the current physical security plan for the station; and 3) installed an electronic monitoring device to the cabinet that houses the CCA.
2013-03-27 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC2012011279 | CIP-006-1 | R1; R1.1 | RFC_URE3 self-reported an issue with CIP-006-3c R1 to ReliabilityFirst. As part of a vendor assessment of RFC_URE3’s CIP compliance program, RFC_URE3 discovered two gaps in the six-wall border of its control center that were greater than 96 square inches. The gaps were heating ventilation and air conditioning (HVAC) ducts, and there was no permanent barrier to physical entry through these ducts. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The ducts are located within RFC_URE3’s system control center, which is staffed 24 hours a day with operators and a security officer. | To mitigate this issue, RFC_URE3: 1) updated the physical drawings to include the location of all HVAC ducts; 2) investigated the issue to determine the accessibility of the ducts within all of its four Physical Security Perimeters (PSPs) and the number of penetration points; and 3) installed physical barriers in each instance where a duct penetrates a PSP.
2013-03-27 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC2013011660 | CIP-007-3 | R3; R3.1 | RFC_URE3 self-reported an issue with CIP-007-3 R3 to ReliabilityFirst. As part of an effort to streamline its patch management program, RFC_URE3 discovered that for certain Cyber Assets, on three separate occasions, it failed to document the assessment of security patches and security upgrades for applicability within 30 calendar days of availability of the patches or upgrades. First, RFC_URE3 failed to review a firmware version upgrade for applicability. The firmware version upgrade was applicable to four keyboard/video/mouse devices. Upon review of the release and vendor notes, RFC_URE3 determined the security-related fixes to be minor, and as a result, the recommended action would have been to defer installation to a later release. This issue occurred because RFC_URE3 solely relied on email notifications regarding product updates which it could too easily overlook or not receive. Second, RFC_URE3 failed to review a software upgrade and a software release for applicability. The software upgrade and release were applicable for four firewall devices. Upon review of the software upgrade, RFC_URE3 determined the security-related fixes to be minor, and as a result, the recommended action would have been to defer installation to a later release. This issue occurred because RFC_URE3 solely relied on email notifications regarding product updates which it could too easily overlook or not receive. Third, RFC_URE3 failed to review a software release for applicability. The software release was applicable to the same four firewall devices at issue above. Upon review of the software release, RFC_URE3 determined the release was related to hardware platforms or unused features. The release should have been applied to maintain a reasonable level of currency with the product code. This issue occurred because the security administration team did not clearly communicate patch releases to the patching subject matter expert (SME). | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The keyboard/video/mouse devices in the first issue were protected by firewalls, authentication to both the Electronic Security Perimeter secure access portal and command center and the disabling of direct access to the devices. In addition, direct access to these devices is disabled. Regarding the firewalls at issue, there was restrictive access to and through the firewalls themselves. | To mitigate this issue, RFC_URE3: 1) completed the patching program enhancement and published an updated procedure; 2) created a monthly notification event in the compliance database, which is a control activity, to check vendor sites for any new released firmware or software patches that relates to security updates; 3) ensured that the individual performing the assessment should not make the assumption that the vendor will directly communicate the existence of newly released patches; 4) updated its patch management procedure to clarify the expectations related to the level of detail for reviews and documentation of security patches and security updates; and 5) reworked the process so that individual reviewers will make their own patch release and review record updates rather than relaying them to the patching SME.
2013-03-27 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC2013011751 | CIP-007-3 | R5; R5.3.3 | RFC_URE3 self-reported an issue with CIP-007-3 R5 to ReliabilityFirst. RFC_URE3 discovered that for four Cyber Assets within the Electronic Security Perimeter (ESP), it failed to annually change passwords. RFC_URE3 installed these four devices, keyboard/video/mouse servers, which was when it set passwords for the local accounts in accordance with the complexity requirements of R5.3. Individuals rarely use these local accounts because support personnel access the servers from the associated client application on their support workstations. RFC_URE3 discovered the issue when an individual accessed the servers through the local account and realized that he had been using the same the password since the previous year and contacted the appropriate individuals regarding whether the password should be changed. RFC_URE3 had an issue with CIP-007-3 R5.3.3 for failing to annually change the password for these devices. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Each of the keyboard/video/mouse servers at issue is physically installed within an access controlled Physical Security Perimeter and an electronically-controlled ESP. In addition, these devices are not connected to the Internet, reducing the risk of unauthorized access. Also, the information available to the account user was not BPS information, reducing the risk to reliability of the BPS. Furthermore, there is no log record of the account being accessed during the time period of the issue. | To mitigate this issue, RFC_URE3: 1) changed the accounts’ passwords and added the accounts to the appropriate teams’ shared account management spreadsheet; 2) contacted all process owners for all non-Windows devices on the Cyber Asset list to verify that they have identified all local accounts on devices supported by their groups and managed the accounts in accordance with the corporate shared account management procedure; and 3) revised the wording on its security posture verification test result documentation forms to include language regarding changing local accounts.
2013-03-27 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 4 (RFC_URE4) | NCRXXXXX | RFC2013011928 | CIP-002-1 | R4 | ReliabilityFirst conducted an off-site Compliance Audit of RFC_URE4. During the Compliance Audit, ReliabilityFirst determined RFC_URE4, for one year, could not provide sufficient evidence demonstrating its senior manager approved its risk-based assessment methodology (RBAM) or the following second year's null list of Critical Assets and Critical Cyber Assets (CCAs) pursuant to CIP-002-1 R4. Specifically, RFC_URE4’s senior manager approved its the first year's null lists for its Critical Assets and CCAs, but did not sign and date the RBAM approval. Additionally, RFC_URE4's senior manager approved the second year's RBAM, but wrote “N/A” for "not applicable" in the location for approval of null lists for Critical Assets and CCAs. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The issue was caused by a documentation error. During the duration of the issue, while RFC_URE4's senior manager did not sign and date the first year's RBAM approval, RFC_URE4 did have a documented RBAM in place which it implemented. Additionally, during the Compliance Audit, RFC_URE4 provided ReliabilityFirst with evidence demonstrating its senior manager approved its RBAM and null lists of Critical Assets and CCAs, for the third year. Finally, although RFC_URE4's manager did not approval null lists for Critical Assets and CCAs in the second year, RFC_URE4 has no, and has never had, Critical Assets or CCAs. | To mitigate this issue, during the Compliance Audit, RFC_URE4 submitted to ReliabilityFirst an approved RBAM and null lists of Critical Assets and CCAs for the third year. ReliabilityFirst determined that RFC_URE4’s senior manager approved its RBAM and null lists for the third year, thereby correcting the documentation issue.
2013-03-27 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 5 (RFC_URE5) | NCRXXXXX | RFC2013011667 | CIP-003-2 | R2; R2.2 | RFC_URE5 self-reported an issue with CIP-003-3 R2.2 to ReliabilityFirst. RFC_URE5 reported that it failed to document changes in the designation of a senior manager within 30 days of the effective date as required by the Standard. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. When the senior manager's employment ended, RFC_URE5 had designated another individual as acting senior manager. The issue was limited to documentation only and was of a short duration. | To mitigate this issue, RFC_URE5 formally designated the acting senior manager as the new senior manager.
2013-03-27 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 6 (RFC_URE6) | NCRXXXXX | RFC2013011725 | CIP-004-3 | R4 | RFC_URE6 self-reported an issue with CIP-004-3 R4 to ReliabilityFirst. During a review of the authorized unescorted physical access list, RFC_URE6 discovered that it inadvertently removed an employee from its authorized unescorted physical access list during a quarterly review and update of the list, but continued to provide the employee with access to RFC_URE6’s Physical Security Perimeters. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The issue involved a clerical error on the access list for only one individual. In addition, the individual had, at all relevant times, a valid and current personnel risk assessment on file and up-to-date cybersecurity training, and was therefore eligible for unescorted physical access rights. | To mitigate this issue, RFC_URE6: 1) corrected it physical access list by reinserting the erroneously removed individual; and 2) required that future reviews include a comparison of the physical access list with other internal tracking lists.
2013-03-27 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC201000629 | CIP-004-2 | R4 | SERC_URE1 submitted a Self-Report to SERC stating that it had an issue with CIP-004-2 R4 because it did not revoke access within seven calendar days for personnel who no longer require such access to Critical Cyber Assets (CCAs). SERC requested and reviewed additional information in order to complete its assessment. An intern with electronic and physical access to CCAs left the employment of SERC_URE1 and no longer required access to CCAs. The intern had physical access to CCAs in a Physical Security Perimeter and electronic access to CCAs within the Energy Management System through two accounts. On the same day, a SERC_URE1 employee sent an email to the help desk reminding them to remove all of the intern’s physical and electronic access to CCAs. The help desk employee who received the email generated a work order for the removal of the intern’s physical access to the CCAs but did not generate a work order for the removal of the intern’s electronic access to the CCAs via the two accounts. SERC_URE1 removed the intern’s physical access to CCAs on the last day of the intern’s employment. Two weeks later, a SERC_URE1 employee sent an email requesting that the SERC_URE1 employees responsible for SERC_URE1's CCA access list review the list to ensure that there were no current or former employees with unauthorized access to CCAs. Six days later, the SERC_URE1 employee responsible for the review of the access list for one of the two accounts discovered that the intern’s electronic access remained enabled. SERC_URE1 reviewed the intern’s access, identified the electronic access to the additional account, and revoked the access to both accounts on the same day. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC_URE1 performed monthly reviews of the access lists to ensure they were up to date and accurate. SERC_URE1 removed the intern’s physical access to the CCAs on the same day that the intern ended employment with SERC_URE1. The intern did not have remote electronic access to CCAs. SERC_URE1 revoked the intern’s electronic access to CCAs 20 days after the intern left the employment of SERC_URE1. | To mitigate this issue, SERC_URE1: 1) disabled the intern's electronic access to all CCAs; and 2) provided training to ensure that all personnel responsible for removing access to CCAs remove both the physical and electronic access to CCAs. SERC has verified the completion of all mitigation activity.
2013-03-27 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2012011464 | CIP-002-3 | R3 | SERC_URE1 submitted a Self-Report to SERC stating that it had an issue with CIP-002-3 R3 because the SERC_URE1 CIP senior manager approved a list of Critical Cyber Assets (CCAs) that did not include a newly installed CCA. SERC requested and reviewed additional information in order to complete its assessment. SERC_URE1 completed the installation of a new workstation identified as a CCA. SERC_URE1's installation process requires SERC_URE1 to amend its CCA list when it adds a new CCA. SERC_URE1 missed this step in the process when it added the CCA workstation. The SERC_URE1 CIP senior manager signed the CCA list, which did not include the newly installed CCA. A month later, SERC_URE1 discovered that the CCA was not on the approved CCA list. SERC_URE1 created and approved an accurate CCA list. In addition, SERC_URE1 completed an assessment that determined there were no more CCAs missing from the CCA list. SERC_URE1 also determined that it had configured the missing CCA for CIP compliance in accordance with its processes and procedures. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although SERC_URE1 omitted the CCA workstation from the CCA list, SERC_URE1 was protecting it as a CCA. SERC_URE1 configured and tested the CCA workstation in accordance with SERC_URE1's procedures prior to commissioning. SERC_URE1 CIP senior manager signed the corrected CCA list 31 days after signing the inaccurate CCA list that did not include the newly installed CCA workstation. | To mitigate this issue, SERC_URE1: 1) added the newly installed CCA to the CCA list; and 2) amended the process for adding devices to include a step to amend the CCA list as appropriate. SERC has verified the completion of all mitigation activity.
2013-03-27 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP201100667 | CIP-002-3 | R4 | During a CIP Compliance Audit, SPP RE discovered that SPP RE_URE1 did not have a signed and dated record of its senior manager or delegate’s approval of its risk-based assessment methodology (RBAM) as prescribed by CIP-002-3 R4. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SPP RE_URE1 had a compliant RBAM in place during the pendency of the issue. Additionally, SPP RE_URE1 produced signed and dated records of its annual approval reviews of its RBAM; however, SPP RE_URE1's director of utilities, who was neither the senior manager nor a delegate of the senior manager, conducted the approval reviews. Notwithstanding, during the same time period, SPP RE_URE1's senior manager did sign and date annual approval reviews of SPP RE_URE1's Critical Asset and Critical Cyber Asset (CCAs) lists. Finally, SPP RE_URE1 applied its compliant RBAM and determined that it has no Critical Assets or CCAs. | SPP RE_URE1 developed an annual approval procedure sheet for CIP-002, which serves as a checklist for the four requirements found in R4, including a step for its senior manager to approve SPP RE_URE1's RBAM. Additionally, SPP RE_URE1 developed a signature sheet to be attached to the RBAM upon approval.
2013-03-27 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPPRE_URE2) | NCRXXXXX | SPP2012011150 | CIP-007-3 | R5.3; R5.3.3 | SPPRE_URE2 submitted a Self-Report to SPP RE stating that it had an issue with CIP-007-3 R5.3.3. SPPRE_URE2 failed to change a password on two servers on its Energy Management System (EMS) at least annually. SPPRE_URE2's EMS vendor advised SPPRE_URE2's that the password could not be changed due to technical limitations. However, SPPRE_URE2 did not request a Technical Feasibility Exception (TFE) for the inability to change the password. This issue lasted for 1 year and 11 months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The password was unchanged on two servers that were protected behind a Physical Security Perimeter (PSP) and Electronic Security Perimeter (ESP) in accordance with CIP-005 and CIP-006. The ESP access points are further overlaid with an intrusion detection system, which monitors for unauthorized access attempts. | SPPRE_URE2 upgraded to an EMS version that allows for annual password changes without the risk of harm to the EMS system. Consequently, a TFE is not required, and SPPRE_URE2 no longer utilizes the password at issue.
2013-03-27 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE201100336 | CIP-002-2 | R4 | Texas RE_URE1 submitted a Self-Report stating that it had an issue with CIP-002-2 R4. The senior manager at the time had approved and signed the Critical Assets and Critical Cyber Assets (CCA) lists, but had not approved and signed the risk-based assessment methodology (RBAM), as required. Texas RE determined that Texas RE_URE1 was in non-compliance from the date when CIP-002-2 became effective, through the date when the senior manager signed the new RBAM. | This issue posed a minimal risk and did not pose a serious or substantial risk to the bulk power system because at no time was Texas RE_URE1's RBAM or Critical Assets and CCA list incorrect or out of date. When reviewed and approved by the senior manager, these documents were not changed in any significant manner. The review and signature of the senior manager had no bearing on the contents of the RBAM or the Critical Assets and CCA list, nor on the operations of Texas RE_URE1. | The senior manager at Texas RE_URE1 had signed the RBAM and Critical Assets and CCA lists. The responsibilities for Texas RE_URE1 have been transferred to its parent company. Texas RE has verified that the parent company of this facility has reviewed its RBAM, and Critical Assets and CCA lists for all of its facilities. These documents have been signed by the senior manager. Texas RE has verified the mitigation activities as complete.
2013-03-27 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2013011741 | CIP-003-1 | R2 | WECC_URE1 submitted a Self-Report citing an issue with CIP-003-1 R2. In the Self-Report, WECC_URE1 stated that it had failed to document and identify by name, title, date of designation, and business phone or address, a single manager with overall responsibility and authority for leading and managing the implementation of, and adherence to, Standards CIP-002-1 through CIP-009-1. Although WECC_URE1 had failed to properly document its senior manager, WECC_URE1 identified and recognized a specific individual as the senior manager with authority over all CIP Standard responsibilities. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. While WECC_URE1 had no documented senior manager, WECC_URE1 did have an identified senior manager identified by name who was tasked with ensuring compliance to all CIP related standards. Additionally, WECC_URE1 applied its risk-based assessment methodology and determined that it does not have any Critical Assets or Critical Cyber Assets. | To mitigate this issue, WECC_URE1 revised its cyber security policy and included a provision clearly identifying by name, title and date of designation, a specific individual, as senior manager with overall responsibility and authority for leading and managing the entity’s implementation of, and adherence to, Standards CIP-002-2 through CIP-009-2.
2013-03-27 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2013011960 | CIP-002-3 | R1 | WECC conducted an off-site Compliance Audit of WECC_URE2. During the Compliance Audit, WECC determined that WECC_URE2 did not have a documented risk-based assessment methodology to identify its Critical Assets. Specifically, WECC_URE2 changed its Critical Asset identification methodology from a risk-based assessment methodology to a bright line criteria methodology. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The potential risks to the BPS were minimized due to compensating measures in place during the duration of the issue. Prior to the bright line criteria methodology becoming effective, WECC_URE2 applied a risk-based assessment methodology and properly identified its Critical Assets. Furthermore, WECC_URE2’s application of its bright line criteria methodology produced a list of Critical Assets nearly identical to that created by its previous risk-based assessment methodology. Additionally, the bright line criteria methodology implemented by WECC_URE2 included proper procedures and considered all asset types as required by CIP-002. WECC_URE2 does not have Critical Cyber Assets associated with its identified Critical Assets. | To mitigate this issue, WECC_URE2 adopted a new risk-based assessment methodology to identify its Critical Assets as required by CIP-002.
2013-02-28 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2012010874 | CIP-004-3 | R4; R4.1 | NPCC_URE1 self-reported an issue with CIP-004-3 R4.1. NPCC_URE1 failed to update its list of personnel with authorized cyber access to Critical Cyber Assets (CCAs) within seven calendar days. NPCC_URE1 was informed by a vendor that one of its personnel with authorized cyber access to CCAs was no longer employed by the vendor. The employee had voluntarily resigned his position 32 days earlier and the vendor immediately revoked cyber access to all of NPCC_URE1’s CCAs for the individual on the date of his termination. Because the vendor did not inform NPCC_URE1 of the employee's access revocation until 32 days had passed, NPCC_URE1's list was not updated within seven days. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). A personnel risk assessment (PRA) had been completed on the individual at issue prior to his being granted access to NPCC_URE1’s CCAs. The PRA was still valid at the time of his resignation. The individual had also completed annual cybersecurity training, as required by NPCC_URE1’s cybersecurity training program. The individual was never issued an identification card or access card by NPCC_URE1. This individual was never granted unescorted physical access to NPCC_URE1’s CCAs. After the employee resigned, the vendor revoked all electronic access to NPCC_URE1 Cyber Assets. NPCC_URE1 has inspected the electronic access logs for NPCC_URE1’s Electronic Security Perimeter and verified that the individual did not access any of NPCC_URE1’s CCAs after the date of termination of his employment. | To mitigate this issue, NPCC_URE1 updated its protected cyber system access list to accurately reflect the status of all applicable personnel. NPCC_URE1 now requires that vendors and contractors notify NPCC_URE1 within 24 hours when the employment status changes for an individual with unescorted physical access or cyber access to NPCC_URE1’s protected Cyber Assets. NPCC_URE1 updated its CIP annual training for vendors and NPCC_URE1 managers to include the review of specific requirements for removal of access and updating of access lists at the time of termination. NPCC_URE1 also revised the PRA section of its contract service agreements to include provisions requiring the vendor to notify NPCC_URE1 within 24 hours when unescorted physical access or cyber access is no longer required or the vendor terminates an employee. Lastly, NPCC_URE1 verified that applicable vendors have procedures to notify NPCC_URE1 within 24 hours when an applicable employee is terminated or there is a relevant change in the employee's status.
2013-02-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2012010753 | CIP-004-1 | R3 | RFC_URE1 self-reported an issue with CIP-004-1 R3 to ReliabilityFirst. RFC_URE1 identified the issue as relating to CIP-006-1 R1.8. ReliabilityFirst subsequently determined that the facts and circumstances constituted an issue with CIP-004-1 R3. RFC_URE1 contracted with a consultant to conduct an annual review of its personnel risk assessment (PRA) program. As a result of that review, RFC_URE1 discovered three instances where it granted its employees authorized cyber access to Critical Cyber Assets without conducting a timely PRA. For two of the employees, RFC_URE1 granted cyber access before it completed the respective PRAs 10 months and 14 months later. For the third employee, RFC_URE1 granted cyber access seven days before the employee completed the PRA. In its Self-Report, RFC_URE1 identified seven additional instances where it granted cyber access to an employee prior to conducting a PRA. ReliabilityFirst determined, however, that these instances were not possible violations because CIP-004-1 R3 was in effect during the time period, which required RFC_URE1 to conduct a PRA within 30 days of granting cyber access. For the seven instances, RFC_URE1 conducted the PRA within 30 days of granting cyber access. | This issue posed a minimal risk and did not pose a serious or substantial risk to reliability of the bulk power system (BPS). A violation of CIP-004 R3 has the potential to affect the reliable operation of the BPS by providing the opportunity for unknown, unverified, or criminal individuals to access Critical Cyber Assets (CCAs), which could result in harm to the integrity of the CCAs. The risk posed to the reliability of the BPS by the issue was mitigated by the following factors. The individuals at issue were part of one of the following two user groups: service dispatchers and IT support. First, the service dispatchers have read-only access to the energy control system in a distribution operator capacity due to RFC_URE1’s use of the energy control system for distribution in addition to transmission. Second, the IT support personnel had cyber access to workstations that are physical access control system assets where the IT support personnel only had operating system access and not application access. Operating system access allows the user to modify only the underlying operating system including device drivers and add or upgrade applications as required for support of corporate services. These individuals had no rights to the physical access control system and could not modify any access rights or privileges within that system. Application access requires an additional level of authentication that these individuals did not have. | To mitigate the issue, RFC_URE1: 1) reviewed the status of all individuals with authorized cyber or authorized unescorted physical access to CCAs; 2) verified that all individuals have current PRAs within seven years; 3) revised its procedures to review the daily report of employee change records to ensure appropriate access grants; and 4) revised its PRA verification procedures to ensure it conducts PRAs prior to granting access.
2013-02-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2012011578 | CIP-005-1 | R1; R1.6 | ReliabilityFirst conducted a Compliance Audit of RFC_URE2. During the Compliance Audit, ReliabilityFirst determined RFC_URE2 did not maintain its documentation pursuant to CIP-005-1 R1.6. Specifically, RFC_URE2 did not synchronize all Electronic Security Perimeter (ESP) related documentation, did not document all Cyber Assets, did not clearly mark all electronic access points to the ESP, and did not categorize Cyber Assets as Critical Cyber Assets or access points. | This issue posed a minimal risk and did not pose a serious or substantial risk to reliability of the bulk power system (BPS). The risk posed to the reliability of the BPS by the issue was mitigated by the fact that this issue was a documentation error. During Compliance Audit, ReliabilityFirst confirmed during a site visit that, although documentation was lacking, RFC_URE2 was properly protecting all of its Cyber Assets within an Electronic Security Perimeter and Physical Security Perimeter. | To mitigate the issue, RFC_URE2: 1) synchronized its documentation related to its ESP; 2) included and properly categorized all Cyber Assets; and 3) ensured its documentation clearly marked electronic access points to the ESP.
2013-02-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2012011579 | CIP-007-1 | R1; R1.3 | ReliabilityFirst conducted a Compliance Audit of RFC_URE2. During the Compliance Audit, ReliabilityFirst determined RFC_URE2 did not document all test results for all change requests, as required by CIP-007-1 R1.3. RFC_URE2 uses a test script worksheet to process all change requests. ReliabilityFirst discovered several instances in which RFC_URE2 did not complete, or only partially completed, test scripts for change requests. | This issue posed a minimal risk and did not pose a serious or substantial risk to reliability of the bulk power system (BPS). The risk posed to the reliability of the BPS by the issue was mitigated by the fact that this issue was a documentation error. This issue was a documentation error because, although RFC_URE2 did not fully document the test results, RFC_URE2 was able to demonstrate that it followed and successfully completed each step listed on its test script worksheet for all change requests. | To mitigate the issue, RFC_URE2 reinforced the requirement that test scripts must be completed for every change request and includes instructions on its test scripts stating, “a Pass or Fail must be entered on every step before form can be closed.”
2013-02-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2012011580 | CIP-007-1 | R3 | ReliabilityFirst conducted a Compliance Audit of RFC_URE2. During the Compliance Audit, ReliabilityFirst determined RFC_URE2 had an issue with CIP-007-1 R3 as it did not document that it assessed security patches and security upgrades within 30 calendar days of availability. ReliabilityFirst also determined RFC_URE2 did not document the compensating measures it applied to mitigate risk exposure for those patches it did not install. | This issue posed a minimal risk and did not pose a serious or substantial risk to reliability of the bulk power system (BPS). The risk posed to the reliability of the BPS by the issue was mitigated by the fact that this issue was a documentation error. During the Compliance Audit RFC_URE2 provided ReliabilityFirst with evidence demonstrating that it kept all its Cyber Assets up to date with the latest available patches even though RFC_URE2 did not document that it assessed security patches and security upgrades within 30 calendar days of availability. | To mitigate the issue, RFC_URE2 updated its security patch management procedure to help ensure it documents its assessment of security patches within 30 calendar days and documents the compensating measures it applies for those patches it does not install.
2013-02-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2012011581 | CIP-007-1 | R6; R6.5 | ReliabilityFirst conducted a Compliance Audit of RFC_URE2. During the Compliance Audit, ReliabilityFirst determined RFC_URE2 had an issue with CIP-007-1 R6.5 as it could not provide documentation that demonstrated it reviewed its system event logs. | This issue posed a minimal risk and did not pose a serious or substantial risk to reliability of the bulk power system (BPS). The risk posed to the reliability of the BPS by the issue was mitigated by the fact that this issue was a documentation error. RFC_URE2 had system event logs, but it did not document its review of those logs. RFC_URE2 reviewed the logs but was unable to demonstrate its review of the logs. Additionally, the risk was mitigated by the fact that RFC_URE2’s network is a closed network with no access to the Internet. Furthermore, RFC_URE2 generates alerts from its access points of events that could pose potential risk to the BPS. | To mitigate the issue, RFC_URE2 revised its monitoring and logging procedure to ensure that RFC_URE2 reviews and maintains records documenting the review of logs of system events related to cybersecurity at least quarterly.
2013-02-28 | ReliabilityFirst Corporation (ReliabilityFirst), Texas Reliability Entity (Texas RE), Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 3 (RFC_URE3, TRE_URE3, SPP RE_URE3) (Collectively, URE_3) | NCRXXXXX | RFC2012009909 TRE2012009940 SPP2012009918 | CIP-004-3 | R4 | This issue involved four incidents of noncompliance with CIP-004-3 R4 by URE_3: 1) URE3 self-reported an issue with CIP-004-3 R4 to three Regional Entities. A contractor in URE3's workplace services department, who had authorized unescorted physical access to Critical Cyber Assets (CCAs), resigned and no longer required such access. URE_3 failed to revoke the employee’s access within seven calendar days as required by the Standard, and revoked the employee’s access 30 days later; 2) URE_3 submitted a Self-Report to three Regional Entities identifying an issue with CIP-004-3 R4. The Self-Report identified one common instance of an issue among the Regional Entites and one additional instance unique only to SPP RE. Subsequently, URE_3 submitted evidence demonstrating that it did not in fact have an issue with CIP-004-3 R4 with respect to the common instance. As a result, the Regional Entities did not pursue this issue. However, the instance unique only to SPP RE was a non-compliant issue. URE3 submitted a Self-Report to SPP RE identifying an issue with CIP-004-3 R4. A building maintenance technician who had physical access to a Physical Security Perimeter resigned and no longer required such access. URE_3 failed to revoke the employee’s access within seven calendar days, and revoked the employee’s access nine days later; 3) URE_3's submitted Self-Reports to the Regional Entities identifying an issue with CIP-004-3 R4. An URE_3 employee within an operations business unit who had authorized cyber access to certain generation control supervisory control and data acquisition system CCAs no longer required such access. URE_3 failed to revoke the employee’s access within seven calendar days, and revoked the employee’s access 36 days later; and 4) URE_3 submitted Self-Reports to the Regional Entities identifying an issue with CIP-004-3 R4. An information technology service desk contractor who had authorized cyber access to CCAs no longer required such access. URE_3 failed to revoke the contractor’s access within seven calendar days and revoked the contractor’s access 18 days later. | This issue posed a minimal risk and did not pose a serious or substantial risk to reliability of the bulk power system (BPS). An issue with CIP-004 R4 has the potential to affect the reliable operation of the BPS by providing the opportunity for personnel that a responsible entity determined should no longer have access to CCAs, with potential access to CCAs. Such continued access could result in harm to the integrity of the CCAs or the reliability of the BPS as a result of actions by an individual who should no longer have physical or electronic access to CCAs. The risk posed to the reliability of the BPS by the issue was mitigated by the following factors. URE_3 discovered these instances of noncompliance due to its internal controls when it performed its routine quarterly reviews of employees and contract employees. In each instance, URE_3 revoked access almost immediately after discovering it had not revoked access, and, in each instance, URE_3 discovered the issue no later than one month after access revocation was required. In addition, all of the employees and contractors in each instance were not terminated for cause and resigned except for one employee, whose manager determined that access was no longer required to perform the job function. Furthermore, the individuals who had physical access no longer had their physical access badges, reducing the likelihood the individuals could gain access to the Physical Security Perimeter. One individual did not have physical access at the time of resignation, and URE_3 collected that individual’s secure identification token at the time of resignation thereby preventing remote access. | To mitigate the issue, URE_3: 1) revoked the individuals’ access rights; 2) identified, developed, and made available awareness and training for managers who have NERC CIP contractors or employees; 3) sent a letter to managers summarizing termination responsibilities; 4) developed a pending revocation report to show all outstanding electronic access revocation requests; and 5) made appropriate clarifications on the form utilized to begin the process of terminating an individual’s electronic access.
2013-02-28 | ReliabilityFirst Corporation (ReliabilityFirst), Texas Reliability Entity (Texas RE), Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 3 (RFC_URE3, TRE_URE3, SPP RE_URE3) (Collectively, URE_3) | NCRXXXXX | RFC2012001311 TRE2012009732 SPP2012009559 | CIP-006-3c | R1; R1.4; R1.6 | URE3 submitted respective Self-Reports to SPP RE, Texas RE, and ReliabilityFirst identifying an issue with CIP-006-3c R1.4. An URE_3 information technology (IT) employee without authorized unescorted physical access entered a Physical Security Perimeter (PSP) by tailgating through a door. The URE_3 IT employee entered the lobby adjoining the PSP. At 13:47, an URE_3 operations employee with authorized unescorted physical access exited the PSP door, and at the same time, the URE_3 IT employee exited the elevator and walked quickly toward the PSP door, grabbing the door handle just before the door closed and locked. The URE_3 IT employee pulled the door open, walked through it, and wandered around the floor before asking for assistance from an administrative assistant. The URE_3 IT employee was escorted to the electronic logging system, received a badge, and was checked in and out as a visitor. 9 minutes later, the URE_3 IT employee was escorted out of the area. URE_3 submitted Self-Reports to ReliabilityFirst and SPP RE identifying an issue with CIP-006-3c R1.6 which stemmed from three instances of noncompliance. First, an instance occurred that impacted ReliabilityFirst and SPP RE. URE_3 staff visited the an URE3 engineer for area development discussion. The discussion occurred in an URE_3 meeting room. During the meeting, the engineer briefly exited the meeting room for 15 to 20 seconds to go to the printer. The visitors remained in the room during this unescorted period because the meeting room, which is located down the hall from the printer, is visible from the printer area and the individual was only outside of the room for a few seconds to retrieve a printout. Second, an instance occurred that impacted ReliabilityFirst and SPP RE. A security guard escorted a vending machine repairman into control center kitchen to repair a vending machine. At an unknown point, the security guard left the repairman alone in the kitchen without transferring escort responsibility to control center personnel. The repairman remained in the kitchen until requesting the control center personnel to let the repairman exit the kitchen. The control center operator escorted the repairman to the main entrance of the control center where the security guard met them and resumed escort out of the center. Third, an instance occurred that impacted SPP RE only. URE_3 received an alarm indicating that a door was forced open at a supervisory control and data acquisition (SCADA) Computer Room main door. The operations center called the room and an URE_3 electrician answered the phone. The electrician reported that when he entered the room, he set the alarm off, and he could not exit the room. The operations center discovered that the electrician did not have the correct access for this room and opened the door for the electrician so he could exit the room. The operations center relocked the door once the electrician exited the room, and asked the electrician to pull on the door to ensure that it was locked. URE_3 conducted a follow-up investigation and discovered that the door magnetic lock was not fully engaged, but the door locks met close enough to show that the door was closed. Furthermore, URE_3 discovered that it had revoked the electrician’s access to that room during quarterly access reviews when the electrician was on a leave of absence. The electrician still maintains authorized unescorted physical access to other areas. URE_3 submitted a Self-Report to ReliabilityFirst identifying an issue with CIP-006-3c R1.6. An URE_3 wireman had visitors at a substation in order to pull new cables into the substation. The wireman called the security department to request the ability to prop a door open at the substation in order to install the new cable runs in the substation. The security department granted the request and advised the wireman to swipe his badge each time he entered and exited the control house at the substation, and sign the visitors in and out each time they entered and exited the control house. The security department advised the wireman to call the security department every time the visitors entered and exited the control house as well and that the wireman should not leave the visitors unescorted in the control house. The security department received a door prop alarm from a door at the substation, as expected. A few hours later, the security department ran a badge analysis history for the wireman because the door had been propped open for several hours, and the security department had received no calls. Two hours later, the security department manager advised the security department to call the control house, at which time the wireman said that the visitors were still onsite and, at one point, the wireman went to his van leaving the visitors unescorted. As a result, URE_3 failed to provide these visitors with a continuous escort. | This issue posed a minimal risk and did not pose a serious or substantial risk to reliability of the bulk power system (BPS). An issue with CIP-006-3c R1 has the potential to affect the reliable operation of the BPS by providing the opportunity to physically access Cyber Assets that are not protected by the implementation of a physical security plan. The risk posed to the reliability of the BPS by the issue was mitigated by the following factors. The issue occurred for a short duration prior to the URE_3 IT employee being logged in and escorted. In addition, at no time was the URE_3 IT employee in proximity to Critical Cyber Assets (CCAs) without an escort. Authorized personnel were in close proximity to the CCAs and would likely have resisted any unauthorized attempts at physical access. All of the escorting employees at issue remain employees of URE_3 who are trusted with authorized unescorted physical access. Regarding the instance where URE3 left meeting attendees unescorted for 15 to 20 seconds, the meeting room has no CCAs and there are multiple layers of security access control devices between the meeting room and the CCAs including a biometric reader, proxy card reader, and man-trap doors. In addition, the engineer attested that the visitors remained in the meeting room during the unescorted period. The visitors remained in the room during this unescorted period because the meeting room, which is located down the hall from the printer, is visible from the printer area and the individual was only outside of the room for a few seconds to retrieve a printout. Regarding the instance with the vending machine repairman, there are no CCAs in the kitchen. The CCA area is isolated and far away from the kitchen. There were six operators on duty in the CCA area during the unescorted period and no one saw the repairman leave the kitchen area until he was finished with the repairs. Regarding the instance with the electrician, the electrician had a valid personnel risk assessment and cybersecurity training. Until his leave of absence, he had authorized unescorted physical access to the computer room. CCAs are protected by username and password, and the Electronic Security Perimeter is protected by an access control list that verifies access rights. URE_3 had not assigned contractors usernames and passwords, so they could not access the CCAs. | URE_3 submitted to ReliabilityFirst a Mitigation Plan to address the issue with CIP-006-3c R1.4. URE_3 enhanced its physical barriers by installing keycard restrictions in the elevators through which the tailgater entered, requiring the use of a building badge for the elevator to stop at the lobby, and modifying the door to ensure it closes more quickly. In addition, URE_3 improved signage at the relevant location by performing an assessment of the existing signage and create and implement a strategy for enhancing existing signage. Furthermore, URE_3 provided additional training for personnel who have authorized unescorted physical access to the relevant PSP on the responsibilities of having such access, including ensuring that doors close securely during ingress and egress and monitoring the activities of individuals in the lobbies outside the PSP to prevent tailgating. URE_3 submitted to ReliabilityFirst a Mitigation Plan to address the issue with CIP-006-3c R1.6. URE_3 revised its communication and operation procedures to minimize human error including security awareness training, signage regarding visitors, minimizing visitors to the control center during off-business hours, and reminding escorts and visitors of the CIP requirements upon sign in. In addition, URE_3 reconfigured the operations center to remove the office area meeting room from the PSP, updated the operations center visitor check-in process, and repaired the SCADA room security door.
2013-02-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC2012010100 | CIP-006-3c | R1; R1.1 | RFC_URE3 submitted a Self-Report to ReliabilityFirst identifying an issue with CIP-006-3c R1.1. While conducting annual preventative maintenance on its security system, RFC_URE3 discovered approximately seven 22 by 12 inch holes with cables running through them above the main door to a telecom room. Two weeks later, RFC_URE3 repaired the holes. RFC_URE3 identified an addition instance of CIP-006-3c R1 in ReliabilityFirst. At a supervisory control and data acquisition (SCADA) computer room Physical Security Perimeter (PSP), RFC_URE3 discovered several instances where there was a 25 to 35 inch gap between the top of the walls and the concrete roof support. 2 weeks later, RFC_URE3 repaired the holes. | This issue posed a minimal risk and did not pose a serious or substantial risk to reliability of the bulk power system (BPS). The risk posed to the reliability of the BPS by the issue was mitigated because there are additional layers of security that one would have to penetrate to enter the PSP. The PSP is located in a small room within a larger room that has a separate door with a keypad lock. The holes did not lead outside the larger room. The SCADA computer room is located inside a building perimeter with partial fencing, and is secured with locks and card readers. | RFC_URE3 submitted to ReliabilityFirst a Mitigation Plan to address the first instance of the issue with CIP-006-3c R1.1. RFC_URE3 patched the gaps in the six-wall border and updated its physical security site survey checklist to remind services to: inspect rooms for potential gaps in the six-wall border; have workplace services and/or physical security personnel inspect all PSPs for any gaps in the six-wall border; review and inspect questionable gaps; and remediate any gaps discovered.
2013-02-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC2012001312 | CIP-006-3c | R5 | RFC_URE3 self-reported an issue with CIP-006-3c R5 to ReliabilityFirst. The station manager for a substation reported an issue to the security department. The station crew had permission to prop open the CIP station control building door while pulling in new control cables. At some point during their work, the crew began searching for materials in the station yard and left the control building unattended with the doors propped open for approximately 20 minutes. The station superintendent brought this to the crew’s attention and reported the issue to the security deparment. RFC_URE3 failed to monitor these physical access point during that time period. | This issue posed a minimal risk and did not pose a serious or substantial risk to reliability of the bulk power system (BPS). An issue with CIP-006 R5 has the potential to affect the reliable operation of the BPS by providing the opportunity to access the Physical Security Perimeter as failure to comply with the Standard means there are inadequate technical and procedural controls to monitor physical access points. The risk posed to the reliability of the BPS by the issue was mitigated by the following factors. RFC_URE3’s station manager identified this issue and reported it immediately as a CIP issue to the security department, illustrating that RFC_URE3’s internal controls caused RFC_URE3 to discover this issue. No unauthorized personnel were in the control house at the time the station superintendent re-entered it. The Critical Cyber Asset devices are protected by access control lists and require usernames and passwords in order to access the devices. In addition, the contractors were working outside in the yard approximately 1,000 feet from the control house. A supervisor was onsite and none of the contractors entered the building. | To mitigate the issue, RFC_URE3: 1) held a meeting with the associated station manager to discuss the mitigation options; 2) held a staff meeting with the department to review the CIP procedures for propping doors open for work; 3) developed a discussion training guide to reinforce the policy and expected conduct; 4) sent out an email reminder with the previous documents and summary; and 5) implemented a reminder script from the security department on the door prop open request for the security department to read to the station staff requesting the door prop.
2013-02-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 4 (RFC_URE4) | NCRXXXXX | RFC2012011126 | CIP-002-1 | R2 | ReliabilityFirst conducted a Compliance Audit of RFC_URE4. During the Compliance Audit, ReliabilityFirst determined that RFC_URE4 did not have a documented risk-based assessment methodology (RBAM) to identify Critical Assets pursuant to CIP-002-1 R1. Therefore, RFC_URE4 could not demonstrate that it applied its RBAM annually to develop a list of Critical Assets pursuant to CIP-002-1 R2. | This issue posed a minimal risk and did not pose a serious or substantial risk to reliability of the bulk power system (BPS). The risk posed to the reliability of the BPS by the issue was mitigated by the fact that RFC_URE4 has no Critical Assets. Throughout the duration of the issue, RFC_URE4 used a spreadsheet with evaluation criteria rather than a documented and approved RBAM to determine if it had Critical Assets. Examples of evaluation criteria RFC_URE4 used include whether an asset at issue is critical to initial restoration and automatic load shedding or functioned as a control center or back-up control center. | To mitigate the issue, RFC_URE4: 1) conducted a NERC Reliability Standard Compliance training program for RFC_URE4 personnel; 2) appointed a compliance coordinator; 3) confirmed it has no Critical Assets; and 4) approved a documented RBAM.
2013-02-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 4 (RFC_URE4) | NCRXXXXX | RFC2012011127 | CIP-002-1 | R4 | ReliabilityFirst conducted a Compliance Audit of RFC_URE4. During the Compliance Audit, ReliabilityFirst determined RFC_URE4 did not have a documented risk-based assessment methodology (RBAM) to identify Critical Assets pursuant to CIP-002-3 R1. Therefore, RFC_URE4 could not demonstrate that it annually approved its RBAM pursuant to CIP-002-3 R4. | This issue posed a minimal risk and did not pose a serious or substantial risk to reliability of the bulk power system (BPS). The risk posed to the reliability of the BPS by the issue was mitigated by the fact that RFC_URE4 has no Critical Assets. Throughout the duration of the issue, RFC_URE4 used a spreadsheet with evaluation criteria rather than a documented and approved RBAM to determine if it had Critical Assets. Examples of evaluation criteria RFC_URE4 used include whether an asset at issue is critical to initial restoration and automatic load shedding or functioned as a control center or back-up control center. | To mitigate the issue, RFC_URE4: 1) conducted a NERC Reliability Standard Compliance training program for RFC_URE4 personnel; 2) appointed a compliance coordinator; 3) confirmed it has no Critical Assets; and 4) approved a documented RBAM.
2013-02-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 4 (RFC_URE4) | NCRXXXXX | RFC2012011128 | CIP-003-3 | R2; R2.2 | During a Compliance Audit. ReliabilityFirst determined that RFC_URE4 could not provide evidence that it documented a change to its senior manager designation within 30 calendar days of the effective date. Specifically, although RFC_URE4 appointed its plant manager as the senior manager for implementation of, and adherence to, the CIP Reliability Standards, RFC_URE4 failed to document this change within 30 calendar days. | This issue posed a minimal risk and did not pose a serious or substantial risk to reliability of the bulk power system (BPS). The risk posed to the reliability of the BPS by the issue was mitigated by the fact that this was a documentation error. It was a documentation error because RFC_URE4 did appoint a senior CIP manager who functioned in that capacity throughout the duration of the issue. RFC_URE4 just neglected to document the change. | To mitigate the issue, RFC_URE4 appointed a senior manager and documented the change.
2013-02-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 4 (RFC_URE4) | NCRXXXXX | RFC2012011129 | CIP-002-1 | R1 | ReliabilityFirst conducted a Compliance Audit of RFC_URE4. During the Compliance Audit, ReliabilityFirst determined that RFC_URE4 did not have a documented risk-based assessment methodology (RBAM) to identify Critical Assets pursuant to CIP-002-3 R1. | This issue posed a minimal risk and did not pose a serious or substantial risk to reliability of the bulk power system (BPS). The risk posed to the reliability of the BPS by the issue was mitigated by the fact that RFC_URE4 has no Critical Assets. Throughout the duration of the issue, RFC_URE4 used a spreadsheet with evaluation criteria rather than a documented and approved RBAM to determine if it had Critical Assets. Examples of evaluation criteria RFC_URE4 used include whether an asset at issue is critical to initial restoration and automatic load shedding or functioned as a control center or back-up control center. | To mitigate the issue, RFC_URE4: 1) conducted a NERC Reliability Standard Compliance training program for RFC_URE4 personnel; 2) appointed a compliance coordinator; 3) confirmed it has no Critical Assets; and 4) approved a documented RBAM.
2013-02-28 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC200900651 | CIP-004-1 | R2 | SERC_URE1 submitted a Self-Report to SERC stating that it had an issue with CIP-004-1 R2.1 because it had failed to establish, maintain, and document an annual cyber security training program for personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets (CCA). SERC_URE1 learned that a contractor for SERC_URE1’s agent had access to CCAs for support and maintenance purposes but was unaware of specific CIP-004 requirements. While the contractor’s firm maintained some cyber security training and awareness, these internal efforts did not cover specific entity policies and access controls, proper use of CCAs, proper handling of CCA information, plans to recover or re-establish CCAs, or documentation of training conducted. It was determined that SERC_URE1 did not have adequate procedures to monitor and ensure CIP-004 R2 compliance of personnel with access to CCAs. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. This issue was for one contractor with only remote electronic access to memory devices. The untrained contractor only provided technical support for memory devices that supported CCA servers. | To mitigate this issue, SERC_URE1's agent implemented a cyber security training program that covered all aspects of CIP-004 R2.
2013-02-28 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC200900652 | CIP-004-1 | R3 | SERC_URE1 submitted a Self-Report to SERC stating that it had an issue with CIP-004-1 R3 because it failed to have a documented personnel risk assessment (PRA) program for personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets (CCAs). SERC_URE1 learned that a contractor for SERC_URE1’s agent had access to Critical Cyber Assets (CCAs) for support and maintenance purposes but was unaware of specific CIP-004 requirements. While the contractor’s firm performed some pre-employment background checks, these internal efforts did not meet the level required by CIP-004-1 R3. It was determined that SERC_URE1 did not have a PRA program that sufficiently addressed contractor personnel with access to CCAs. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. This issue was for one contractor with only remote electronic access to memory devices. The contractor only provided support for memory devices that supported CCA servers. | To mitigate this issue, SERC_URE1's agent implemented a PRA program for contractors with access to CCAs.
2013-02-28 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC200900653 | CIP-004-1 | R4 | SERC_URE1 submitted a Self-Report to SERC stating that it had an issue with CIP-004-1 R4 because it failed to maintain list(s) of personnel with authorized cyber or authorized unescorted physical access to Critical Cyber Assets (CCAs), including their specific electronic and physical access rights to CCAs. SERC_URE1 learned that a contractor for SERC_URE1's agent had access to CCAs for support and maintenance purposes but was unaware of specific CIP-004 requirements. It was determined that SERC_URE1 did not include the contractor on its list of personnel with authorized cyber or authorized unescorted physical access to CCAs, including his or her specific electronic and physical access rights to CCAs. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. This issue was for one contractor with only remote electronic access to memory devices. The contractor only provided support for memory devices that supported CCA servers. | To mitigate this issue, SERC_URE1's agent implemented an automated process for tracking contractors and employees with authorized cyber or unescorted physical access to CCAs.
2013-02-28 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC200900654 | CIP-004-1 | R4 | SERC_URE1 submitted a Self-Report to SERC stating that it had an issue with CIP-004-1 R4 because it failed to maintain list(s) of personnel with authorized cyber or authorized unescorted physical access to Critical Cyber Assets (CCA), including their specific electronic and physical access rights to CCAs. It was found that 19 employees of SERC_URE1’s agent who had access to CCAs were reassigned and were not removed from the list within the allowed seven day revocation period for employees who no longer need access to CCAs. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. All the missed individuals had valid and current personnel risk assessments and CIP cyber security training. | To mitigate this issue, SERC_URE1's agent implemented an automated process for tracking contractors and employees with authorized cyber or unescorted physical access to CCAs. This automated process also includes features that enable the removal of access within the timeframes specified by CIP-004 R4 .
2013-02-28 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC200900655 | CIP-005-1 | R2 | SERC_URE1 submitted a Self-Report to SERC stating that it had an issue with CIP-005-1 R2 because the firewall of SERC_URE1’s agent was inadvertently configured to the “any-any” access rule, and was not set-up to deny access by default. It was determined that the firewall that formed the Electronic Security Perimeter (ESP) was installed prior to the date of mandatory compliance by SERC_URE1's agent and had a default access rule used for testing and trouble-shooting the pre-production system that was left intact once the system went into production. Pursuant to SERC_URE1 agent’s ESP procedure, this rule should have been removed prior to the mandatory and effective date of CIP-005-1 R2; however, this rule replacement did not occur. During an evaluation of the ESP, SERC_URE1's agent discovered the overly permissive “any-any” access rule and initiated an internal investigation of all other ESP firewalls. SERC_URE1 agent’s investigation concluded and SERC_URE1's agent removed the “any-any” rule and replaced it with a more stringent rule that denies access by default on this ESP firewall. No other instances of the permissive “any-any” rule were found on any ESP forming firewalls. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC_URE1's agent had a corporate firewall that had a deny-by-default access setting that had to be traversed in order to reach the ESP firewall. Only employees that had met the training and screening requirements of CIP-004 were allowed access through the corporate firewall, which is outside the ESP firewall. | To mitigate this issue, SERC_URE1's agent: 1) removed the non-compliant firewall and installed a CIP-005 R2 compliant firewall in its place; 2) determined if there were any other production ESP firewalls not in compliance with CIP-005 R2; 3) revised its procedures for ESP firewalls; and 4) notified SERC_URE1 that it completed training for the SERC_URE1 agent's employees working on CIP-005 R2.
2013-02-28 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC201000660 | CIP-003-1 | R3 | SERC_URE1 submitted a Self-Report to SERC stating that it had an issue with CIP-003-1 R3 because it had been unable to perform personnel risk assessments (PRAs) on some of the individuals with access to Critical Cyber Assets (CCAs) due to a collective bargaining agreement (CBA) issue. Because of this, SERC_URE1 should have taken an exception to its cyber security policy (CSP), but it failed to do so. It was determined that, as of the date of mandatory compliance, SERC_URE1’s agent had implemented a CSP but had not taken an exception to the CSP on the issue of PRAs for its union employees. SERC_URE1 agent’s management realized that the CBA with its union employees did not allow for the performance of the PRA for those employees, and recognized this issue required an exception to the CSP that was never sought. SERC_URE1's agent obtained the authority to conduct PRAs on represented employees with access to CCAs. All required PRAs for the union employees were completed. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The exception to the CSP was only necessary because of a CBA that prevented the performance of PRAs for union employees. CIP-004 R3 explicitly notes that the requirement to perform PRAs for personnel with authorized access to CCAs is subject to existing collective bargaining unit agreements. | To mitigate this issue, SERC_URE1's agent completed all PRAs for union employees with access to CCAs.
2013-02-28 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC201000661 | CIP-006-1 | R1 | SERC_URE1 submitted a Self-Report to SERC stating that it had an issue with CIP-006-1 R1 because it had not considered the application that monitors and controls the physical access to Physical Security Perimeters (PSPs) as a Cyber Asset, and all employees who used the system did not have valid personnel risk assessments (PRAs). It was determined that the subject of this Self-Report was a physical access control system (PACS) that managed physical access to Critical Cyber Assets (CCAs) and other secure areas not covered by the CIP standards. The PACS system was designed and segmented by permissions, so employees that managed PSPs were required to have PRAs and employees and contractors who managed non-CIP secure areas were not required to have PRAs since they could not access, manage, or control the PSPs. As understanding and knowledge of the CIP requirements regarding PACS increased, SERC_URE1 became aware that all employees with access to the PACS system should have valid PRAs and training. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The PACS system was set-up and segmented to prevent non-CIP users from being able to access the CIP designated PSPs. The PACS system is not directly tied to the Energy Management System. | To mitigate this issue, SERC_URE1's agent: 1) assembled a list of all personnel who had access to the security application that monitors and controls physical access to PSPs and processed PRAs for these employees and notified the manager upon completion of the PRAs; 2) determined if any other Cyber Assets or CCAs were not protected at the access point similar to the security application and reported its findings; 3) modified its cyber security policy and associated procedures to ensure that it is clear that all Cyber Assets and CCAs are protected at the access point; 4) modified its cyber security policy and associated procedures to require PRAs prior to granting an employee or contractor access to a Cyber Assets subject to CIP-006 R1.8; 5) trained all personnel, as applicable, on the revised procedures developed in items 3 and 4 above; and 6) revoked the access of any personnel who did not pass the PRA.
2013-02-28 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC201000662 | CIP-007-1 | R1 | SERC_URE1 submitted a Self-Report to SERC stating that it had an issue with CIP-007-1 R1.1 because the test procedures did not specifically call out for tests of cyber security controls, but were instead focused on application and functional testing. It was determined that the test procedure did not address adverse effects to the production environment and were focused solely on application and functionality testing instead of also including specific instructions for testing cyber security controls. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SERC_URE1's agent addressed cyber security controls in its initial designs, and its change request process required a design document review in which security controls would be reviewed. Only documented and allowed traffic from outside the Electronic Security Perimeter (ESP) is permitted into the ESP. | To mitigate this issue, SERC_URE1's agent: 1) modified its testing procedures to explicitly include cyber security controls for significant changes in the test plan checklist; and 2) developed a training class on CIP-007 for all personnel responsible for the process of testing significant changes to ensure that the test plan checklist includes cyber security controls.
2013-02-28 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC201000663 | CIP-007-1 | R2 | SERC_URE1 submitted a Self-Report to SERC stating that it had an issue with CIP-007-1 R2 because during a review of the ports and services documentation, operator workstations (which are Cyber Assets) within the Electronic Security Perimeter (ESP) were found to be missing from that initial compliance review. It was determined that SERC_URE1 had a procedure in place that detailed how to determine and document ports and services for each type of operating system in service as Critical Cyber Assets (CCAs) or non-critical Cyber Assets within the ESP. The original investigation between SERC_URE1 and SERC_URE1’s agent determined that subparts of the procedure were violated, and ports and services for certain Cyber Assets within the ESP (the operator workstations) were not documented. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. These missing workstations were exclusively available to operators within the Physical Security Perimeter and ESP, where only permitted traffic is allowed, and were not accessible from outside the ESP. These workstations were located within the ESP, they were protected by anti-virus and current software patches and monitored in real-time by an intrusion detection system. | To mitigate this issue, SERC_URE1's agent: 1) determined if any other Cyber Assets within the ESPs were not compliant with CIP-007 and developed a plan to bring any such assets back into compliance; 2) trained all personnel responsible for change management process on the plan; and 3) completed all outstanding tasks from the plan.
2013-02-28 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC201000739 | CIP-003-1 | R1 | SERC_URE1 submitted a Self-Report to SERC stating that it had an issue with CIP-003-1 R1.2 because it had failed to ensure the cyber security policy (CSP) of SERC_URE1’s agent, was readily available to all personnel who had access to, or were responsible for, Critical Cyber Assets (CCA). SERC_URE1 learned that the CSP had not been provided to all contractors who had access to or were responsible for CCAs. This issue resulted from a lack of understanding that the contractors who had access to CCAs must also have ready access to the CSP. A copy of the CSP was later provided to the affected contract employees. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. This issue was limited to 12 contractors with remote electronic access. The contractors were from reputable companies that supported multiple cyber systems, so they were well aware of applicable cyber security controls. | To mitigate this issue, SERC_URE1's agent installed a computer kiosk at the entrance to the Electronic Security Perimeter with a copy of the SERC_URE1's agent's CSP to facilitate availability of the CSP for escorted personnel.
2013-02-28 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC201000740 | CIP-002-1 | R3 | SERC_URE1 submitted a Self-Report to SERC stating that it had an issue with CIP-002-1 R3 because it failed to identify certain workstations and laptops in its control center and back-up control center as Critical Cyber Assets (CCAs). SERC_URE1 learned that certain control centers and back-up control center workstations and laptops were not on its CCA list. The identified Cyber Assets that were deemed critical were added to the CCA list and all required CCA controls and protections were put into place. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. All workstations were protected by standard company security control practices for electronic and physical access. All workstations and laptops were located within the control center, a secure area. | To mitigate this issue, SERC_URE1's agent added each newly identified CCA to its official list.
2013-02-28 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2012009935 | CIP-007-1 | R5; R5.2.2 | During a CIP Compliance Audit, SPP RE determined that SPP RE_URE1 was noncompliant with CIP-007-3 R5.2.2. Specifically, although SPP RE_URE1 had a documented list identifying individuals with access to shared accounts, the list did not include those individuals with access to one default shared local account for a Microsoft SQL Server database default account. This account is associated with a non-critical cyber asset located within the Electronic Security Perimeter (ESP), which is used solely as a historical data warehouse. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SPP RE_URE1 only failed to document the individuals that had access to the shared local account for the Microsoft SQL Server database default account but the remaining individuals were identified correctly. Furthermore, the Microsoft SQL Server account only contained SPP RE_URE1 historical Energy Management System (EMS) data. The cyber asset did not have real-time capabilities; therefore any cyber security compromises to this asset would not have affected real-time operations. Finally, although undocumented, any individual who had access to the Microsoft SQL server would have had a documented Personal Risk Assessment (PRA) per SPP RE_URE1's access request and authorization process. | SPP RE_URE1 identified all individuals having access to the subject shared account and updated its shared user account list accordingly. SPP RE verified completion of the mitigating activities.
2013-02-28 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE2012009947 | CIP-002-1 | R1.2 | During a Compliance Audit of Texas RE_URE1, Texas RE discovered an issue with Reliability Standard CIP-002-1 R1.2. Texas RE discovered that Texas RE_URE1 did not consider all assets listed in R1.2 when developing its risk-based assessment methodology (RBAM). Texas RE_URE1 had delegated certain function activities to a contractor but had failed to include the contractor’s control center in its consideration of Critical Assets. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. After Texas RE_URE1 considered the contractor’s facilities, Texas RE_URE1's list of Critical Assets or Critical Cyber Assets (CCA) remained null because the control center was deemed not to be a Critical Asset. The contractor does not perform any of the operations related to Texas RE_URE1's generation unit. The contractor is used as a communications medium between Texas RE_URE1's generation unit and other entities. Additionally, at the time of the issue, there was communication redundancy from the contractor to the plant that included four means of communication. | Texas RE_URE1 has included the contractor’s control center as a consideration in its RBAM. The RBAM has been reviewed and signed by the current senior manager. Texas RE has verified the mitigation activities as complete.
2013-02-28 | TRE_URE1liability Entity (TRE_URE1) | Unidentified Registered Entity 2 (TRE_URE2) | NCRXXXXX | TRE2012011389 | CIP-002-3 | R4 | TRE_URE1_URE2 self-reported an issue with CIP-002-3 R4. Specifically, TRE_URE1_URE2 stated that it failed to follow its own procedures to have its risk-based assessment methodology (RBAM) and Critical Assets/Critical Cyber Assets (CCA) lists reviewed and signed annually by its CIP senior manager. TRE_URE1 verified that TRE_URE1_URE2 did review its RBAM and Critical Assets/CCA lists in the prior year, and that the CIP senior manager responsible for signing the documents did so prior to the annual deadline. However, with the transition to a new CIP senior manager in the next year, TRE_URE1_URE2 failed to have these documents reviewed and signed by the annual deadline. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Once TRE_URE1_URE2 did review its RBAM, and its Critical Assets and CCA lists, no changes were noted. Therefore, TRE_URE1_URE2 had been operating with a complete list of Critical Assets/CCAs for the 12 days that the issue occurred. | TRE_URE1_URE2's new delegated CIP senior manager reviewed and signed the documents. Furthermore, to prevent reoccurrence, TRE_URE1_URE2 has implemented an automated notification system, which sends out notices to the appropriate personnel when the time for the annual review comes up. TRE_URE1 has verified that these activities have been completed.
2013-02-28 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2012011470 | CIP-006-3c | R2 | WECC_URE1 submitted a Self-Report to WECC citing an issue with CIP-006-3c R2. WECC_URE1 reported that it had been revising its risk-based assessment methodology (RBAM) and that based on the revised RBAM it was going to remove three facilities from its Critical Asset list. WECC_URE1 stated that prior to finalization of the new Critical Asset list, WECC_URE1 employees transferred certain Physical Access Control System (PACS) devices, which controlled access and logged information for the three facilities, from the PACS virtual local area networks (VLAN), which provides all of the protections required by CIP-006-3c R2.2, to the corporate security VLAN. WECC_URE1 noted that the corporate security VLAN does not provide all the requirements of CIP-006-3c R2.2. The PACS devices remained on the Corporate Security VLAN for four days until WECC_URE1’s senior manager approved the new Critical Asset list removing the three facilities. WECC_URE1 reported that the PACS devices, which protected the facilities, were not afforded all of the protections required by CIP-006-3c R2.2. Specifically, when placed on the Corporate Security VLAN, WECC_URE1 failed to apply the protections afforded by CIP-003-3 R6, CIP-005-3 R2.4 and R2.5, CIP-006-3 R5, CIP-007-3 R1, and CIP-007-3 R7.2 and R7.3. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The risks posed by this issue were, to an extent, limited given the scope of the issue and compensating measures in place. The issue duration period is limited to four days, thus reducing vulnerabilities given the limited window of opportunity for possible intentional or unintentional misuse or intrusion. Further, the scope of the issue is limited to four PACS devices that were relocated to WECC_URE1’s Corporate VLAN. WECC_URE1’s Corporate VLAN is an isolated access network. Similar to an Electronic Security Perimeter (ESP), electronic access to the VLAN is controlled and monitored. Individuals who accessed the Corporate Security VLAN had completed Critical Infrastructure Protection training and a personnel risk assessment. Similarly, physical access to the PACS devices was controlled and monitored. Individuals with unescorted physical access completed training and were on the WECC_URE1’s unescorted access list. The PACS devices were located within a Physical Security Perimeter (PSP). Furthermore, during the four day period, WECC_URE1 continued to log access to the PSPs containing PACS devices. | To mitigate this issue, WECC_URE1: 1) approved its revised RBAM and removed the three related facilities from its Critical Asset list; and 2) WECC_URE1 senior management discussed the issue and reiterated the importance of clear communications and Standard Owner responsibilities. WECC has verified the completion of all mitigation activity.
2013-02-28 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2012010363 | CIP-004-3 | R4 | WECC_URE2 submitted a Self-Report citing an issue with CIP-004-3 R4, specifically R4.1. WECC_URE2 reported that a telecommunications agent, who had authorized unescorted physical access to Critical Cyber Assets (CCAs) within the Physical Security Perimeter (PSP) located at WECC_URE2’s system operations control center, was terminated from his position. WECC_URE2 noted that the individual did not have logical access to CCAs and was required to have physical access to the PSP as part of his job duties. WECC_URE2 reported that upon termination, the individual’s access was revoked and his badge was collected by Human Resources but the personnel access list for CCAs was not updated to reflect the termination. WECC_URE2 stated that the assistant manager of system and trading operations discovered that the terminated individual no longer needed to be on the CCA authorized personnel list. On that same day, the assistant manager informed the personnel access list manager that the terminated employee no longer needed access to CCAs and the personnel access list manager subsequently deactivated the individual’s physical access to the control system and removed the individual from the physical access list. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The risks posed by WECC_URE2’s issue are, to an extent, minimized by the scope of the issue as well as compensating measures in place during the issue duration. The scope of the issue is limited to one employee. WECC_URE2 has procedures that include removing access badges and keys from employees after such employees have been terminated. Additionally, WECC_URE2 removes logical access to CCAs immediately upon termination. Furthermore, WECC_URE2 has a policy of training all employees who have access to CCAs and has all employees with such access undergo a personnel risk assessment (PRA). Moreover, the system control center is monitored by human observation 24 hours a day 7 days a week. Finally, in this case, WECC_URE2 revoked the employee’s access and did collect the employee’s access card (badge), thus precluding the employee from gaining access during pendency of the remediated issue and WECC_URE2 updated its access list within 11 days of the employee’s departure. | To mitigate this issue, WECC_URE2: 1) updated the personnel access list and removed the terminated person from the list; 2) WECC_URE2’s Human Resources department updated its notification and distribution process to include the system trading operations manager, personnel access list manager, and the system administrator to update the access list for personnel who no longer require access to CCAs as a result of separation actions; and 3) WECC_URE2’s procedure for personnel access to CCAs was modified to include Human Resources and system trading operations manager notification. WECC has verified the completion of all mitigation activity.
2013-02-28 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2012011000 | CIP-002-2 | R4 | WECC performed an off-site Compliance Audit of WECC_URE3. During the Audit, the audit team concluded that WECC_URE3 had an issue with CIP-002-2 R4 for failing to have a CIP Senior Manager, or delegate thereof, sign and approve its risk-based assessment methodology (RBAM), its null list of Critical Assets, and its null list of Critical Cyber Assets (CCAs). WECC_URE3’s general manager, who designated the CIP senior manager but is not the CIP designated senior manager or a delegate thereof, did approve WECC_URE3’s RBAM, its null list of Critical Assets, and its null list of CCAs during the duration of the issue. In addition, WECC_URE3’s CIP senior manager did sign an attestation documenting the annual dates on which he approved WECC_URE3’s risk-based methodology, its null list of Critical Assets, and its null list of CCAs. The dates of the designated CIP senior manager’s annual review and approval of WECC_URE3’s risk-based methodology and the results of the assessment, which led to null lists of Critical Assets and CCAs, are identified in the attestation and align with WECC_URE3’s other compliance documentation. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. As compensating measures, WECC_URE3’s general manager had reviewed and approved its risk-based methodology, its null list of Critical Assets, and its null list of CCAs during the duration of the issue. Furthermore, there are documented emails from the CIP senior manager noting his awareness of the lists of Critical Assets and CCAs. The designated CIP senior manager reports directly or indirectly to the general manager. Accordingly, WECC_URE3 was aware that it did not have any Critical Assets or CCAs. | To mitigate this issue, WECC_URE3’s CIP senior manager signed an attestation noting the annual dates on which he reviewed and approved its risk-based methodology, its null list of Critical Assets, and its null list of CCAs.
2013-02-28 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC2012011468 | CIP-004-3 | R4 | WECC_URE4 submitted a Self-Report citing an issue with CIP-004-3 R4. WECC_URE4 reported that it failed to revoke physical access to Critical Cyber Assets (CCAs) within seven days for an individual who no longer required such access. An individual employed by WECC_URE4 no longer required physical access to a single Physical Security Perimeter (PSP) containing CCAs. Per CIP-004-3 R4.3, access rights should have been revoked within seven days. Access was revoked within ten days. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The risk posed by WECC_URE4's issue is limited given the scope of the issue and the compensating measures in place during the duration of the issue. The individual maintained physical access rights to a single PSP for a period of three days beyond the period prescribed in R4.2. The individual in scope of the issue completed a personnel risk assessment, and cyber security training. The individual in scope did not attempt to physically access the CCAs. All of the CCAs to which the individual had access were contained within a Physical Security Perimeter. Physical access thereto was controlled and monitored. Unauthorized physical access attempts would have triggered alarming. The CCAs were also electronically secured within an Electronic Security Perimeter (ESP). Electronic access was controlled and monitored. Electronic access was limited to specific staff members who required such access. Cyber security events within the ESP containing the CCAs would have triggered alarming. | To mitigate this issue, WECC_URE4: 1) revoked individual’s access to CCAs; and 2) implemented additional training and workload/resource management to prevent future instances of a similar nature.
2013-01-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2012001272 | CIP-004-3 | R3 | RFC_URE1 submitted a Self-Report to ReliabilityFirst identifying an issue with CIP-004-3 R3. RFC_URE1 discovered that two of its employees were granted authorized unescorted physical access to Critical Cyber Assets (CCAs) without obtaining personnel risk assessments (PRAs) as required by RFC_URE1 documented PRA program. The issue was discovered about eight months after the employees were granted such access. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The employees involved in the issue had cybersecurity training and were seasoned RFC_URE1 employees. One individual has been employed with RFC_URE1 for over ten years. The other individual had been employed by RFC_URE1 over twenty years and recently retired. The individuals did not attempt to gain access to unauthorized areas. When RFC_URE1 conducted PRAs for the two individuals, it discovered no negative results. | RFC_URE1 revoked the two individuals’ access to CIP-controlled areas and then initiated and successfully completed PRAs for the two individuals. RFC_URE1 subsequently completed its corrective discipline process with the single supervisor of both individuals.
2013-01-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2012001273 | CIP-004-3 | R4 | RFC_URE1 submitted a Self-Report to ReliabilityFirst identifying an issue with CIP-004-3 R4. For the second quarter of one year, RFC_URE1 failed to conduct a review of its list of personnel who have authorized cyber access to Critical Cyber Assets (CCAs) at a power plant, as required by CIP-004-3 R4.1. RFC_URE1 conducted the review three months outside its scheduled review period. In addition, RFC_URE1 failed to timely revoke access to CCAs for three individuals that transferred from positions within RFC_URE1 at facilities containing CCAs to positions at facilities that do not contain CCAs. Despite the transfer, RFC_URE1 failed to revoke the three individuals’ authorized cyber and authorized unescorted physical access to CCAs within seven calendar days, as required by CIP-004-3 R4.2. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Regarding the issue with CIP-004-3 R4.1, when RFC_URE1 conducted the quarterly review, it discovered no changes to the access list were required. In addition, except for incidents in issue tracking numbers RFC2012001272 and RFC2012010433, all employees had cybersecurity training and valid personnel risk assessments (PRAs). Regarding the issue with CIP-004-3 R4.2, the individuals had valid PRAs and cybersecurity training. In addition, the individuals did not attempt to utilize their access after they transferred positions. | To mitigate the issue with CIP-004-3 R4.1, RFC_URE1 conducted regularly scheduled CIP-004 R4 reviews pursuant to its documented procedure. In addition, RFC_URE1 conducted a gap analysis assessment of its current process and developed countermeasures of probable root causes of the issue. Furthermore, RFC_URE1 expanded its email notifications to include alternate individuals to review the access lists. To mitigate the issue with CIP-004-3 R4.2, RFC_URE1 revoked access for all employees at issue, and completed training for all individuals at issue.
2013-01-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2012010421 | CIP-004-3 | R3 | RFC_URE1 submitted a Self-Report to ReliabilityFirst identifying an issue with CIP-004-3 R3. During its quarterly access review, RFC_URE1 discovered that it mistakenly granted unescorted physical access to one of its power plant Physical Security Perimeters (PSPs) containing Critical Cyber Assets (CCAs) to an individual without a personnel risk assessment, as required by CIP-004-3 R3. The individual who required access has the same first and last name as the individual to which RFC_URE1 mistakenly granted access. In addition, the individuals belong to the same department, have the same supervisor and the same job title. Around two weeks after it discovered the issue, RFC_URE1 revoked the individual’s access. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The individual did not physically access any of the PSPs at issue, and the individual did not have an identification access card with which to access the PSPs. The process in place to verify correct access authorization quarterly permitted RFC_URE1 to identify and eliminate the incorrectly authorized access rights. Furthermore, the power plant perimeter is protected by vehicle and pedestrian gates, identification card access, and security personnel on duty 24 hours a day. As a result, the individual at issue would have been denied access at the perimeter and been unable to physically access the CCAs located inside the perimeter. | RFC_URE1 revoked the individual’s unauthorized access. In addition, RFC_URE1 conducted a personnel risk assessment, conducted a review to identify the root cause of the issue, and implement a mitigation strategy. RFC_URE1 created a specific business unit procedure documenting the corporate process and criteria for granting access to a Cyber Asset and conduct reinforcement training for employees in the business unit on that process. RFC_URE1 also conducted general reinforcement training for access requirements for all relevant Cyber Asset owners to review the procedures and criteria for granting access to Cyber Assets.
2013-01-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2012010433 | CIP-004-3 | R2; R2.1 | RFC_URE1 submitted a Self-Report to ReliabilityFirst identifying an issue with CIP-004-3 R2. During its quarterly access review, RFC_URE1 discovered that it mistakenly granted unescorted physical access to the one of its power plant's Physical Security Perimeters (PSPs) containing Critical Cyber Assets (CCAs) to an individual without cybersecurity training, as required by CIP-004-3 R2. The individual who required access has the same first and last name as the individual to which RFC_URE1 mistakenly granted access. In addition, the individuals belong to the same department, have the same supervisor and the same job title. Around two weeks after it discovered the issue, RFC_URE1 revoked the unauthorized individual’s access. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The individual did not physically access any of the PSPs at issue, and the individual did not have an identification access card with which to access the PSPs. The process in place to verify correct access authorization quarterly permitted RFC_URE1 to identify and eliminate the incorrectly authorized access rights. Furthermore, the power plant perimeter is protected by vehicle and pedestrian gates, identification card access, and security personnel on duty 24 hours a day. As a result, the individual at issue would have been denied access at the perimeter and been unable to physically access the CCAs located inside the perimeter. | RFC_URE1 revoked the unauthorized access and revised its process for granting unescorted physical access to CCAs to ensure the uniqueness of the individual prior to granting access.
2013-01-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2012011348 | CIP-006-3c | R2; R2.2 | RFC_URE1 submitted a Self-Report to ReliabilityFirst identifying an issue with CIP-004-3 R3. Subsequently, ReliabilityFirst determined that one of the two issues identified in that Self-Report indicated that RFC_URE1 had an issue with CIP-006-3c R2.2. A RFC_URE1 IT employee transferred from one IT department to another for a temporary assignment. RFC_URE1 placed this employee in a group with administrative access to servers administered through a new business unit. Four of these servers contain Cyber Assets that authorize and/or log access to the Physical Security Perimeter. Two days later, RFC_URE1 discovered through regular internal access reviews, that it had granted such access to these servers without conducting a personnel risk assessment (PRA), as required by CIP-004-3 R3. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. When RFC_URE1 conducted the PRA, it discovered no negative results for the employee and granted the employee authorized cyber access to the assets. In addition, the employee had cybersecurity training. Furthermore, RFC_URE1 controls access to Cyber Assets by providing three levels of access: operating system; database; and application access. The employee had operating system level access to the servers at issue, which prevents an individual from modifying or viewing physical access control data, application configuration, and database elements. The employee, a nine year RFC_URE1 employee, did not attempt to access the Cyber Assets. | RFC_URE1 revoked the employee's access and conducted a PRA. In addition, RFC_URE1 investigated the root cause and created a specific business unit procedure documenting the corporate process and criteria for granting access to a Cyber Asset. Furthermore, RFC_URE1 conducted training for employees in this business unit to review the new procedure and reinforce the corporate procedures and criteria for granting access to Cyber Assets. RFC_URE1 also conducted training for individuals responsible for Cyber Assets to reinforce the procedures and criteria for granting access to Cyber Assets.
2013-01-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2012010077 | CIP-004-3 | R4.2 | RFC_URE2 self-reported an issue with CIP-004-3 R4.2. RFC_URE2 determined it failed to revoke an employee’s unescorted physical access to Critical Cyber Assets (CCAs) within a Physical Security Perimeter. The employee’s supervisor submitted a ticket stating that the employee no longer required unescorted physical access to CCAs and that the employee’s unescorted physical access should be revoked. However, a previously unknown ticketing system failure prevented an automated alert, resulting in the operator not updating the ticket until two months later. Furthermore, the report generated by the operator did not include the employee’s name or employee ID, only the employee’s position ID. As a result, RFC_URE2 did not take action to revoke the employee's unescorted physical access at that time. Two months after the operator updated the ticket, during an internal compliance review, RFC_URE2 determined the employee lacked a business need for unescorted physical access and revoked the employee’s access rights. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The employee had already completed CIP training and possessed an up-to-date personnel risk assessment during the duration of the issue. Therefore, the employee was qualified to receive unescorted physical access to CCAs during the duration of the issue. Also, the employee’s supervisor submitted a ticket to revoke the employee’s access because the employee lacked a business need for access, not for cause. RFC_URE2 revoked the employee’s access the same day it discovered the issue. Finally, the employee remains an employee of RFC_URE2 supporting IT applications that are unrelated to CCAs. | RFC_URE2 revoked the employee’s unescorted physical access rights. RFC_URE2 also implemented a manual step requiring personnel to review and provide email notification of pending ticket tasks. RFC_URE2 also conducted an internal review of its access management system to ensure all individuals with cyber or authorized unescorted physical access have employee names and employee ID numbers that correspond with their respective position ID. Finally, RFC_URE2 conducted an internal review of the ticketing system and determined there were no other instances in which it revoked access rights outside the seven calendar days pursuant to CIP-004-3 R4.2.
2013-01-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2012010078 | CIP-004-3 | R3.2 | RFC_URE2 self-reported an issue CIP-004-3 R3.2 to ReliabilityFirst. RFC_URE2 determined that it did not perform a personnel risk assessment (PRA) reassessment for an employee within seven years. The employee had both authorized cyber and authorized unescorted physical access to Critical Cyber Assets (CCAs). RFC_URE2 runs a monthly automated query on all employees with a PRA date that identifies those employees with PRA dates that have reached the age of six years and nine months. However, a previously unidentified dependency within the query excluded the employee from a monthly report. As a result, RFC_URE2 did not conduct a PRA reassessment for the employee within seven years pursuant to CIP-004-3 R3.2. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Prior to the issue, RFC_URE2 conducted a PRA for the employee which revealed no adverse findings that would preclude the employee from receiving access to CCAs. Additionally, upon completion of the PRA reassessment RFC_URE2 determined there were no adverse findings that would have precluded the employee from receiving access to CCAs during the duration of the issue. Finally, the employee is a longstanding RFC_URE2 employee who continues to have a business need to access the CCAs. | RFC_URE2 revoked the employee's access to CCAs and performed the PRA reassessment on the same date it discovered the issue. Additionally, RFC_URE2 modified the automated query it runs to determine whether its employees needed a reassessed PRA and corrected the previously unidentified dependency, thereby addressing the root cause of the issue. Finally, RFC_URE2 conducted a review of all PRA dates and determined no other individuals with CCA access had overdue PRA reassessments.
2013-01-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2012009754 | CIP-007-3 | R4 | SPP RE_URE1 self-reported noncompliance with CIP-007-3 R4. Specifically, SPP RE_URE1 went live with a new supervisory control and data acquisition (SCADA) system and new networking equipment. The SCADA system and networking equipment were installed as part of a mitigation plan from a previous issue of noncompliance. The Global Positioning System (GPS) clocks and virtual private network (VPN) appliance associated with the new equipment were not capable of running anti-virus software or malware prevention tools, and SPP RE_URE1 failed to submit a Technical Feasibility Exception (TFE) for the GPS clocks and VPN appliance. | SPP RE determined that the issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SPP RE_URE1's GPS clocks and VPN appliance are housed behind a firewall set to deny access by default and the assets are monitored at all times by a security incident and event management (SIEM) server, which is set to alert administrators of suspicious activities occurring on the network. | SPP RE_URE1 submitted a TFE for its GPS clocks and VPN appliance. Although SPP RE_URE1 does not anticipate the GPS clocks and VPN appliance will be capable of supporting anti-malware in the foreseeable future, SPP RE_URE1 has installed a centralized SIEM server that monitors logs from networking equipment where anti-virus software cannot be installed. SPP RE has accepted SPP RE_URE1's TFE.
2013-01-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2012009755 | CIP-007-3 | R6 | SPP RE_URE1 self-reported noncompliance with CIP-007-3 R6, regarding security status monitoring of system events. Specifically, SPP RE_URE1 went live with a new supervisory control and data acquisition (SCADA) system and new networking equipment. The SCADA system and networking equipment were installed as part of a mitigation plan from a previous issue of noncompliance. The Global Positioning System (GPS) clocks associated with the new equipment were not capable of enabling security logging. Therefore, SPP RE_URE1 should have submitted a Technical Feasibility Exception (TFE); however, SPP RE_URE1 did not submit a TFE for the GPS clocks. | SPP RE determined that the issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SPP RE_URE1's GPS clocks are housed behind a firewall set to deny access by default and are within an environment monitored at all times by a security incident and event management (SIEM) server, which is set to alert administrators of suspicious activities occurring on the network. | SPP RE_URE1 submitted a TFE for its GPS clocks. The GPS clocks are housed within a Physical Security Perimeter and Electronic Security Perimeter (ESP). There is a SIEM server operating within the ESP that alerts administrators when anomalous activity occurs in all other systems within the ESP, as well as at all access points to the ESP. SPP RE has accepted SPP RE_URE1's TFE.
2013-01-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2012009948 | CIP-007-3 | R5; R5.3 | SPP RE_URE1 self-reported noncompliance with CIP-007-3 R5, regarding account management. Specifically, SPP RE_URE1 went live with a new supervisory control and data acquisition (SCADA) system and new networking equipment. The SCADA system and networking equipment were installed as part of a mitigation plan from a previous issue of noncompliance. SPP RE_URE1 discovered that its database serving the new SCADA system environment contained an administrative user which cannot enforce the password rules set forth by CIP-007 R5.3 (password length, complexity, and age). However, SPP RE_URE1 did not submit the appropriate Technical Feasibility Exception (TFE) in a timely manner, as required by this Standard. | SPP RE determined that the issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The user account is only accessible to system administrators and is used only on initial database setup and configuration. Access to the account is limited to only a select group of administrators. These administrators are trained annually to use only complex password and change them regularly. Furthermore, the account is monitored at all times by a security incident and event management (SIEM) server, which is set to alert administrators of suspicious activities occurring on the network. | SPP RE_URE1 submitted a TFE for its account’s password complexity issue. SPP RE has accepted SPP RE_URE1's TFE.
2013-01-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPPRE_URE2) | NCRXXXXX | SPP2012011235 | CIP-004-3 | R2; R2.1; R2.3 | SPPRE_URE2 self-reported noncompliance with CIP-004-3 R2.1 and R2.3. As to CIP-004-3 R2.1, SPPRE_URE2 identified employees whose initial training records could not be located to substantiate that the employees received Critical Cyber Assets (CCA) training prior to being granted physical access to its CCAs. As to CIP-004-3 R2.3, SPPRE_URE2 identified employees with authorized access to CCAs that did not receive the required annual cyber security training for 2010. | SPP RE determined that the issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although SPPRE_URE2 failed to provide an identified number of its employees the required annual training in 2010, all of the identified employees: 1) were trained on cyber security in 2009, prior to gaining them actual access to CCAs; 2) received 2011 and 2012 CCA training; and 3) have qualified personal risk assessments and are current on all cyber security training required by the SPPRE_URE2 training program. With regard to the employees for whom SPPRE_URE2 could not substantiate that they had received CCA training prior to being granted physical access to its CCAs, SPPRE_URE2 subsequently located documentation for one of the employees. Therefore, it was determined that the employee did receive training prior to being granted access to the CCAs. Except for the employee whose training documentation has not been located, no other instances of access being granted prior to training have been identified. | SPPRE_URE2 provided annual cyber security training for all its employees with unescorted physical or logical access to CCAs in 2012. SPPRE_URE2 also added a CIP compliance administrator position to oversee all CIP compliance activities. One of the responsibilities of the CIP compliance administrator is to ensure all CIP training is conducted in accordance with SPPRE_URE2's procedures. The CIP compliance administrator has created a calendar to track all activities associated with CIP compliance, including the annual cyber security training.
2013-01-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPPRE_URE2) | NCRXXXXX | SPP2012011234 | CIP-004-3 | R4 | SPPRE_URE2 self-reported noncompliance with CIP-004-3 R4, because during an internal assessment of its cyber security training program, SPPRE_URE2 discovered that: 1) it did not have documentation that it performed its quarterly review of the list of personnel with authorized cyber access to Critical Cyber Assets (CCAs) in the second and third quarters of 2011; 2) an identified number of SPPRE_URE2 employees were not added to the list of SPPRE_URE2 personnel with authorized unescorted physical access to CCAs until after authorized access was granted, which was a documentation error; 3) and an SPPRE_URE2 employee with access to the backup control center Physical Security Perimeter (PSP) did not have his access revoked until nine days after a job responsibility change which eliminated the need for access to the backup control center. | SPP RE determined that the issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although SPPRE_URE2 did not have documentation for the second and third quarter of 2011 review of its list of personnel with authorized cyber access, SPPRE_URE2 had reviewed its list of personnel with authorized cyber access to CCAs in the first and fourth quarters of 2011 and had documentation of these reviews. Although an identified number of SPPRE_URE2 employees were not added to the authorized access list until after access was granted, these employees had personal risk assessments (PRAs) on file and were current on all required cyber security training. The employee whose access was not revoked within the seven day requirement had a valid PRA on file and current cyber security training. The employee’s access was revoked two days later because of a job responsibility change and not termination for cause. Additionally, the employee did not access the backup control center PSP during the two days access was not revoked. | To mitigate its noncompliance with CIP-004-3 R4, SPPRE_URE2 conducted a thorough review of all personnel lists applicable to CIP-004-3 and ensured that all information on each list is current. SPPRE_URE2 created a detailed process for maintaining all lists applicable to CIP-004-3. This process included the appointment of a CIP compliance administrator to ensure that all CIP related lists are maintained and reviewed in accordance with SPPRE_URE2's policies and procedures.
2013-01-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 3 (SPPRE_URE3) | NCRXXXXX | SPP2012009703 | CIP-003-1 | R4 | SPP RE_URE3 self-reported noncompliance with CIP-003-1 R4 for failing to identify, classify and protect nine documents containing information associated with its Critical Cyber Assets (CCAs). Specifically, SPP RE_URE3 did not place a “confidential” label on its disaster recovery plans, wiring plans, and an incident response plan, as required by CIP-003-1 R4. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although SPP RE_URE3 did not label all of its documents containing information associated with its CCAs, these documents were still protected through other means. The nine identified documents were all inter-department documents that were distributed on a need-to-know basis only. Additionally, these files were treated as confidential materials under SPP RE_URE3's information protection program even though they did not bear a “confidential” label. This treatment included the files being stored on a restricted file share folder and located within secured network drives that were protected against unauthorized access. | SPP RE_URE3 revised its energy management systems incident response plan, disaster recovery plans, and wirings plans, consolidated some of the documents as needed, and labeled each revised document according to its information protection program. Additionally, SPP RE_URE3 revised its information protection program to include more information concerning protecting information associated with its CCAs. Finally, SPP RE_URE3 conducted training to educate its CIP staff of the requirements set forth in its updated information protection and access control program.
2013-01-30 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE2012011460 | CIP-002-1 | R3 | From a Self-Report, Texas RE determined that Texas RE_URE1 did not develop a list of Critical Cyber Assets (CCAs) using the list of Critical Assets determined through an application of Texas RE_URE1's risk-based assessment methodology (RBAM). Specifically, Texas RE determined that one device was incorrectly excluded from the list of CCAs because Texas RE_URE1 failed to follow its RBAM for developing a list of CCAs. An inaccurate filtering criteria was assigned to the device that caused it to be marked as not being a CCA. However, Texas RE_URE1 was aware that the device was a CCA and afforded all the security measures required by the reliability standards to it. This issue lasted for three months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The CCA at issue was located inside a Physical Security Perimeter (PSP), was monitored by an electronic entrance, and was firewalled. In addition, the CCA was subject to staff oversight at Texas RE_URE1's Electronic Security Perimeters and the PSP, and it was accessible only to designated staff members with personnel risk assessments. Documents show that the CCA at issue was considered a part of Texas RE_URE1's CCA list. The security of the CCA was not compromised during the three-month period of Texas RE_URE1's noncompliance. | To mitigate this issue Texas RE_URE1 has provided a CCA list document, showing that the device has been documented as a CCA. The document was signed by the senior manager.
2013-01-30 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE2012011461 | CIP-004-2 | R2 | From a Self-Report, Texas RE determined that Texas RE_URE1 did not update its cyber security training program at least annually. Texas RE_URE1's annual training stated that updating of its cyber security incident response plan as per CIP-008-1 R1.4 is required within ninety calendar days of any changes made. However, when Version 2 of the CIP Standards became effective on April 1, 2010, Texas RE_URE1 failed to update its annual training materials that reference CIP 008-1 R1.4. Texas RE_URE1 failed to provide a reference to the new Version of the Standard, CIP-008-2 R1.4, which requires any changes to be made within thirty calendar days instead of ninety calendar days. As a result, Texas RE_URE1 included incorrect information into its training materials, which presented an issue with CIP-004-2 R2. This issue existed for approximately two years and seven months. Furthermore, Texas RE found an additional issue during a Compliance Audit. An indicated number of Texas RE_URE1 contractors with access to Critical Cyber Assets (CCAs) were not trained as required by CIP-004-2 R2.3. The contractors were last trained in January 2010 and should have been trained again in February 2011. However, Texas RE_URE1 failed to train them by that date and did not revoke their access until four days after training should have been completed. As a result, Texas RE determined that Texas RE_URE1 had an issue with CIP-004-2 R2.3 for the four days after training should have been completed. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Although Texas RE_URE1 employees were being trained with training materials that did not fully reflect a change in the reliability standards versions, the employees received a timely training on all other aspects of the Standard. Also, all trained employees at issue had personnel risk assessments (PRAs) performed and were knowledgeable about Texas RE_URE1's CCAs security practices. For CIP-004-2 R2.3, the contractors having access to these CCAs had previously had cyber security training, and their PRAs were current. Therefore, Texas RE determined that these contractors were familiar with Texas RE_URE1's security practices. Finally, Texas RE_URE1 was noncompliant with CIP-004-2 R2.3 for a period of four days, which reduced the risk to the BPS to minimal. | To mitigate this issue, Texas RE_URE1 provided an updated training program document, which reflects the change from Version 1 to Version 2 of this CIP Standard. Texas RE_URE1 also trained the contractors at issue.
2013-01-30 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE2012011462 | CIP-008-2 | R1.4 | From a Self-Report, Texas RE determined that Texas RE_URE1's cyber security incident response plan stated that changes to the plan are to be incorporated into the plan within ninety days, not within thirty days, as required by Version 2 of this Standard CIP-008-2 R1.4. Version 1 of this Standard required that any change be incorporated within ninety days. Texas RE further determined that this issue existed from when Version 2 of this Standard became mandatory and enforceable, until when the plan was updated. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Texas RE determined that this remediated issue is documentation-related and administrative in nature because there were no changes to the plan during the period of noncompliance. Further, any changes to the plan would still have been incorporated within ninety days, thereby further reducing the risk to the BPS. | Texas RE_URE1 updated its cyber security incident response plan, which is part of its training program, to require that any changes are incorporated within thirty days.
2013-01-30 | TRE_URE1liability Entity (TRE_URE1) | Unidentified Registered Entity 2 (TRE_URE2) | NCRXXXXX | TRE2012010293 | CIP-005-1 | R1 | During a Compliance Audit, TRE_URE1 discovered that TRE_URE1_URE2 did not document the Electronic Security Perimeter (ESP) and all access points to the perimeter. TRE_URE1_URE2's ESP diagram did not include the clock for the backup dispatch center area. This clock is on TRE_URE1_URE2's Critical Cyber Assets list for 2010 but was not depicted on the ESP diagram. The duration of this issue was from when this Standard became mandatory and enforceable for TRE_URE1_URE2, to when the ESP diagram was updated. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because the clock at issue was included on TRE_URE1_URE2's Cyber Asset list even before this Standard became mandatory and enforceable. As a result, the clock was afforded the protective measures applicable to all Critical Assets on the list. TRE_URE1 considered this issue to be documentation-related because the equipment was not on the ESP diagram but was listed as a Critical Asset and afforded the protective measures applicable to Critical Assets. | TRE_URE1 determined that TRE_URE1_URE2's more recent version of its ESP diagram includes the clock at issue and all access points to the ESP. TRE_URE1 has verified that the mitigation activities are complete.
2013-01-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2012010835 | CIP-002-1 | R1 | WECC_URE1 submitted four Self-Reports citing noncompliance with NERC Standard Requirements CIP-002-1 R1, R2, R3, and R4. Specifically, WECC_URE1 reported that it could not provide evidence of compliance with CIP-002-1 R1, R2, R3, and R4 between January 1, 2010, and May 2011. WECC subject matter experts (SMEs) reviewed WECC_URE1’s Self-Report. The SMEs determined that WECC_URE1 is required to demonstrate compliance with CIP-002-1 Requirements as of January 1, 2010. The SMEs, therefore, requested the following evidence: 1) WECC_URE1’s risk-based assessment methodology (RBAM) in effect on January 1, 2010, as required under CIP-002-1 R1; 2) WECC_URE1’s Critical Asset list in effect on January 1, 2010, pursuant to CIP-002-1 R2; 3) WECC_URE1’s Critical Cyber Asset (CCA) list in effect on January 1, 2010, pursuant to CIP-002-1 R3; and 4) A signed and dated record of senior manager or delegate(s)’s approval of the Critical Asset and CCA lists (even if such lists are null), for 2010. In response to the SMEs’ request, WECC_URE1 provided an RBAM, a Critical Asset list, a CCA list, and evidence of management approval, effective as of May 2011. WECC_URE1 disclosed that it could not provide CIP-002-1 documentation required under CIP-002-1 R1, R2, R3, and R4 in effect prior to May 2011. SMEs reviewed WECC_URE1’s RBAM, null Critical Asset list, and null CCA list. SMEs determined that CIP-002-1 documentation provided by WECC_URE1 appeared to satisfy CIP-002-1 R1, R2, R3, and R4. SMEs also determined, however, that between January 1, 2010 and May 2011, WECC_URE1 failed to develop an RBAM under CIP-002-1 R1. Further, the SMEs determined that between January 1, 2010, and May 2011, WECC_URE1 failed to develop lists of Critical Assets and CCAs for management review pursuant to CIP-002-1 R2, R3, and R4. The SMEs forwarded their findings regarding this issue to WECC Enforcement (Enforcement). Enforcement reviewed WECC_URE1’s Self-Report and the SMEs’ findings. Consistent with the SMEs findings, Enforcement determined that WECC_URE1 failed to demonstrate compliance with CIP-002-1 R1, R2, R3, and R4 between January 1, 2010, and May 2011. Enforcement also determined, however, that WECC_URE1 remediated noncompliance in May 2011. Enforcement, therefore, determined that WECC_URE1 remediated the CIP-002-1 R1, R2, R3, and R4 issues. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Failure to develop an RBAM, Critical Asset and CCA list per CIP-002-1 R1, R2, R3, and R4, renders Critical Asset and associated CCAs vulnerable to cyber attack or misuse. In this case, WECC_URE1 failed to identify and document an RBAM and failed to document null Critical Asset and null CCA lists per CIP-002-1 R1, R2, R3, and R4. WECC_URE1 has limited connectivity to the BPS. It owns and operates substations operating at or below 69 kV, none of which are Critical Assets. Further, WECC_URE1 does not own or operate any CCAs. WECC_URE1 has physically secured all facilities. Each of the substations is surrounded by 10-foot fencing topped with razor wire that limits physical access. WECC, therefore, determined that WECC_URE1's CIP-002-1 R1, R2, R3, and R4 remediated issues posed a minimal risk to the BPS. | WECC_URE1 provided its RBAM, a null Critical Asset list, a null CCA list, and evidence of managerial review, in effect as of May 2011. WECC reviewed WECC_URE1 CIP-002 documentation and determined that WECC_URE1 remediated noncompliance. Further, WECC determined that to avoid future issues with CIP-002 compliance, WECC_URE1 implemented a CIP-002 document tracking system. The system maintained CIP-002 documentation and issued annual alerts for document revision and review. WECC_URE1 reorganized its Compliance office, bringing on new management. WECC, therefore, determined that WECC_URE1 remediated CIP-002-1 R1, R2, R3, and R4 compliance issues.
2013-01-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2012010890 | CIP-002-1 | R4 | WECC_URE1 submitted four Self-Reports citing noncompliance with NERC Standard Requirements CIP-002-1 R1, R2, R3, and R4. Specifically, WECC_URE1 reported that it could not provide evidence of compliance with CIP-002-1 R1, R2, R3, and R4 between January 1, 2010, and May 2011. WECC subject matter experts (SMEs) reviewed WECC_URE1’s Self-Report. The SMEs determined that WECC_URE1 is required to demonstrate compliance with CIP-002-1 Requirements as of January 1, 2010. The SMEs, therefore, requested the following evidence: 1) WECC_URE1’s risk-based assessment methodology (RBAM) in effect on January 1, 2010, as required under CIP-002-1 R1; 2) WECC_URE1’s Critical Asset list in effect on January 1, 2010, pursuant to CIP-002-1 R2; 3) WECC_URE1’s Critical Cyber Asset (CCA) list in effect on January 1, 2010, pursuant to CIP-002-1 R3; and 4) A signed and dated record of senior manager or delegate(s)’s approval of the Critical Asset and CCA lists (even if such lists are null), for 2010. In response to the SMEs’ request, WECC_URE1 provided an RBAM, a Critical Asset list, a CCA list, and evidence of management approval, effective as of May 2011. WECC_URE1 disclosed that it could not provide CIP-002-1 documentation required under CIP-002-1 R1, R2, R3, and R4 in effect prior to May 2011. SMEs reviewed WECC_URE1’s RBAM, null Critical Asset list, and null CCA list. SMEs determined that CIP-002-1 documentation provided by WECC_URE1 appeared to satisfy CIP-002-1 R1, R2, R3, and R4. SMEs also determined, however, that between January 1, 2010 and May 2011, WECC_URE1 failed to develop an RBAM under CIP-002-1 R1. Further, the SMEs determined that between January 1, 2010, and May 2011, WECC_URE1 failed to develop lists of Critical Assets and CCAs for management review pursuant to CIP-002-1 R2, R3, and R4. The SMEs forwarded their findings regarding this issue to WECC Enforcement (Enforcement). Enforcement reviewed WECC_URE1’s Self-Report and the SMEs’ findings. Consistent with the SMEs findings, Enforcement determined that WECC_URE1 failed to demonstrate compliance with CIP-002-1 R1, R2, R3, and R4 between January 1, 2010, and May 2011. Enforcement also determined, however, that WECC_URE1 remediated noncompliance in May 2011. Enforcement, therefore, determined that WECC_URE1 remediated the CIP-002-1 R1, R2, R3, and R4 issues. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Failure to develop an RBAM, Critical Asset and CCA list per CIP-002-1 R1, R2, R3, and R4, renders Critical Asset and associated CCAs vulnerable to cyber attack or misuse. In this case, WECC_URE1 failed to identify and document an RBAM and failed to document null Critical Asset and null CCA lists per CIP-002-1 R1, R2, R3, and R4. WECC_URE1 has limited connectivity to the BPS. It owns and operates substations operating at or below 69 kV, none of which are Critical Assets. Further, WECC_URE1 does not own or operate any CCAs. WECC_URE1 has physically secured all facilities. Each of the substations is surrounded by 10-foot fencing topped with razor wire that limits physical access. WECC, therefore, determined that WECC_URE1's CIP-002-1 R1, R2, R3, and R4 remediated issues posed a minimal risk to the BPS. | WECC_URE1 provided its RBAM, a null Critical Asset list, a null CCA list, and evidence of managerial review, in effect as of May 2011. WECC reviewed WECC_URE1 CIP-002 documentation and determined that WECC_URE1 remediated noncompliance. Further, WECC determined that to avoid future issues with CIP-002 compliance, WECC_URE1 implemented a CIP-002 document tracking system. The system maintained CIP-002 documentation and issued annual alerts for document revision and review. WECC_URE1 reorganized its Compliance office, bringing on new management. WECC, therefore, determined that WECC_URE1 remediated CIP-002-1 R1, R2, R3, and R4 compliance issues.
2013-01-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2012010892 | CIP-002-1 | R2 | WECC_URE1 submitted four Self-Reports citing noncompliance with NERC Standard Requirements CIP-002-1 R1, R2, R3, and R4. Specifically, WECC_URE1 reported that it could not provide evidence of compliance with CIP-002-1 R1, R2, R3, and R4 between January 1, 2010, and May 2011. WECC subject matter experts (SMEs) reviewed WECC_URE1’s Self-Report. The SMEs determined that WECC_URE1 is required to demonstrate compliance with CIP-002-1 Requirements as of January 1, 2010. The SMEs, therefore, requested the following evidence: 1) WECC_URE1’s risk-based assessment methodology (RBAM) in effect on January 1, 2010, as required under CIP-002-1 R1; 2) WECC_URE1’s Critical Asset list in effect on January 1, 2010, pursuant to CIP-002-1 R2; 3) WECC_URE1’s Critical Cyber Asset (CCA) list in effect on January 1, 2010, pursuant to CIP-002-1 R3; and 4) A signed and dated record of senior manager or delegate(s)’s approval of the Critical Asset and CCA lists (even if such lists are null), for 2010. In response to the SMEs’ request, WECC_URE1 provided an RBAM, a Critical Asset list, a CCA list, and evidence of management approval, effective as of May 2011. WECC_URE1 disclosed that it could not provide CIP-002-1 documentation required under CIP-002-1 R1, R2, R3, and R4 in effect prior to May 2011. SMEs reviewed WECC_URE1’s RBAM, null Critical Asset list, and null CCA list. SMEs determined that CIP-002-1 documentation provided by WECC_URE1 appeared to satisfy CIP-002-1 R1, R2, R3, and R4. SMEs also determined, however, that between January 1, 2010 and May 2011, WECC_URE1 failed to develop an RBAM under CIP-002-1 R1. Further, the SMEs determined that between January 1, 2010, and May 2011, WECC_URE1 failed to develop lists of Critical Assets and CCAs for management review pursuant to CIP-002-1 R2, R3, and R4. The SMEs forwarded their findings regarding this issue to WECC Enforcement (Enforcement). Enforcement reviewed WECC_URE1’s Self-Report and the SMEs’ findings. Consistent with the SMEs findings, Enforcement determined that WECC_URE1 failed to demonstrate compliance with CIP-002-1 R1, R2, R3, and R4 between January 1, 2010, and May 2011. Enforcement also determined, however, that WECC_URE1 remediated noncompliance in May 2011. Enforcement, therefore, determined that WECC_URE1 remediated the CIP-002-1 R1, R2, R3, and R4 issues. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Failure to develop an RBAM, Critical Asset and CCA list per CIP-002-1 R1, R2, R3, and R4, renders Critical Asset and associated CCAs vulnerable to cyber attack or misuse. In this case, WECC_URE1 failed to identify and document an RBAM and failed to document null Critical Asset and null CCA lists per CIP-002-1 R1, R2, R3, and R4. WECC_URE1 has limited connectivity to the BPS. It owns and operates substations operating at or below 69 kV, none of which are Critical Assets. Further, WECC_URE1 does not own or operate any CCAs. WECC_URE1 has physically secured all facilities. Each of the substations is surrounded by 10-foot fencing topped with razor wire that limits physical access. WECC, therefore, determined that WECC_URE1's CIP-002-1 R1, R2, R3, and R4 remediated issues posed a minimal risk to the BPS. | WECC_URE1 provided its RBAM, a null Critical Asset list, a null CCA list, and evidence of managerial review, in effect as of May 2011. WECC reviewed WECC_URE1 CIP-002 documentation and determined that WECC_URE1 remediated noncompliance. Further, WECC determined that to avoid future issues with CIP-002 compliance, WECC_URE1 implemented a CIP-002 document tracking system. The system maintained CIP-002 documentation and issued annual alerts for document revision and review. WECC_URE1 reorganized its Compliance office, bringing on new management. WECC, therefore, determined that WECC_URE1 remediated CIP-002-1 R1, R2, R3, and R4 compliance issues.
2013-01-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2012010920 | CIP-002-1 | R3 | WECC_URE1 submitted four Self-Reports citing noncompliance with NERC Standard Requirements CIP-002-1 R1, R2, R3, and R4. Specifically, WECC_URE1 reported that it could not provide evidence of compliance with CIP-002-1 R1, R2, R3, and R4 between January 1, 2010, and May 2011. WECC subject matter experts (SMEs) reviewed WECC_URE1’s Self-Report. The SMEs determined that WECC_URE1 is required to demonstrate compliance with CIP-002-1 Requirements as of January 1, 2010. The SMEs, therefore, requested the following evidence: 1) WECC_URE1’s risk-based assessment methodology (RBAM) in effect on January 1, 2010, as required under CIP-002-1 R1; 2) WECC_URE1’s Critical Asset list in effect on January 1, 2010, pursuant to CIP-002-1 R2; 3) WECC_URE1’s Critical Cyber Asset (CCA) list in effect on January 1, 2010, pursuant to CIP-002-1 R3; and 4) A signed and dated record of senior manager or delegate(s)’s approval of the Critical Asset and CCA lists (even if such lists are null), for 2010. In response to the SMEs’ request, WECC_URE1 provided an RBAM, a Critical Asset list, a CCA list, and evidence of management approval, effective as of May 2011. WECC_URE1 disclosed that it could not provide CIP-002-1 documentation required under CIP-002-1 R1, R2, R3, and R4 in effect prior to May 2011. SMEs reviewed WECC_URE1’s RBAM, null Critical Asset list, and null CCA list. SMEs determined that CIP-002-1 documentation provided by WECC_URE1 appeared to satisfy CIP-002-1 R1, R2, R3, and R4. SMEs also determined, however, that between January 1, 2010 and May 2011, WECC_URE1 failed to develop an RBAM under CIP-002-1 R1. Further, the SMEs determined that between January 1, 2010, and May 2011, WECC_URE1 failed to develop lists of Critical Assets and CCAs for management review pursuant to CIP-002-1 R2, R3, and R4. The SMEs forwarded their findings regarding this issue to WECC Enforcement (Enforcement). Enforcement reviewed WECC_URE1’s Self-Report and the SMEs’ findings. Consistent with the SMEs findings, Enforcement determined that WECC_URE1 failed to demonstrate compliance with CIP-002-1 R1, R2, R3, and R4 between January 1, 2010, and May 2011. Enforcement also determined, however, that WECC_URE1 remediated noncompliance in May 2011. Enforcement, therefore, determined that WECC_URE1 remediated the CIP-002-1 R1, R2, R3, and R4 issues. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Failure to develop an RBAM, Critical Asset and CCA list per CIP-002-1 R1, R2, R3, and R4, renders Critical Asset and associated CCAs vulnerable to cyber attack or misuse. In this case, WECC_URE1 failed to identify and document an RBAM and failed to document null Critical Asset and null CCA lists per CIP-002-1 R1, R2, R3, and R4. WECC_URE1 has limited connectivity to the BPS. It owns and operates substations operating at or below 69 kV, none of which are Critical Assets. Further, WECC_URE1 does not own or operate any CCAs. WECC_URE1 has physically secured all facilities. Each of the substations is surrounded by 10-foot fencing topped with razor wire that limits physical access. WECC, therefore, determined that WECC_URE1's CIP-002-1 R1, R2, R3, and R4 remediated issues posed a minimal risk to the BPS. | WECC_URE1 provided its RBAM, a null Critical Asset list, a null CCA list, and evidence of managerial review, in effect as of May 2011. WECC reviewed WECC_URE1 CIP-002 documentation and determined that WECC_URE1 remediated noncompliance. Further, WECC determined that to avoid future issues with CIP-002 compliance, WECC_URE1 implemented a CIP-002 document tracking system. The system maintained CIP-002 documentation and issued annual alerts for document revision and review. WECC_URE1 reorganized its Compliance office, bringing on new management. WECC, therefore, determined that WECC_URE1 remediated CIP-002-1 R1, R2, R3, and R4 compliance issues.
2013-01-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2011009028 | CIP-006-3c | R2 | WECC_URE2 submitted a Self-Report to WECC for CIP-006-3c R2. WECC_URE2 failed to afford the protective measure of CIP-007 R1 to Cyber Assets that authorize and/or log access to the Physical Security Perimeters (PSPs) as required by CIP-006 R2.2. Specifically, WECC_URE2 installed a printer driver update on a physical access control system (PACS) server and failed to perform security testing for this change. The test procedures that WECC_URE2 developed for compliance with CIP-007 R1 included provisions for testing significant changes that could adversely affect existing cyber security controls as required by NERC, but also included provisions to test additional IT changes that exceed NERC CIP compliance (best practices) (e.g., testing for printer driver changes). WECC_URE2 did not follow its test procedures for a change control to a Cyber Asset used for monitor or control of its PSPs. Thus, WECC_URE2 had an issue with CIP-006-2 R2.2. WECC_URE2 reviewed its configuration to ensure all relevant security controls remained in place following the driver update and conducted functional testing to ensure the change did not adversely affect the operating environment, thus remediating the issue. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The PACS server is located in a PSP and has intrusion detection and firewall protection and has anti-virus software installed. Also, this device is located on an isolated demilitarized zone (DMZ) network. Additionally, the entity did perform functional testing and analysis of the change and was aware of the change that took place. Finally, the printer driver is not a significant update and such updates are routine. | WECC_URE2 reviewed its configuration to ensure all relevant security controls remained in place following the driver update and WECC_URE2 conducted functional testing to ensure the change did not adversely affect the operating environment. WECC_URE2 addressed this issue through the following six steps to mitigate the root cause of the issue and to mitigate the risk of reoccurrence: 1) Reviewed all change controls prior to discovery of the issue to verify that test procedures were followed as required back to the applicable enforcement date; 2) Validated that all relevant security controls were in place and functioning after the change was implemented; 3) Updated the test procedures documentation to provide additional clarity as to what type of changes require NERC CIP testing; 4) Developed refresher training specific to the test procedures and its updated verbiage which includes checks for comprehension; 5) Ensured test procedures retraining is completed by all applicable employees; and 6) Updated the required NERC CIP annual training to include a test procedure training module for personnel responsible for approving or implementing NERC CIP related changes. The updated annual training is required for new change control personnel. Existing personnel who engage in change controls are required to receive this training as part of their annual refresher training.
2013-01-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2012011384 | CIP-004-3 | R4 | WECC_URE3 submitted a Self-Report citing noncompliance with CIP-004-3 R4. WECC_URE3 reported that it failed to update its control center Critical Cyber Asset (CCA) access list within seven days of an employee’s retirement. WECC subject matter experts (SMEs) reviewed WECC_URE3’s Self-Report. The SMEs determined that a WECC_URE3 employee with access to CCAs associated with the control center had retired. The SMEs also determined that WECC_URE3 revoked that employee’s physical access rights to CCAs located within the control center the day before. Although that employee’s access rights were revoked, WECC_URE3 failed to update its physical access list within seven days of access revocation per CIP-004-3 R4.1. Rather, the SMEs determined that WECC_URE3 updated its access list 20 days after access revocation. The SMEs’ therefore, found WECC_URE3 in noncompliance with CIP-004-3 R4 and forwarded their findings to WECC Enforcement (Enforcement). Enforcement reviewed the Self-Report and the SMEs’ findings. Enforcement determined that compliance with CIP-004-3 R4.1 required WECC_URE3 to update its access list within seven days of access revocation. In this case, WECC_URE3 updated its list approximately 20 days after access revocation. Enforcement, therefore, determined that WECC_URE3 was in noncompliance with CIP-004-3 R4. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The risk posed by this noncompliance was reduced given the limited scope of the issue and the compensating measures in place during the period of noncompliance. The scope of the remediated issue is limited to a single individual whose physical access to CCAs associated with the control center was revoked. The individual retired in good standing. At the time of the individual’s departure, the individual was current with cyber security training required under CIP-004-3 R2 and had completed a current personnel risk assessment per CIP-004-3 R3. Further, all CCAs are secured within a Physical Security Perimeter (PSP). PSP egress and ingress is logged, controlled and monitored. Any unauthorized PSP access attempts on the part of the individual would have triggered alarms. CCAs associated with the Control Center are also electronically protected within an Electronic Security Perimeter (ESP). In this case the individual did not have authorized electronic access to CCAs. Nonetheless, ESP access is controlled and monitored. Any unauthorized electronic access attempt would have triggered alarming. In this case, the individual in scope of the remediated issue did not make any electronic access attempts. | WECC_URE3 completed the following activity to remediate the CIP-004-3 R4 compliance issue described herein: 1) WECC_URE3 completed refresher training with staff to emphasize CCA access list maintenance; 2) WECC_URE3 revised internal access list procedures to ensure timely list updates; 3) WECC_URE3 implemented biweekly audit reports that will alert staff to discrepancies between an individual’s position end date and CCA access end dates; and 4) WECC_URE3 implemented software upgrades to its access tracking systems that will automatically remove unescorted physical and cyber access rights when an employee is separated, terminated, or retired.
2012-12-31 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2012010993 | CIP-006-3c | R5 | MRO_URE1 self-reported noncompliance with CIP-006-3c R5 for failing to monitor a physical access point of a designated Physical Security Perimeter (PSP). MRO_URE1's air conditioning unit located inside its Physical Security Perimeter (PSP) was not functioning, resulting in an elevation of temperature in this room. Inside the room lies communications equipment for MRO_URE1's communications network, used to connect and monitor field equipment to the primary control center. This room also houses the equipment associated with the operation of MRO_URE1's Energy Management System (EMS). Rising temperature in this room could cause failures with this equipment. To reduce the elevated heat in the room, Doors 4 and 5 of the PSP were propped open. Specifically, Door 4 was propped open for approximately one hour. Door 5 was propped open for approximately 14 hours. Door 4 leads into a hallway, while Door 5 leads into the Communications Department work area. The Communications Department work area has a door which leads into the same hallway as Door 4, and this door has a key lock on the door knob. There are no other doors that can provide access to the Communications Department work area besides Door 5 and the door leading into the hallway. While Door 4 was propped open, the operator on duty monitored the door for any unauthorized physical access to the PSP. While Door 5 was propped open, the Communications Department work area was locked down by locking the door that leads to the same hallway as Door 4. While Door 5 was propped open, there was no human observation of the access point. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Access to the building in which the rooms in question are located is controlled at all times. The incident occurred on a Sunday afternoon, continuing through Monday morning, so activity in the building was minimal. Additionally, physical access logs were reviewed. According to the logs, during the time that Door 4 was open, only one individual without authorized unescorted physical access was present in the building. In addition, the operator was present the entire time Door 4 was open. Because of the raised flooring in the area, the operator can hear if someone is present in the adjacent rooms. During the time that Door 5 was open, the door between the room and the adjacent hallway was locked and could only be opened/unlocked from the inside. It is only opened/unlocked during the day, when the room is manned. According to the logs, one of the individuals that works in the room was present for a portion of the duration of the issue. From that time onward, there was human observation of Door 5. No additional individuals without unescorted physical access entered the building prior to that time. Given the limited activity in the building, and the fact that PSP access was effectively controlled for the majority of the time because of Door 5 was locked, MRO determined that this issue posed a minimal risk to the BPS. | MRO_URE1 performed the following actions to mitigate the issue: 1) Discussed the physical security plan with supervisors and reminded them of the importance of security and raised awareness of the security restrictions for the PSP; 2) Trained staff on security awareness regarding propped open doors, presence of unauthorized individuals, and the risks associated with such situations; and 3) Included a quarterly article in the company newsletter to provide information on existing MRO_URE1 policy, or changes related to the NERC Reliability Standards, and general information related to NERC and cybersecurity.
2012-12-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2012010277 | CIP-003-3 | R5; R5.1 | RFC_URE1 self-reported an issue with CIP-003-3 R5 to ReliabilityFirst. RFC_URE1 stores its Critical Cyber Asset (CCA) information in electronic files within a document management system and at specific locations at a generating plant. While RFC_URE1 verified the list of personnel responsible for authorizing access to CCA information within the document management system in 2011, RFC_URE1 failed to verify the list of personnel responsible for authorizing access to CCA information at the generating plant in 2011. RFC_URE1 documented and approved the two changes to the list of personnel responsible for authorizing access through its change management process. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). RFC_URE1's internal controls, specifically preparation for the annual CIP self-certification, enabled RFC_URE1 to discover and remediate the issues. In addition, RFC_URE1 documented and approved the two changes to the list of personnel responsible for authorizing access through RFC_URE1's change management process. The list of personnel responsible for authorizing access is six people, and the two individuals who approve such authorizing authority during this period were aware that the six individuals were responsible for authorizing access. As a result, it was less likely that anyone would have been improperly included on the list of personnel responsible for authorizing access to CCA information. | RFC_URE1 created and implemented a compliance action item tool to alert the appropriate personnel of specific compliance actions to be taken and the due date for each action. RFC_URE1 trained all necessary personnel on this tool.
2012-12-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2012010278 | CIP-005-1 | R2; R2.6 | RFC_URE1 self-reported an issue with CIP-005-1 R2 to ReliabilityFirst. RFC_URE1 discovered that 16 of its firewalls, which are Cyber Assets that reside within an Electronic Security Perimeter, were displaying the appropriate use banner after the login process is completed rather than prior to login. RFC_URE1 failed to submit a Technical Feasibility Exception (TFE) for this issue. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The incorrect implementation of the appropriate use banner does not affect operation of the firewalls. In addition, the following compensating measures, as submitted in the TFE, have been in place for several years. RFC_URE1 physically stores all devices within a controlled access Physical Security Perimeter. RFC_URE1 also enables and monitors security logging for unauthorized access attempts, and configuration changes. Furthermore, an intrusion detection system actively monitors for anomalous traffic. Lastly, logon banners are correctly presented prior to login and are presented in a secure shell session after login and must be acknowledged before the session can continue. | RFC_URE1 completed the following mitigating actions: 1) employed the use of banners on three firewalls; 2) submitted a TFE for 12 firewalls; and 3) replaced one firewall with a model able to timely display the appropriate use banner.
2012-12-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2012010323 | CIP-007-3 | R2; R.2.1 | RFC_URE1 self-reported an issue with CIP-007-1 R2 to ReliabilityFirst. Specifically, RFC_URE1 had not enabled only those ports and services required for normal and emergency operations. RFC_URE1 had disabled other ports and services on four printers and two time servers, the only function of which is to provide accurate time. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The printers at issue are not accessible from outside the RFC_URE1 system and are not connected to the Internet. In addition, the printers have directory service security groups established to limit unauthorized access to them. The time servers at issue are not connected to the Internet and have no visibility from the corporate or outside networks, though they do allow time synchronization with the local control system network. The only function of the time servers is to provide accurate time. RFC_URE1 installs, maintains, and monitors antivirus on the time servers appropriately. Furthermore, RFC_URE1 configured the Electronic Security Perimeter (ESP) to restrict access to these devices, enabled logging and monitored those logs for unauthorized access attempts and configuration changes. Lastly, an intrusion detection system actively monitors for anomalous traffic. | RFC_URE1 removed the printers from within the ESP and restricted the ports and services of the time servers.
2012-12-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2012010324 | CIP-007-1 | R4 | RFC_URE1 self-reported an issue with CIP-007-1 R4 to ReliabilityFirst. RFC_URE1 discovered that it had not installed antivirus software and malware prevention tools on 18 printers and two time servers because it is not technically feasible to do so. RFC_URE1 failed to submit a Technical Feasibility Exception (TFE) for these Cyber Assets, which are located within the Electronic Security Perimeters (ESPs). | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The printers at issue are not accessible from outside the RFC_URE1 system and are not connected to the Internet. In addition, the printers have directory service security groups established to limit unauthorized access to them. Futhermore, the time servers at issue, although they do allow time synchronization with the local control system network, are not connected to the Internet and have no visibility from the corporate or outside networks. The only function of the time servers is to provide accurate time. Also, the following compensating measures, as submitted in the TFE, have been in place for several years: 1) appliances are physically stored in a controlled access physical security perimeter; 2) logical access is controlled by directory service group membership, remote authentication is controlled by directory service protocol authentication, and all authentications enforce password complexity; 3) security logging is enabled and monitored for unauthorized access attempts; 4) there is an intrusion detection system actively monitoring for anomalous network traffic; 5) local administrative passwords are set manually to meet (or exceed) the NERC CIP password complexity requirements; and 6) all servers and workstations based on a specific operating system have antivirus installed, maintained, and monitored appropriately. | RFC_URE1 replaced or installed a firmware upgrade to the time servers enabled installation of antivirus and malware prevention or submitted a TFE for those time servers where it was not possible to do so. In addition, RFC_URE1 removed certain printers from within the ESP and submitted a TFE for certain printers.
2012-12-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2012010325 | CIP-007-1 | R5; R5.3 | RFC_URE1 self-reported an issue with CIP-007-1 R5 to ReliabilityFirst. RFC_URE1 discovered that it had not required passwords to have the following characteristics: 1) a minimum of six characters; 2) a combination of alpha, numeric and “special” characters; and 3) are changed at least annually on 18 printers and two time servers because it is not technically feasible to do so. RFC_URE1 failed to submit a Technical Feasibility Exception (TFE) for these Cyber Assets within the Electronic Security Perimeter (ESP). | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The printers at issue are not accessible from outside the RFC_URE1 system and are not connected to the Internet. The time servers at issue, although they do allow time synchronization with the local control system network, are not connected to the Internet and have no visibility from the corporate or outside networks. The only function of the time servers is to provide accurate time. In addition, the following compensating measures for printers, as submitted in the TFE, have been in place for several years: 1) all printers are physically stored within a controlled access Physical Security Perimeter (PSP); 2) procedural controls are in place to manually enforce password requirements for: a) a six-character minimum length; b) a combination of alpha, numeric and special characters; and c) annual password reset; 3) remote logical access to printer interface is controlled by directory service authentication; 4) security logging is enabled and monitored for unauthorized access attempts; and 5) there is an intrusion detection system actively monitoring for anomalous traffic. For the servers, the following compensating measures, as submitted in the TFE, have been in place since 2012: 1) time server appliances are physically stored within an access controlled PSP; 2) access to these devices are controlled within the ESP; 3) only ports and services required for normal operation of the device are enabled; 4) logging is enabled and monitored for unauthorized access attempts and configuration changes; and 5) passwords for devices are under the control of three individuals who are aware of the password complexity requirements and of RFC_URE1's cybersecurity policy stating those requirements, therefore no password would be entered that did not meet the Standards. | RFC_URE1 replaced or installed a firmware upgrade to the time servers, enabled installation of antivirus and malware prevention or submitted a TFE for those time servers where it was not possible to do so. In addition, RFC_URE1 removed certain printers from within the ESP and submitted a TFE for certain printers.
2012-12-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2012010326 | CIP-007-1 | R6; R6.1 | RFC_URE1 self-reported an issue with CIP-007-1 R6 to ReliabilityFirst. RFC_URE1 discovered that it had not ensured four printers and two time servers were implementing automated tools or organizational process controls to monitor system events that are related to cybersecurity because it is not technically feasible to do so. RFC_URE1 failed to submit a Technical Feasibility Exception (TFE) for these Cyber Assets within the Electronic Security Perimeter (ESP). | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The printers at issue are not accessible from outside the RFC_URE1 system and are not connected to the Internet. In addition, the printers have directory service security groups established to limit unauthorized access to them. The time servers at issue, although they do allow time synchronization with the local control system network, are not connected to the Internet and have no visibility from the corporate or outside networks. The only function of the time servers is to provide accurate time. RFC_URE1 installs, maintains, and monitors antivirus on the time servers appropriately. Furthermore, RFC_URE1 configured the ESP to restrict access to these devices, enabled logging and monitored those logs for unauthorized access attempts and configuration changes. Lastly, an intrusion detection system actively monitors for anomalous traffic. | RFC_URE1 removed the printers from within the ESP and replaced or updated firmware for the time servers.
2012-12-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2012010327 | CIP-007-3 | R8; R8.2 | RFC_URE1 self-reported an issue with CIP-007-3 R8 to ReliabilityFirst. RFC_URE1 discovered that it had not included in its cyber vulnerability assessment a review to verify that only ports and services required for operation of four printers and two time servers, Cyber Assets within the Electronic Security Perimeter (ESP), are enabled. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The printers at issue are not accessible from outside the RFC_URE1 system and are not connected to the Internet. In addition, the printers have directory service security groups established to limit unauthorized access to them. The time servers at issue, although they do allow time synchronization with the local control system network, are not connected to the Internet and have no visibility from the corporate or outside networks. The only function of the time servers is to provide accurate time. RFC_URE1 installs, maintains, and monitors antivirus on the time servers appropriately. Furthermore, RFC_URE1 configured the ESP to restrict access to these devices, enabled logging and monitored those logs for unauthorized access attempts and configuration changes. An intrusion detection system actively monitors for anomalous traffic. | RFC_URE1 removed the printers from within the ESP and restricted the ports and services of the time servers.
2012-12-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2012010410 | CIP-006-3c | R6 | RFC_URE1 self-reported an issue with CIP-006-3c R6 to ReliabilityFirst. A RFC_URE1 employee without authorized unescorted physical access to a control room was working in that control room. A RFC_URE1 employee with authorized unescorted physical access to the control room escorted the unauthorized employee, but failed to manually log the unauthorized employee’s access. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. RFC_URE1's internal controls enabled RFC_URE1 to discover and remediate the issues quickly. In addition, the employee was escorted at the time of the incident and was just not documented in the manual log. Furthermore, it was unlikely that the employee was a threat to RFC_URE1's system because the employee works for RFC_URE1 and RFC_URE1 had scheduled the employee to be in the control room that day. | RFC_URE1 restricted escorted visitor access to only one door, deactivated remote door unlock functionality of certain doors, and investigated other locations that have remote door unlock capabilities and evaluated them for deactivation.
2012-12-31 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP201100537 | CIP-007-3 | R4 | SPP RE_URE1 self-reported noncompliance with CIP-007-3 R4, regarding its failure to install malware prevention software on its Critical Cyber Assets (CCA). SPP RE_URE1 filed a Technical Feasibility Exception for its Cyber Assets using its operating system because these assets were not running anti-virus and malware protection software, and SPP RE_URE1 had been instructed by its supervisory control and data acquisition (SCADA) vendor that anti-virus and malware protection programs had not been approved or tested for these assets. This TFE was accepted by SPP RE. SPP RE disapproved the TFE because it determined that anti-virus products were available for the operating system. The TFE disapproval was made effective March 1, 2011. SPP RE_URE1 self-reported a noncompliance of CIP-007-3 R4 because it failed to install and began running anti-virus software on its operating system Cyber Assets until 22 days after the TFE disapproval effective date. | SPP RE determined that the issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Although SPP RE_URE1 allowed 22 days to pass between the effective disapproval date and the date in which it installed and began running anti-virus software on its operating system Cyber Assets, SPP RE_URE1's Cyber Assets were still under the protective mitigation measures that it had implemented for the TFE. These protective measures included housing all assets behind a firewall, which was set to deny access by default, and monitoring these assets 24 hours a day, seven days a week by a security event and incident management server, which is set to alert administrators of suspicious activities. Additionally, SPP RE_URE1's Cyber Assets that used the operating system had patches applied, and these patches were kept up to date. Therefore, although these devices did not have anti-virus or malware prevention tools, they were protected from vulnerabilities. | SPP RE_URE1 implemented anti-virus software on operating systems and enrolled these systems in SPP RE_URE1's CIP-007 R4 Anti-malware and Anti-virus Program.
2012-12-31 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPPRE_URE2) | NCRXXXXX | SPP2012010282 | CIP-005-1 | R1; R1.6 | During a Compliance Audit, the SPP RE Audit Team determined that SPPRE_URE2 was noncompliant with CIP-005-1 R1 and R1.6. With regard to CIP-005-1 R1, the Audit Team found that SPPRE_URE2's documentation of its Electronic Security Perimeter (ESP) did not properly identify five firewalls that existed beyond the ESP. The firewalls' management ports were connected to a network segment within the ESP. Additionally, SPPRE_URE2 had not appropriately identified three host servers which were serving as access control devices between the GPS clocks and the SPPRE_URE2 system control and data acquisition (SCADA)/energy management systems (EMS) as Electronic Access Control Systems (EACS) /ESP access points. With regard to R1.6, the Audit Team found that SPPRE_URE2's documentation supporting compliance with CIP-005-1 R1.6, i.e., the lists of Critical Cyber Assets (CCAs), Protected Cyber Assets, Electronic Access Control and monitoring Systems, and Physical Access Control Systems (collectively Master Lists) did not properly identify the active directory servers, the firewall management console, and the firewall as EACS. | SPP RE determined that the issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Although SPPRE_URE2 did not properly identify all electronic access points to the ESPs and the Cyber Assets deployed for the access control and monitoring of these access points on its master lists, SPPRE_URE2 did have the controls required by CIP-005-1 R1.5 in place prior to October 1, 2010. Therefore, all affected Cyber Assets and CCAs were afforded protective measures in accordance with the CIP Standards. SPPRE_URE2's non-compliance was documentation-related and did not represent a material lapse in the protection of its ESPs, CCAs or Cyber Assets deployed for the access control and monitoring of its access points. | SPPRE_URE2 modifed its master lists as follows: 1) reclassified the five firewalls beyond the defined ESP, whose management ports are connected to a network segment within the ESP; 2) identified and classified three host servers serving as the access point control devices between the GPS clocks and the SCADA/EMS servers as EACS / ESP Access Points on the master lists; 3) updated its ESP diagrams to more clearly designate all ESP access points; and 4) added two active directory servers to the master lists as EACS for their access control and monitoring functions. The administrative error that temporarily omitted the firewall management console from the master lists was corrected. SPPRE_URE2 reviewed the versions of the master lists and validated that the firewall and the firewall management console were correctly listed.
2012-12-31 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPPRE_URE2) | NCRXXXXX | SPP2012010284 | CIP-005-1 | R3 | During a Compliance Audit, the SPP RE Audit Team determined that SPPRE_URE2 was noncompliant with CIP-005-1 R3. SPPRE_URE2 was not performing monitoring and logging of access attempts at all of the access point to its Electronic Security Perimeters (ESPs) twenty-four hours a day, seven days a week. SPPRE_URE2 had implemented a process for monitoring and logging access at access points to its ESP which relied on its ConsoleWorks server to monitor and automatically review logs for Virtual Private Network (VPN) access and access to the Cyber Assets within its ESPs. ConsoleWorks provides real-time alerts of failed logon attempts. The Audit Team found that SPPRE_URE2 was not capturing and manually reviewing all access logs when the ConsoleWorks server is down for maintenance. | SPP RE determined that the issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The SPP RE Audit Team determined that SPPRE_URE2 had implemented and documented processes for monitoring and logging access at access points to its ESPs twenty-four hours a day, seven days a week. It was only during those brief periods when the ConsoleWorks server was down for maintenance that logs for VPN access and access to the Cyber Assets in SPPRE_URE2's ESPs were not captured and automatically reviewed. Electronic dial-up access to SPPRE_URE2's ESPs and Cyber Assets is not allowed and access to firewalls is monitored through a separate process in which firewall logs are monitored and alerts are sent to SPPRE_URE2 IT Security Staff on failed access attempts. SPPRE_URE2 maintains a robust physical security program providing in-depth protection to its Cyber Assets. | SPPRE_URE2 implemented a second ConsoleWorks server to provide for continuous monitoring and automatic reviews of logs for VPN access and access to the Cyber Assets in its ESP when one of its ConsoleWorks servers is offline for maintenance.
2012-12-31 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPPRE_URE2) | NCRXXXXX | SPP2012010285 | CIP-006-3 | R1; R1.6 | During a Compliance Audit, the SPP RE Audit Team determined that SPPRE_URE2 was noncompliant with CIP-006-3 R1.6. SPPRE_URE2's manual visitor log for the Physical Security Perimeter (PSP) at SPPRE_URE2's central control center did not denote the exit time for one visitor. | The SPP RE determined that the issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The SPP RE Audit Team determined that SPPRE_URE2 had implemented procedures at each of its PSPs to manually or electronically log access information details that are sufficient to uniquely identify individuals not authorized for unescorted access, and to identify the date and time of access of these individuals. SPPRE_URE2's physical access program was sufficiently robust to provide substantial protection to its PSPs. The issue represented a single lapse in SPPRE_URE2's physical security program and is not indicative of a systemic problem. | SPPRE_URE2 verified that its physical security plan and corresponding visitor control program contained the necessary language pertaining to the requirement to log the entry and exit of visitors to restricted areas, including the date and time, to and from PSPs. It validated that the log controllers and security services are reviewing restricted area visitor logs to ensure required information is documented and legible. SPPRE_URE2 added an additional camera installation on the inside of the PSP Access Point to record the logging of visitors to supplement the requirement to log visitor access to restricted areas.
2012-12-31 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPPRE_URE2) | NCRXXXXX | SPP2012010288 | CIP-007-1 | R6; | During a Compliance Audit, the SPP RE Audit Team determined that SPPRE_URE2 was noncompliant with CIP-007-1 R6. SPPRE_URE2 had not properly implemented automated tools or organizational process controls to monitor system events that are related to cyber security. SPPRE_URE2 had implemented a process for monitoring and logging access at access points to its Electronic Security Perimeter (ESP) which relied on the ConsoleWorks server to monitor system events, send alerts and automatically review logs for Virtual Private Network (VPN) access and access to the Cyber Assets in its ESPs. The Audit Team found that SPPRE_URE2 was not receiving alerts of detected cyber security incidents nor capturing and manually reviewing all logs of system events related to cyber security when the ConsoleWorks server is down for maintenance. | SPP RE determined that the issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The SPP RE Audit Team determined that SPPRE_URE2 had implemented and documented processes for monitoring and logging access at access points to its ESPs twenty-four hours a day, seven days a week. These processes provided SPPRE_URE2 with alerts of detected cyber security incidents and ensured that logs of system events related to cyber security were captured. It was only during those brief periods when the ConsoleWorks server was down for maintenance that alerts were unavailable and logs for VPN access and access to the Cyber Assets in its ESPs were not captured and automatically reviewed. Additionally, SPPRE_URE2 had protective measures in place to protect Cyber Assets and Critical Cyber Assets during the isolated times the ConsoleWorks server was down for maintenance, including card swipes for sensitive areas, locking drawers, video surveillance, password and lockout policies, and personnel physical and cyber access reviews and control processes. | SPPRE_URE2 installed a second server running ConsoleWorks as a backup. Security event logs are sent to both the primary and backup ConsoleWorks servers to evaluate, capture, and alert. Automated failover is configured, as is the ability to manually switch for routine maintenance activities. The ConsoleWorks server was reconfigured to store security event logs indefinitely.
2012-12-31 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 3 (SPPRE_URE3) | NCRXXXXX | SPP2012009933 | CIP-007-3 | R1.3 | During a CIP Compliance Audit, the SPP RE CIP Audit Team determined that SPP RE_URE3 was noncompliant with CIP-007-3 R1. SPP RE_URE3 did not have documentation of test results for changes to Cyber Assets (CAs) within the Electronic Security Perimeter (ESP) as required by R1.3. The SPP Audit Team discovered the noncompliance while reviewing SPP RE_URE3's test procedures for adding new CAs to the ESP or significantly changing existing CAs within the ESP. | SPP RE determined that the issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Although SPP RE_URE3 did not have documentation of the test results for new CAs or changes to existing CAs, the CIP Audit Team found that SPP RE_URE3 had change management tickets directing the testing of changes to CAs within the ESP. SPP RE_URE3's change management records included observation comments for changes made to SPP RE_URE3 CAs within the ESP. While these comments do not constitute test results, they do evidence that changes took place under SPP RE_URE3 observation. | SPP RE_URE3 has incorporated a description of the test it performed on any changes to CAs within the ESP as well as the results of those tests into its change management tickets.
2012-12-31 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE2012011001 | CIP-003-3 | R2; R2.1; R2.2 | Texas RE_URE1 submitted a Self-Report after an internal audit revealed that the change in senior managers with overall responsibility and authority for leading and managing Texas RE_URE1's implementation of, and adherence to, Standards CIP-002-3 through CIP-009-3 was not documented within 30 days, as required by CIP-003-3 R2.2. The operation supervisor served as a senior manager for two years and one month and this designation was documented pursuant to CIP-003-1 R1 criteria. However, when the operation supervisor left, the appointment of the new senior manager was not documented to reflect the change. In addition, Texas RE_URE1 self-reported that it failed to show documentation of how the new senior manager hired was identified in Texas RE_URE1's documents by name, title, and date of designation, as required by CIP-003-3 R2.1. | This issue posed a minimal risk and did not pose a serious or substantial risk to the bulk power system (BPS). Although Texas RE_URE1 failed to document the designation of the new senior manager within 30 days, the senior manager was operating in his new capacity and was clear about his overall responsibility and authority for leading and managing Texas RE_URE1's implementation of, and adherence to, Standards CIP-002-3 through CIP-009-3. Further, due to the small staff size, Texas RE_URE1 reported that all the employees were made aware verbally of the new senior manager and his role within the company. Finally, Texas RE_URE1 did not experience a gap in senior leadership for CIP Standards, thereby reducing the risk to the BPS to minimal. | This remediated issue was mitigated when the leadership delegation document, identifying the senior manager, was signed. Texas RE has verified the mitigation activities as complete. To prevent future oversights and to ensure timely replacement of departing senior managers, a transfer note with instructions were placed in the personnel file of the person who is presently designated as the senior manager. The note clarifies that: 1) he is the senior manager for the applicable CIP Standards; and (2) he must take appropriate action to properly transfer the senior manager duties and responsibilities prior to his departure, retirement or other personnel status change. Also, Texas RE_URE1 has adopted and implemented a CIP document that specifically states that changes to the senior manager position must be documented within 30 days of the change.
2012-12-31 | TRE_URE1liability Entity (TRE_URE1) | Unidentified Registered Entity 2 (TRE_URE2) | NCRXXXXX | TRE2012010376 | CIP-002-3 | R1 | An Audit conducted by TRE_URE1 revealed that TRE_URE1_URE2 failed to identify and document a risk-based assessment methodology (RBAM) to use to identify its Critical Assets. A draft RBAM document existed since mid-March, 2012, but it was not approved and had not been implemented. An approved RBAM was submitted to the Audit Team. TRE_URE1 determined the duration of this remediated issue to be five weeks, from the date when TRE_URE1_URE2 was required to comply with this Standards, to the date when the RBAM was approved and documented. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because TRE_URE1_URE2 does not have any Critical Assets or Critical Cyber Assets (CCAs). In addition, TRE_URE1_URE2 provided RBAM, showing that TRE_URE1_URE2 went through the Critical Asset criteria included in the approved RBAM and found no Critical Assets or CCAs, indicating that during the pendency of this remediated issue, TRE_URE1_URE2 had no Critical Assets or CCAs. Further, TRE_URE1_URE2's Transmission Operator provided documentation indicating that it did not consider TRE_URE1_URE2's assets to be critical. Finally, the period of noncompliance was five weeks, thereby reducing the risk to the BPS. | TRE_URE1_URE2 took immediate action to correct this remediated issue. The senior manager with overall responsibility and authority for leading and managing TRE_URE1_URE2's implementation of, and adherence to all CIP Standards approved and implemented an RBAM. TRE_URE1_URE2 provided TRE_URE1 with an approved, implemented, and completed RBAM and a list of Critical Assets and CCAs, which showed that TRE_URE1_URE2 did not have any Critical Assets or CCAs. TRE_URE1 has verified the mitigation activities as complete.
2012-12-31 | TRE_URE1liability Entity (TRE_URE1) | Unidentified Registered Entity 2 (TRE_URE2) | NCRXXXXX | TRE2012010377 | CIP-002-3 | R3 | An Audit conducted by TRE_URE1 revealed that TRE_URE1_URE2 failed to develop a list of associated Critical Cyber Assets (CCAs) essential to the operation of its Critical Assets. During the period of noncompliance, TRE_URE1_URE2 did not have a documented RBAM, and therefore could not identify a list of Critical Assets through application of its RBAM. However, TRE_URE1_URE2 had a draft RBAM during that period. Because TRE_URE1_URE2 did not have a list of Critical Assets, it could not develop a list of associated CCAs. TRE_URE1 determined the duration of this remediated issue to be five weeks, from the date when TRE_URE1_URE2 was required to comply with this Standards, to the date when the RBAM was approved and documented and TRE_URE1_URE2 developed a list of Critical Assets and associated CCAs. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because TRE_URE1_URE2 does not have any Critical Assets or CCAs. TRE_URE1_URE2 provided a list of assets through the risk assessment criteria included in the approved RBAM. The list showed that TRE_URE1_URE2 has no Critical Assets or CCAs. Additionally, TRE_URE1_URE2's Transmission Operator provided documentation indicating that it did not consider TRE_URE1_URE2's assets to be critical. Finally, the period of noncompliance was five weeks, thereby reducing the risk to the BPS. | TRE_URE1_URE2 took immediate action to correct this remediated issue. The senior manager with overall responsibility and authority for leading and managing TRE_URE1_URE2's implementation of, and adherence to all CIP Standards accepted and implemented an RBAM. TRE_URE1_URE2 provided TRE_URE1 with an approved, implemented, and completed RBAM and a list of Critical Assets and CCAs, which showed that TRE_URE1_URE2 did not have any Critical Assets or CCAs. TRE_URE1 has verified the mitigation activities as complete.
2012-12-31 | TRE_URE1liability Entity (TRE_URE1) | Unidentified Registered Entity 2 (TRE_URE2) | NCRXXXXX | TRE2012010378 | CIP-002-3 | R4 | An Audit conducted by TRE_URE1 revealed that TRE_URE1_URE2 was noncompliant with CIP-002-3 R4. TRE_URE1_URE2's senior manager or delegate(s) failed to approve annually the risk-based assessment methodology (RBAM), the list of Critical Assets and the list of Critical Cyber Assets (CCAs). TRE_URE1 verified that the entity documented and implemented a RBAM. TRE_URE1 determined the duration of this remediated issue to be five weeks, from the date when TRE_URE1_URE2 was required to comply with this Standards, to the date when the senior manager approved the RBAM and the list of CA and CCAs. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). While the RBAM and the list of Critical Assets and CCAs were not formally accepted and signed by the senior manager, an evaluation of the assets was performed using the implemented RBAM and no Critical Assets or associated CCAs were found Additionally, TRE_URE1_URE2's Transmission Operator provided documentation indicating that it did not consider TRE_URE1_URE2's assets to be critical. Finally, the period of noncompliance was five weeks, thereby reducing the risk to the BPS. | TRE_URE1_URE2 took immediate actions to correct this remediated issue. The senior manager with overall responsibility and authority for leading and managing TRE_URE1_URE2's implementation of and adherence to all CIP standards accepted and implemented an RBAM. TRE_URE1_URE2 provided TRE_URE1 with an approved, implemented, and completed RBAM and a list of Critical Assets and CCAs. TRE_URE1 has verified the mitigation activities as complete.
2012-12-31 | TRE_URE1liability Entity (TRE_URE1) | Unidentified Registered Entity 2 (TRE_URE2) | NCRXXXXX | TRE2012010379 | CIP-002-3 | R2 | An Audit conducted by TRE_URE1 revealed that TRE_URE1_URE2, failed to develop a list of its identified Critical Assets determined through an annual application of its risk-based assessment methodology (RBAM), as required by CIP-002-3 R2. During the period of noncompliance, TRE_URE1_URE2 did not have a documented and approved RBAM, and therefore could not identify a list of Critical Assets through the application of its RBAM. However, TRE_URE1_URE2 had a draft RBAM during this period. TRE_URE1 determined the duration of this remediated issue to be five weeks, from the date when TRE_URE1_URE2 was required to comply with this Standards, to the date when the RBAM was approved and documented and TRE_URE1_URE2 developed a list of Critical Assets. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because TRE_URE1_URE2 does not have any Critical Assets or Critical Cyber Assets (CCAs). TRE_URE1_URE2 provided a list of assets evaluated through the risk assessment criteria included in the approved RBAM. The list showed that TRE_URE1_URE2 has no Critical Assets or CCAs. Additionally, TRE_URE1_URE2's Transmission Operator provided documentation indicating that it did not consider TRE_URE1_URE2's assets to be critical. Finally, the period of noncompliance was five weeks, thereby reducing the risk to the BPS. | TRE_URE1_URE2 took immediate action to correct this remediated issue. The senior manager with overall responsibility and authority for leading and managing TRE_URE1_URE2's implementation of, and adherence to all CIP Standards accepted and implemented an RBAM. TRE_URE1_URE2 provided TRE_URE1 with an approved, implemented, and completed RBAM and a list of Critical Assets and CCAs, which showed that TRE_URE1_URE2 did not have any Critical Assets or CCAs. TRE_URE1 has verified the mitigation activities as complete.
2012-11-30 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2012010994 | CIP-002-1 | R1; R1.2.1 | During a CIP Audit, FRCC determined that FRCC_URE1 had an issue with CIP-002-1 R1. Specifically, the evidence submitted by FRCC_URE1 was insufficient to demonstrate that FRCC_URE1 considered control centers and back-up control centers in its risk-based assessment methodology (RBAM) for a period of approximately two and a half years. Although FRCC_URE1 does not own any control centers or back-up control centers, FRCC_URE1 failed to consider them in its RBAM, as required by CIP-002-1 R1.2.1. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). FRCC_URE1 considered all asset types required by CIP-002 R1, based on an inventory of all BPS assets it owned and did not consider control centers as it does not own control centers or a back-up control center. | To mitigate this issue, FRCC_URE1 updated its RBAM and the procedure to include control centers and back-up control centers.
2012-11-30 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2012009952 | CIP-005-3a | R1; R1.5 | MRO_URE1 self-reported an issue with CIP-005-3a R1.5 because it failed to afford Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeter the protective measures specified in CIP-007-3 R3 (security patch management). MRO_URE1 failed to properly assess five patches within 30 days, for devices used in the control and monitoring of electronic access points. Upon assessment, MRO_URE1 reported that none of the patches were applicable to its devices. Two of the patches were assessed on the 31st day (one day beyond the required 30 days). One patch was assessed on the 63rd day (33 days late). Another patch was assessed on the 86th day (56 days late). Finally, the fifth patch was originally incorrectly assessed as applicable and then correctly assessed as not applicable 73 days later. The patches were not assessed for over three months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. MRO_URE1 has a documented patch management process which includes several layers of review. MRO_URE1 assessed 49 patches during the issue time period. After completing this process, MRO_URE1 had only failed to assess a small percentage of its total number of patches (10%). Additionally, none of the patches were applicable to MRO_URE1's devices and the duration of issues was an average of 32 days. Furthermore, MRO_URE1 discovered, mitigated and self-reported this issue due to internal audit controls. | Meetings between MRO_URE1's IT and MRO_URE1's NERC CIP leadership are now held every two weeks to discuss outstanding patch applicability assessments. This meeting will achieve leadership engagement and will prevent reoccurrence of delayed applicability assessments. Additionally, MRO_URE1 has added two escalation notifications, as well as recipients to the existing notifications. At 15 calendar days past the release, the subject matter expert and the team lead for the affected infrastructure group are added to the notification. At 21 and 28 days, additional layers of leadership are added to the notification. This is an ongoing control that will remain implemented.
2012-11-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2012009853 | CIP-004-3 | R4; R4.2 | NPCC_URE1 self-reported an issue with CIP-004-3 R4.2. NPCC_URE1 failed to timely revoke unescorted physical access to Physical Security Perimeters (PSPs) containing Critical Cyber Assets (CCAs). Specifically, an employee transferred to a job that no longer required unescorted access, but the employee’s access rights were not revoked until 11 days after the transfer. The Standard requires the employee's access to be revoked within seven calendar days. The action to revoke because the employee no longer required access was not communicated in a timely manner to staff responsible for revoking access. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The employee transferred from working within the PSP to being a field worker. During the 11-day period, the access logs show that the employee did not access the PSPs. The transferred employee was reassigned to another part of the company where he assumed the responsibility of his newly-appointed position. During the 11-day period, the transferred employee was receiving training associated with his new position. The employee had undergone a personnel risk assessment and had previously received training concerning the responsibilities of unescorted physical access to PSPs containing CCAs. | To mitigate this issue, NPCC_URE1 completed the revocation 11 days after the employee transferred. NPCC_URE1 will prevent or minimize the risk of inconsistencies in the implementation of NPCC_URE1’s access control procedures by providing additional training for all staff responsible for the implementation of NPCC_URE1's access control procedures and issuing a guidance document to responsible staff regarding initiating and revoking user access rights.
2012-11-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2012010642 | CIP-006-3c | R1; R1.6.2 | NPCC_URE1 self-reported an issue with CIP-006-3c R1.6.2. NPCC_URE1 reported that an unescorted employee-in-training was in the Physical Security Perimeter (PSP) without having authorized unescorted access to Critical Cyber Assets. The PSP access door’s locking mechanism was not functioning properly. The unauthorized employee was in the PSP removing garbage for a period of seven minutes before exiting the PSP. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. NPCC_URE1's security command post received an alarm for “invalid access group” indicating a denial of access from the card key reader at the control room door for an access attempt by an unauthorized employee. This alarm was immediately followed by a “forced door” alarm. Security’s response and investigation into these alarms determined that the previously-tested PSP access door’s locking mechanism was no longer functioning properly, which allowed the PSP access door to be pushed open. During the period that the PSP access door’s physical locking mechanism was not functioning properly, the involved PSP area was continuously occupied by a number of staff members with authorized access. Lastly, the unauthorized employee that entered the PSP had satisfied the conditions precedent to being authorized for access to the PSP, although he was not actually authorized. The employee had both a valid personnel risk assessment and had taken the mandatory CIP cybersecurity 2012 training course. | To mitigate this issue, NPCC_URE1 stationed a security officer at the PSP door until it was repaired. NPCC_URE1 also conducted training covering specific information on this incident and actions to adhere to in the future should similar situations occur. NPCC_URE1 conducted a staff meeting to improve awareness of NERC CIP and physical security. NPCC_URE1 conducted an inspection of PSP access points for signage identifying the area as restricted/limited access requiring authorization or an escort, and if needed, posted additional signage.
2012-11-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 2 (NPCC_URE2) | NCRXXXXX | NPCC2012011151 | CIP-007-3 | R6; R6.4 | NPCC_URE2 self-reported an issue with CIP-007-3 R6.4. NPCC_URE2 incurred a problem with two Cyber Assets not forwarding their logs from the backup control center to the server at the new control center for a period of 90 days. A firewall located between the new control center and the former control center blocked the communication to the server at the former control center. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system due to the redundancy of the LANs at the control centers. Also, during this period the daily operations were handled by the a control center. The backup control center is a dedicated site with assets that are ready to handle operations if the operations at the other control center are compromised. If backup control center operations were required, a type of LAN was in operation with no loss of visibility. These two assets were functioning and were logging (to themselves), but were not forwarding their logs to the server, which resulted in a log retention problem. The absence of a router or switch log will not prevent a system operator from performing his duties. | To mitigate this issue, NPCC_URE2 moved the server. This move eliminated the firewall block between both the new and former control centers. NPCC_URE2 also updated its control test plan documentation to include a section requiring verification that logging is working successfully as a result of any changes to Critical Cyber Assets.
2012-11-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2012010409 | CIP-003-3 | R2 | RFC_URE1 self-certified an issue with CIP-003-3 R2. The CIP senior manager has been performing the role and functions as required in CIP-003-3 R2, but RFC_URE1 failed to properly identify the senior manager by name, title and date of designation in a cyber security policy procedure, as required by CIP-003-3 R2.1. | ReliabilityFirst determined that this issue posed a minimal risk to the reliability of the bulk power system (BPS). The risk to the reliability of the BPS was mitigated by the following factors. The CIP senior manager was performing the role and functions as required by CIP-003-3 R2 even though this designation was not documented in a cyber security policy procedure, as required by the Standard. In addition, RFC_URE1 has no Critical Assets. | RFC_URE1 created and implemented a procedure to identify the CIP senior manager by name, title and date of designation and included a delegate.
2012-11-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2012010102 | CIP-007-3 | R4 | RFC_URE2 self-reported an issue with CIP-007-3 R4 to ReliabilityFirst. RFC_URE1 has in place a process for the update of anti-virus and malware prevention signatures that includes testing and installing the signatures. RFC_URE2’s system administrator, however, failed to test the signatures for four electronic access control and/or monitoring systems prior to installing the signatures. The system administrator failed to follow RFC_URE2’s change management procedures, which did not authorize updates to these systems without testing the signatures. | ReliabilityFirst determined that this issue posed a minimal risk to the reliability of the bulk power system (BPS). The risk to the reliability of the BPS was mitigated by the following factors. RFC_URE2 self-identified this issue and the systems at issue do not provide control functions for the BPS. In addition, RFC_URE2 has in place a process for the update of anti-virus and malware prevention signatures. In this case, an individual failed to follow the process in this isolated instance. Further, the systems at issue are located behind firewalls with access rules restricting the traffic allowed to pass to and from the systems. | RFC_URE2 created a management position to provide additional oversight of certain CIP-related processes, including change management. This manager will perform reviews of changes prior to implementation to help ensure compliance with the CIP Reliability Standards. In addition, during formal training for necessary personnel, RFC_URE2 reinforced the CIP Reliability Standards and the documented RFC_URE2 procedures.
2012-11-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2012010417 | CIP-005-3a | R1 | RFC_URE2 self-reported to ReliabilityFirst an issue with CIP-005-3a R1. RFC_URE2 placed a new electronic access control and monitoring system into service. The servers supporting this system exist on a virtual platform. The virtual platform allows multiple operating systems, or “guests,” to operate concurrently on one host server. RFC_URE2 conducted and documented security patch evaluations for all guest operating systems residing on the virtual platform. RFC_URE2, however, failed to assess two security patches for the devices that run the virtual platform, operating on the physical server, which are Cyber Assets used in the access control and/or monitoring of the Electronic Security Perimeter, within 30 calendar days of availability of the patches, as required by CIP-007-3 R3.1. RFC_URE2 therefore installed the patches without assessing them for applicability. | ReliabilityFirst determined that this issue posed a minimal risk to the reliability of the bulk power system (BPS). The risk to the reliability of the BPS was mitigated by the following factors. RFC_URE2 self-identified this issue, and the systems at issue do not provide control functions for the BPS. RFC_URE2 affords these systems, which are located within the Physical Security Perimeter, the remaining protections specified in CIP-005-3a R1.5. | To address the issue that involved CIP-007-3 R4, RFC_URE2 added a review of software security advisories to its existing patch identification processes for its operating systems. The process requires an assigned individual to obtain all advisories as they are issued, and then the individual reviews each advisory for the severity level within 30 days using a spreadsheet for tracking. In addition, RFC_URE2 created a management position to provide additional oversight of certain CIP-related processes, including patch management. During formal training for necessary personnel, RFC_URE2 reinforced the CIP Reliability Standards and the documented RFC_URE2 procedures. To address the issue that involved CIP-007-3 R8, RFC_URE2 updated its cyber vulnerability assessment procedure to guide the third-party or internal tester in performing the assessment. In addition, RFC_URE2 completed the cyber vulnerability assessment.
2012-11-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2012010418 | CIP-004-3 | R4 | RFC_URE2 self-reported to ReliabilityFirst an issue with CIP-006-3c R2.2. ReliabilityFirst assigned this CIP-006-3c R2.2 issue a tracking number, RFC2012001321. The Self-Report also indicated an issue with CIP-004-3 R4. ReliabilityFirst, however, did not assign a new tracking number. Instead RFC_URE2 self-certified the issue with CIP-004-3 R4 to ReliabilityFirst. A RFC_URE2 employee who had authorized unescorted physical access to a Physical Security Perimeter (PSP) no longer required such access. RFC_URE2 failed to disable the employee’s physical access to an emergency exit from the PSP within seven calendar days. This error occurred because the name of the emergency exit did not match the name of the other doors in the PSP. RFC_URE2 revoked the employee’s access. | ReliabilityFirst determined that this issue posed a minimal risk to the reliability of the bulk power system (BPS). The risk to the reliability of the BPS was mitigated by the following factors. The employee at issue transferred departments within RFC_URE2. RFC_URE2 monitors the door through badge access and visual monitoring, and the door is only accessible through a vacant adjacent room that itself is only accessible through a door that is normally locked when unattended. RFC_URE2 revoked the employee’s access from all other entrances to the PSP, as well as the employee’s authorized cyber access. As a result, it is unlikely that the individual would have gained access unnoticed through this door and cause harm to the integrity of the Critical Cyber Assets. Furthermore, RFC_URE2 discovered this issue during one of its periodic entitlement reviews of physical security access privileges, and the employee had a valid personnel risk assessment and cybersecurity training. | RFC_URE2 revoked the employee’s authorized unescorted physical access to the emergency exit door and changed the name of the emergency exit to conform with the rest of the entrances to the PSP.
2012-11-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2012010443 | CIP-007-1 | R8; R8.2; R8.3 | ReliabilityFirst conducted a Compliance Audit of RFC_URE2 during which ReliabilityFirst discovered an issue with CIP-007-1 R8 by RFC_URE2. A third-party vendor performs RFC_URE2’s cyber vulnerability assessment of the Cyber Assets within the Electronic Security Perimeter (ESP). RFC_URE2’s third-party vendor deleted the detailed evidence related to the cyber vulnerability assessment. As a result, RFC_URE2 provided a summary report from the third-party vendor that it: (a) performed a review to verify that only ports and services required for operations for Cyber Assets within the ESP were enabled (R8.2); and (b) included a review of controls for default accounts (R8.3). RFC_URE2, however, was unable to provide detailed evidence to support the summary report. | ReliabilityFirst determined that this issue posed a minimal risk to the reliability of the bulk power system (BPS). The risk to the reliability of the BPS was mitigated by the following factors. A third-party vendor performs RFC_URE2’s cyber vulnerability assessment of the assets used in the access control and monitoring of the ESP. RFC_URE2’s third-party vendor deleted the detailed evidence related to the cyber vulnerability assessment. As a result, RFC_URE2 provided a summary report from the third-party vendor that it: (a) performed a review to verify that only ports and services required for operations for Cyber Assets within the ESP were enabled; and (b) included a review of controls for default accounts. RFC_URE2’s evidence was simply inadequate to demonstrate the extent of RFC_URE2’s cyber vulnerability assessment. | RFC_URE2 updated its cyber vulnerability assessment procedure to guide the third-party or internal tester to perform the assessment. In addition, RFC_URE2 completed the annual cyber vulnerability assessment
2012-11-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP201100647 | CIP-002-1 | R1.1 | During a SPP RE CIP Compliance Audit of SPP RE_URE1, the SPP RE CIP audit team identified an instance of noncompliance with CIP-002-1 R1.1. Specifically, the CIP audit team observed that SPP RE_URE1's risk-based assessment methodology (RBAM) for identifying Critical Assets did not include evaluation criteria for assessing Critical Assets. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Although SPP RE_URE1's RBAM did not include evaluation criteria, SPP RE_URE1 did have a documented RBAM that it used to identify its Critical Assets. The original RBAM still considered the assets listed in CIP-002-1 R1.2 and SPP RE_URE1 determined that it did not have any Critical Assets or Critical Cyber Assets using the original RBAM. | SPP RE_URE1 revised its RBAM to include evaluation criteria for Critical Asset identification.
2012-11-30 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE201100506 | CIP-002-1 | R1.2.1 | A Compliance Audit of TRE_URE1 resulted in the finding that TRE_URE1 had a risk-based assessment methodology (RBAM) that did not consider reliability-related to its function services. The services were provided by and performed by its qualified scheduling entity (QSE). Specifically the RBAM did not consider the QSE's control center and backup control center. This remediated issue period was from the date TRE_URE1 was required to be compliant with the Standard, to when a revised RBAM was issued. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because although the RBAM did not consider the control center and backup control center of TRE_URE1's QSE, the Critical Asset identification process employed by TRE_URE1 for CIP-002-1 R2 did include the control center and backup control center at issue. Additionally, the QSE did not have any direct control over the physical operation of the facility. The QSE served only as a communication conduit. Communications could have been accommodated by the facility alone in the event of loss of communications by the QSE control center and the backup control center. | TRE_URE1 issued a revised RBAM that considered the QSE control center and backup control center. All mitigating activities have been verified as complete by Texas RE.
2012-11-30 | TRE_URE1liability Entity (TRE_URE1) | Unidentified Registered Entity 2 (TRE_URE2) | NCRXXXXX | TRE2012011192 | CIP-004-1 | R4 | During an Audit, a review of TRE_URE2's original personnel Critical Cyber Assets (CCA) access list revealed that the list did referenced general electronic access rights, but lacked the required electronic access rights specific detail. The original list simply stated if an employee had electronic access rights but not the scope of their specific rights. Reliability Standard CIP-004-1R4 instructs the Responsible Entity to maintain “list(s) of personnel with authorized cyber or authorized unescorted access to Critical Cyber Assets, including their specific electronic and physical access rights to Critical Cyber Assets.” Therefore, the CCA list utilized by TRE_URE2 was noncompliant. The remediated issue period was from the date the Standard was enforceable for TRE_URE2, to the date the revised list was implemented. | The issue posed a minimal risk and did not pose a serious or substantial risk to the bulk power system (BPS) because TRE_URE2 was consistently monitoring personnel electronic access rights and relied upon documented policies and procedures to manage personnel CCA electronic access rights. However, its monitoring efforts lacked sufficient documented detail regarding the scope of an employee's electronic access rights which had the potential to compromise BPS reliability in the event the original list alone was relied upon to grant electronic access. Further, the CCA access list is reviewed weekly in team meetings and necessary amendments are immediately documented by the meeting leader. Lastly, despite the lack of active list providing sufficient detail regarding specific electronic access rights, since TRE_URE2's registration, the same four employees (in a department of five) have managed electronic access authorizations and were familiar with the TRE_URE2's personnel and procedures. Based on these facts, TRE_URE1 determined that the issue is primarily documentation related. | The violation remediated issue was fully mitigated with the implementation of the revised personnel CCA access list. The new list includes greater detail regarding more specific electronic access rights information. All mitigating activities have been verified as complete by TRE_URE1.
2012-11-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2012011055 | CIP-002-3 | R4 | WECC_URE1 submitted a Self-Report addressing an issue with CIP-002-3 R4. According to the Self-Report, during the calendar year 2010, WECC_URE1 failed to document annual approval of its risk-based assessment methodology (RBAM). Per CIP-002-3 R4, WECC_URE1 is required to keep a signed and dated record of the senior manager or delegate’s annual approval of the RBAM, the list of Critical Assets (CAs) and the list of Critical Cyber Assets (CCAs). WECC_URE1 discovered that it did not have a signed and dated record of the then-senior manager’s approval of the RBAM (the associated lists, however, had been approved, signed and dated). A WECC Subject Matter Expert (SME) reviewed the Self-Report and discussed the issue with WECC_URE1's compliance personnel. The SME determined that WECC_URE1 had identified and documented an RBAM to use to identify its CAs, and had developed a list of its identified CAs and associated CCAs, through an annual application of the RBAM. When WECC_URE1 applied the RBAM, it resulted in null lists because WECC_URE1 had no CAs or associated CCAs. These null lists had been reviewed and approved by the then senior manager. However, that senior manager did not sign and date a copy of the RBAM for 2010. The SME forwarded these findings to the WECC Enforcement Department (Enforcement). Enforcement reviewed the Self-Report and the auditors’ findings, and determined that WECC_URE1 had an issue with CIP-002-3 R4, because it failed to have documentation that a senior manager or delegate approved the risk-based assessment methodology for 2010. | This issue posed a minimal and not serious or substantial risk to the reliability of the bulk power system. WECC_URE1 did not have any CAs or CCAs. Although WECC_URE1’s senior manager failed to sign the RBAM during calendar year 2010, he did sign and approve the null lists of CAs and CCAs. | WECC_URE1 remediated this issue. In April 2011, WECC_URE1 created a single point of contact, eliminated dual responsibility across its affiliated entities, and made one senior manager the delegate for all of its affiliated entities. The senior manager approved the RBAM for all WECC_URE1’s registered entities.
2012-11-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2012011027 | CIP-007-3 | R7 | WECC_URE2 submitted a Self-Report citing an issue with CIP-007-3 R7. WECC_URE2 reported that it failed to follow its CIP-007-3 R7 procedure when disposing of a Critical Cyber Asset (CCA). WECC Subject Matter Experts (SMEs) reviewed WECC_URE2’s Self-Report. SMEs contacted WECC_URE2 to request additional information. SMEs determined that one CCA associated with WECC_URE2 failed and could not be rebooted. WECC_URE2 staff usually assigned to handle CIP equipment failures were out of the office. The router was, therefore, removed by a technician who was not familiar with WECC_URE2’s CIP-007-3 R7 disposal procedure. Instead of completing the decommissioning checklist required under WECC_URE2’s CIP-007-3 R7 process, the technician followed the WECC_URE2 corporate cyber asset removal procedure and completed corporate documentation. The technician removed the router and sent the device back to the vendor without completing the CIP-007-3 R7 checklist necessary for CCA disposal. SMEs determined that WECC_URE2 had a possible issue with CIP-007-3 R7 and forwarded their findings to WECC Enforcement (Enforcement). Enforcement reviewed WECC_URE2’s Self-Report and SMEs’ findings. Enforcement determined that WECC_URE2’s failure to follow CCA disposal procedures when decommissioning a CCA on May 21, 2012, constitutes an issue with CIP-007-3 R7. | This issue posed a minimal and not a serious or substantial risk to the reliability of the bulk power system. The risk posed by WECC_URE2’s failure is minimal because there were compensating measures in place. Although the WECC_URE2 technician did not complete the WECC_URE2 decommissioning checklist required under WECC_URE2’s CIP-007-3 R7 process for CCA disposal, the technician did follow WECC_URE2 Corporate Policy regarding Cyber Asset disposal. The technician documented the device’s failure and removal. The technician returned the device to the vendor. At the time of removal, the device would not reboot or power on, and the device was password protected. This minimized the risk of unauthorized retrieval of WECC_URE2's data, and the risk that the device could be used as an access point to the Electronic Security Perimeter. WECC_URE2 received confirmation from the vendor that the device was received and destroyed. | WECC_URE2 completed the following remediation activities: The device was destroyed. WECC_URE2 completed the CIP-007-3 R7 checklist required for device disposal. WECC_URE2 revised its CIP-007-3 R7 procedures to address a new decommissioning process to be followed for all devices. Further, as preventative measures, WECC_URE2 undertook training or retraining for any personnel that have access to any CIP network device on this new procedure.
2012-11-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC201001975 | CIP-002-1 | R1 | WECC_URE3 submitted a Self-Certification addressing its possible noncompliance with CIP-002-1 R1. Specifically, WECC_URE3 reported its status as "Beginning Work." The Audit Team determined WECC_URE3 did not have a documented RBAM until August 30, 2010, as WECC had previously alleged. The Audit Team also determined that the appropriate application of WECC_URE3’s RBAM resulted in null lists for Critical Assests (CAs) and Critical Cyber Assets (CCAs) essential to the operation of a CA. On August 6, 2010, WECC found WECC_URE3 had an issue with CIP-002-1 R1 for failing to identify or document a Risk-Based Assessment Methodology (RBAM) to identify its Critical Assets as required by R1. | This issue posed a minimal and not a serious or substantial risk to the reliability of the bulk power system (BPS). WECC_URE3 applied its RBAM in 2011 and determined that it never had any CCAs essential to the operation of the CA. WECC subsequently verified this fact at an on-site Compliance Audit. Therefore, WECC determined WECC_URE3 does not have CCAs essential to the operation of the BPS. Moreover, the issues herein stem from WECC_URE3’s failure to implement and document an RBAM for the period from December 31, 2009 to August 29, 2010. Because WECC_URE3 does not have CAs or CCAs, the BPS was never exposed or compromised by WECC_URE3's failure to comply with the documentation requirements of CIP-002-1 R1. | WECC_URE3 mitigated the issue with CIP-002-1 R1 by identifying and documenting its RBAM.
2012-11-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC201001976 | CIP-002-1 | R2 | WECC_URE3 submitted a Self-Certification addressing its possible issue with CIP-002-1 R2. Specifically, WECC_URE3 reported its status as “Beginning Work.” WECC found WECC_URE3 had an issue with CIP-002-1 R2 for failing to develop a list of its identified Critical Assets (CAs) from the application of an RBAM as required by R2. The Audit Team determined WECC_URE3 did not have a documented RBAM until August 30, 2010. The Audit Team also determined that the appropriate application of WECC_URE3’s RBAM resulted in null lists for CAs and Critical Cyber Assets (CCAs) essential to the operation of a CA. | This issue posed a minimal and not a serious or substantial risk to the reliability of the bulk power system (BPS). WECC_URE3 applied its RBAM in 2011 and determined that it never had any CAs or CCAs essential to the operation of the CA. WECC subsequently verified this in an on-site Compliance Audit. Therefore, WECC determined WECC_URE3 does not have CCAs essential to the operation of the BPS. Moreover, the issues herein stem from WECC_URE3’s failure to implement and document an RBAM for the period from December 31, 2009 to August 29, 2010. Because WECC_URE3 does not have CAs or CCAs, WECC determined that the issues with CIP-002-1 R2 posed a minimal risk to the reliability of the BPS. | WECC_URE3 mitigated the issue with CIP-002-1 R2 by applying the RBAM developed in R1 to identify its CAs. As a result of this process, WECC_URE3 determined that it did not have any CAs.
2012-11-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC201001977 | CIP-002-1 | R4 | WECC_URE3 submitted a Self-Certification addressing its possible issue with CIP-002-1 R4. Specifically, WECC_URE3 reported its status as “Beginning Work.” WECC found that WECC_URE3 failed to have a list of Critical Assets (CAs) and a list of Critical Cyber Assets (CCAs) that were approved by a senior manager as required by R4. The Audit Team determined WECC_URE3 did not have a documented RBAM until August 30, 2010, as WECC had previously alleged. The Audit Team also determined that the appropriate application of WECC_URE3’s RBAM resulted in null lists for CAs and CCAs essential to the operation of a CA. | This issue posed a minimal and not a serious or substantial risk to the reliability of the bulk power system (BPS). WECC_URE3 applied its RBAM in 2011 and determined that it did not have any CAs or CCAs essential to the operation of the CA. WECC subsequently verified this in an on-site Compliance Audit. Therefore, WECC determined WECC_URE3 does not have CCAs essential to the operation of the BPS. Moreover, the issues herein stem from WECC_URE3’s failure to implement and document an RBAM for the period from December 31, 2009 to August 29, 2010. | WECC_URE3 mitigated the issue with CIP-002-1 R4 by providing a signed and dated record of the senior manager’s approval of the null list of CAs and the null list of CCAs.
2012-11-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2011008673 | CIP-002-1 | R3 | As a result of a Compliance Audit, WECC found that WECC_URE3 had an issue with CIP-002-1 R3 for its failure to develop a list (albeit a null list) of associated Critical Cyber Assets (CCAs) essential to the operation of a Critical Asset (CA). The Audit Team determined WECC_URE3 did not have a documented RBAM until August 30, 2010, as WECC had previously alleged. The Audit Team also determined that the appropriate application of WECC_URE3’s RBAM resulted in null lists for CAs and CCAs essential to the operation of a CA. | This issue posed a minimal and not a serious or substantial risk to the reliability of the bulk power system (BPS). WECC_URE3 applied its RBAM in 2011 and determined that it never had any CCAs essential to the operation of the CA. WECC subsequently verified this in an on-site Compliance Audit. Therefore, WECC determined WECC_URE3 does not have CCAs essential to the operation of the BPS. Moreover, the issues herein stem from WECC_URE3’s failure to implement and document an RBAM for the period from December 31, 2009 to August 29, 2010. | WECC_URE3 mitigated the issue with CIP-002-1 R3, WECC_URE3 used the null list of CAs, and developed a subsequent null list of CCAs essential to the operation of the CAs.
2012-10-31 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2012010722 | CIP-007-3 | R6; R6.2 | MRO_URE1 self-reported noncompliance with CIP-007-3 R6 because it did not have automatic alerting enabled on several Critical Cyber Assets (CCAs) for 129 days. More specifically, two physical servers and nine virtual servers were deployed with improper configuration; therefore automatic alerts for detected cybersecurity incidents would not have been sent, as required by R6.2. When implementing new devices, MRO_URE1 executes a compliance readiness checklist. The checklist contains each configuration task for setting up controls used for achieving compliance. The checklists for these devices were completed successfully. However, the script used to configure alerting had a typo, so the alerts were not being received. The misconfiguration was identified and corrected after 129 days. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The devices were protected by several layers of cybersecurity controls including: anti-virus/anti-malware software; up-to-date security patches; and authentication controls such as complex passwords. The CCAs were also located in an Electronic Security Perimeter and a Physical Security Perimeter as required. Finally, logs covering the entire period were available, and a review of the logs confirmed that no cybersecurity incidents had occurred. | Upon discovery, MRO_URE1 immediately corrected the alerting and monitoring functionality. Additionally, logs were reviewed to verify that no events occurred during the lapse in alerting. Lastly, the compliance readiness process has been updated to include a test verifying the functionality of alerting at the time of implementation. This should result in the immediate detection of any configuration errors before any lapse in alerting occurs. MRO verified that MRO_URE1 completed its mitigating activities.
2012-10-31 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2012010723 | CIP-004-3 | R4 | MRO_URE1 self-reported noncompliance with CIP-004-3 R4 because it failed to maintain its list of individuals authorized for unescorted physical and/or cyber access to Critical Cyber Assets (CCAs). Specifically, one employee was granted cyber access accidentally outside of the standard process, so the access was not properly documented in the list. The issue was identified during a quarterly review process and was mitigated within 55 days, outside the 7 calendar days of any change of personnel with access, as required by R4.1. The quarterly review encompassed all individuals with CCA access. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because the access granted to the employee was read-only, and was appropriate for the employee’s role. Additionally, the employee in question was already approved for other CCA access and had a proper personnel risk assessment and cybersecurity training as required by the Standards. | Upon discovery, the access approval was documented in the NERC CIP access management tool, which recorded the business need as determined by the designated approver and synched up the authorized and configured access lists. Because controls are already implemented for access management, the processes for obtaining access were not changed. Instead, additional reminders were sent to management via letter regarding following established procedures, and a quick reference card was distributed to all personnel responsible for NERC CIP access configuration. MRO verified that MRO_URE1 completed its mitigating activities.
2012-10-31 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2012010669 | CIP-005-1 | R1; R1.6 | NPCC_URE1 self-reported an issue with CIP-005-1 R1.6. Specifically, two servers that are Cyber Assets used to support systems within the Electronic Security Perimeter (ESP) were connected to a switch using a virtual LAN that was not documented as a non-critical Cyber Asset. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because BPS operations would not be impacted if the systems at issue sustained an outage. Additionally, the devices are non-critical Cyber Assets, and accordingly are afforded the protections of CIP-002 through CIP-009 applicable to non-critical Cyber Assets. Lastly, the undocumented switch was contained in the same Physical Security Perimeter (PSP). | NPCC_URE1 mitigated this issue by disconnecting the devices at issue and the undocumented switch and re-connecting it to switches that were documented. NPCC_URE1 reviewed the logs on the devices and found no evidence that there was any unauthorized access to the system via the undocumented switch.
2012-10-31 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 2 (NPCC_URE2) | NCRXXXXX | NPCC2012009847 | CIP-005-1 | R1.5 | During an on-site Compliance Audit, NPCC discovered that NPCC_URE2 had an issue with CIP-005-1 R1.5. Specifically, four NPCC_URE2 Cyber Assets that control or monitor access to the Electronic Security Perimeter (ESP) were not running anti-virus and anti-malware tools, as required by CIP-007-1 R4. NPCC_URE2 failed to submit a timely Technical Feasibility Exception (TFE) request for the four devices. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because NPCC_URE2 had existing compensating measures in place. Specifically, the Critical Cyber Assets (CCAs) within the ESP had mitigating measures in place to minimize the impact of a virus. Specifically, NPCC_URE2 utilizes a service contractor to monitor the ESP, and any intrusions or attempts to breach the ESP are immediately detected and reported to properly mitigate any risk. This is an open-ended TFE and the compensating measures have been in place since 2010. | This issue was mitigated through the TFE process. NPCC_URE2 filed the Part A TFE with NPCC. NPCC accepted the Part A TFE. NPCC completed and accepted the Part B TFE approval.
2012-10-31 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 2 (NPCC_URE2) | NCRXXXXX | NPCC2012009849 | CIP-007-1 | R4 | During an on-site Compliance Audit, NPCC discovered that NPCC_URE2 had an issue with CIP-007-1 R4. Specifically, three devices inside the Electronic Security Perimeter (ESP) were not running anti-virus and anti-malware tools, as required by the Standard. NPCC_URE2 failed to submit a timely Technical Feasibility Exception (TFE) request for the three Cyber Assets. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because NPCC_URE2 had existing compensating measures in place. Specifically, NPCC_URE2 had firewalls in place and the devices at issue did not have access to the Internet. These devices are all located within the NPCC_URE2 ESP. The devices are only connected through a VPN router. NPCC_URE2 utilizes a procedure that disables the VPN router when not needed to reduce the risk of intrusions. The VPN router is only enabled when updates are necessary. When the updates are completed, the VPN router is again disabled. This process is logged. This procedure was identified by the NPCC auditors as a Best Practice during the on-site CIP Audit. This is an open-ended TFE and the compensating measures have been in place since 2010. | This issue was mitigated through the TFE process. NPCC_URE2 filed the Part A TFE with NPCC. NPCC accepted the Part A TFE. NPCC completed and accepted the Part B TFE approval.
2012-10-31 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 2 (NPCC_URE2) | NCRXXXXX | NPCC2012009850 | CIP-007-1 | R5 | During an on-site Compliance Audit, NPCC discovered that NPCC_URE2 had an issue with CIP-007-1 R5. Specifically, three NPCC_URE2 devices inside the Electronic Security Perimeter (ESP) are not capable of technically enforcing strong passwords. NPCC_URE2 failed to submit a timely Technical Feasibility Exception (TFE) request for the three devices. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because NPCC_URE2 had existing compensating measures in place. NPCC_URE2 utilizes a procedural control for passwords for the devices at issue. The administrator for these devices ensures that strong passwords are used and that the password is changed annually or whenever there is a change in authorized personnel. The administrator is the person who sets the shared password for these devices, and changes the password when required. This is an open-ended TFE and the compensating measures have been in place since 2009. | This issue was mitigated through the TFE process. NPCC_URE2 filed the Part A TFE with NPCC. NPCC accepted the Part A TFE. NPCC completed and accepted the Part B TFE approval.
2012-10-31 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 2 (NPCC_URE2) | NCRXXXXX | NPCC2012010134 | CIP-006-3a | R1; R1.1; R1.2 | During an on-site Compliance Audit, NPCC discovered that NPCC_URE2 had an issue with CIP-006-3 R1. Specifically, NPCC_URE2's control room Physical Security Perimeter (PSP) had a dropped ceiling that did not have a solid wall extending up to the ceiling, as required by R1.1 and R1.2. NPCC_URE2 failed to submit a timely Technical Feasibility Exception (TFE) request for the PSP. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the control room was manned 24 hours a day, seven days a week. The control room also has an alarm system, physical access system, cameras and defense in depth, meaning that there are several security systems that monitor the PSP. Additionally, any visitors are escorted and signed in and out per NPCC_URE2's cybersecurity policy. This is an open-ended TFE and the compensating measures have been in place since 2009. | This issue was mitigated through the TFE process. NPCC_URE2 filed the Part A TFE with NPCC. NPCC accepted the Part A TFE. NPCC completed and accepted the Part B TFE approval.
2012-10-31 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 2 (NPCC_URE2) | NCRXXXXX | NPCC2012010135 | CIP-006-3a | R2 | During an on-site Compliance Audit, NPCC discovered that NPCC_URE2 had an issue with CIP-006-3 R2. Specifically, two NPCC_URE2 physical access control devices were not running anti-virus or anti-malware software, as required by CIP-007-3 R4.1. Specifically, certain parts of the devices do not support the installation of anti-virus software, as they do not contain an operating system with this capability. NPCC_URE2 failed to submit a timely Technical Feasibility Exception (TFE) request for the two devices. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the physical security systems at issue are not used to monitor or control Critical Cyber Assets and would have no impact on NPCC_URE2's Critical Cyber Assets if compromised. NPCC_URE2's Cyber Assets that authorize or log access to Physical Security Perimeters (PSPs) are afforded the protections specified in CIP-006-3a R2, with the exception of the parts of the devices described herein. These parts are located within the PSP. This is an open-ended TFE and the compensating measures have been in place since 2009. | This issue was mitigated through the TFE process. NPCC_URE2 filed the Part A TFE. NPCC accepted the Part A TFE. NPCC completed and accepted the Part B TFE approval.
2012-10-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2012010440 | CIP-006-3c | R8 | During a Compliance Audit, ReliabilityFirst discovered that RFC_URE1 had an issue with CIP-006-3c R8. RFC_URE1 produced an inspection report stating that it must replace a door contact pursuant to its maintenance and testing program for physical security systems. The contractor who could fix the door was onsite at RFC_URE1 that day, so RFC_URE1 requested the contractor to repair the door. As a result, RFC_URE1 repaired the door the same day it discovered the issue. RFC_URE1, however, did not create a formal work order for the repair, and therefore failed to retain the record for the maintenance, as required by CIP-006-3c R8.2. | ReliabilityFirst determined that this issue posed a minimal risk to the reliability of the bulk power system (BPS). The risk to the reliability of the BPS was mitigated because RFC_URE1 repaired the door contact the same day it discovered the issue and had just failed to document the maintenance work. The CIP-006 R8 issue discovered during the Audit began nine days prior to the discovery date. The problem with the door was that a contact was misaligned. The misaligned contact did not affect the magnetic lock on the door, so there was never unimpeded access. The door would only operate when an authorized individual swiped a badge. The bad contact only affected the transmission of the status of the door (“open” or “closed”) to the central monitoring system. The door in question is on a specific floor of RFC_URE1’s corporate headquarters. In order to access that door, there are two other sets of security protections. In order to gain unescorted access to the corporate headquarters an individual must pass through one of four turnstiles which are opened using a corporate ID card. Visitors must be escorted in order to gain access. Additionally, access to the entire floor is restricted by sliding glass doors on either end of the elevator bank access corridor. The remainder of the floor is only accessible to employees who have associated access privileges. Visitors must call someone and be met at one of the doors to gain access to the floor. The door in question resides behind both of these physical protections. | RFC_URE1 reinforced the requirement of documenting maintenance, with appropriate personnel including minor repairs completed when a technician is already on-site for other work. In addition, RFC_URE1 revised its maintenance and testing form to include two additional categories: "Follow Up/Date" and "Service Ticket Number" to document the work performed. Furthermore, RFC_URE1 now includes invoices documenting repairs in the maintenance and testing form.
2012-10-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2012010434 | CIP-005-3a | R5 | RFC_URE2 self-reported an issue with CIP-005-3a R5 to ReliabilityFirst. Typically, RFC_URE2’s electronic access logs are automatically transferred daily from routers to a central log repository. Two issues occurred that prevented logging from these routers. First, the routers ran out of virtual memory which caused subsequent log records to overwrite previous log records. Second, the vendor’s technical issue prevented the automatic backup and storage of the logs on the central log repository. As a result, a portion of the log data that includes logging for attempts at or actual unauthorized access for these routers were not captured in the central log repository for over four months. RFC_URE2 began employing an alternate source on for one router and, 22 days later, for the remaining two routers, which successfully captured and retained logs for these three routers. As a result, there was a net loss of logs of 55 days for two routers and 35 days for the remaining router. | ReliabilityFirst determined that this issue posed a minimal risk to the reliability of the bulk power system because the logging issue did not affect alerting for attempts at or actual unauthorized access as RFC_URE2's system issues alerts in real time. These alerts do not rely on the storage of log files in the central log repository. In addition, RFC_URE2 subsequently retrieved and retained log files resulting in the recovery of log files for one router and 22 days later for the other two routers. | RFC_URE2 committed to take certain actions to mitigate the issue. RFC_URE2 implemented an alternate logging source, which began capturing and retaining logs. In addition, RFC_URE2 ensured that the vendor resolved the technical issue on the centralized log repository.
2012-10-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC2012009866 | CIP-004-3 | R4 | RFC_URE3 self-reported an issue with CIP-004-3 R4. A RFC_URE3 contract security officer resigned from the RFC_URE3 contractor. RFC_URE3 previously granted the contract security officer authorized unescorted physical access to areas containing Critical Cyber Assets (CCAs). RFC_URE3, however, failed to update its list of personnel who have physical access to (CCAs) until about 5 months after the contract security officer resigned which was not within seven calendar days of this change in access rights of personnel, as required by CIP-004-3 R4.1. In addition, RFC_URE3 failed to disable the contract security officer’s physical access badge within seven calendar days, as required by CIP-004-3 R4.2. RFC_URE3 disabled the contract security officer’s physical access badge; however, the contract security officer still had the physical access badge when RFC_URE3 discovered the issue. 15 days after RFC_URE3 disabled the physical access badge, the contract security officer voluntarily surrendered the badge. | ReliabilityFirst determined that this issue posed a minimal risk to the reliability of the bulk power system because prior to the time period of the issue, the contract security officer had cybersecurity training and a valid personnel risk assessment, which included an extensive background check similar to that required for unescorted access to nuclear power plants, a driving record review and stringent fitness for duty testing. In addition, the contract security officer never had authorized cyber access to CCAs, and operations personnel occupy the areas to which the contract security officer had access 24 hours a day. As a result of the foregoing, it was less likely that the contract security officer could gain access unnoticed and cause harm to the integrity of the CCAs. Furthermore, the contract security officer did not physically access the areas containing CCAs during the time period of the issue. | RFC_URE3 committed to take certain actions to mitigate the issue. RFC_URE3 disabled the contract security officer’s physical access badge. In addition, RFC_URE3 established an internal process whereby the security contractor will communicate employee status changes to appropriate RFC_URE3 management personnel regarding security personnel that is distinct from the pre-existing weekly roster updates. Furthermore, the security contractor will follow up within 24 hours of that out-of-service effective date to verify that RFC_URE3 has removed access within 24 hours. If RFC_URE3 has not removed access, the system will send a second notification. In addition, RFC_URE3 began generating weekly automated emails that provide to its contractors and vendors lists of its employees who have authorized unescorted physical access to CCAs. The contractors and vendors are directed to review the lists to determine whether access is still required and to reply whether any require cancellation. If there is no reply during the same week, RFC_URE3 will cancel access for those individuals.
2012-10-31 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP2012009705 | CIP-007-1 | R5.3 | SPP RE_URE1 submitted two Self-Reports to SPP RE stating that it was noncompliant with CIP-007-1 R5.3.2 and R5.3.3. Because CIP-007-1 R5.3.2 and R5.3.3 are closely related, SPP RE consolidated the two Self-Reports into one Self-Report. Regarding R5.3.2, SPP RE_URE1 reported that during an internal compliance audit, SPP RE_URE1 identified 23 accounts with access to its Energy Management System (EMS) that had passwords that did not consist of a combination of the three required character types (alpha, numeric and "special" characters). The passwords did consist of at least seven characters, and contained alpha and numeric characters, but failed to include a “special” character, as prescribed by R5.3.2. Regarding R5.3.3, SPP RE_URE1 identified three devices that had not had their passwords changed annually. | SPP RE determined that the issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Although SPP RE_URE1 had accounts that did not fully conform to the CIP-007-1 R5.3.2 requirement, these accounts did conform to two out of the three criteria listed in the subrequirement. Furthermore, all of the accounts that were not compliant with CIP-007-1 R5.3 were under continuous monitoring via an automated event and monitoring solution that provided unauthorized access detection. There were no incidents or events of unauthorized access detected during SPP RE_URE1's period of noncompliance. | SPP RE_URE1 changed passwords on its EMS Critical Cyber Assets (CCAs), Protected Cyber Assets (PCAs), and electronic access control systems (EACSs) to meet the following requirements: 1) Length: Passwords shall be a minimum of 8 characters. 2) Complexity: Passwords shall consist of a combination of upper and lower alpha, numeric, and “special” characters. 3) Frequency: Passwords, at a minimum, shall be changed on an annual basis. SPP RE_URE1 also notified users of the requirement to select and use passwords that meet the complexity requirements as detailed in its passwords requirement document. Finally, SPP RE_URE1 changed passwords on every EMS CCA, PCA and EACS to comply with the CIP-007-1 R5.3 Requirements.
2012-10-31 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPPRE_URE2) | NCRXXXXX | SPP2012009924 | CIP-004-1 | R4.1 | During a CIP Compliance Audit of SPPRE_URE2, the SPP RE CIP Audit Team identified noncompliance with CIP-004-1 R4.1 related to the quarterly reviews of SPPRE_URE2's list of personnel with access to Critical Cyber Assets (CCAs). Specifically, the audit team determined that SPPRE_URE2 could not demonstrate that it had reviewed its lists of personnel with electronic access to CCAs on a quarterly basis during the audit period. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Although SPPRE_URE2 could not show that it had reviewed the list of personnel with electronic access to CCAs quarterly, it did demonstrate that it reviewed the list of personnel with physical access to CCAs quarterly, as required by this Standard. Furthermore, SPPRE_URE2 demonstrated that it had conducted an annual review of access privileges, including electronic access, to CCA information, as required by CIP-003-3 R5. Finally, SPPRE_URE2 has a small number of employees with electronic access, and a low employee turn-over rate. Accordingly, changes to these employees' electronic access privileges would have been noticed by SPPRE_URE2 IT staff, despite the lack of a quarterly review. | SPPRE_URE2 conducted quarterly reviews of electronic access rights, transferring the responsibility to perform these reviews to the CIP compliance specialist, who is knowledgeable about electronic access rights. Additionally, SPPRE_URE2 updated its list to more efficiently identify those individuals with electronic access.
2012-10-31 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPPRE_URE2) | NCRXXXXX | SPP2012009929 | CIP-006-1 | R1 | During a CIP Compliance Audit of SPPRE_URE2, the SPP RE CIP Audit Team identified SPPRE_URE2's noncompliance with CIP-006-1 R1. A SPPRE_URE2 employee inappropriately gave itself physical access to a Physical Security Perimeter (PSP), the control room (SPPRE_URE2's backup control center), without following the procedures established in the SPPRE_URE2 Physical Security Plan. SPPRE_URE2's Physical Security Plan requires employees to get permission from the appropriate manager or supervisor and to complete the authorized access procedures before being granted access. The employee accessed the control room PSP in order to perform testing of the security door contact. The PSP in which the employee granted itself access to was a recently re-designated PSP. The re-designation had split one PSP into two PSPs. The SPPRE_URE2 employee lacked permission to access the re-designated PSPs. However, prior to the re-designation, the SPPRE_URE2 employee did have access to the one PSP. The SPPRE_URE2 employee granted itself access at 12:23 p.m., and terminated access at 12:25 p.m., after testing the door devices. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Although the SPPRE_URE2 employee inappropriately gave itself physical access to the control room, the employee had access to the control room prior to its re-designation from one PSP, to two PSPs. Additionally, records show that the employee's access to the control room existed only for a total of two minutes for the purpose of testing the doors. The employee had the necessary training and Personnel Risk Assessment (PRA). | SPPRE_URE2 took disciplinary action against the SPPRE_URE2 employee and counseled the employee on the correct process to follow to gain access to PSPs. SPPRE_URE2 granted the employee authorized access to the control room PSP.
2012-10-31 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPPRE_URE2) | NCRXXXXX | SPP2012009931 | CIP-006-1 | R3 | During an SPP RE CIP Compliance Audit of SPPRE_URE2, the SPP RE CIP Audit Team discovered a remediated issue of CIP-006-3 R5. The Audit Team observed that SPPRE_URE2 had not implemented technical controls for monitoring physical access at an access point between two Physical Security Perimeters (PSP), SPPRE_URE2's control room and SPPRE_URE2's computer room. | SPP RE determined that the issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Although SPPRE_URE2 did not have monitoring measures in place for the access point between its control room and computer room, the access point did have a keyed lock securing SPPRE_URE2's control room from any entry from the computer room. The keyed lock at the access point did not secure SPPRE_URE2 computer room from entry from the control room. Individuals with approved access to SPPRE_URE2's control room also have approved access to the computer room. Besides having a physical access control for the access point between the two PSPs, SPPRE_URE2 also had security measures in place at the access point to the building that housed the two PSPs. The building housing the PSPs has security guards, a barbed-wire fence surrounding the building, two steel doors, which were alarmed and a magnetically locked access door. | SPPRE_URE2 combined the two PSPs thereby negating the need to monitor the door connecting them.
2012-10-31 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPPRE_URE2) | NCRXXXXX | SPP2012009932 | CIP-006-3c | R6 | During a CIP Compliance Audit of SPPRE_URE2, the SPP RE CIP Audit Team identified SPPRE_URE2's noncompliance with CIP-006-3c R6. Specifically, the Audit Team identified three instances in which SPPRE_URE2 did not adhere to its Physical Security Plan when logging the escorted physical access of three visitors to SPPRE_URE2's control room Physical Security Perimeter (PSP). This remediated issue involved one SPPRE_URE2 employee and two outside visitors. According to SPPRE_URE2's Physical Security Plan, visitors must fill out a visitor’s log in order to gain access to certain areas within SPPRE_URE2's facilities. The visitor logs identify the name of the visitor, the entry/exit date and time, and the name of the accompanying SPPRE_URE2 escort. In one instance, a SPPRE_URE2 employee visitor failed to record the PSP exit time, and in the second instance SPPRE_URE2 failed to record the PSP exit time of one outside visitor as well as the PSP exit time and name of the SPPRE_URE2 escort for another outside visitor. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Although SPPRE_URE2 did not follow its procedures by recording the times that the three individuals exited a SPPRE_URE2 PSP, all three individuals went through multiple layers of security to gain access to the PSP. The additional security measures included: a check-in with SPPRE_URE2 security, issuance of a visitor’s badge, and escorted access to enter the PSP. Additionally, the one SPPRE_URE2 employee that failed to record the SPPRE_URE2 PSP exit time, had been in the SPPRE_URE2 control center before, and had appropriately and completely filled out the visitor logs during those times. None of the outside visitors had the capability to enter the PSP without an escort. Finally, SPPRE_URE2's control room is manned 24/7 and has 24-hour visual security monitoring. | SPPRE_URE2 circulated a company-wide e-mail to all personnel reminding them of the need to follow the company procedures related to logging physical access to the PSPs. Furthermore, SPPRE_URE2 held training for employees regarding the procedures for entering and leaving its PSPs.
2012-10-31 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE201100242 | CIP-005-1 | R3.2 | TRE_URE1 self-reported that it failed to submit a technical feasibility exception (TFE) on a device CIP-005-1 R3.2 requirements. The device is not a Critical Cyber Assets (CCA) nor is it essential to the operation of any Cyber Assets. Previously, TRE_URE1 had filed a TFE for this device but for a different Standard. Therefore, Texas RE determined that the device is not a new device that was overlooked. The oversight occurred when filling out the TFEs because TRE_URE1 failed to file a TFE for this Standard. The mitigating measures put in place in accordance with the previously filed TFE for this device served as a mitigating measure during the period of this issue. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the device is not a CCA nor is it essential to the operation of any Cyber Assets. Further, Texas RE determined that the risk was mitigated by the fact that during the pendency of this issue, there were no means to gain cyber access this device. Additionally, this device had been included in a previously filed TFE and all mitigating measures put in place in accordance with the previous TFE were also in place during the pendency of this issue. Furthermore, the device is always protected by the surrounding protective systems on the PSPs and ESPs. This device is inside an Electronic Security Perimeter (ESP) and Physical Security Perimeter (PSP). | Because the device was covered by a previous TFE, the mitigation measures put in place for the previous TFE also serve to mitigate the risk of this instance of noncompliance.
2012-10-31 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE201100269 | CIP-005-1 | R3.2 | TRE_URE1 self-reported that it failed to submit a technical feasibility exception (TFE) on a device. The device is not a Critical Cyber Assets (CCA) nor is it essential to the operation of any Cyber Assets. Previously, TRE_URE1 had filed a TFE for this device but for a different Standard and Texas RE approved the TFE. Therefore, Texas RE determined that the device is not a new device that was overlooked. The oversight occurred when filling out the TFEs because TRE_URE1 failed to file a TFE for this Standard. The mitigating measures put in place in accordance with the previously filed TFE for this device served as a mitigating measure during the period of this issue. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the device is not a CCA nor is it essential to the operation of any Cyber Assets. Further, Texas RE determined that the risk was mitigated by the fact that during the pendency of this issue, there were no means to gain cyber access this device. Additionally, this device had been included in a previously filed TFE and all mitigating measures put in place in accordance with the previous TFE were also in place during the pendency of this issue. Furthermore, the device is always protected by the surrounding protective systems on the PSPs and ESPs. This device is inside an ESP and PSP. | Because the device was covered by a previous TFE, the mitigation measures put in place for the previous TFE also serve to mitigate the risk of this instance of noncompliance.
2012-10-31 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE2012009765 | CIP-004-2 | R2 | During an Audit it was discovered that TRE_URE1 did not update its cyber security training program at least annually. TRE_URE1's annual training stated that updating of its cyber security incident response plan as per CIP 008-1 R1.4 is required within ninety calendar days of any changes made. However, when Version 2 of the CIP Standards became effective on April 1, 2010, TRE_URE1 failed to update its annual training materials that reference CIP 008-1 R1.4. TRE_URE1 failed to provide a reference to the new Version of the Standard- CIP-008-2 R1.4, which requires any changes to be made within thirty calendar days instead of 90 calendar days. As a result, TRE_URE1 included incorrect information into its training materials. This issue existed from April 1, 2010 to January 11, 2012. Furthermore, Texas RE found an additional remediated issue during the Compliance Audit. Seven TRE_URE1 contractors with access to Critical Cyber Assets (CCAs) were not trained as required by CIP-004-2 R2.3. However, TRE_URE1 failed to train them by that date and did not revoke their access until four days after training should have been completed. As a result, Texas RE determined that TRE_URE1 had a remediated issue with CIP-004-2 R2.3. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Although TRE_URE1 employees were being trained with training material that did not fully reflect a change in the Reliability Standards Versions, the employees received a timely training on all other aspects of the Standard. Also, all trained employees at issue had Personnel Risk Assessment (PRAs) performed and were knowledgeable about TRE_URE1's CCAs' security practices. For sub requirements R2.3, the contractors having access to these CCAs had previously had cyber security training, and their PRAs were current. Therefore, Texas RE determined that these contractors were familiar with TRE_URE1's security practices. Finally, TRE_URE1 was noncompliant with R2.3 for a period of four days, which reduced the risk to the BPS to minimal. | To mitigate this issue TRE_URE1 has provided an updated training program document, which reflects the change from Version 1 to Version 2 of this CIP Standard. TRE_URE1 also trained the contractors at issue.
2012-10-31 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE2012009766 | CIP-002-1 | R3 | During a Compliance Audit Texas RE discovered that TRE_URE1 did not develop a list of Critical Cyber Assets (CCAs) using the list of Critical Assets determined through an application of TRE_URE1's risk-based assessment methodology (RBAM). Specifically, Texas RE determined that one device was incorrectly excluded from the list of CCAs because TRE_URE1 failed to follow its RBAM for developing a list of CCAs. An inaccurate filtering criteria was assigned to the device that caused it to be marked as not being a CCA. However, TRE_URE1 was aware that the device was a CCA and afforded all the security measures required by the Reliability Standards to it. No other instances of incorrect filtering were discovered during the Compliance Audit. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The CCA at issue was located inside a Physical Security Perimeter (PSP), was monitored by an electronic entrance, and was firewalled. In addition, the CCA was subject to staff oversight at TRE_URE1's Electronic Security Perimeters (ESPs) and the PSP, and it was accessible only to designated staff members with Personnel Risk Assessments (PRAs). Documents show that the CCA at issue was considered as part of the CCA list. The security of the CCA was not compromised during the three-month period of TRE_URE1's noncompliance. | To mitigate this issue TRE_URE1 has provided a CCA list document, showing that marketing PC1 been documented as a CCA. The document was signed by the Senior Manager.
2012-10-31 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE2012009773 | CIP-008-2 | R1.4 | During a Compliance Audit, Texas RE discovered that TRE_URE1's Cyber Security Incident response plan (Versions 2009 and 2011) stated that changes to the plan are to be incorporated into the plan within 90 days, not within 30 days, as required by Version 2 of this Standard -CIP-008-2 R1.4. Version 1 of this Standard required that any change be incorporated within 90 days. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Texas RE determined that this remediated issue is documentation- related and administrative in nature because there were no changes to the plan during the period of noncompliance. Further, any changes to the plan would still have been incorporated within 90 days, thereby further reducing the risk to the BPS. | TRE_URE1 updated its Cyber Security Incident response plan, which is part of its training program, to require that any changes are incorporated within 30 days.
2012-10-31 | TRE_URE1liability Entity (TRE_URE1) | Unidentified Registered Entity 2 (TRE_URE2) | NCRXXXXX | TRE201100155 | CIP-006-1 | R1.8 | TRE_URE2 self-reported noncompliance with CIP-006-1 R1.8. As part of the annual cyber vulnerability assessment (CVA), TRE_URE2 identified noncompliance. TRE_URE1 determined that the system was not afforded the protective measured required by this Standards, a process to grant access was not used, not all accounts have been changed because the vendor has indicated that there may be negative impacts, the documented process for granting access to the device and associated hardware was not used to grant access, shared accounts that did not meet the password complexity and annual change frequency requirement, physical security monitoring alarm processes were not correctly followed by one employee per documented procedures, the devices were configured to enable all users with a network account to log on locally, employees were given system access to the badging servers prior to completion of background check, and responsibility for patch management for the badging servers was not defined or automated, and patches were not installed. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). TRE_URE2 badging servers are completely separate from TRE_URE2’s Supervisory Control and Data Acquisition (SCADA) and Distributed Control Systems (DCS). Exposure was limited by the fact that the devices were in Physical Security Perimeters (PSPs) with controlled access, essentially limiting access to only people with the appropriate Personnel Risk Assessment (PRAs). TRE_URE1 determined that in the worst case scenario would result in TRE_URE2 PSP doors unlocking. Even if this occurred, TRE_URE2 facilities are protected 24/7. Also, the device quadruple (4X) is redundant. TRE_URE2's assessed the other security layers and determined that no actual intrusion or criminal activity occurred as a result of this failure to follow procedure. The servers had up to date monitored antivirus. | TRE_URE2 stated that the following mitigation activities have been completed: 1) CIP-005-3 R2: This was corrected and validated by TRE_URE2's gap analysis team. Access authorization documentation and procedures have been reviewed. 2) CIP-007-3 R5.1: Local logon service has been reduced to allow only personnel with a business need to logon to the system. 3) CIP-007-3 R3: device was updated with current security patches and verified by a vulnerability assessment scanning tool. Responsibility for patch installation has been clearly defined. 4) CIP-007-3 R5, R5.2, R5.3: The process has been documented and implemented. As a future improvement, all access control and verification will be performed with a single access control tool. Not all of the accounts have been changed because the vendor has indicated that there may be negative impacts. TRE_URE2 worked with the vendor to resolve this issue. 5) CIP-006-3 R5: The employee received corrective training to ensure documented procedures will be followed, along with monitoring of compliance for this specific physical security monitoring function.
2012-10-31 | TRE_URE1liability Entity (TRE_URE1) | Unidentified Registered Entity 2 (TRE_URE2) | NCRXXXXX | TRE201100400 | CIP-005-1 | R1.5 | TRE_URE2 self-reported noncompliance with CIP-005-1 R1.5 for a failure to afford the protective measures specified in Standards CIP-007 R1 and R3 through R9. TRE_URE2 utilizes several applications and servers to administer firewalls, to provide logs, and to produce email alerts and reports for malicious activities for its Electronic Security Perimeter (ESP). As part of the CIP gap analysis, TRE_URE2 identified and self-reported noncompliance with CIP-005-1 R1.5 because it failed to afford all of the protective measures required by this Standard for two applications and two servers. The servers are physically located inside the PSP, but outside the Electronic Security Perimeter (ESP). For an application, TRE_URE2 failed to implement an acceptable use banner on one instance, the application did not log user activity, server access was not reviewed on annual basis, and three shared accounts did not identify and document individual users for the servers. For another application, TRE_URE2 identified three shared accounts with default passwords that allow access, and two of the accounts did not meet the password complexity requirement. TRE_URE2 failed to implement a patch management process for other servers. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because: 1) Remote access to the servers at issue is limited. The default account can only be accessed locally, within a protected physical area. Individuals that can logon to the microcontrollers have a current and valid Personnel Risk Assessment (PRA) and cyber security training. Interactive login was limited to specific workstations with static IP addresses. These workstations were assigned to employees who already had authorized access, and who had PRAs and had completed cyber security training. 2) The systems at issue are not directly accessible from the Internet, reside in a PSP with limited access, are physically and electronically segregated from TRE_URE2's Supervisory Control and Data Acquisition (SCADA) and Distributed Control Systems (DCS), and run anti-virus scans. No virus detections have occurred during the pendency of this remediated issue. | TRE_URE2 completed all mitigating activities related to this issue, including the following measures: 1) Acceptable use banners on the application and servers were installed; 2) Logging capability for the application and servers were enabled; 3) TRE_URE2 expanded its existing cyber security procedures; 4) The passwords complexities were identified on the accounts at issue; and 5) System patches and security updates were completed and verified by a vulnerability assessment scan.
2012-10-31 | TRE_URE1liability Entity (TRE_URE1) | Unidentified Registered Entity 2 (TRE_URE2) | NCRXXXXX | TRE2012009733 | CIP-007-1 | R5.2 | TRE_URE2 self-reported an issue with CIP-007-1 R5.2 for a failure to implement a policy to minimize and manage the scope and acceptable use of administrator, shared, and other generic account privileges including factor default accounts. TRE_URE2 utilizes its Energy Management System (EMS) to monitor and control its Transmission Operator (TOP) area. The EMS has been identified as a Critical Cyber Asset (CCA) per TRE_URE2's methodology. As part of its CIP gap analysis, TRE_URE2 self-reported noncompliance with CIP-007-1 R5.2. For three shared accounts, TRE_URE2 could not demonstrate compliance, as specified in Requirement 5, with the documentation procedures required by its account management program. The policy requires identification of all computers with shared accounts. In addition, TRE_URE2 could not identify those individuals with access to one of the three shared accounts. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because: 1) The EMS system is located within the Electronic Security Perimeter (ESP) and Physical Security Perimeter (PSP). The system is only accessible to personnel with approved unescorted access to the Critical Cyber Asset. 2) TRE_URE2 demonstrated its password policy was compliant with the requirements of CIP-007-1 R5.3. TRE_URE2 implemented its policy for all three shared accounts . | The following mitigation activities have been completed: TRE_URE2 documented the computers with shared access implementing their policy to minimize and manage the use of shared account privileges.
2012-10-31 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 3 (TRE_URE3) | NCRXXXXX | TRE2012010289 | CIP-003-1 | R1.1 | During a Compliance Audit Texas RE found that TRE_URE3 was noncompliant with CIP-003-1 R1 because its cyber security policy failed to address the requirements in Standards CIP-002 through CIP-009. Texas RE determined that TRE_URE3 2009 and 2010 versions of its cyber security policy did not address the requirements in Standards CIP-002 through CIP-009, but its 2011 Version did address these Requirements. Specifically, TRE_URE3's policy presented failed to adequately address the following two requirements: CIP-007-2 R5 and CIP-003-2 R5. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). TRE_URE3 was able to provide documentation on all other aspects of their NERC Cyber Security Policy document for 2010 and 2009 and the updated version for 2011 addressed the requirements of this Standard. Texas RE determined that the risk was mitigated by the fact that TRE_URE3 had a policy prior to the mandatory compliance date. TRE_URE3's Cyber Security Plan has been in place for years, annually reviewed, updated according to TRE_URE3's' internal document control procedures, and adequately addressed the vast majority of the requirements in Standards CIP-002-2 thorough CIP-009-2. TRE_URE3's policies did not contain low-level, specific details and requirements related to the implementation of the policy. However, these details were contained in other processes and procedures that supported compliance with the security policy | The updated policy addresses each applicable CIP standard and requirement. Under each requirement there is a brief description of how TRE_URE3 meets that requirement. The updated policy mitigates this remediated issue.
2012-10-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2012010304 | CIP-007-1 | R4 | WECC_URE1, as a Balancing Authority, Generator Operator, Generator Owner, Load Serving Entity, Transmission Operator, Transmission Owner, and Transmission Service Provider, self-reported an issue with of CIP-007-1 R4. A WECC Subject Matter Expert (SME) contacted WECC_URE1 to discuss its Self-Report. According to the WECC SME, WECC_URE1 stated that for five devices it failed to use anti-virus software and other malicious software prevention tools. WECC_URE1 also stated that it is technically infeasible to use anti-virus or anti-malware software on these devices and intended to file a Technical Feasibility Exception (TFE). The WECC SME concluded that WECC_URE1 had an issue with CIP-007-1 R4 and referred the matter to Enforcement. Enforcement determined that WECC_URE1 had an issue with CIP-007-1 R4 because it neither installed anti-virus or anti-malware software on the CCAs described above, nor did WECC_URE1 file TFEs for the devices involved. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because The CCAs are devices used as a communication link for managing serially connected devices. As compensating measures, the devices are located in an Electronic Security Perimeter and have technical and procedural mechanisms for control of electronic access at all access points. WECC_URE1 enabled only those ports and services necessary at the access points and required username and passwords to access the devices. Also, all devices are located within a Physical Security Perimeter with procedural controls to manage physical access, including 24/7 logging and monitoring of physical access. Additionally, if the devices were to lose connectivity, alarms alert staff. WECC_URE1 filed TFEs for the devices because it was technically infeasible to install anti-virus and anti-malware software on the devices. WECC approved the TFEs. | WECC_URE1 completed mitigation of this issue.
2012-10-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2012010965 | CIP-006-3c | R2.2 | WECC_URE2, as a Balancing Authority, Generator Operator, Load Serving Entity, Transmission Operator, Transmission Owner, and Transmission Service Provider, self-reported an issue with CIP-006-3c R2.2. WECC_URE2 reported that it failed to file Technical Feasibility Exceptions (TFE) for two Critical Cyber Assets (CCAs) that authorize and/or log physical access to a Physical Security Perimeter (PSP). WECC Subject Matter Experts (SMEs) reviewed WECC_URE2’s Self-Report and TFE requests. SMEs determined it is technically infeasible for WECC_URE2 to install anti-virus software on the two devices. WECC Enforcement reviewed WECC_URE2’s Self-Report, the SMEs’ findings, and TFE approvals and determined that WECC_URE2 failed to submit a TFE as required under CIP-007-3 R4. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because WECC_URE2 had compensating measures in place to secure the devices against misuse or malicious attack. CIP-006-3 R2.2 requires entities to afford these devices protections specified in twenty-four Standard Requirements. In this case, WECC_URE2 failed to afford two devices one protection specified in CIP-007-3 R4. Specifically, WECC_URE2 failed to file TFEs for two devices on which it was technically infeasible to implement anti-virus software. WECC_URE2 secured both devices within an Electronic Security Perimeter (ESP). Electronic access was logged and monitored. Individuals with electronic access completed Personnel Risk Assessments (PRAs) and cyber security training. WECC_URE2 controlled access to the ESP with restricted user accounts, passwords, intrusion detection, and alarms. WECC_URE2 installed alarms to alert personnel of unauthorized physical access to the Physical Security Perimeter. WECC_URE2 secured the devices within a facility to which access was controlled and monitored. Individuals with physical access to the devices completed PRAs. WECC_URE2 enabled only necessary ports and services on both devices. | WECC_URE2 completed mitigation of this issue.
2012-10-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2012010468 | CIP-002-3 | R1 | During a compliance audit WECC determined that WECC_URE3 had an issue with CIP-002-3 R1. WECC discovered that WECC_URE3 implemented a revised version of its risk-based assessment methodology (RBAM). Although the document contained procedures and evaluation criteria, it failed to contain a risk-based assessment component. The WECC Audit Team referred its finding to the WECC Enforcement (Enforcement). Enforcement reviewed the Audit Team’s findings and determined that WECC_URE3 had an issue with CIP-002-3 R1, because it failed to identify and document an RBAM to identify its Critical Assets (CAs) and Critical Cyber Assets (CCAs). | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because WECC_URE3 does not have CAs and does not have CCAs. As compensating measures, WECC_URE3’s previous applications of its RBAMs generated null lists of CAs and CCAs. The WECC Audit Team determined that the existing null lists were accurate. | WECC_URE3 completed mitigation of the issue. WECC_URE3 proposed to revise its RBAM to document the risk-based component in detail. WECC_URE3 evaluated its Cyber Assets through an application of the updated RBAM to determine WECC_URE3’s CAs. This process yielded a null set of Critical Assets for WECC_URE3.
2012-10-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC2012010763 | CIP-003-1 | R1 | WECC_URE4 self-certified an issue with CIP-003-1 R1.3. A WECC Subject Matter Expert (SME) discussed with WECC_URE4 its self-certification. WECC_URE4 stated that it did not annually review its entire cyber security policy in the calendar year. Specifically, WECC_URE4 did not review cyber security policies that were outdated and not used by WECC_URE4. The WECC SME concluded that WECC_URE4 had an issue with CIP-003-1 R1.3 and referred the matter to WECC Enforcement. WECC Enforcement determined that WECC_URE4 had an issue with CIP-003-1 R1.3 because it did not perform a complete annual review of its cyber security policy for the calendar year. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because the cyber security policies were outdated and not used by WECC_URE4. As compensating measures, WECC_URE4 stated that it did annual reviews and approved the current policies in use. WECC_URE4 did a full review of the cyber security policy in other calendar years. | WECC_URE4 completed mitigation of this issue. WECC_URE4 reviewed its cyber security policy in calendar year and removed the outdated items.
2012-10-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC2012010765 | CIP-006-3c | R1 | WECC_URE4 self-certified an issue with CIP-006-3c R1. A WECC SME contacted WECC_URE4 to discuss its self-certification. WECC_URE4 stated that one of its employees gained access to one of its Physical Security Perimeters (PSP) without having authorized access to the PSP. The employee involved accessed the PSP by walking through a door opened by another employee who had authorized access to the PSP. After the employee involved gained access to the PSP, alarms activated and the employee contacted WECC_URE4’s security guards from a phone located next to the PSP door. Security instructed the employee to leave the PSP, which the employee did. The employee was inside the PSP for approximately one minute and did not access any Critical Cyber Assets (CCAs). The WECC SME concluded that WECC_URE4 had an issue with CIP-006-3c R1 and referred the matter to WECC Enforcement. WECC Enforcement reviewed the WECC SME’s findings and the WECC_URE4 self-certification. Enforcement determined that WECC_URE4 had an issue with CIP-006-3c R1. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because the employees immediately contacted WECC_URE4’s security guards and left the PSP without accessing any CCAs. As compensating measures, WECC_URE4 monitored the PSP 24 hours per day and each PSP access point has an alarm to alert of unauthorized physical access. In addition, WECC_URE4 staffs security at the facility 24/7. WECC_URE4’s procedures for monitoring for unauthorized access proved effective as an alarm sounded, the employee immediately contacted WECC_URE4 security, and security instructed the employee to leave the PSP. | WECC_URE4 completed mitigation of this issue. WECC_URE4 remediated this issue when the employee who gained unauthorized access to the PSP left the PSP. WECC_URE4 trained personnel to instruct individuals who enter a WECC_URE4 PSP without an escort to immediately leave the PSP
2012-10-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 5 (WECC_URE5) | NCRXXXXX | WECC2012010361 | CIP-004-3 | R3 | WECC_URE5 self-reported a an issue with CIP-004-3 R3. According to the Self-Report, one of WECC_URE5 employees had physical access to the a WECC_URE5 Physical Security Perimeter (PSP) for a period of 43 days after his personnel risk assessment (PRA) had expired. WECC determined that WECC_URE5 had an issue of CIP-004-3 R3 for failing to have an updated PRA for one of its employees. | WECC determined that the issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because all Critical Cyber Assets (CCAs) reside within an identified PSP and Electronic Security Perimeter. Therefore, the CCAs were monitored and afforded the protections of CIP-005 and CIP-006. In addition, the employee involved had CIP-004 R2 training and is in good standing with WECC_URE5. | WECC_URE5 submitted a mitigation plan to address this issue. WECC approved the mitigation plan and certified its completion.
2012-09-28 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2011008471 | CIP-006-1 | R1; R1.1 | FRCC_URE1 self-reported an issue with CIP-006-1 R1. Specifically, during an internal inspection of the Physical Security Perimeters (PSPs) at the primary energy control center (ECC) and a generation site, it was discovered that there was a gap in the existing six-wall border for two PSPs. One of the gaps was at the primary ECC and the other was at a generation site. Specifically, the gap at the generating plant was at a height of 12 feet and the opening was two feet tall and 8 feet wide. This gap was obstructed by insulation and other construction material. The gap at the ECC was at height of 15 feet and the opening was two feet tall and 10 feet wide, but was behind the reception area in the visitor's lobby of the ECC. The visitor's lobby is staffed by a receptionist during the normal working hours and the entrance door is locked outside of normal working hours. The front entrance is also monitored with a video camera monitoring device. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because both of the facilities are restricted access. Although the PSP did not have a completely enclosed six-wall border, the openings were not visible or identifiable. There was no easy access to the openings and crawl space was limited by sufficient obstructions. Both of the facilities maintained proper monitoring and security controls for all outside access to the facility and only trusted and verified visitors are allowed on the premises. | To mitigate this issue, FRCC_URE1 immediately restricted access to the subject PSP by implementing a new temporary access procedure that included camera monitoring and posting of guards. FRCC_URE1 then extended the primary ECC PSP and added plywood restrictions at the generating plant.
2012-09-28 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2011008473 | CIP-007-2a | R6 | FRCC_URE1 self-reported an issue with CIP-007-2a R6. Specifically, a distributed control system (DCS) human machine interface (HMI) device within FRCC_URE1's generation site was being monitored by the security event monitoring system, but due to a communications failure, twenty-four hour a day, seven day a week (24/7) monitoring was lost. This condition existed for a period of approximately 45 days. The communication error was caused by an error in the internal clock of the device that expired the security event monitoring system account prematurely. For the duration of this issue, alarming was only available for communication failure and intrusion detection system alerts. The device at issue is a computer workstation used for chemistry control and monitoring of the water pH level in the boiler. The device is mostly active during start-up and otherwise is used mostly for periodic monitoring. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the device was within a secured Physical Security Perimeter (PSP) and was not accessible remotely from outside the Electronic Security Perimeter (ESP). Even though cybersecurity event logs were not stored on the central log monitoring systems, additional logs were available on the local device to limit or analyze any additional risk that may have resulted from unauthorized access. FRCC_URE1 also maintained a network intrusion detection system to monitor the complete network and any unauthorized access. No unauthorized access was detected for the duration of the issue. Although FRCC_URE1 has one prior violation and one prior remediated issue with this Standard, the instant remediated issue nonetheless does not represent recurring conduct by the registered entity. The prior violation for this requirement resulted from hardware failure of the log collector device and was promptly corrected by FRCC_URE1 after replacing the faulty device. The prior remediated issue was the result of late-filed Technical Feasibility Exceptions by FRCC_URE1, and is therefore not related to the instant issue. | To mitigate this issue, FRCC_URE1 re-established communication, set up a centralized time server and created a process for network devices which point to that machine to capture time. FRCC_URE1 also implemented automated rules to send an alert if a device that is being monitored by the access monitoring system does not communicate with the access monitoring system.
2012-09-28 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2011008536 | CIP-007-1 | R5; R5.1 | FRCC_URE1 self-reported an issue with CIP-007-1 R5. Specifically, for five of its Cyber Assets, FRCC_URE1 did not ensure that individual and shared system accounts and authorized access permissions were consistent with the concept of “need to know” with respect to work functions performed, as required by R5.1. FRCC_URE1 also did not ensure that user accounts for these five systems were implemented as approved by the designated personnel, as documented in CIP-003-3 R5. These systems had individual and shared accounts but were pre-set to log in using a pre-configured account, allowing shared access to all users who had physical access to the system, instead of individual user access as required by the "need-to-know" concept. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the devices were within a secured Physical Security Perimeter (PSP) and were not accessible remotely from outside the Electronic Security Perimeter (ESP). All five systems at issue had user accounts and associated passwords configured as required by the CIP Standards, but allowing pre-configured auto log-in could have allowed an unauthorized person to use unassigned privileges. However, the risk in this case was mitigated by the fact that only the five authorized personnel (with access to the subject shared account) had access to the PSP where the systems were located. Although FRCC_URE1 has three prior violations and one prior remediated issue with this Standard, the instant issue nonetheless does not represent a failure to mitigate a prior violation. One of FRCC_URE1's prior CIP-007 R5 violations and the prior issue involved FRCC_URE1's failure to file timely Technical Feasibility Exceptions, and are therefore unrelated to the instant issue. FRCC_URE1's second prior violation involved FRCC_URE1's failure to change default settings on access control and monitoring equipment. FRCC_URE1's third prior violation resulted from lack of documentation of shared accounts for certain Cyber Assets, but FRCC distinguishes this from the instant issue, which resulted from erroneous implementation and failed controls unrelated to the previous violation. | To mitigate this issue, FRCC_URE1 created a shared account for two of the systems that only allows personnel with account credentials to access the process network. On the other three systems, FRCC_URE1 shut down the automated default log-in and required access to be granted as needed to perform job duties.
2012-09-28 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2011008522 | CIP-005-1 | R3 | FRCC_URE1 self-reported an issue with CIP-005-1 R3. Specifically, FRCC_URE1 failed to implement security monitoring processes to detect and alert for all actual unauthorized access into the Electronic Security Perimeters (ESPs) at one of its generation Critical Assets. FRCC_URE1 configured two access point devices to log traffic, including drops and denies, but failed to configure the access points to log all accepts. As a result, the logs were insufficient to demonstrate all actual unauthorized access at the two access points. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the access points were correctly configured for logging and alerting all denies and drops, limiting the risk of unauthorized access. Although the access points were not configured to log successful log-ins, strong two-factor authentication was configured for all remote interactive access. Further, FRCC_URE1 utilized intrusion detection systems on all its perimeter devices and inside network traffic, limiting any external exploit. | To mitigate this issue, FRCC_URE1 corrected its access point entries to capture logs of all incoming requests. Previously these devices were configured to log failed and unsuccessful requests but not the successful requests. Further, FRCC_URE1 updated its policy and procedure for any new device to require logging of all traffic including accepts, drops, and denies.
2012-09-28 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO201100376 | CIP-004-1 | R2 | During a Spot Check, MRO discovered that MRO_URE1 failed to review its cybersecurity training program annually. Specifically, MRO_URE1 failed to review training program material used to train third-party contractors and vendors that had access to its energy management system. MRO_URE1 relied on its vendors and contractors to train their own employees as required per a written agreement between the parties. However, MRO_URE1 did not review the training material provided to those vendors and contractor employees. | This issue posed a minimal risk and not a serious or substantial risk to the reliability of the bulk power system (BPS) because all of MRO_URE1's employees and contractor's received cybersecurity training within 90 days of being granted access. Additionally, although MRO_URE1 failed to review the training provided by its vendors and contractors annually, MRO_URE1 had a written agreement with its vendors and contractors which required them to provide training, and MRO_URE1 determined that the training program provided by the vendors and contractors met the requirements set forth in CIP-004-1 R2. | MRO_URE1 now collects annual training content from the vendors and contractors and reviews it annually, to ensure alignment with the required components and corporate policies. MRO verified that MRO_URE1 completed its mitigating activities.
2012-09-28 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 2 (MRO_URE2) | NCRXXXXX | MRO201100373 | CIP-007-1 | R5; R5.1.2 | MRO_URE2 self-reported noncompliance with CIP-007-1 R5 because it failed to establish methods, processes, and procedures that generate logs of sufficient detail to create historical audit trails of individual user account access activity for a minimum of ninety days for some Critical Cyber Assets. Specifically, access activity event logs were not kept on Front End Processing (FEP) equipment used in controlling bulk power system (BPS) remote terminal units. Logging was not possible because: (1) FEP configuration for log events did not include user access activity events and was not configured with clock source or timestamp logs; (2) hardware was unable to support the operating system version that performs logging of user access activity; and (3) the electric SCADA application was unable to support current operating system features to perform logging of user access activity through remote authentication via the access control system server. The issue was resolved with a system upgrade. | This issue posed a minimal risk and not a serious or substantial risk to the reliability of the BPS because less than 6% of MRO_URE2's FEP devices were incapable of generating logs, and these FEPs do not control major BPS equipment and are mainly used for distribution breakers, voltage regulators and capacitors. In addition, all communications from the FEPs to the field is done through serial communications. Also, the devices without configured logging were within an Electronic Security Perimeter and a Physical Security Perimeter with documented firewall rules and implemented network traffic monitoring systems. | MRO_URE2 performed the following mitigating actions: (1) researched operating system versions available on existing hardware to try to find one that will run with the current memory and provide features that perform logging of user access activity; (2) configured and tested remote authentication via the access control server to try to capture user access activity events in the log without breaking the SCADA application functionality; and (3) performed a full system upgrade and removed the equipment from the NERC CIP inventory. The upgrade included a complete hardware and software replacement and the configuration of necessary logging controls. MRO_URE2verified that MRO_URE2 completed its mitigating activities.
2012-09-28 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 2 (MRO_URE2) | NCRXXXXX | MRO201100382 | CIP-004-1 | R2 | During a Spot Check, MRO_URE2discovered that MRO_URE2 failed to review its cybersecurity training program annually. Specifically, MRO_URE2 failed to review training program material used to train third-party contractors and vendors that had access to its energy management system. MRO_URE2 relied on its vendors and contractors to provide training to their employees as required per a written agreement between the parties. However, MRO_URE2 did not review the training material provided to those vendors and contractor employees. | This issue posed a minimal risk and not a serious or substantial risk to the reliability of the bulk power system (BPS) because all of MRO_URE2's employees and contractor's received cybersecurity training within 90 days of being granted access. Additionally, although MRO_URE2 failed to review the training provided by its vendors and contractors annually, MRO_URE2 had a written agreement with its vendors and contractors which required them to provide training, and MRO_URE2determined that the training program provided by the vendors and contractors complied with the requirements set forth in CIP-004-1 R2. | MRO_URE2 now collects annual training content from the vendors and contractors and reviews it annually, to ensure alignment with the required components and corporate policies. MRO_URE2verified that MRO_URE2 completed its mitigating activities.
2012-09-28 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 3 (MRO_URE3) | NCRXXXXX | MRO201100313 | CIP-006-1 | R6; R6.1 | During a regularly scheduled Compliance Audit, MRO discovered that MRO_URE3 failed to demonstrate that all physical security mechanisms had been tested on a cycle no longer than three years. Although MRO_URE3 conducted comprehensive testing of access and monitoring controls two times in 2010, it did not conduct any testing prior to those dates. Two of the card readers were installed or reconfigured more than three years prior to the 2010 testing. MRO_URE3 failed to test 46% of its access points within the three-year cycle. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The access points that were not tested until the first instance in 2010 were access points to the dispatch room, which is staffed with personnel 24 hours per day, seven days per week. Additionally, MRO_URE3's physical access control system logs demonstrated that the access points were working throughout the duration of the compliance issue. Finally, MRO_URE3 tested all of its access points at least annually between 2010 and 2012. | MRO_URE3 completed testing and maintenance of all physical security mechanisms. MRO verified that MRO_URE3 completed its mitigating activities.
2012-09-28 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2012009157 | CIP-007-1 | R4.1 | During an on-site Compliance Audit, NPCC discovered that NPCC_URE1 had an issue with CIP-007-1 R4.1. During the course of fieldwork and in reviewing various NPCC_URE1 network diagrams, NPCC discovered that eight devices in total residing at four different substations were contained within the Electronic Security Perimeter (ESP) and not equipped with anti-virus and malware prevention tools. The eight devices at issue do not run on an operating system which supports or allows the installation of anti-virus and malware prevention tools, but NPCC_URE1 neglected to file a Technical Feasibility Exception (TFE) request with NPCC. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because NPCC_URE1's procedure limited employee electronic access. Additionally, NPCC_URE1 has, since June 30, 2009, had protections in place for assets inside the ESP, such as firewall protection, device authentication, and network security monitoring. This is an open-ended TFE because the hardened operating system in question does not support third-party software. | This issue was mitigated through the TFE process. NPCC_URE1 filed the Part A TFE with NPCC. NPCC accepted the Part A TFE. NPCC completed and accepted the Part B TFE approval.
2012-09-28 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 2 (NPCC_URE2) | NCRXXXXX | NPCC2011007720 | CIP-006-2 | R6 | NPCC_URE2 self-reported an issue with CIP-006-2 R6 for a period of approximately 14 months. During this period, NPCC_URE2's procedure incorrectly stated the requirement for logging physical entry into a Physical Security Perimeter (PSP) to be limited to the initial entry at the start of the work day. Once a NPCC_URE2 worker utilized his or her credentials to enter the PSP, the worker would then exit and re-enter the PSP as the work day progressed. For example, after an initial entry and logging, a worker would exit the PSP to retrieve tools and then re-enter the PSP to continue work, which he or she did without re-logging entry. This issue is limited to those persons who were granted authorized unescorted access to PSPs. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the employees that were not re-logging entry into the PSP were all authorized for unescorted access. | NPCC_URE2 mitigated this issue by updating the governing operating procedure to include logging workers' entry and exit each time they enter the PSP and providing in-person training. The training consisted of a review of changes to the operating procedure and a review of the proper way to enter and exit the PSP.
2012-09-28 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 2 (NPCC_URE2) | NCRXXXXX | NPCC2011007721 | CIP-006-2 | R6 | NPCC_URE2 self-reported an issue with CIP-006-2 R6 for a period of approximately 14 months. This issue relates to those persons (Visitors) not granted authorized unescorted access to Physical Security Perimeters (PSPs). During this period, NPCC_URE2's procedure incorrectly stated the requirement for logging physical entry into a PSP to be limited to the initial entry at the start of the work day, and final exit at the end of the work day. Once a Visitor was escorted into the PSP, the Visitor would then proceed to exit and re-enter the PSP as the work day progressed. For example, after an initial entry and logging, a Visitor would exit the PSP to retrieve tools and then re-enter the PSP to continue work, which he or she did without re-logging entry. At the conclusion of the work day, the Visitor would log the exit time. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the locations in question were in field control houses that were being staffed by NPCC_URE2 employees with authorized unescorted access at the time, and the Visitors were continuously escorted while in the PSP. | NPCC_URE2 mitigated this issue by updating the governing operating procedure to include correctly logging Visitors' access to PSPs and completing in-person training with persons with unescorted physical access to the PSP. The training consisted of a review of changes to the operating procedure and a review of the proper way to enter and exit the PSP and escort visitors.
2012-09-28 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 2 (NPCC_URE2) | NCRXXXXX | NPCC2011007722 | CIP-006-3c | R1.6 | NPCC_URE2 self-reported an issue with CIP-006-3c R1.6. This issue relates to those persons (Visitors) not granted authorized unescorted access to Physical Security Perimeters (PSPs). On the effective compliance enforcement date of CIP-006-3c, NPCC_URE2 had procedures for escorting Visitors and logging Visitor entry and exit to and from PSPs. NPCC_URE2 interpreted the requirement of CIP-006-3 R1.6 to be consistent with the existing logging practice associated with CIP-006-3 R6. NPCC_URE2 incorrectly understood the requirement for logging physical entry into a Physical Security Perimeter (PSP) to be limited to the initial entry at the start of the work day and final exit at the end of the work day. Once a Visitor was escorted into the PSP, the Visitor would then proceed to exit and re-enter the PSP as the work day progressed. For example, a Visitor would exit the PSP to retrieve tools and then re-enter the PSP to continue work, which he or she did without re-logging entry. At the conclusion of the work day, the Visitor would log the exit time. The Visitors were continuously escorted while in the PSP. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the locations in question were in field control houses that were being staffed by NPCC_URE2 employees with authorized unescorted access at the time, and the Visitors were continuously escorted while in the physical security perimeter. | NPCC_URE2 mitigated this issue by updating the governing operating procedure to include correctly logging Visitors' access to PSPs and completing in-person training with persons with unescorted physical access to the PSP. The training consisted of a review of changes to the operating procedure and a review of the proper way to log access to PSPs and to escort visitors.
2012-09-28 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 2 (NPCC_URE2) | NCRXXXXX | NPCC2011007723 | CIP-006-2 | R5 | NPCC_URE2 self-reported an issue with CIP-006-2 R5 for a period of approximately sixteen months. NPCC_URE2 monitors physical access at access points to the Physical Security Perimeter (PSP) via a remote guard station, known as the monitoring station. When a door is opened without an electronic card being utilized to unlock the door, a "forced door open" (FDO) alarm is generated and observed at the monitoring station. The security officer is provided a standing desk procedure, which requires the officer to call the substation. If an authorized person answers the phone, the officer is to acknowledge and clear the alarm. If no one answers the officer is required to: (a) contact the designated on-call supervisor for a response, and (b) check the substation camera system to determine if the unauthorized access (break-in) can be confirmed. If an unauthorized access attempt is confirmed, the officer is required to contact local police and the on-call supervisor immediately. If unauthorized access cannot be confirmed through the camera system, the officer is to notify the on-call supervisor for a response. If an unauthorized access is confirmed by the supervisor, then the cyber incident response plan is activated. NPCC determined that NPCC_URE2's security officer did not follow the standing desk procedure for determining if an unauthorized access attempt had occurred. In lieu of following the standing desk procedure, the security officer, when receiving a FDO alarm, would properly acknowledge the alarm on the monitor and then determine if the person in the substation was a NPCC_URE2 employee by utilizing the camera system and waiting for the person to utilize the electronic key at another access point to the PSP. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the security officer was following a process to conclude that an actual breach did not occur. | NPCC_URE2 mitigated this issue by: (1) updating its operating procedure, including the desk procedure at issue, to include responding to alarms; (2) ensuring that each security officer reviewed the desk procedure for responding to an intrusion alarm; and (3) reviewing the operating procedure with the security officers to reinforce the response requirements to an alarm, the process to enter and exit substations, and visitor logging.
2012-09-28 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 2 (NPCC_URE2) | NCRXXXXX | NPCC2011009011 | CIP-008-2 | R1.4 | NPCC_URE2 self-reported an issue with CIP-008-2 R1.4. On April 1, 2010, Version 2 of NERC Standard CIP-008 became effective and changed the requirement for updating the Cyber Security Incident response plan from within 90 days to within 30 days of a change. NPCC_URE2 revised its Cyber Security Incident Response & Reporting Plan (Plan) but did not include the change in requirement from 90 to 30 days. NPCC_URE2 revised its Plan again the following year as part of the annual review and again did not identify this error. Later that year, UI identified the error in its Plan and corrected the error. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the issue is a documentation error and administrative in nature. | NPCC_URE2 mitigated this issue by correcting and updating its Plan from 90 days to 30 days.
2012-09-28 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 2 (NPCC_URE2) | NCRXXXXX | NPCC2011009012 | CIP-007-1 | R5.3 | NPCC_URE2 self-reported an issue with CIP-007-1 R5.3. NPCC_URE2's physical access control system utilizes four Cyber Assets that are required to comply with the password requirements of CIP-007-1 R5.3. First, NPCC_URE2 reported that 11 accounts on the operating system did not have passwords changed annually, as required by the Standard. These issues were discovered during a cyber vulnerability assessment. Second, NPCC_URE2 was notified by the vendor conducting the cyber vulnerability assessment that two passwords were not changed annually, and NPCC_URE2 then corrected those issues. Subsequently, NPCC_URE2 requested information from the vendor about any other passwords that were greater than 365 days old on this system and was informed that an additional nine passwords were not compliant and NPCC_URE2 corrected those. The passwords are associated with administrative and user accounts for the operating systems on these four Cyber Assets. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the devices at issue are located within an access controlled room. Additionally, there is no remote access to the devices. | NPCC_URE2 mitigated this issue by disabling or changing the accounts identified in the Self-Report. NPCC_URE2 reviewed the final cyber vulnerability assessment report for similar account and password violations and found none. In addition, NPCC_URE2 issued a memo to the managers of Cyber Assets reinforcing the need to change passwords at least annually and to verify accounts annually at both the application and operating system level.
2012-09-28 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 3 (NPCC_URE3) | NCRXXXXX | NPCC2011008240 | CIP-006-1 | R1.2 | NPCC_URE3 self-reported an issue with CIP-006-1 R1.2. NPCC_URE3 discovered that two emergency exit-only doors on the Physical Security Perimeter (PSP) were not identified as physical access points. Additionally, the access control alarms for the two emergency exit-only doors were not configured in NPCC_URE3's physical access control intrusion detection system to alarm upon opening as a CIP alarm. Although the two emergency exit-only doors were configured to report any activity to the access control intrusion detection system alarm history log, this is not the required configuration. The required configuration is that opening the door (defined as a break in the door contacts in the door and frame) will trigger an alarm in the access control intrusion detection system for resolution and the unique determination of the emergency exit-only door usage by NPCC_URE3's centralized security operations center. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the PSP is manned 24 hours a day, seven days a week by authorized personnel. Second, NPCC_URE3 conducts annual training and quarterly re-enforcement training for the recognition and reporting of suspicious activity for site personnel. Third, the site is regulated under the Maritime Transportation Security Act of 2002, which requires stringent physical security measures, including prohibiting an unescorted individual from entering an area of the facility that is designated as a secure area unless the individual holds a duly issued transportation worker identification credential and is authorized to be in the area. Lastly, the two emergency exit-only doors are not able to be opened from the outside without a special tool, which was not readily available. | NPCC_URE3 mitigated this issue by: (1) issuing a security awareness bulletin to the CIP area access managers and compliance managers on the proper use of physical access points and how to detect an issue with or misuse of a physical access point or physical security protection; (2) updating corporate security procedure on how to conduct a physical walk-down of a PSP and its physical access points before a site is declared compliant; (3) labeling and identifying in the physical security plan drawing the two emergency exit doors as access points, and approving the drawings and uploading them to the appropriate documentation office; (4) performing a door check and reviewing output of the door check with site personnel; (5) reconfiguring the two emergency exit only doors and verifying that opening of the door generates an alarm to the security operations center; (6) training corporate security personnel on the updated procedure; (7) updating yearly awareness training for corporate security personnel of their requirements for a site-walk down; and (8) extending the event analysis procedure to be completed at each of the regulated PSPs to include a review and physical walk-down of all the “six-wall” physical access points to ensure that each physical access point is identified on the physical security drawing, as well as within the access control intrusion detection system.
2012-09-28 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 3 (NPCC_URE3) | NCRXXXXX | NPCC2011008241 | CIP-006-1 | R4 | NPCC_URE3 self-reported an issue with CIP-006-1 R4. NPCC_URE3 discovered that two emergency exit-only doors on the Physical Security Perimeter (PSP) were not identified as physical access points. As a result of this, NPCC_URE3 did not implement and document the technical and procedural mechanisms for logging physical entry at these two access points for a period of approximately 21 months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the PSP is manned 24 hours a day, seven days a week by authorized personnel. Second, NPCC_URE3 conducts annual training and quarterly re-enforcement training for the recognition and reporting of suspicious activity for site personnel. Third, the site is regulated under the Maritime Transportation Security Act of 2002, which requires stringent physical security measures, including prohibiting an unescorted individual from entering an area of the facility that is designated as a secure area unless the individual holds a duly issued transportation worker identification credential and is authorized to be in the area. Lastly, the two emergency exit-only doors are not able to be opened from the outside without a special tool, which was not readily available. | NPCC_URE3 mitigated this issue by: (1) issuing a security awareness bulletin to the CIP area access managers and compliance managers on the proper use of physical access points and how to detect an issue with or misuse of a physical access point or physical security protection; (2) updating corporate security procedure on how to conduct a physical walk-down of a PSP and its physical access points before a site is declared compliant; (3) labeling and identifying in the physical security plan drawing the two emergency exit doors as access points, and approving the drawings and uploading them to the appropriate documentation office; (4) performing a door check and reviewing output of the door check with site personnel; (5) reconfiguring the two emergency exit only doors and verifying that opening of the door generates an alarm to the security operations center; (6) training corporate security personnel on the updated procedure; (7) updating yearly awareness training for corporate security personnel of their requirements for a site-walk down; and (8) extending the event analysis procedure to be completed at each of the regulated PSPs to include a review and physical walk-down of all the “six-wall” physical access points to ensure that each physical access point is identified on the physical security drawing, as well as within the access control intrusion detection system.
2012-09-28 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 3 (NPCC_URE3) | NCRXXXXX | NPCC2011008242 | CIP-006-1 | R3 | NPCC_URE3 self-reported an issue with CIP-006-1 R3. NPCC_URE3 discovered that two emergency exit-only doors on the Physical Security Perimeter (PSP) were not identified as physical access points. Additionally, the access control alarms for the two emergency exit-only doors were not configured in NPCC_URE3's physical access control intrusion detection system to alarm upon opening as a CIP alarm. Although the two emergency exit-only doors were configured to report any activity to the access control intrusion detection system alarm history log, this is not the required configuration. The required configuration is that opening the door (defined as a break in the door contacts in the door and frame) will trigger an alarm in the access control intrusion detection system for resolution and the unique determination of the emergency exit-only door usage by NPCC_URE3's centralized security operations center. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because the PSP is manned 24 hours a day, seven days a week by authorized personnel. Second, NPCC_URE3 conducts annual training and quarterly re-enforcement training for the recognition and reporting of suspicious activity for site personnel. Third, the site is regulated under the Maritime Transportation Security Act of 2002, which requires stringent physical security measures, including prohibiting an unescorted individual from entering an area of the facility that is designated as a secure area unless the individual holds a duly issued transportation worker identification credential and is authorized to be in the area. Lastly, the two emergency exit-only doors are not able to be opened from the outside without a special tool, which was not readily available. | NPCC_URE3 mitigated this issue by: (1) issuing a security awareness bulletin to the CIP area access managers and compliance managers on the proper use of physical access points and how to detect an issue with or misuse of a physical access point or physical security protection; (2) updating corporate security procedure on how to conduct a physical walk-down of a PSP and its physical access points before a site is declared compliant; (3) labeling and identifying in the physical security plan drawing the two emergency exit doors as access points, and approving the drawings and uploading them to the appropriate documentation office; (4) performing a door check and reviewing output of the door check with site personnel; (5) reconfiguring the two emergency exit only doors and verifying that opening of the door generates an alarm to the security operations center; (6) training corporate security personnel on the updated procedure; (7) updating yearly awareness training for corporate security personnel of their requirements for a site-walk down; and (8) extending the event analysis procedure to be completed at each of the regulated PSPs to include a review and physical walk-down of all the “six-wall” physical access points to ensure that each physical access point is identified on the physical security drawing, as well as within the access control intrusion detection system.
2012-09-28 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 3 (NPCC_URE3) | NCRXXXXX | NPCC2011008243 | CIP-006-1 | R2 | NPCC_URE3 self-reported an issue with CIP-006-1 R2. NPCC_URE3 discovered that two emergency exit-only doors on the Physical Security Perimeter (PSP) were not identified as physical access points. As the result of this, NPCC_URE3 did not document and implement the technical and procedural controls to manage physical access at these two access points 24 hours a day, seven days a week. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the PSP is manned 24 hours a day, seven days a week by authorized personnel. Second, NPCC_URE3 conducts annual training and quarterly re-enforcement training for the recognition and reporting of suspicious activity for site personnel. Third, the site is regulated under the Maritime Transportation Security Act of 2002, which requires stringent physical security measures, including prohibiting an unescorted individual from entering an area of the facility that is designated as a secure area unless the individual holds a duly issued transportation worker identification credential and is authorized to be in the area. Lastly, the two emergency exit-only doors are not able to be opened from the outside without a special tool, which was not readily available. | NPCC_URE3 mitigated this issue by: (1) issuing a security awareness bulletin to the CIP area access managers and compliance managers on the proper use of physical access points and how to detect an issue with or misuse of a physical access point or physical security protection; (2) updating corporate security procedure on how to conduct a physical walk-down of a PSP and its physical access points before a site is declared compliant; (3) labeling and identifying in the physical security plan drawing the two emergency exit doors as access points, and approving the drawings and uploading them to the appropriate documentation office; (4) performing a door check and reviewing output of the door check with site personnel; (5) reconfiguring the two emergency exit only doors and verifying that opening of the door generates an alarm to the security operations center; (6) training corporate security personnel on the updated procedure; (7) updating yearly awareness training for corporate security personnel of their requirements for a site-walk down; and (8) extending the event analysis procedure to be completed at each of the regulated PSPs to include a review and physical walk-down of all the “six-wall” physical access points to ensure that each physical access point is identified on the physical security drawing, as well as within the access control intrusion detection system.
2012-09-28 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 4 (NPCC_URE4) | NCRXXXXX | NPCC2012009964 | CIP-007-3 | R5.3 | NPCC_URE4 self-reported an issue with CIP-007-3 R5.3. Specifically, 20 NPCC_URE4 Cyber Assets within the Electronic Security Perimeter (ESP) did not have technical controls for strict compliance with the password requirements of R5.3, and the Cyber Assets were not covered under an existing Technical Feasibility Exception (TFE). NPCC_URE4 failed to submit a TFE request for all 20 Cyber Assets. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because of the compensatory procedures and technical controls that NPCC_URE4 implemented. Access to the devices at issue is monitored. Physical access is required to configure the devices, and physical access controls restrict unauthorized physical access. Additionally, NPCC_URE4's operating procedures require that passwords meet minimum length requirements and personnel are trained on the procedures. NPCC_URE4's minimum password strength exceeds requirements. NPCC_URE4's operating procedures require that passwords are changed at least annually and personnel are trained on the procedures. The operating procedures require that passwords contain the required combination of characters. Complex password policy has been enabled on the devices at issue. Also, these devices have been configured to require a minimum password length of eight characters. The resulting passwords exceed the password complexity required by CIP-007-3 R5.3. This is an open-ended TFE. | This issue was mitigated through the TFE process. NPCC_URE4 filed the Part A TFE. NPCC accepted the Part A TFE. NPCC completed and accepted the Part B TFE approval.
2012-09-28 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 5 (NPCC_URE5) | NCRXXXXX | NPCC2012010462 | CIP-007-1 | R3 | NPCC_URE5 self-reported an issue with CIP-007-1 R3. Specifically, 14 NPCC_URE5 devices were not able to be patched because security patches are no longer supplied by the application vendors. NPCC_URE5 failed to submit Technical Feasibility Exception (TFE) requests for all 14 devices. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because of the compensatory procedures and technical controls that NPCC_URE5 implemented. The devices at issue are protected in that all reside within Physical Security Perimeters (PSPs) and Electronic Security Perimeter (ESP). The incident response plan will notify support personnel to take action in the event a device is compromised; the facility IT contact will interface with the Corporate Cyber Incident Response Team to provide assistance with communication and remediation. Lastly, network isolation prevents exposure of these devices to un-trusted networks, including the internet and business network. These are open-ended TFEs. | This issue was mitigated through the TFE process. NPCC_URE5 filed the Part A TFEs. NPCC accepted the Part A TFEs. NPCC completed and accepted the Part B TFEs approval.
2012-09-28 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 5 (NPCC_URE5) | NCRXXXXX | NPCC2012010463 | CIP-007-1 | R4.1 | NPCC_URE5 self-reported an issue with CIP-007-1 R4. Specifically, the operating systems on 54 devices did not have anti-virus and anti-malware tools installed and therefore were not patched on a regular basis. NPCC_URE5 failed to submit Technical Feasibility Exception (TFE) requests for all 54 devices. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because of the compensatory procedures and technical controls that NPCC_URE5 implemented. The devices at issue are protected by the Electronic Security Perimeter (ESP) and Physical Security Perimeter (PSP), which are controlled and monitored. Network isolation also prevents exposure of the devices to un-trusted networks, including the internet and business networks. Additionally, the incident response plan will notify support personnel to take action in the event a device is compromised; the facility IT contact will interface with the Corporate Cyber Incident Response Team to provide assistance with communication and remediation. This is an open-ended TFE. | This issue was mitigated through the TFE process. NPCC_URE5 filed the Part A TFEs. NPCC accepted the Part A TFEs. NPCC completed and accepted the Part B TFEs approval.
2012-09-28 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 5 (NPCC_URE5) | NCRXXXXX | NPCC2012010464 | CIP-007-1 | R5.3 | NPCC_URE5 self-reported an issue with CIP-007-1 R5. Specifically, the operating systems on 54 devices do not have technical controls for password length, character complexity, or password change frequency, as required by CIP-007-1 R5.3. NPCC_URE5 failed to submit Technical Feasibility Exception (TFE) requests for all 54 devices. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because of the compensatory procedures and technical controls that NPCC_URE5 implemented. First, the devices at issue are protected by the Electronic Security Perimeter (ESP) and Physical Security Perimeter (PSP). Additionally, personnel risk assessments and training ensure that only vetted personnel have access to these devices. Lastly, proprietary machine language for instructions inhibits plug-in and control by a potential hacker. This is an open-ended TFE. | This issue was mitigated through the TFE process. NPCC_URE5 filed the Part A TFEs. NPCC accepted the Part A TFEs. NPCC completed and accepted the Part B TFEs approval.
2012-09-28 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 6 (NPCC_URE6) | NCRXXXXX | NPCC2012010500 | CIP-007-1 | R3 | NPCC_URE6 self-reported that one device could not being patched, resulting in an issue with CIP-007-1 R3. NPCC_URE6 failed to submit a Technical Feasibility Exception (TFE) request for this device. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because of the compensatory procedures and technical controls that NPCC_URE6 implemented. The device at issue is protected by the fact that it resides within a Physical Security Perimeter (PSP) and an Electronic Security Perimeter (ESP). The incident response plan will notify support personnel to take action in the event the device is compromised; the Facility IT contact will interface with the Corporate Cyber Incident response team providing assistance with communication and remediation. Network isolation prevents exposure of device to un-trusted networks, including the Internet and business network. This is an open-ended TFE. | This issue was mitigated through the TFE process. NPCC_URE6 filed the Part A TFE. NPCC accepted the Part A TFE. NPCC completed and accepted the Part B TFE approval.
2012-09-28 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 6 (NPCC_URE6) | NCRXXXXX | NPCC2012010501 | CIP-007-1 | R4.1 | NPCC_URE6 self-reported an issue with CIP-007-1 R4. Specifically, the operating systems on five devices did not have anti-virus and anti-malware tools installed. NPCC_URE6 failed to submit Technical Feasibility Exception (TFE) requests for all five devices. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because of the compensatory procedures and technical controls that NPCC_URE6 implemented. The devices at issue are protected by the fact that they reside within a Physical Security Perimeter (PSP) and an Electronic Security Perimeter (ESP). The incident response plan will notify support personnel to take action in the event a device is compromised; the Facility IT contact will interface with the Corporate Cyber Incident response team providing assistance with communication and remediation. Network isolation prevents exposure of device to un-trusted networks, including the Internet and business network. This is an open-ended TFE. | This issue was mitigated through the TFE process. NPCC_URE6 filed the Part A TFEs. NPCC accepted the Part A TFEs. NPCC completed and accepted the Part B TFE approvals.
2012-09-28 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 6 (NPCC_URE6) | NCRXXXXX | NPCC2012010502 | CIP-007-1 | R5.3 | NPCC_URE6 self-reported an issue with CIP-007-1 R5.3. Specifically, one device did not have technical controls for password length, character complexity, or password change frequency. NPCC_URE6 failed to submit Technical Feasibility Exception (TFE) requests for this device. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because of the compensatory procedures and technical controls that NPCC_URE6 implemented. The device at issue is protected by the fact that it resides within a Physical Security Perimeter (PSP) and an Electronic Security Perimeter (ESP). The incident response plan will notify support personnel to take action in the event the device is compromised; the Facility IT contact will interface with the Corporate Cyber Incident response team providing assistance with communication and remediation. Network isolation prevents exposure of device to un-trusted networks, including the Internet and business network. This is an open-ended TFE. | This issue was mitigated through the TFE process. NPCC_URE6 filed the Part A TFEs. NPCC accepted the Part A TFEs. NPCC completed and accepted the Part B TFE approvals.
2012-09-28 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 6 (NPCC_URE6) | NCRXXXXX | NPCC2012010503 | CIP-007-1 | R6 | NPCC_URE6 self-reported an issue with CIP-007-1 R6. Specifically, two devices were not capable of generating internal logs of system events including security and authentication-related incidents. NPCC_URE6 failed to submit Technical Feasibility Exception (TFE) requests for these devices. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because of the compensatory procedures and technical controls that NPCC_URE6 implemented. The devices at issue are protected by the fact that they reside within a Physical Security Perimeter (PSP) and an Electronic Security Perimeter (ESP). The incident response plan will notify support personnel to take action in the event a device is compromised; the Facility IT contact will interface with the Corporate Cyber Incident response team providing assistance with communication and remediation. Network isolation prevents exposure of device to un-trusted networks, including the Internet and business network. This is an open-ended TFE. | This issue was mitigated through the TFE process. NPCC_URE6 filed the Part A TFEs. NPCC accepted the Part A TFEs. NPCC completed and accepted the Part B TFE approvals.
2012-09-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2012010441 | CIP-006-3a | R1 | During a compliance audit, ReliabilityFirst discovered that RFC_URE1 had an issue with CIP-006-3c R1.6. RFC_URE1 failed to maintain completed visitor logs in certain instances. ReliabilityFirst discovered deficiencies on four dates where visitor logs were missing exit or log out information. | ReliabilityFirst determined that this issue posed a minimal risk to the reliability of the bulk power system (BPS). The risk to the reliability of the BPS was mitigated by the following factors. RFC_URE1 has in place an internal auditing system of its visitor logs where, every few days, its security personnel ensure that the logs contain the correct information. RFC_URE1, therefore, noticed the discrepancies in the logs and corrected them within a few days of the discrepancies occurring. | RFC_URE1 performed the following mitigating activities: 1) reinforced the visitor procedure requirements with the appropriate individuals, including executives; 2) held a meeting with operations managers to discuss NERC CIP issues including the requirement for visitor procedures; and 3) reinforced the visitor procedure through posted signage, training, and ongoing awareness measures.
2012-09-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2012010442 | CIP-007-3 | R9 | During a compliance audit, ReliabilityFirst discovered that RFC_URE1 had an issue with CIP-007-1 R9. For one of its CIP-007 documents, RFC_URE1 performed an annual review in 2010 and 2011, but failed to document all changes resulting from modifications to the systems or controls within thirty calendar days of completing the changes. Instead, RFC_URE1 gradually documented the changes in a manner which resulted in several versions where it was unclear which date applied to which change. In two instances, RFC_URE1 documented changes four months and two months after modifications, past the 30 days required by the Standard. | ReliabilityFirst determined that this issue posed a minimal risk to the reliability of the bulk power system (BPS). The risk to the reliability of the BPS was mitigated by the fact that RFC_URE1 documented the changes resulting from modifications to the systems or controls within four months for 2010 and within two months for 2011, although not within the required 30 days. Although RFC_URE1 could not provide documentation as evidence of completed the updates, RFC_URE1 asserted that it had actually completed the updates within 30 calendar days. | RFC_URE1 documented the changes resulting from modifications to the systems or controls. In addition, RFC_URE1 now utilizes software to more effectively document the dates it makes modifications.
2012-09-28 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2012010444 | CIP-005-1 | R4 | During a compliance audit, ReliabilityFirst discovered that RFC_URE1 had an issue with CIP-005-1 R4. A third-party vendor performs RFC_URE1 cyber vulnerability assessment of the electronic access points to the Electronic Security Perimeter (ESP). RFC_URE1 third-party vendor deleted the detailed evidence related to the cyber vulnerability assessment. As a result, RFC_URE1 provided a summary report from the third-party vendor that it: (a) performed a review to verify that only ports and services required for operations at electronic access points to the ESP were enabled (R4.2); (b) included the discovery of all access points to the ESP (R4.3); and (c) performed a review of controls for default accounts, passwords, and network management community strings (R4.4). RFC_URE1, however, was unable to provide detailed evidence to support the summary report and that it had fulfilled all the subrequirements of R4. | ReliabilityFirst determined that this issue posed a minimal risk to the reliability of the bulk power system (BPS). The risk to the reliability of the BPS was mitigated by the following factors. RFC_URE1 performed the required actions in its cyber vulnerability assessment and provided a summary of the cyber vulnerability assessment. RFC_URE1's evidence was simply inadequate to demonstrate the extent of RFC_URE1's cyber vulnerability assessment. | RFC_URE1 revised its cyber vulnerability assessment procedure with the vendor to ensure detailed requirements for performing the assessment and to ensure production of evidence and retention of the evidence to support the evaluation of the state of the controls measured against the Reliability Standards. In addition, the procedure requires the final evaluation of all requirements to be substationed with detailed evidence to support all conclusions.
2012-09-28 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC200900395 | CIP-003-1 | R1.2 | The SERC Spot Check team reported an issue with CIP-003-1 R1.2, stating that SERC_URE1 failed to provide evidence that its cyber security policy (CSP) was readily available to all personnel who have access to, or are responsible for, Critical Cyber Assets (CCAs). During the CIP Spot Check, SERC_URE1 indicated that personnel were only able to access the portions of the CSP that were deemed applicable to their job responsibilities and not the entire CSP. SERC staff requested and reviewed additional information in order to complete its assessment. SERC staff learned that the CSP consisted of multiple variations that were available to provide the level of detail pertinent to the roles and responsibilities of the person with access to or responsibility for CCAs. These various abridged role-based CSPs also contained operational data that assisted the employee in performance of their specific duties. SERC_URE1 made the CSP readily available by placing the CSP required by the employee’s role on the SERC_URE1 intranet. SERC_URE1 also covered the CSP in its annual cyber security training pursuant to CIP-004 R2. In the training, SERC_URE1 informed each user where to find the training on the intranet, as well as contact information if the user needed or wished to receive a copy of the CSP. If the trainee did not have access to the intranet and the online training, the trainer would cover the CSP at the time of the training and would also provide the trainee with contact information for a copy of the CSP and with any questions after the training concluded. The trainer was typically a senior employee or supervisor, and trainers typically advised trainees to see their manager or any employee with intranet access for a copy of the CSP. Only 3.5% of personnel with CCA access did not have log-in capabilities to the intranet at the time of the Spot Check. | SERC staff determined that the issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because: 1. SERC_URE1 provided applicable portions of the CSP to personnel based on the roles and responsibilities they were performing; and 2. Only 3.5% of personnel with access to CCAs did not have intranet access and needed to depend on their manager or other users to obtain a hard copy of the CSP. These individuals were told during cyber security training who they could contact for a copy of the full CSP. | SERC staff verified that SERC_URE1 completed the following actions: 1. Revised the CSP to more clearly address CIP-002 through CIP-009, and to incorporate and supersede all associated policies and procedures; 2. Electronically posted the revised policy both internally and on SERC_URE1's website so that it may be readily accessible by all personnel with electronic access; 3. Physically placed the revised policy at each of SERC_URE1's Physical Security Perimeters so that it is readily accessible by all personnel with physical access; and 4. Notified all personnel with access to CCAs of the revised CSP and the various places it will be readily available.
2012-09-28 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP201000246 | CIP-003-1 | R4 | During the course of a Multi-Region Spot Check, SPP RE found SPP RE_URE1 to be in noncompliance with CIP-003-1 R4 for failing to identify, classify, and protect information associated with Critical Cyber Assets (CCAs). Specifically, SPP RE_URE1 failed to label certain documents as prescribed in its energy information security classification policy. Subsequent to the CIP Spot Check, SPP RE_URE1's parent company conducted an overarching review of documents affected by the energy information security classification policy as part of the measures used to mitigate this particular remediated issue. SPP RE_URE1's parent company found 18 additional documents that were not labeled appropriately, four of which belonged to SPP RE_URE1. | SPP RE determined that the issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The documents that were not labeled as prescribed by SPP RE_URE1's energy information security classification policy were in electronic form at the time the issue occurred. SPP RE_URE1 has a document software package for document security which limits electronic access to authorized users, thus protecting SPP RE_URE1's information associated with its CCAs. The documents which were not marked confidential in accordance with the SPP RE_URE1 energy information security classifications policy were restricted access documents within the SPP RE_URE1 document security system. Only a limited number of authorized users were able to access the documents. | SPP RE_URE1 performed the following actions to mitigate the issue: 1) conducted a comprehensive review to ensure compliance with all requirements under CIP-003-1; and 2) marked all relative documents in accordance with its energy information security classification policy.
2012-09-28 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2012010061 | CIP-004-3 | R3 | WECC_URE1 submitted a Self-Report addressing an issue with this Standard. According to the Self-Report, during a routine review of personnel risk assessment (PRA) tickets, the WECC_URE1 Human Resource Department identified a PRA that was not renewed seven years after the initial assessment. WECC_URE1 stated the overdue PRA is for a control room operator with both physical and cyber access to the supervisory control and data acquisition (SCADA) system inside the control rooms Physical Security Perimeter (PSP) and Electronic Security Perimeter (ESP). WECC_URE1 stated further that the operator's completion of the most current PRA was five weeks beyond the CIP-004 R3.2 allowable timeframe. According to WECC_URE1, upon identification of the overdue PRA, Human Resources immediately informed Physical Security who took action to initiate the overdue PRA. The PRA was completed within 24 hours of its discovering its expiration. WECC concluded that WECC_URE1 had an issue of CIP-004-3 R3 for failing to renew the control room operator’s PRA within seven years as required by R3.2. WECC determined that WECC_URE1 had an issue of CIP-004-3 R3.2 for failing to timely renew the PRA for one employee. | WECC determined that the issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because although WECC_URE1 failed to timely renew a PRA, the operator in scope had a previous PRA, had completed current CIP training, and was a long time employee who had authorized access to the control room to perform his daily duties. Also, the SCADA system resides within the control room’s PSP and ESP with continuous video monitoring. Additionally, WECC_URE1 employs onsite security personnel at all access points and at all PSPs. | WECC_URE1 submitted a Mitigation Plan to address this issue. The Mitigation Plan required WECC_URE1 to: (1) redeploy the individual responsible for initiating the PRA process; (2) review the current CCA holders to verify that all PRAs are current; (3) begin duplicate monitoring of PRAs. This process included the creation of daily reports that lists the pending PRAs 90 days in advance and recently completed PRAs. Also, this process incorporates a review of PRA status during WECC_URE1’s annual badge renewal cycle; and (4) Human Resources will independently monitor the completion of PRAs and escalate to management any PRA tickets that are not closed within the first month.
2012-09-28 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2012010524 | CIP-004-3 | R2 | WECC_URE2 submitted a Self-Report citing noncompliance with CIP-004-3 R2. Specifically, WECC_URE2 reported that a contractor was granted cyber access to Critical Cyber Assets (CCAs) prior to completing cyber security training. WECC determined that on WECC_URE2 granted a contractor access to CCAs prior to his completion of cyber security training. WECC also determined that PGE detected and revoked the contractor’s access rights within that same day. | WECC determined that the issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because the risk posed by WECC_URE2 noncompliance is offset given the duration and scope, as well as by compensating measures in place during the issue period. The scope of the issue was limited to a single individual with cyber access to CCAs associated with the control center and backup control center for a period of a single day. Within hours of granting the contractor access, WECC_URE2 detected its error. WECC_URE2 revoked the contractor’s access. During the period in which the contractor had access to CCAs, there were a number of compensating security measures in place that offset the risk of possible noncompliance with R2.1. The CCAs were protected by an electronic intrusion detection system. All access to CCAs was logged and monitored. Further, the CCAs were physically secured within a Physical Security Perimeter (PSP), where physical access was controlled and monitored. | WECC_URE2 revoked the contractor’s access to CCAs, thereby remediating the issue. The contractor was given cyber security training.
2012-09-28 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2012010525 | CIP-004-3 | R3 | WECC_URE2 submitted three Self-Reports citing issues of CIP-004-3 R3, CIP-005-3 R1 and CIP-006-3 R2. CIP-004-3 R3 requires that entities ensure a personnel risk assessment (PRA) is completed prior to granting individuals electronic or physical access to Critical Cyber Assets (CCAs). CIP-005-3 R1 and CIP-006-3 R2 incorporate by reference CIP-004-3 R3, thereby requiring a PRA prior to any grant of access to Cyber Assets provisioning electronic access control and monitoring and Cyber Assets provisioning physical and access control and monitoring, respectively. WECC determined that WECC_URE2 granted a single contractor physical and electronic access to CCAs and Cyber Assets provisioning physical and electronic access control and monitoring. WECC determined that the contractor was granted access without first completing a PRA under CIP-004-1 R3. WECC also determined that the contractor was also granted access to Cyber Assets provisioning electronic and physical access control and monitoring in noncompliance with CIP-005-3 R1 and CIP-006-3 R2. | WECC determined that the issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because the noncompliance stems from a single instance in which WECC_URE2 granted access to a contractor, before that contractor completed a PRA. The scope of the issue is, therefore, limited. The contractor had access for less than a twenty-four hour period. The contractor subsequently completed a PRA and was given access to Cyber Assets and CCAs. All CCAs and Cyber Assets were located within an Electronic Security Perimeter and Physical Security Perimeter. All access was logged and monitored. | WECC_URE2 terminated the contractor’s electronic and physical access rights to CCAs thereby remediating the issue. The contractor subsequently completed a PRA and was given access to Cyber Assets and CCAs.
2012-09-28 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2012010393 | CIP-005-3a | R5 | WECC_URE2 submitted a Self-Report citing possible noncompliance with CIP-005-3 R5. Specifically, WECC_URE2 reported that it failed to update documentation to reflect modification of network or controls within 90 calendar days of the change. WECC determined that WECC_URE2 added four Access Control and Monitoring (ACM) devices to the Electronic Security Perimeter (ESP). Per CIP-005-3 R5.2, WECC_URE2 was required to update ESP documentation to reflect this change within 90 days. WECC determined, however, that WECC_URE2 did not update ESP documentation to reflect this change in ESP controls until 397 days later when WECC_URE2 completed remediation activity. | WECC determined that the issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because the four ACM devices were only used to monitor Critical Cyber Assets and Cyber Assets within the ESP during vulnerability assessments. Further, these devices were afforded a number of protections. Devices were contained within an ESP. Access to the ESP was controlled, monitored and logged during the issue period. The ESP was alarmed for cyber security events. Individuals with access to the devices completed cyber security training and personnel risk assessments (PRAs). The devices were physically secured within a Physical Security Perimeter (PSP). Physical access thereto was logged, controlled and monitored. | WECC_URE2 submitted a completed Mitigation Plan. In its Mitigation Plan, WECC_URE2 outlined the following actions completed: WECC_URE2 determined that the Network team that supports the EMS environment reviewed and updated the ESP drawings. Once these drawings were up to date with the current physical environment, WECC_URE2 proactively updates the documents whenever a relevant change to the environment exists.
2012-09-28 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2012010517 | CIP-005-3a | R3 | WECC_URE2 submitted two Self-Reports citing possible noncompliance with CIP-005-3 R3 and CIP-007-3 R6 at its backup control center (BUCC). Specifically, WECC_URE2 reported that it failed to review BUCC logs as required by CIP-005-3 R3.2 and CIP-007-3 R6.5. Pursuant to CIP-007 R6.5, WECC_URE2 is required to review logs of all system events. Similarly, under CIP-005-1 R3.2, WECC_URE2 is required to review Electronic Security Perimeter (ESP) access logs every 90 calendar days. WECC_URE2’s BUCC review process under CIP-007-1 R6.5 required that all logs be maintained on BUCC primary servers. As of the mandatory and enforceable date of the Standard, however, system events associated with four Cyber Assets within the ESP were stored on BUCC backup servers. Consequently, WECC_URE2’s review of system event logs did not include logs stored on the BUCC backup servers. Similarly, WECC_URE2’s BUCC review process under CIP-005-3 R3.2 required that WECC_URE2 review BUCC ESP access logs maintained on primary servers every 90 days. In this case, WECC_URE2 reported that when it installed two BUCC ESP access points, it did not configure the devices to forward access logs to BUCC primary servers. Instead, access logs for the two devices were maintained on BUCC backup servers. WECC reviewed WECC_URE2’s Self-Reports and logging documents. WECC determined that although WECC_URE2 did maintain logs under CIP-005-3 R3 and CIP-007-3 R6, WECC_URE2 failed to review these logs. | WECC determined that the issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because the scope of the issues were limited to six devices associated with WECC_URE2’s BUCC. Access logs and system event logs were being generated and maintained on backup servers. All devices within scope of both issues were secured within Physical Security Perimeters. Electronic and physical access to these devices was restricted to authorized personnel. Further, these devices were protected by layered security. Remote logical access to the devices was available only through the virtual private network (VPN). VPN logs were maintained and reviewed during the duration of the issue. | WECC_URE2 submitted a completed Mitigation Plan and Certification of Mitigation Plan Completion. The Mitigation Plan summarized mitigation action completed by WECC_URE2. WECC_URE2 installed new secondary log servers for both the System Control Center (SCC) and the BUCC. As part of this change, a spreadsheet was developed that listed each CIP-applicable Cyber Asset associated with the EMS (including the network devices at the BUCC). That list is derived from the list of CIP-applicable Cyber Assets maintained by the CIP program manager. A thorough review was completed to verify that each of those CIP-applicable Cyber Assets within the EMS environment that is capable of generating logs sends those logs to the appropriate primary and secondary log servers, as technically feasible. After reception of those logs are confirmed, WECC_URE2 ensured that each of the CIP-applicable Cyber Assets that is capable of generating logs associated with the EMS are included as “log sources” in pre-established alerting rules. These rules, at a minimum, include low and high logging thresholds. These alerts help to identify when logs sources either do not send logs within a certain timeframe (low-level threshold) or when they send too many logs within a certain timeframe (high-level threshold).
2012-09-28 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2012009457 | CIP-006-3c | R5 | WECC_URE2 submitted a Self-Certification citing possible noncompliance with CIP-006-3c R5. Specifically, WECC_URE2 disclosed that it failed to ensure 24 hours a day, seven days a week monitoring of physical access to a Physical Security Perimeter (PSP) for a period of approximately four hours and 22 minutes. WECC determined that there was a communication failure of physical access control panels at WECC_URE2’s backup control center (BCC). Consequently, WECC_URE2 alarming at the BCC PSP was disabled. After a period of four hours and 22 minutes, WECC_URE2 security personnel discovered the failure and immediately dispatched onsite security personnel to monitor the PSP using human observation. | WECC determined that the issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because the scope of the issue is limited to a single PSP for a period of four hours and 22 minutes. During the issue period, access to the PSP was controlled and logged through a card reader. After reviewing access logs, WECC_URE2 confirmed that there were no unauthorized access attempts that would have triggered alarming. Further, the BCC was not in operation during the issue period. | WECC_URE2 submitted a completed Mitigation Plan describing the following mitigation activities: 1. Incident review and training. Corporate security reviewed the sequence of events with the on-duty security personnel and provided guidance on response actions for alarms related to operational failures. The security supervisor also did a follow-up with personnel and provided direction on the importance and criticality of immediate response and notification of alarms related to CIP Assets; 2. Update to CIP alarm response protocol and recognition. Corporate security modified the designators of all CIP impacted components (node controllers, card readers) to include a CIP designation to better identify associated alarms. This provides a better visual cue to on-duty security personnel in order to react and respond to alarms related to CIP Assets. Corporate security also provided an update to the response protocol to all security personnel stressing the importance of notifying corporate security in a timely manner to ensure appropriate response and mitigation of CIP controls (physical access, monitoring, and logging) for all outages.
2012-09-28 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2012010518 | CIP-007-1 | R6 | WECC_URE2 submitted two Self-Reports citing possible noncompliance with CIP-005-3 R3 and CIP-007-3 R6 at its backup bontrol benter (BUCC). Specifically, WECC_URE2 reported that it failed to review BUCC logs as required by CIP-005-3 R3.2 and CIP-007-3 R6.5. Pursuant to CIP-007 R6.5, WECC_URE2 is required to review logs of all system events. Similarly, under CIP-005-1 R3.2, WECC_URE2 is required to review Electronic Security Perimeter (ESP) access logs every 90 calendar days. WECC_URE2’s BUCC review process under CIP-007-1 R6.5 required that all logs be maintained on BUCC primary servers. As of the mandatory and enforceable date of the Standard, however, system events associated with four Cyber Assets within the ESP were stored on BUCC backup servers. Consequently, WECC_URE2’s review of system event logs did not include logs stored on the BUCC backup servers. Similarly, WECC_URE2’s BUCC review process under CIP-005-3 R3.2 required that WECC_URE2 review BUCC ESP access logs maintained on primary servers every 90 days. In this case, WECC_URE2 reported that when it installed two BUCC ESP access points, it did not configure the devices to forward access logs to BUCC primary servers. Instead, access logs for the two devices were maintained on BUCC backup servers. WECC reviewed WECC_URE2’s Self-Reports and logging documents. WECC determined that although WECC_URE2 did maintain logs under CIP-005-3 R3 and CIP-007-3 R6, WECC_URE2 failed to review these logs. | WECC determined that the issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because the scope of the issues was limited to six devices associated with WECC_URE2’s BUCC. Access logs and system event logs were being generated and maintained on backup servers. All devices within scope of both issues were secured within Physical Security Perimeters. Electronic and physical access to these devices was restricted to authorized personnel. Further, these devices were protected by layered security. Remote logical access to the devices was available only through the virtual private network (VPN). VPN logs were maintained and reviewed during the duration of the issue. | WECC_URE2 submitted a completed Mitigation Plan and Certification of Mitigation Plan Completion. The Mitigation Plan summarized mitigation action completed by WECC_URE2: WECC_URE2 installed new secondary log servers for both the system control center (SCC) and the BUCC. As part of this change, a spreadsheet was developed that listed each CIP-applicable Cyber Asset associated with the EMS (including the network devices at the BUCC). That list is derived from the list of CIP-applicable Cyber Assets maintained by the CIP program manager. A thorough review was completed to verify that each of those CIP-applicable Cyber Assets within the EMS environment that is capable of generating logs sends those logs to the appropriate primary and secondary log servers, as technically feasible. After reception of those logs are confirmed, WECC_URE2 ensured that each of the CIP-applicable Cyber Assets that is capable of generating logs associated with the EMS are included as “log sources” in pre-established alerting rules. These rules, at a minimum, include low and high logging thresholds. These alerts help to identify when logs sources either do not send logs within a certain timeframe (low-level threshold) or when they send too many logs within a certain timeframe (high-level threshold).
2012-09-28 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2012010528 | CIP-007-3 | R5 | WECC_URE2 submitted a Self-Report citing possible noncompliance with CIP-007-3 R5. Specifically,WECC_URE2 reported that access to a user account was granted to an individual without the approval of designated personnel as required by CIP-007-1 R5.1.1. Based on additional information disclosed by WECC_URE2, WECC determined that WECC_URE2 granted access to user accounts without the approval of designated personnel on three occasions. WECC determined that in each instance, a single individual was granted access to a user account without the approval of designated personnel. Further, WECC determined that in each instance, WECC_URE2 revoked access to the user account on the same day unapproved access was granted. | WECC determined that the issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because each instance spanned a period of 24 hours. Two of the individuals involved completed cyber security training and the personnel risk assessments prior to receiving user account access. Each of the three individuals in scope required access to the user accounts. The devices that could be accessed through the user accounts were all secured within an Electronic Security Perimeter (ESP) and Physical Security Perimeters (PSPs). All access to the Cyber Assets and Critical Cyber Assets was logged and monitored. The ESP and PSP were set to alarm security personnel in the event of unauthorized access attempts or security events. | WECC_URE2 revoked the individual’s access to a user account after discovering that access had been granted without the requisite approval. WECC_URE2 revoked the individual’s access to a user account after discovering that access had been granted without requisite approval. WECC_URE2 revoked the individual’s access to a user account after discovering that access had been granted without requisite approval. WECC_URE2 retrained personnel on access procedures.
2012-09-28 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2012010738 | CIP-005-1 | R2 | During a Compliance Audit of WECC_URE3, the Audit team determined that WECC_URE3 failed to display a warning banner (i.e., an appropriate use banner) on access points to Electronic Security Perimeters (ESP) for interactive access prior to login. Pursuant to the Standard, all attempts of interactive access must display an appropriate use banner upon access and prior to successful login. As documented in WECC_URE3’s access point configuration files and as validated through physical observation during site visits, the access points have only defined the command which does not display the banner as part of the initial user access prior to login. Based on this, WECC determined WECC_URE3’s configuration is incorrect for not displaying the appropriate use banner prior to login. WECC further determined WECC_URE3 could not demonstrate that the configuration for these access points had been correct since the mandatory compliance date of CIP-005-1. | WECC determined that this issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because, WECC_URE3 has defined processes and procedures for granting access, which include strict access controls to Critical Cyber Assets. Additionally, WECC_URE3 has active monitoring and automatic alert mechanisms, as well as physical separation from external access through the use of firewall technology. Finally, WECC_URE3 did have appropriate use banners on the majority of its electronic access devices, however, in this instance, WECC_URE3 configured the devices to display the appropriate use banner after a user logged into the system and not upon all interactive access attempts. | WECC_URE3 configured the devices to display the appropriate use banner upon interactive access attempts. Specifically, WECC_URE3 configured the devices to display the appropriate use banner prior to access attempts. WECC_URE3 further maintains a document identifying the content of the banner.
2012-09-28 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC2012010307 | CIP-007-3 | R3 | During WECC_URE4’s on-site compliance Audit, the WECC Audit Team reviewed compliance with CIP-007-3 R3. During the course of the Audit, the Audit Team discovered that WECC_URE4 failed to document the assessment of two security patches within 30 calendar days of availability. The Audit team reviewed the assessment of 35 applicable patches for WECC_URE4. Of the 35 security patches, two were reviewed and assessed later than 30 days. Specifically, the vendor released patches on for the identification of potential security vulnerabilities. WECC_URE4 received the patch information but failed to document the correct release date. Consequently, WECC_URE4 failed to assess and install the security patches until four days and seven days after the 30 day requirement had lapsed. | WECC determined that the issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because WECC_URE4 did establish and implement a security patch management program and a configuration management process for all system patches. The two security patches addressed herein were reviewed for applicability within a week after the 30 day requirement, and the Audit team determined that the assessment of security patches were up to date. The assets in scope are protected within WECC_URE4’s Electronic Security Perimeters and Physical Security Perimeters, and have 24 hour a day logging and monitoring. | WECC_URE4 reviewed, assessed and installed the security patch applications. WECC_URE4's patch management process was reviewed and updated as follows: 1. The review of the Supervisory Control and Data Acquisition (SCADA) vendor patch report will no longer be considered during the assessment of security patches for applicability. 2. SCADA vendor patch reports will be referenced during the testing phase of the patch management process. 3. The documented results of patch management meetings will be reviewed and signed-off by two Emergency Management System (EMS) personnel. 4. The training of applicable staff on new/updated patch process.
2012-09-28 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 5 (WECC_URE5) | NCRXXXXX | WECC2012009101 | CIP-007-1 | R4 | WECC_URE5 submitted a Self-Report addressing possible noncompliance with CIP-007-1 R4. Specifically, WECC_URE5 reported that it failed to use anti-virus software or other malware prevention tools on 64 firewalls and 361 routers and switches within 50 Electronic Security Perimeters (ESPs). Upon further review, WECC_URE5 determined there are no anti-virus applications available for the operating systems associated with the Cyber Assets and, as a result, submitted two late-filed TFEs addressing technical infeasibility with CIP-007-1 R4. | WECC determined that the issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because WECC_URE5’s noncompliance is limited given compensating measures that were in place prior to the due date on which all TFE requests were to originally be submitted to WECC. Specifically, the Cyber Assets are located in an ESP and have technical and procedural mechanisms for control of electronic access at all access points. Also, all devices are located within a Physical Security Perimeter (PSP) and have technical and procedural controls to manage physical access to the PSPs including 24 hour a day, seven day a week logging and monitoring of physical access. Additionally, WECC_URE5 requires username and passwords on all Critical Assets and uses a passive triggering mechanism to monitor any changes. | WECC_URE5 submitted a Mitigation Plan for CIP-007-1 R4. WECC_URE5 submitted two TFEs for the 425 assets in scope. WECC_URE5’s plan requires the development and implementation of training for personnel supporting and maintaining assets in scope for NERC-CIP requirements. This training will ensure that the appropriate personnel have an appropriate understanding of TFEs that includes training on submission of timely TFEs. WECC approved the late filed TFEs associated with CIP-007-1 R4 network devices.
2012-08-31 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2011007636 | CIP-002-2 | R3 | FRCC_URE1 self-reported an issue with CIP-002-1 R3. Specifically, three Cyber Assets that were incorrectly identified as Critical Cyber Assets (CCAs) did not reside in the Electronic Security Perimeter (ESP). Additionally, one CCA was well-secured within the ESP but was not listed on the CCA list, resulting in an issue with CIP-002-3 R3. This issue existed for approximately thirteen months, until the CCA list was corrected. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because FRCC_URE1 only failed to document the list accurately and the CCA which was left off of the CCA list was within the secured ESPs and afforded the protections required for CCAs under the NERC CIP Standards. FRCC_URE1 also included three corporate workstations on the CCA list that were neither CCAs nor resided in the ESP. The error was documentary in nature and did not cause significant risk to BPS reliability because these Cyber Assets had no applications installed on them that could impact BPS reliability. | To mitigate this issue, FRCC_URE1 updated its risk-based assessment methodology (RBAM) to re-evaluate and reapply risk-based criteria based on recently approved NERC Critical Asset selection criteria. FRCC_URE1 also updated and corrected its list of associated CCAs.
2012-08-31 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 2 (FRCC_URE2) | NCRXXXXX | FRCC2012010599 | CIP-002-1 | R4 | During a FRCC CIP Compliance Audit, it was determined that FRCC_URE2 did not maintain a null list of Critical Cyber Assets (CCAs) and did not obtain the required signature of the senior manager, resulting in an issue with CIP-002-1 R4. Specifically, beginning on the mandatory and enforceable date of the Standard, FRCC_URE2's risk-based assessment methodology (RBAM) included a documented Critical Asset (CA) null list and this document contained the senior manager's typed name, but not the ink signature. This version of FRCC_URE2's RBAM also did not contain a null list of CCAs, as required by the Standard. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because FRCC_URE2 documented the null list with no CAs but failed to document the null list with no CCAs. With respect to the signature requirement, a typed name was in the signature block, but was not an ink signature until the RBAM was revised. This issue resulted from lack of documentation, as FRCC_URE2 has no CAs or CCAs. | To mitigate this issue, FRCC_URE2 created the CCA null list and obtained the senior manager's signed and dated approval. Additionally, FRCC_URE2 scheduled the review of the future application of its RBAM and its results.
2012-08-31 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2012010126 | CIP-007-3 | R5; R5.3.3 | MRO_URE1 self-reported an issue with CIP-007-3 R5.3.3 for failing to ensure that Critical Cyber Asset (CCA) passwords were changed at least annually. MRO_URE1 uses a custom script to report the status of account passwords (expired, locked, or OK). The script incorrectly reported the status of two CCA user accounts as being "locked," when in fact they were not. The CCAs had an operating system automatic lock by means of password expiration. However two accounts did not have this expiration enabled and therefore were still accessible without an annual password change. | MRO determined that this issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although the two affected shared accounts did not have their passwords changed in the calendar year, both of the accounts had limited privileges and neither account had administrative privileges. The accounts are only used to launch the energy management system console applications, which require additional application-specific login credentials. Additionally, the account passwords were unchanged for less than two months (54 days) after expiration of the "annual" (once per calendar year) window. | MRO_URE1 performed a manual review of the database. The two user accounts were updated. The coding error within the custom script was identified and corrected. MRO verified that MRO_URE1 completed its mitigation activities.
2012-08-31 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2011008450 | CIP-006-3a | R2.2 | NPCC_URE1 self-reported an issue with CIP-006-3a R2.2. NPCC_URE1 has a management services agreement pursuant to which a third party company serves as agent for NPCC_URE1 to perform reliability compliance functions and monitoring associated with NPCC_URE1's responsibilities as a NERC Registered Entity. During a NPCC CIP Compliance Audit of the third party's affiliate, it was determined that the third party, on behalf of NPCC_URE1, failed to timely perform a cyber vulnerability assessment for the servers that are involved with the physical access control system (PACS), as specified in CIP-007-3 R8. All other required assessments for NPCC_URE1's assets were completed, but a cyber vulnerability assessment had never been performed on the servers by the second quarter of 2010 as required by the Standard. The cyber vulnerability assessment was performed six months later. The third party company's parent company performs vulnerability assessments on a corporate level. Failure to complete the vulnerability assessment, as described above, affected multiple registered entities, including NPCC_URE1. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the servers at issue are not used to monitor or control BPS assets. They control the card-reader system that is utilized to control the Physical Security Perimeter's (PSP) physical access points. In addition to the card-reader system, NPCC_URE1 utilizes security guards and video cameras to monitor access to the PSP. NPCC_URE1 also has strict controls in place for providing physical access to Critical Cyber Assets. | To mitigate this issue, the third party company, acting as the agent for NPCC_URE1, completed the vulnerability assessment for the servers at issue and revised its compliance assessment process document.
2012-08-31 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 2 (NPCC_URE2) | NCRXXXXX | NPCC2012010670 | CIP-006-3a | R1; R1.7 | NPCC_URE2 self-reported an issue with CIP-006-3a R1.7. Specifically, NPCC_URE2 failed to update the physical security plan within 30 calendar days of the completion of any physical security system redesign or reconfiguration. The physical security plan was updated 155 days past the 30-day requirement. The issue was discovered while performing the "extent of condition analysis milestone" for a Mitigation Plan associated with another NPCC_URE2 subsidiary. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the issue was administrative in nature. NPCC_URE2 updated the physical security plan, as required by the Standard, but did not do so within the specified time frame. In addition, all physical access control devices that provide access control, monitoring, and logging at the designated Physical Security Perimeters (PSPs) were functioning and operating properly. | To mitigate this issue, NPCC_URE2 updated its physical security plan to include that the physical security plan will be signed by the appropriate delegate for CIP-006. NPCC_URE2 also updated its corporate security workflow documentation for CIP-006 R1.7 to include a notification to the appropriate employee, as a checkpoint, when a physical security configuration change ticket is closed out for any physical security reconfiguration or redesign of PSPs at designated Critical Assets. NPCC_URE2 conducted an extent of condition analysis of PSPs at designated Critical Assets to determine whether there are other instances in which the physical security plan was not updated within 30 days following a reconfiguration or redesign change. NPCC_URE2 did not identify any additional issues in this analysis. NPCC_URE2 has communicated via email and conducted training with the applicable business areas regarding the changes to the enterprise physical security plan implemented by this Mitigation Plan.
2012-08-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2012009848 | CIP-004-3 | R4 | RFC_URE1 self-reported an issue with CIP-004-3 R4 to ReliabilityFirst. A RFC_URE1 employee transferred from a position that required authorized cyber and authorized unescorted physical access to Critical Cyber Assets (CCAs) to a position that did not require such access. RFC_URE1's access revocation process is initiated by a Human Resource notification generated when RFC_URE1 updates an employee’s personnel record to reflect a transfer. RFC_URE1 had revoked the employee’s authorized cyber access. Due to the employee’s transfer occurring on a holiday; RFC_URE1 did not update the personnel record that would initiate the access revocation process until three days after RFC_URE1 was required to revoke physical access. Upon discovery of the failure to revoke authorized unescorted physical access RFC_URE1 revoked such access. | ReliabilityFirst determined that this issue posed a minimal risk and not a serious or substantial risk to the reliability of the bulk power system. The RFC_URE1 employee transferred to a new position within the company and was still subject to its parent company's Code of Conduct and Corporate Policy for Cyber Security. Furthermore, prior to the time period of the issue, the employee had a valid personnel risk assessment as well as cybersecurity training. Finally, the employee did not physically access the CCAs during the time period of the issue, and RFC_URE1 timely revoked the employee’s authorized cyber access. | RFC_URE1 provided refresher training to all human resource consultants responsible for initiating transfer employee access revocation and established an electronic reporting mechanism, which will reduce the manual intervention by multiple individuals and therefore reduce the risk of a repeat occurrence.
2012-08-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2012001320 | CIP-004-3 | R4 | RFC_URE2 self-reported an issue with CIP-004-3 R4 to ReliabilityFirst. The day after an employee resigned, RFC_URE2 revoked this employee’s authorized cyber and authorized unescorted physical access to Critical Cyber Assets (CCAs), within the seven calendar days required. However, RFC_URE2 failed to update its authorized access list for several CCAs to reflect that this employee no longer had cyber access to CCAs. Eight days later, RFC_URE2 removed this employee from the authorized access list, as required by R4.1. | ReliabilityFirst determined that this issue posed a minimal risk and not a serious or substantial risk to the reliability of the bulk power system (BPS). The risk to the BPS was mitigated by the following factors. RFC_URE2 timely revoked the employee’s authorized cyber and authorized unescorted physical access to all CCAs. Thus, the employee had no ability to gain access to CCAs. In addition, the employee was not terminated for cause. | RFC_URE2 removed the employee from the authorized access list. In addition, RFC_URE2 counseled the individual's supervisor on the responsibilities for tickets submitted to process employee retirement, resignation, termination and displacement. Furthermore, RFC_URE2 enhanced its security request system to improve the timing and visibility of access removal requests. RFC_URE2 then communicated all improvements to the affected supervisors.
2012-08-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC2012009854 | CIP-004-3 | R4 | RFC_URE3 self-reported an issue with CIP-004-3 R4 to ReliabilityFirst. RFC_URE3 initially verbally self-reported this issue but seven days later memorialized this Self-Report in a Self-Report Form. The day after an employee retired, RFC_URE3 revoked this employee’s authorized cyber and authorized unescorted physical access to Critical Cyber Assets (CCAs), within the seven calendar days required. However, RFC_URE3 failed to update its shared account authorized access list for one CCA to reflect that this employee no longer had access to the CCA. The CCA at issue is used for plant operation twenty-four hours a day and is typically logged on at all times to facilitate plant operation. RFC_URE3 discovered this issue during the quarterly verification of the authorized access list and removed this employee from the list approximately six weeks after his retirement date, as required by R4.1. | ReliabilityFirst determined that this issue posed a minimal risk and not a serious or substantial risk to the reliability of the bulk power system (BPS). The risk to the BPS was mitigated by the following factors. RFC_URE3 timely revoked the employee’s authorized cyber and authorized unescorted physical access to all CCAs, including the one at issue. In addition, RFC_URE3 timely changed the password to the shared account for the CCAs at issue. Thus, the employee had no ability to gain access to the CCA. In addition, the employee retired and was not terminated for cause. Furthermore, the CCA at issue is typically logged on at all times to facilitate plant operation. Therefore, it was less likely that the employee’s name remaining on the access list would have caused unauthorized logons to the CCAs. | RFC_URE3 removed the employee from the authorized access list. In addition, RFC_URE3 updated the existing email distribution list in use for automatic notification of applicable employment status changes to include appropriate generation technical services compliance personnel. This revision will ensure that such individuals receive notice of employment status changes which will enable them to ensure the required updating of the authorized access lists.
2012-08-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 4 (RFC_URE4) | NCRXXXXX | RFC2012010023 | CIP-007-3 | R5 | RFC_URE4 self-reported an issue with CIP-007-3 R5.3 to ReliabilityFirst. RFC_URE4 discovered that it did not change the passwords on 2 server accounts and 46 database accounts at least annually. RFC_URE4 determined that it incorrectly classified the servers as user accounts in its password database and missed the servers in its annual change activity. RFC_URE4 determined it failed to implement the procedure it has in place to initiate password changes for the 46 database accounts. | ReliabilityFirst determined that this issue posed a minimal risk and not a serious or substantial risk to the reliability of the bulk power system (BPS). The risk to the BPS was mitigated by the following factors. Neither the 2 server accounts nor the 46 database accounts are related to assets supporting real-time control or monitoring functions. Additionally, both systems associated with the passwords at issue exist within an Electronic Security Perimeter (ESP) which requires separate active directory user accounts to gain access. Additionally, the directory user accounts necessary to gain access to the ESP expire on a 45-day cycle, resulting in multiple password changes to the directory user accounts during the duration of the issue. | In its Self-Report, RFC_URE4 stated that it had already changed, disabled and/or removed the passwords at issue. Additionally, RFC_URE4 revised its internal procedure to conduct password changes every six months, thereby decreasing the likelihood of exceeding the annual timeframe required by CIP-007-3 R5.
2012-08-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 5 (RFC_URE5) | NCRXXXXX | RFC2012009858 | CIP-006-3c | R1.6.2 | RFC_URE5 self-reported an issue with CIP-006-3c R1.6 to ReliabilityFirst. RFC_URE5 did have a visitor control program for visitors and a log to document the entry and exit of visitors, as required by R1.6; however, RFC_URE5 discovered that four individuals, three contractors and one employee (Employee), were not continuously escorted while inside a Physical Security Perimeter (PSP) for approximately 30 minutes on a single day. The Employee continuously escorted the three contractors; however, the Employee did not have authorized unescorted access to the PSP at issue. ReliabilityFirst determined the issue with CIP-006-3c R1 did not evidence an issue of CIP-004-3. CIP-004-3 sets forth personnel and training requirements for individuals with access to Critical Cyber Assets (CCAs). RFC_URE5’s issue with CIP-006-3c R1 involved only Cyber Assets, not CCAs. | ReliabilityFirst determined that this issue posed a minimal risk and not a serious or substantial risk to the reliability of the bulk power system (BPS). The risk to the BPS was mitigated by the following factors. At the time of the issue, the PSP at issue was in the process of being decommissioned and did not enclose an Electronic Security Perimeter (ESP) or any active Cyber Assets. The PSP at issue contained Cyber Assets that had been removed from an ESP and were in storage until RFC_URE5 completed the disposal process. Also, prior to the Employee escorting the three contractors within the PSP, the Employee completed CIP training and RFC_URE5 performed a personnel risk assessment that revealed no issues that would preclude RFC_URE5 from granting the Employee access to the PSP at issue. The Employee qualified for authorized access to the PSP and, prior to the issue, RFC_URE5 properly granted the Employee unescorted physical access to other nearby PSPs. Furthermore, RFC_URE5 has a physical security plan and visitor control program that requires escorted access of visitors. This was an isolated incident in which the Employee and Employee's supervisor mistakenly believed the Employee was authorized to serve as an escort in the PSP at issue because the Employee was authorized to serve as an escort in surrounding PSP. RFC_URE5 conducted training, prior to and during the duration of the issue, on appropriate visitor control to help ensure compliance with CIP-006-3c R1.6. | RFC_URE5 subsequently granted the Employee access to the PSP at issue shortly after the issue. RFC_URE5 also provided the Employee with refresher training and feedback regarding RFC_URE5’s visitor control program.
2012-08-31 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2012010122 | CIP-002-1 | R1 | During an audit, SERC determined that SERC_URE1 failed to provide evidence of procedures and evaluation criteria for its risk-based assessment methodology (RBAM) that was in place at the beginning of the compliance period in accordance with CIP-002-1 R1. SERC requested and reviewed additional information from SERC_URE1 in order to complete its assessment. SERC_URE1's initial RBAM consisted of printed copies of Standard CIP-002-1 with handwritten notes indicating that SERC_URE1 did not own assets listed in each of the R1.2 sub-requirements, and handwritten dates indicating review of the printed copy of CIP-002-1 and the hand-written notes. Based on this assessment, SERC_URE1 identified no Critical Assets. SERC staff determined that this document did not meet the requirements of CIP-002 R1. SERC_URE1 developed a RBAM that meets the requirements of CIP-002-3 R1. | SERC determined that the issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because: 1. SERC_URE1 conducted an assessment to determine Critical Assets each year, even though it did not include evaluation criteria as required by the Standard; and 2. SERC_URE1 has no Critical Assets and does not own or operate any facilities that would meet any of the Critical Asset criteria set forth in CIP-002-4. | SERC verified that SERC_URE1 completed the following actions: SERC_URE1 implemented a RBAM that meets the requirements of CIP-002-3 R1.
2012-08-31 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 2 (SERC_URE2) | NCRXXXXX | SERC200900345 | CIP-004-1 | R4 | The SERC spot check team reported an issue with CIP-004-1 R4, stating that SERC_URE2 could not provide evidence that it maintained lists of personnel with authorized cyber or authorized unescorted physical access to Critical Cyber Assets (CCAs) going back to when it was required to comply with the Standard. SERC_URE2 provided SERC with quarterly reviews of personnel with authorized cyber or authorized unescorted physical access to CCAs for the second, third, and fourth quarters of the year it was required to comply with the Standard. These quarterly reviews demonstrated that SERC_URE2 did not update its access lists in a timely manner and missed 30.93% of the total personnel. SERC_URE2 stated that the 30.93% of the individuals missing from the lists were authorized and had completed Personal Risk Assessments (PRA) and CIP cyber security training. SERC_URE2 provided evidence that PRAs had been conducted for sampled personnel and provided CIP cyber security training records for sampled personnel. Additionally, SERC_URE2 provided evidence showing that the missing individuals were accounted for and on a managed access list for the applicable individuals. | SERC determined that the issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because: SERC_URE2 had authorized cyber or unescorted physical access to the 30 missing personnel and they had valid PRAs and CIP cyber security training. | SERC verified that SERC_URE2 completed the following actions: 1. Established a new written procedure that describes how the quarterly review of the list for access to Critical Cyber Assets located at a Control Center is to be conducted; 2. Under the new written procedure, the quarterly review of the list of personnel who have access to Critical Cyber Assets will take place within 14 calendar days after the last day of the quarter; 3. As part of its quarterly review, SERC_URE2 will compare the list of those who actually have access (the print out form the server controlling the control center card access system) against the working list (a paper document kept at the control center security desk); 4. If no discrepancies are identified from this comparison, the print out from the server controlling the control center card access system will become the new working list for purposes of the next quarter; 5. If a discrepancy is identified, the discrepancy will be resolved to assure that physical access is granted only to those employees who need daily access to the control center and who have completed the required personnel risk assessment and training. The new working list for purposes of the next quarter will reflect the resolution of these discrepancies; and 6. The first quarterly review portion of this procedure was completed.
2012-08-31 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 3 (SERC_URE3) | NCRXXXXX | SERC2011008613 | CIP-002-1 | R1 | During an audit, SERC determined that SERC_URE3 had failed to develop a sufficient risk-based assessment methodology (RBAM) for determining whether or not it had Critical Assets that included all of the requirements in accordance with CIP-002-1 R1. The documentation provided by SERC_URE3 to demonstrate its compliance with CIP-002-1 R1 failed to describe a RBAM that included procedures and evaluation criteria for identifying Critical Assets and failed to address the assets in R1.2.1 through R1.2.7 and how SERC_URE3 would evaluate whether any such assets should be considered Critical Assets in the event SERC_URE3 acquired them. | SERC determined that the issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because: 1. SERC_URE3 has no Critical Assets and does not own or operate any facilities that would meet any of the Critical Asset Criteria set forth in CIP-002-4. | SERC staff verified that SERC_URE3 completed the following actions: SERC_URE3 developed a RBAM that includes procedures and evaluation criteria for identifying Critical Assets and addresses all the assets identified in CIP-002-1 R1.
2012-08-31 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 3 (SERC_URE3) | NCRXXXXX | SERC2011008614 | CIP-003-1 | R2 | During an audit, SERC determined that SERC_URE3 failed to provide evidence assigning a senior manager with overall responsibility for leading and managing SERC_URE3's implementation of, and adherence to, Standards CIP-002-1 to CIP-009-1 in accordance with CIP-003-1 R2 for approximately three years. SERC_URE3 provided documentation demonstrating that it had authorized the signing of documents on behalf of SERC_URE3 by senior vice-presidents for SERC and NERC matters and identified a single point of contact for the SERC_URE3 internal compliance program, but the documentation did not demonstrate that SERC_URE3 had assigned a senior manager responsible for leading and managing SERC_URE3's implementation of, and adherence to, Standards CIP-002 through CIP-009 for approximately three years. | SERC determined that the issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because: 1. SERC_URE3 had identified a senior manager as its single point of contact for the SERC_URE3 utilities program. This single point of contact was responsible for approving the risk-based methodology, list of Critical Assets, and list of Critical Cyber Assets; and 2. SERC_URE3 has no Critical Assets and does not own or operate any facilities that would meet any of the Critical Asset criteria set forth in CIP-002-4. | SERC verified that SERC_URE3 completed the following actions: SERC_URE3 assigned a senior manager with overall responsibility for leading and managing SERC_URE3's implementation of, and adherence to, Standards CIP-002 to CIP-009.
2012-08-31 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 3 (SERC_URE3) | NCRXXXXX | SERC2012010547 | CIP-002-1 | R4 | SERC_URE3 self-reported an issue with CIP-002-1 R4, stating that a SERC_URE3 employee approved the risk-based assessment methodology (RBAM), the null list of Critical Assets, and the null list of Critical Cyber Assets prior to being designated as the senior manager with overall responsibility for leading and managing SERC_URE3's implementation of, and adherence to, Standards CIP-002 through CIP-009. This Self-Report was submitted in response to an inquiry from SERC staff during an assessment of a separate enforcement action. SERC determined that SERC_URE3 did not formally assign a senior manager with overall responsibility for leading and managing SERC_URE3's implementation of, and adherence to, CIP-002 through CIP-009 for approximately three years. Accordingly, all of SERC_URE3's approvals of its RBAM, Critical Asset list, and Critical Cyber Asset list prior to the designation of a senior manager were not in compliance with the relevant Reliability Standards. | SERC determined that the issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because: 1. SERC_URE3 had identified a senior manager as its single point of contact for the SERC_URE3 utilities program. This single point of contact was responsible for approving the risk-based methodology, list of Critical Assets, and list of Critical Cyber Assets; and 2. SERC_URE3 has no Critical Assets and does not own or operate any facilities that would meet any of the Critical Asset criteria set forth in CIP-002-4. | SERC verified that SERC_URE3 completed the following actions: SERC_URE3's newly appointed senior manager with overall responsibility for leading and managing SERC_URE3's implementation of, and adherence to, Standards CIP-002 through CIP-009 signed and approved SERC_URE3's RBAM, Critical Asset list, and Critical Cyber Asset list.
2012-08-31 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 4 (SERC_URE4) | NCRXXXXX | SERC2012010138 | CIP-002-3 | R2 | During an audit, SERC determined that SERC_URE4 failed to provide evidence of a Critical Asset list determined through its annual application of the risk-based assessment methodology (RBAM) in accordance with CIP-002-3 R2. SERC reviewed documents provided by SERC_URE4 and determined that SERC_URE4 had RBAMs from three prior years. The three prior years' RBAMs stated that SERC_URE4 had no Critical Assets and no Critical Cyber Assets (CCAs). SERC staff determined that SERC_URE4 could not provide evidence it developed its list of Critical Assets in a prior year. | SERC determined that the issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because: 1. SERC_URE4 has no Critical Assets and does not own or operate any facilities that would meet any of the Critical Asset criteria set forth in CIP-002-4; and 2. SERC_URE4 applied three prior years' RBAMs, resulting in null lists for Critical Assets, indicating that SERC_URE4 did not acquire any Critical Assets in the missing year. | SERC verified that SERC_URE4 completed the following actions: 1. Completed the annual review and approval of its RBAM, including the approval of null lists for Critical Assets and CCAs; and 2. Added review dates for the annual review of its RBAM, Critical Assets, and CCAs and required approvals to calendar reminders for the responsible parties.
2012-08-31 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 4 (SERC_URE4) | NCRXXXXX | SERC2012010139 | CIP-002-3 | R3 | During an audit, SERC determined that SERC_URE4 failed to provide evidence of an associated list of Critical Cyber Assets (CCAs) derived from its list of Critical Assets in a prior year in accordance with CIP-002-3 R3. SERC reviewed documents provided by SERC_URE4 and determined that SERC_URE4 had risk-based assessment methodologies (RBAMs) from three prior years. The three prior years' RBAMs stated that SERC_URE4 had no Critical Assets and no CCAs. SERC staff determined that SERC_URE4 could not provide evidence that it had developed a list of CCAs in a prior year. | SERC determined that the issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because: 1. SERC_URE4 has no Critical Assets and does not own or operate any facilities that would meet any of the Critical Asset criteria set forth in CIP-002-4; and 2. SERC_URE4 applied three prior years' RBAMs, resulting in null lists for Critical Assets and CCAs, indicating that SERC_URE4 did not acquire any Critical Assets or CCAs in the missing year. | SERC verified that SERC_URE4 completed the following actions: 1. Completed the annual review and approval of its RBAM, including the approval of null lists for Critical Assets and CCAs; and 2. Added review dates for the annual review of its RBAM, Critical Assets, and CCAs and required approvals to calendar reminders for the responsible parties.
2012-08-31 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 4 (SERC_URE4) | NCRXXXXX | SERC2012010140 | CIP-002-2 | R4 | During an audit, SERC determined that SERC_URE4 failed to present a signed and dated record of the Senior Manager or delegate’s approval of the risk-based assessment methodology (RBAM), the list of Critical Assets, and the list of Critical Cyber Assets (CCAs) for a calendar year in accordance with CIP-002-2 R4. SERC reviewed documents provided by SERC_URE4 and determined that SERC_URE4 failed to approve the RBAM, the list of Critical Assets, and the list of CCAs for one year. SERC staff determined that SERC_URE4 personnel signed the null list of Critical Assets and the null list of CCAs in three prior years. Despite this fact, the individuals signing these lists in two prior years were not valid signers because they had not been assigned responsibility in writing for SERC_URE4's compliance with the CIP standards as required by CIP-003 R2. Therefore, SERC_URE4's issue with CIP-002 R4 extended back to when SERC_URE4 was required to be compliant with the Standard. Also, the RBAM was not approved in two prior years as required by versions 2 and 3 of the Standard. | SERC determined that the issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because: 1. SERC_URE4 has no Critical Assets and does not own or operate any facilities that would meet any of the Critical Asset criteria set forth in CIP-002-4; and 2. SERC_URE4 applied three prior years' RBAMs, resulting in null lists for Critical Assets and CCAs, indicating that SERC_URE4 did not acquire any Critical Assets or CCAs in the missing year. | SERC verified that SERC_URE4 completed the following actions: 1. Completed the annual review and approval of its RBAM, including the approval of null lists for Critical Assets and CCAs; 2. Added review dates for the annual review of its RBAM, Critical Assets, and CCAs and required approvals to calendar reminders for the responsible parties; and 3. Reformatted the RBAM signoff to incorporate an approval signature.
2012-08-31 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 4 (SERC_URE4) | NCRXXXXX | SERC2012010141 | CIP-003-2 | R2 | During an audit, SERC determined that SERC_URE4 failed to provide evidence showing that the designated senior manager was assigned the role at the beginning of the compliance period in accordance with CIP-003-2 R2. SERC reviewed documents provided by SERC_URE4 and determined that SERC_URE4 did not properly assign a Senior Manager with overall responsibility and authority for leading and managing SERC_URE4's implementation of, and adherence to the CIP Standards. However, because SERC_URE4 identified that it had no Critical Cyber Assets in a prior year it was exempt from compliance with CIP-003-1 R2, and was only required to be compliant when CIP-003-2 R2 became effective. | SERC determined that the issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because: 1. SERC_URE4 has no Critical Assets and does not own or operate any facilities that would meet any of the Critical Asset criteria set forth in CIP-002-4; and 2. SERC_URE4 applied three prior years' RBAMs, resulting in null lists for Critical Assets and CCAs, indicating that SERC_URE4 did not acquire any Critical Assets or CCAs in the missing year. | SERC verified that SERC_URE4 completed the following actions: Created a document that properly defines the single CIP Senior Manager by title, name, and date of designation.
2012-08-31 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 5 (SERC_URE5) | NCRXXXXX | SERC2012010638 | CIP-003-3 | R2 | SERC_URE5 self-reported an issue with CIP-003-3 R2, stating that SERC_URE5 did not designate a new senior manager within 30 days of the departure of SERC_URE5's previous senior manager. SERC requested and reviewed documentation of SERC_URE5's designation of the senior manager. SERC_URE5 provided documentation showing that a senior manager was designated and documented, but the senior manager left unexpectedly approximately seven months later. SERC_URE5 failed to formally assign a new senior manager until 193 days later, but did have a plant manager acting as the CIP senior manager during this period. SERC_URE5 also provided a document detailing its leadership designation program, which requires the identification of the senior manager, delegates, and any changes to the senior manager be documented within 30 calendar days of the effective date. SERC_URE5's leadership designation program stated that there were no exceptions identified for its cyber security policy. SERC_URE5 also confirmed that it had not assigned any delegates. SERC found that SERC_URE5 had a documented program in place that met the intent of the Requirement but that SERC_URE5 had failed to comply with its documented program. | SERC determined that the issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because: 1. SERC_URE5 had a plant manager acting as the CIP senior manager during the period in question even though he was not officially delegated; and 2. SERC_URE5 has no Critical Assets and does not own or operate any facilities that would meet any of the Critical Asset criteria set forth in CIP-002-4. | SERC verified that SERC_URE5 completed the following actions: 1. SERC_URE5 designated a new senior manager; and 2. SERC_URE5 placed a transfer note with instructions in the plant manager's personnel file stating that he is the senior manager with responsibility for the CIP standards and instructing the plant manager to properly transfer the senior manager duties to an appropriate plant staff member upon transfer, retirement, or other long-term change in status with the facility.
2012-08-31 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 5 (SERC_URE5) | NCRXXXXX | SERC2012010676 | CIP-002-1 | R4 | SERC_URE5 self-reported an issue with CIP-002-1 R4, stating that SERC_URE5 failed to have a senior manager or delegate(s) annually approve the list of Critical Assets and Critical Cyber Assets (CCAs) in two prior years. SERC requested and reviewed additional information in order to complete its assessment. SERC found that SERC_URE5 applied its established risk-based assessment methodology (RBAM) to all associated assets, resulting in null lists for Critical Assets and CCAs. SERC_URE5’s senior manager failed to sign and date the Critical Asset and CCA list for two prior years. SERC_URE5's senior manager signed the RBAM for four consecutive years. SERC_URE5's senior manager approved and signed the Critical Asset and CCA lists, which were null, for two prior years. | SERC determined that the issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because: 1. SERC_URE5's senior manager approved and signed the RBAM; and 2. SERC_URE5 has no Critical Assets and does not own or operate any facilities that would meet any of the Critical Asset criteria set forth in CIP-002-4. | SERC verified that SERC_URE5 completed the following actions: 1. Hired a third party to replace SERC_URE5's existing compliance program with a new reliability compliance program; 2. Used the new reliability compliance program to determine and document if SERC_URE5 had any Critical Assets or CCAs; 3. Had the senior manager sign the RBAM, Critical Asset list, and CCA list for two prior years; and 4. Filed documentation appropriately at the facility as evidence of compliance.
2012-08-31 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP201000247 | CIP-004-1 | R3 | During a Multi-Region Spot Check, SPP RE determined that SPPRE_URE1 had an issue with CIP-004-1 R3 for a failure to perform personnel risk assessments (PRAs) to all personnel with unescorted physical access to Critical Cyber Assets (CCAs). The Spot Check team sampled PRA records of individuals having authorized cyber or authorized unescorted physical access to SPPRE_URE1's CCAs. At the time of the Spot Check, SPPRE_URE1 had an agreement in place with Entity A, which co-owns and operates Substation A. SPPRE_URE1 owns the 115 kV assets located at Substation A, including certain assets that were, at the time of the Spot Check, deemed CCAs. The agreement provided that Entity A would perform PRAs on its employees that were granted authorized unescorted physical access to the CCAs at Substation A. SPPRE_URE1 requested and received quarterly confirmation via email that Entity A personnel with CCA access met the requirements of CIP-004-1, including the PRA requirement. One such Entity A employee was included in the group of PRA records sampled by the Spot Check team for CIP-004-1 R3 compliance. When SPPRE_URE1 requested PRA documentation from Entity A for that employee, Entity A informed SPPRE_URE1 that the PRAs had not been performed for the fifteen Entity A employees with authorized unescorted physical access to Substation A and that the quarterly emails verifying compliance had been provided in error. As a result, SPPRE_URE1 did not comply with CIP-004-1 R3 because it did not ensure that PRAs were performed for all personnel with authorized unescorted physical access to CCAs. | SPP RE determined that the issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Although Entity A did not perform PRAs on its employees who were granted access to the Entity A / SPPRE_URE1 substation that housed SPPRE_URE1's CCAs, the access that the Entity A employees had was physical only. The Entity A employees did not have electronic access to the CCAs – the devices were only accessible by dial-up and used non-routable protocols. According to a NERC CIP-006-1 interpretation, because there is minimal risk of compromising other CCAs, dial-up devices that use non-routable protocols, such as the ones at issue, are not required to be enclosed within a “six-wall” physical border. Because no “six-wall” physical border is required for these devices, unescorted physical access to the devices presents a minimal risk. Therefore, SPP RE determined that the unescorted physical access to the SPPRE_URE1's devices at issue presented a minimal risk to the reliability of the BPS. | When SPPRE_URE1 determined that Entity A had not complied with its agreement with SPPRE_URE1, immediate action was taken to remove physical access for all Entity A employees pending implementation of other measures. That physical access was removed shortly after the issue was identified during the Spot Check and before the day was over. Subsequently, SPPRE_URE1 removed the modem and the dial-up telephone line connection to the CCAs; therefore, the devices at the substation in question were no longer CCAs. SPPRE_URE1 subsequently updated the status of these devices on the CCA list to non-critical. A new agreement was executed between SPPRE_URE1 and Entity A specifying that the parent company for SPPRE_URE1 will perform PRA's for Entity A employees or contractors requiring access to CCAs in SPPRE_URE1 substations. SPP RE verified completion of these mitigating activities.
2012-08-31 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPPRE_URE2) | NCRXXXXX | SPP2012009412 | CIP-005-3a | R2; R2.2 | SPPRE_URE2 self-certified a noncompliance of CIP-005-3a R2.2 for a failure to enable only ports and services required for operations and for monitoring Cyber Assets (CAs) within the Electronic Security Perimeter (ESP). SPPRE_URE2 reported that two of its Unified Threat Management (UTM) devices, which acted as routers and as access points to an ESP, had ports open that were not specific to the operation and monitoring of CAs within the ESP. | SPP RE determined that the issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The UTM devices were connecting a control center ESP with another control center ESP via a private microwave link owned and operated by SPPRE_URE2. The UTMs were not linked to the outside world and only connected the control center ESPs, thereby reducing the risk to minimal. | After discovery of the open ports on the two UTM network devices, SPPRE_URE2 reviewed documentation concerning the ports and services to the UTMs, made modifications to the configuration files, uploaded new configurations to the UTMs in the test environment, and ran the complete system for 48 hours to ensure the new configurations did not affect the test system and that the test system operated in a reliable manner. Once the 48-hour window of testing was complete, SPPRE_URE2 loaded the newly tested configuration to the live system UTMs. SPPRE_URE2 successfully uploaded the new configuration and the EMS/SCADA system operated in a reliable manner.
2012-08-31 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 3 (SPPRE_URE3) | NCRXXXXX | SPP2012009923 | CIP-003-3 | R1; R1.1 | During a SPP RE CIP Audit of SPPRE_URE3 the SPP RE Audit team discovered an issue with CIP-003-3 R1.1 for a failure to address all of the requirements in Standards CIP-002-3 through CIP-009-3 in its cyber security policy. Specifically, SPP RE found that SPPRE_URE3 failed to address one NERC requirement CIP-003-3 R4 (information protection associated with CCAs) in its cyber security policy, which is required by CIP-003-3 R1.1. | SPP RE determined that the issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). This instance of noncompliance presented a documentation issue. Prior versions of SPPRE_URE3's cyber security policy did include all requirements in NERC Standards CIP-002 through CIP-009; the latest revision, however, failed to include the one requirement. Furthermore, while SPPRE_URE3 failed to include CIP-003-3 R4 in its cyber security policy, SPPRE_URE3 did have an implemented and documented program to identify, classify, and protect information associated with CCAs, as required by CIP-003-3 R4. | SPPRE_URE3 amended its cyber security policy to include CIP-003-3 R4. SPP RE verified completion of the mitigation activities.
2012-08-31 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE2012009949 | CIP-002-1 | R1 | During an Audit, Texas RE determined that Texas RE_URE1's documented risk-based assessment methodology (RBAM) did not include its Qualified Scheduling Entity (QSE) control centers within the scope of assets to be considered for evaluation when identifying Critical Assets (CAs), which presented an issue with CIP-002-1 R1. Texas RE_URE1 has delegated some of its responsibilities to its QSE. As a result, the QSE control centers were not included in Texas RE_URE1's RBAM used to identify CAs. Texas RE determined that the start date of this issue was from when Texas RE_URE1 was required to comply with this Standard to when Texas RE_URE1 updated its RBAM and re-performed its CAs identification with consideration given to its QSE's control centers. The identification showed that Texas RE_URE1 had no CAs. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because Texas RE_URE1 did not and does not own any CAs or Critical Cyber Assets (CCAs) at any time. The inclusion of the QSE in Texas RE_URE1 RBAM did not yield any new CAs or CCAs. Also, the QSE that was not considered does not have the ability to control the Texas RE_URE1 facility. Therefore, Texas RE determined that this issue was documentation related. | Texas RE_URE1 revised its procedures to include consideration of its QSE when performing its RBAM. Texas RE_URE1 has also re-performed its CAs identification and has determined that it does not own any CA or CCAs. Texas RE verified completion of the mitigation activities.
2012-08-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2012010360 | CIP-006-2 | R1 | During an internal review of CIP-006 compliance, WECC_URE1 self-reported an issue with CIP-006-2 R1. WECC_URE1 failed to ensure its Physical Security Plan was reviewed and approved by the CIP senior manager or delegate. While WECC_URE1 did document, implement and maintain a Physical Security Plan approved by a senior manager, it failed to implement the approval required upon the effective date of CIP-006 Version 2. WECC reviewed WECC_URE1’s Self-Report and determined the Physical Security Plan was not approved by “the” Senior Manger as required by CIP-006 R1 Versions 2 and 3. Although WECC_URE1's Physical Security Plan was approved by “a” senior manager, this was not “the” assigned Senior Manager or delegate at the time of the approval. WECC_URE1 stated that this was a result of failure to update the approval required for the Physical Security Plan upon the effective date of Version 2. Specifically, CIP-006 R1 changed from “The Responsible Entity shall create and maintain a physical security plan approved by a senior manager” in Version 1 to “The Responsible Entity shall document, implement, and maintain a physical security plan, approved by the senior manager” in Version 2. Based on the Physical Security Plan documentation, WECC_URE1 did document, implement and maintain a plan, however it failed to recognize the implications of the change in wording of the CIP-006 Standard from Version 1 to Version 2. Once identified, WECC_URE1 delegated the individual responsible for approving the CIP-006 Plan per its CIP-003 R2 senior manager assignment. WECC determined that WECC_URE1 failed to implement CIP-006-2 R1. | WECC determined this issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because even though the Physical Security Plan was not maintained and approved by the assigned CIP Manager, it was maintained and approved by the individual who is responsible for WECC_URE1’s overall corporate security. Additionally, after the noncompliance was discovered, WECC_URE1 assigned the individual as a delegate for the CIP Senior Manager. WECC determined that this was WECC_URE1's second occurrence of CIP-006 R1. Although this is WECC_URE1’s second occurrence of CIP-006 R1, WECC determined that the issue addressed herein involves different conduct. Specifically, the CIP-006 violation addressed herein is distinct from the previous CIP-006 violation in that the first violation pertained to unescorted access, whereas the current CIP-006 issue was a result of WECC_URE1 failing to update the approval required for the Physical Security Plan upon the effective date of Version 2. For these reasons, WECC determined WECC_URE1’s CIP-006 compliance history should not preclude the current CIP-006 issue from being an FFT. Therefore, WECC determined that FFT was appropriate for the current CIP-006 issue. | WECC_URE1’s Physical Security Plan approval was completed. WECC_URE1 prepared a letter of delegation, signed by the assigned CIP Senior Manager to include a delegate for the CIP Senior Manager. Further, WECC_URE1 implemented an automated tracking tool to help track due dates of recurring requirements. WECC reviewed this evidence and verified WECC_URE1’s completion of the Mitigation Plan.
2012-08-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2012009855 | CIP-003-1 | R1.3 | WECC_URE2 self-certified noncompliance with CIP-003-1 R1.3 stating that it did not annually review its entire cyber security policy in 2009 and 2010. The policies that were not reviewed were outdated and not used by WECC_URE2 but, nevertheless, were a part of its cyber security policy. WECC_URE2 employees were aware not to follow the outdated policies. WECC determined that WECC_URE2 failed to perform a complete annual review of its cyber security policy for the calendar years 2009 and 2010. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because in this instance, while policies that are a part of the cyber security policy were not reviewed, those policies were outdated and not used by the entity. As compensating measures, WECC_URE2 performed annual reviews and approved the current policies in use. | WECC_URE2 reviewed its cyber security policy in calendar year 2011 and removed the outdated items.
2012-08-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2012010762 | CIP-003-1 | R1.3 | WECC_URE3, self-certified noncompliance with CIP-003-1 R1.3. According to WECC, WECC_URE3 stated that it did not annually review its entire cyber security policy in calendar year 2010. The policies that were not reviewed were outdated and not used by WECC_URE3 but, nevertheless, were a part of WECC_URE3’s cyber security policy. WECC determined that WECC_URE3 failed to perform a complete annual review of its cyber security policy for the calendar year 2010. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because while policies that are a part of the policy were not reviewed, those policies were outdated and not used by the entity. As compensating measures, WECC_URE3 stated that it did annual reviews and approved the current policies in use. | WECC_URE3 reviewed its cyber security policy in calendar year 2011 and removed the outdated items.
2012-08-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC2012010696 | CIP-002-1 | R3 | WECC performed an offsite compliance audit of WECC_URE4’s compliance with, among other Reliability Standards, CIP-002-1 R3. The Audit Team concluded that WECC_URE4 had an issue of CIP-002-1 R3 because it failed to develop a null list of its Critical Cyber Assets (CCAs). The Audit Team also concluded that WECC_URE4 knew it did not have any CCAs because it had developed a null list of its Critical Assets. WECC has determined that WECC_URE4 had an issue of CIP-002-1 R3 because it failed to develop a null list of its CCAs. WECC further determined that the duration of the issue was from when the Standard became enforceable for WECC_URE4, until when it developed its null list of CCAs. | WECC determined that this issue posed a minimal risk and not a serious or substantial risk to the reliability of the bulk power system. WECC_URE4 had previously applied its risk-based assessment methodology and knew prior to the start of the issue that it did not have any Critical Assets and, therefore, did not have any CCAs. Thus, the potential for malicious conduct to CCAs did not exist. | WECC_URE4 developed a null list of its CCAs.
2012-08-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC2012010697 | CIP-002-1 | R4 | WECC performed an offsite compliance audit of WECC_URE4’s compliance with, among other Reliability Standards, CIP-002-1 R4. The Audit Team concluded that WECC_URE4 had an issue of CIP-002-1 R4 because it failed to have a CIP senior manager sign its null list of its Critical Cyber Assets CCAs. However, the Audit Team also concluded that WECC_URE4 knew it did not have any CCAs because it had developed a null list of its Critical Assets. WECC determined that WECC_URE4 had an issue of CIP-002-1 R4 because it failed to have a CIP senior manager sign its null list of Critical Assets and CCAs. WECC further determined that the duration of the issue was from when the Standard became enforceable for WECC_URE4, until when its CIP senior manager signed its null list of Critical Assets and CCAs. | WECC determined that this issue posed a minimal risk and not a serious or substantial risk to the reliability of the bulk power system. After applying its risk-based assessment methodology, WECC_URE4 knew it did not have any Critical Assets and therefore did not have any CCAs prior to the issue. Thus, the potential for malicious conduct to CCAs did not exist. | WECC_URE4’s CIP senior manager signed its null list of its CCAs.
2012-08-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC2012010699 | CIP-003-1 | R2 | WECC performed an offsite compliance audit of WECC_URE4’s compliance with, among other Reliability Standards, CIP-003-1 R2. The Audit Team concluded that WECC_URE4 had an issue of CIP-003-1 R2 because it failed to designate a CIP senior manager with overall responsibility and authority for CIP-002 through CIP-009. The Audit Team also concluded that WECC_URE4 knew it did not have any Critical Cyber Assets because it had developed a null list of its Critical Assets. WECC determined that WECC_URE4 had an issue of CIP-003-1 R2 because it failed to designate a CIP senior manager with overall responsibility and authority for CIP-002 through CIP-009. WECC further determined that the duration of the issue was from when the Standard became enforceable for WECC_URE4, until when it designated a CIP senior manager with overall responsibility and authority for CIP-002 through CIP-009. | WECC determined that this issue posed a minimal risk and not a serious or substantial risk to the reliability of the bulk power system. After applying its risk-based assessment methodology, WECC_URE4 knew it did not have any Critical Assets and therefore did not have any CCAs prior to the issue. Thus, the potential for malicious conduct to CCAs did not exist. | WECC_URE4 designated a CIP senior manager with overall responsibility and authority for CIP-002 through CIP-009.
2012-08-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 5 (WECC_URE5) | NCRXXXXX | WECC2012009653 | CIP-003-3 | R5 | WECC_URE5 submitted a Self-Report citing facts consistent with an issue of CIP-003-1 R5.3. Specifically, WECC_URE5 reported two instances in which employees were granted access to Critical Cyber Asset (CCA) information without completing request training required under WECC_URE5’s CCA program. The first instance occurred after an employee was granted electronic access to WECC_URE5’s CIP document library (Library) without completing training per WECC_URE5’s CIP program. The second instance of noncompliance occurred after an employee was granted access to the Library in error. WECC_URE5 detected the mistake and revoked this employee’s access rights. Enforcement reviewed WECC_URE5’s Self-Report and determined these two instances demonstrate that WECC_URE5 failed to manage access to CCA information in compliance with its CCA program. | WECC determined this issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The purpose of CIP-003 is to ensure that Responsible entities have minimum security management controls in place to protect CCAs. To that end, CIP-003-1 R5 requires entities to document and implement a program for managing access to protected CCA information. In this case, WECC_URE5 granted access to CCA information to two individuals who did not complete requisite training per WECC_URE5’s CCA program. The risks, posed by WECC_URE5 noncompliance are, however, offset in that WECC_URE5 quickly detected and mitigated both instances of noncompliance within 23 days. Further, based on WECC_URE5’s prompt detection and mitigation, there is evidence that demonstrates WECC_URE5 regularly reviews its access privilege lists throughout the year instead of waiting for an annual review. Risks are further mitigated given the limited scope of the issue. The first individual granted access had only to complete training, a requirement unique of WECC_URE5’s program that is above and beyond the criteria prescribed under R5. In the second instance, although WECC_URE5 mistakenly granted access to the second individual, that individual never accessed or attempted to access CCA information during the 23 days prior to WECC_URE5’s detection and revocation of that individual’s access. Enforcement, therefore, determined that the risks posed by WECC_URE5 noncompliance posed a minimal risk to the bulk power system. | WECC_URE5 ensured that the first individual completed request training. WECC_URE5 revoked access for the second individual.
2012-08-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 6 (WECC_URE6) | NCRXXXXX | WECC2011009022 | CIP-006-3a | R2.2 | WECC_URE6 self-reported an issue of CIP-006-3 R2.2. A WECC subject matter expert (WECC SME) contacted WECC_URE6 to discuss its Self-Report. According to the WECC SME, WECC_URE6 stated that it did not afford two panels the protections of CIP-007 R6. The panels involved control access to all of WECC_URE6’s Physical Security Perimeters (PSPs). | WECC determined this issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The panels are located in a PSP inside a locked cabinet with restricted key access to which fewer than five individuals have access. The locked cabinets also have tamper switches installed to alert the entity upon opening the enclosures. For these reasons, WECC determined these issues posed minimal risk to the reliability of the bulk power system. | WECC_URE6 stated that the panels are located in a PSP inside a locked cabinet with restricted key access to which few individuals have access. The locked cabinets also have tamper switches installed to alert the entity upon opening the enclosures. WECC_URE6 submitted a Technical Feasible Exception for the devices involved.
2012-08-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 7 (WECC_URE7) | NCRXXXXX | WECC2011008706 | CIP-005-3a | R1 | WECC_URE7 submitted a Self-Report to WECC for CIP-005-3a R1. WECC_URE7 decommissioned hard drives associated with firewall management consoles, which were Cyber Assets used in the access control and monitoring WECC_URE7’s Electronic Security Perimeter. During the disposal and decommissioning process, WECC_URE7 did not provide the protective measure specified in CIP-007 R7.3 to the hard drives. Specifically, WECC_URE7 did not follow its CIP-007 R7 disposal and redeployment procedures, resulting in an issue with CIP-005-1 R1. | WECC determined this issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. WECC_URE7 stored the hard drives in a locked cabinet in a secure facility that requires card key access. Further, only IT personnel had access to the area in which the hard drives resided. Additionally, the hard drives were part of a redundant array of independent disks (RAID) where no single disc would have been available for data retrieval without the other participating discs in that RAID array. For these reasons, WECC determined the issue posed minimal risk to the reliability of the bulk power system. | WECC_URE7 moved the hard drives into a Physical Security Perimeter upon discovering the issue. Further, WECC_URE7 took the following five steps to mitigate the root cause of the issue: 1) Added an additional requirement to the WECC_URE7 change management procedure requiring persons reviewing and approving changes to review all documentation. 2) Provided additional clarity in documented procedures on safeguarding of Cyber Assets during disposal and redeployment. 3) Developed refresher training specific to disposal and redeployment procedures which includes testing for comprehension and retention. 4) Ensured disposal and redeployment re-training is completed by all applicable WECC_URE7 employees. 5) Updated required annual NERC CIP Training to include a module specific to disposal and redeployment.
2012-07-31 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO2012010158 | CIP-004-3 | R4; R4.1 | MRO_URE1 self-reported an issue with CIP-004-3 R4 for failing to revoke a contractor's unescorted physical access to two substations containing Critical Cyber Assets (CCAs) within seven days. The contractor did not provide MRO_URE1 with a timely notification of a change in its personnel. The contractor's access was not revoked within the seven calendar days required by the Standard due to a misunderstanding. The contractor incorrectly thought that taking possession of the individual's badge would revoke access; however, access to both substations is controlled by a combination of personal identification numbers and biometrics, and not just a badge. | MRO determined that this issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The contractor's training and personnel risk assessment were both current. In addition, this was an isolated incident. MRO_URE1 reviewed its access records and did not identify any other instances of unauthorized access. Furthermore, the contractor's access privileges were not used during the period between voluntary termination and revocation, and the contractor did not have electronic access to MRO_URE1's CCAs. | MRO_URE1 revoked the contractor's access privileges. MRO verified that MRO_URE1 completed its mitigating activities.
2012-07-31 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 2 (MRO_URE2) | NCRXXXXX | MRO2012009921 | CIP-007-3 | R4; R4.2 | MRO_URE2 self-reported an issue with CIP-007-3 R4.2 for failing to keep anti-virus and malware prevention signatures updated on several Cyber Assets, which were Critical Cyber Assets (CCAs). Specifically, these Cyber Assets made up 11% of MRO_URE2's total CCAs. The Cyber Assets were being retired from the system, but had not been removed from the network when they were replaced. MRO_URE2's malicious software prevention policy required monthly checks for new virus signatures. For one month, MRO_URE2 did not perform a monthly check for the retired devices. | MRO_URE2determined that this issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because only 11% of MRO_URE2's total CCAs were affected, those devices were being retired from MRO_URE2's system and were not actively used. Additionally, MRO_URE2 only missed the anti-virus signature update by 18 days. The devices were protected in accordance with all of the other applicable CIP requirements. | MRO_URE2 removed the Cyber Assets from its system. MRO_URE2verified that MRO_URE2 completed its mitigating activities.
2012-07-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2011001002 | CIP-007-3 | R9 | RFC_URE1 self-reported an issue with CIP-007-3 R9. RFC_URE1 changed its anti-virus software on all of its Critical Cyber Assets (CCAs). RFC_URE1 discovered that it had not updated its cybersecurity procedure within thirty calendar days of the change pursuant CIP-007-3 R9. ReliabilityFirst determined that RFC_URE1 had an issue with CIP-007-3 R9 for failing to document a change resulting from the modifications to its anti-virus system within thirty calendar days of RFC_URE1 completing the change. | ReliabilityFirst determined that this issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). This risk to the reliability of the BPS was mitigated by the fact that at all times RFC_URE1's Cyber Assets and CCAs were protected by anti-virus software. In addition, the issue incident was an isolated incident in which RFC_URE1 did not follow its documented cybersecurity procedure. | RFC_URE1 performed additional training on all staff engaged in managing Cyber Assets within the Electronic Security Perimeter on its cybersecurity procedure. RFC_URE1 also included, in its additional training, an emphasis on the need to update all relevant documentation within the required timeframe.
2012-07-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2011001047 | CIP-006-2a | R1; R1.2 | RFC_URE1 self-reported an issue with CIP-006-2a R1.2. Prior to mandatory compliance with Reliability Standard CIP-006-2a R1, RFC_URE1 installed a steel cage in the ceiling of its transmission control room to create a completely enclosed six-wall border. Upon further examination, RFC_URE1 determined that the way in which the steel cage was installed allowed for access into the transmission control room from the ceiling above. ReliabilityFirst determined that RFC_URE1 had had an issue with CIP-006-2a R1 for not identifying this physical access point or taken measures to control entry at that access point. | ReliabilityFirst determined that this issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk to the reliability to the BPS was mitigated by the following factors. RFC_URE1’s transmission control room is located within RFC_URE1’s generation control room, which is locked at all times with cipher locks (key pad devices that require a specific code to be entered before authorizing access), the combination of which is only given to individuals who have received authorization from RFC_URE1. Additionally, RFC_URE1 monitors access to the transmission control room with security cameras. | RFC_URE1 installed the equipment necessary to create a complete six-wall border surrounding its transmission control room that eliminates the access point into the transmission control room from the ceiling above.
2012-07-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2011001071 | CIP-005-3a | R5; R5.3 | RFC_URE1 self-reported an issue with CIP-005-3a R5.3. RFC_URE1 determined that it had not retained electronic access logs for at least 90 calendar days. Specifically, RFC_URE1 discovered that as the result of a service outage of its primary centralized log server, the primary centralized log server was not retaining access logs. | ReliabilityFirst determined this issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk to the reliability of the BPS was mitigated by the following factors. RFC_URE1 was collecting logs and sending alerts through its backup centralized log server during the duration of the remediated issue; however, the backup log server only retained access logs for 30 calendar days, rather than the required 90 days. RFC_URE1 was still logging access to the applicable devices and appropriate personnel still received alerts from the backup centralized log server. Additionally, RFC_URE1 did not detect any security incidents through the backup centralized log server during the duration of the remediated issue. | RFC_URE1 configured the settings on its centralized server to retain access logs for 90 calendar days.
2012-07-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2011001072 | CIP-007-3 | R6; R6.4 | RFC_URE1 self-reported an issue with CIP-007-3 R6.4. RFC_URE1 determined that it had not retained all system security logs related to its system that monitors all network devices and acts as RFC_URE1's system log based network performance monitoring software, for at least 90 calendar days. Specifically, RFC_URE1 discovered that as the result of a service outage of its primary centralized log server, it was not retaining access logs for the required 90 days. | ReliabilityFirst determined this issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk to the reliability of the BPS was mitigated by the following factors. Through a backup centralized log server, RFC_URE1 retained all logs required by CIP-007-2a R6 for 30 calendar days. Also, RFC_URE1 was performing real time logging for access to the applicable devices and appropriate personnel received alerts from the backup centralized log server during the duration of the remediated issue. Additionally, RFC_URE1 did not detect any security incidents through the backup centralized log server and review of the logs for the duration of the remediated issue. | RFC_URE1 configured the settings on its centralized server to retain access logs for 90 calendar days.
2012-07-31 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE201100523 | CIP-002-2 | R1 | During a Spot-Check, Texas RE concluded that Texas RE_URE1 did not have adequate documentation of a risk-based assessment methodology (RBAM) to use to identify Critical Assets (CAs) at a newly purchased station, as required by CIP-002-2 R1. Texas RE_URE1 had an issue with this Standard for a period of four months, after acquiring the station and registering with NERC. Texas RE_URE1 conducted a high-level review shortly after acquiring the station and concluded that it had no CAs or Critical Cyber Assets (CCAs). However, Texas RE_URE1 used a RBAM that applied to other assets from its fleet to identify CAs and CCAs at this station. Texas RE_URE1 also concluded that it needed to update the RBAM created by the previous station owner to reflect the requirements included in its current fleet program and to fully address this Standard. Texas RE_URE1 also mistakenly concluded it had two years to update its RBAM. Texas RE_URE1 documented an acceptable RBAM that addressed the requirements of this Standard four months after its registration. Therefore, Texas RE determined that the start date of the issue was the date of Texas RE_URE1's registration with NERC to the date an updated RBAM was created and approved. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the issue was documentation in nature as Texas RE_URE1 realized that it needed to update its RBAM, and that it had no CAs or CCAs, but failed to update its RBAM for four months. Also, during the pendency of the issue, Texas RE_URE1 had a RBAM in place that was also applicable to other assets, and performed a high-level review of this particular facility and determined that it had no CAs or CCAs. After Texas RE_URE1 documented an RBAM that addressed the requirements of this Standard, and applied the updated RBAM, it identified no CAs or CCAs at the facility at issue. In addition, the duration of this remediated issue was limited to four months. Because the risk to the BPS was mitigated by the existence of an RBAM at the time of the issue, although not fully compliant with this Standard, because there were no CAs and CCAs during the pendency of the issue or thereafter, and because the issue lasted for four months, Texas RE determined this issue presented a minimal risk to the BPS. | Texas RE_URE1 updated the RBAM for the facility at issue to address the requirements of this Standard. Texas RE verified completion of these mitigating activities.
2012-07-31 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE201100524 | CIP-002-2 | R2 | During a Spot-Check, Texas RE concluded that Texas RE_URE1 did not develop a list of its identified Critical Assets (CAs) determined through an annual application of the risk-based assessment methodology (RBAM), as required by CIP-002-2 R2. Texas RE_URE1 conducted a high-level review of a newly acquired station shortly after acquiring the station and registering with NERC. Texas RE_URE1 used a RBAM that applied to other assets from its fleet to identify CAs and Critical Cyber Assets (CCAs) within its station, determined that it had no CAs and CCAs but failed to document its findings. However, the list of identified CAs and CCAs created by the previous owner of the station was redacted and therefore unreadable, thus presenting an issue with CIP-002-2 R2. This noncompliant list was in place for four months until Texas RE_URE1 documented an updated RBAM for its newly acquired station, and used the RBAM to develop a list of its CAs, which addressed the requirements of CIP-002-2 R2. Texas RE determined that the start date of the issue was the date of Texas RE_URE1's registration with NERC to the date an updated RBAM was created and approved. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the issue was documentation in nature as Texas RE_URE1 realized that it needed to update its RBAM, and that it had no CAs or CCAs, but failed to update the RBAM and the existing list of CAs and CCAs, as required by this Standard. Also, the duration was limited to four months. After applying the updated RBAM, Texas RE_URE1 confirmed and documented that there were no CAs or CCAs at the facility at issue. Also, during the pendency of the issue, Texas RE_URE1 had a RBAM in place that was also applicable to other assets, and performed a high-level review of this particular facility and correctly determined that it had no CAs or CCAs, thereby reducing the risk to the BPS to minimal. | Texas RE_URE1 updated the RBAM for the facility at issue and created a list of CAs applying the updated RBAM. The list indicated that there were no CAs or CCAs at this facility. Texas RE verified completion of these mitigating activities.
2012-07-31 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE201100525 | CIP-002-2 | R3 | During a Spot-Check, Texas RE concluded that Texas RE_URE1 did not develop a list of associated Critical Cyber Assets (CCAs) essential to the operation of the Critical Assets (CAs), as required by CIP-002-2 R3. Texas RE_URE1 conducted a high-level review of a newly acquired station shortly after purchasing the station and registering with NERC. Texas RE_URE1 used a risk-based assessment methodology (RBAM) that applied to other assets from its fleet to identify CAs and CCAs within its station, determined that it had no CAs and CCAs but failed to document its findings. However, the list of identified CAs and CCAs created by the previous owner of the station was redacted and therefore unreadable, thus presenting an issue with CIP-002-2 R2. This noncompliant list was in place for four months until Texas RE_URE1 documented an updated RBAM for its newly acquired station, and used the RBAM to develop a list of CCAs, which addressed the requirements of CIP-002-2 R3. Texas RE determined that the start date of this issue was from the date of Texas RE_URE1's registration with NERC to the date an updated RBAM was created and approved. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the issue was documentation in nature as Texas RE_URE1 realized that it needed to update its RBAM, and that it had no CAs or CCAs, but failed to update the RBAM and the existing list of CAs and CCAs, as required by this Standard. Also, the duration was limited to four months. After applying the updated RBAM, Texas RE_URE1 determined that there were no CAs and CCAs at the facility at issue. Also, during the pendency of the issue, Texas RE_URE1 had a RBAM in place that was also applicable to other assets, and performed a high-level review of this particular facility and correctly determined that it had no CAs or CCAs, thereby reducing the risk to the BPS to minimal. | Texas RE_URE1 updated the RBAM for the facility at issue and created a list of CAs and CCAs by applying the updated RBAM. The list indicated that there were no CAs or CCAs at this facility. Texas RE verified completion of these mitigating activities.
2012-07-31 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE201100526 | CIP-002-2 | R4 | During a Spot-Check, Texas RE concluded that Texas RE_URE1 did not keep a signed and dated record of the senior manager or delegate(s)' annual approval of the risk-based assessment methodology (RBAM), the list of Critical Assets (CAs) and the list of Critical Cyber Assets (CCAs), as required by CIP-002-2 R4. Texas RE_URE1 conducted a high-level review of a newly acquired station shortly after purchasing the station and registering with NERC. Texas RE_URE1 used a RBAM that applied to other assets from its fleet to identify CAs and CCAs within its new station, determined that it had no CAs and CCAs but failed to document its findings. This noncompliant RBAM was used for four months until Texas RE_URE1 documented an updated RBAM for its newly acquired station, and used the updated RBAM to develop lists of CAs and CCAs. The updated RBAM, and lists of CAs and CCAs was approved by the senior manager or delegates four months after Texas RE_URE1 purchased the station and registered with NERC. Texas RE determined that the start date of this issue was the date of Texas RE_URE1's registration with NERC to the date an updated RBAM and lists of CAs and CCAs were created and approved by the senior manager. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the issue was documentation in nature as Texas RE_URE1 realized that it needed to update its RBAM, and that it had no CAs or CCAs, but failed to update the RBAM and the existing list of CAs and CCAs, and to keep a record of the senior manager's approval of these documents, as required by this Standard. After applying the updated RBAM, Texas RE_URE1 determined that there were no CAs and CCAs at the facility at issue, and the senior manager or delegates approved the RBAM and the null lists of CCAs and CAs. Also, during the pendency of the issue, Texas RE_URE1 had a RBAM in place that was also applicable to other assets, performed a high-level review of this particular facility and correctly determined that it had no CAs or CCAs, thereby reducing the risk to the BPS to minimal. | Texas RE_URE1 updated the RBAM for the facility at issue and created a list of CAs and CCAs applying the updated RBAM. The list indicated that there were no CAs or CCAs at this facility. Texas RE_URE1's senior manager approved the RBAM and lists of CAs and CCAs. Texas RE verified completion of these mitigating activities.
2012-07-31 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE201100527 | CIP-003-2 | R2 | During a Spot-Check, Texas RE concluded that Texas RE_URE1 did not assign a single manager with overall responsibility and authority for leading and managing Texas RE_URE1's implementation of, and adherence to, Standards CIP-002-2 through CIP-009-2, as required by CIP-003-2 R2. Texas RE determined that when Texas RE_URE1 first registered with NERC, it properly assigned a single manager, as per CIP-003-2 R2. However another person, who was not the delegated single manager, approved Texas RE_URE1's updated risk-based assessment methodology (RBAM), the list of Critical Assets (CAs) and the list of Critical Cyber Assets (CCAs). Texas RE_URE1 realized the discrepancy and prepared documentation, stating that the person who approved the RBAM and the list of CAs and CCAs was in fact the proper, delegated manager and had authority to approve these documents. Texas RE determined that because a person other than the initially authorized single manager signed the RBAM and list of CAs and CCAs, Texas RE_URE1 was noncompliant with CIP-003-2 R2. Texas RE determined that the issue duration was for a period of about three months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because Texas RE_URE1 had a senior manager with overall responsibility for compliance with CIP-002-2 through CIP-009-2 at all times. However, for the period of about three months the delegation of authority to a single senior manager with overall responsibility existed but was not documented. Texas RE determined that this issue was documentation in nature, thereby reducing the risk to the BPS to minimal. | Texas RE_URE1 documented the delegation of authority to a single senior manager. Texas RE verified completion of these mitigating activities.
2012-07-31 | TRE_URE1liability Entity (TRE_URE1) | Unidentified Registered Entity 2 (TRE_URE2) | NCRXXXXX | TRE201100530 | CIP-002-2 | R1 | During a Spot-Check, TRE_URE1 concluded that TRE_URE1_URE2 did not have adequate documentation of a risk-based assessment methodology (RBAM) to use to identify Critical Assets (CAs) at a newly purchased station, as required by CIP-002-2 R1. TRE_URE1_URE2 was noncompliant with this Standard for a period of four months, after purchasing the station and registering with NERC. TRE_URE1_URE2 conducted a high-level review shortly after acquiring the station and concluded that it had no CAs or Critical Cyber Assets (CCAs). However, TRE_URE1_URE2 used a RBAM that applied to other assets from its fleet to identify CAs and CCAs at this station. TRE_URE1_URE2 also concluded that it needed to update the RBAM created by the previous station owner to reflect the requirements included in its current fleet RBAM and to fully address this Standard. TRE_URE1_URE2 also mistakenly believed that it had two years to update its current RBAM. TRE_URE1_URE2 documented an acceptable RBAM that addressed the requirements of this Standard four months after its registration with NERC. Therefore, TRE_URE1 determined that the issue duration was from the date TRE_URE1_URE2 was registered with NERC to the date an updated RBAM was created and approved. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the issue was documentation in nature as TRE_URE1_URE2 realized that it needed to update its RBAM, and that it had no CAs or CCAs, but failed to update its RBAM for four months. Also, during the pendency of this issue, TRE_URE1_URE2 had a RBAM in place that was also applicable to other assets, and performed a high-level review of this particular facility and determined that it had no CAs or CCAs. After TRE_URE1_URE2 documented a RBAM that addressed the requirements of this Standard, and applied the updated RBAM, it identified no CAs or CCAs at the facility at issue. In addition, the duration of this remediated issue was limited to four months. Because the risk to the BPS was mitigated by the existence of an RBAM at the time of the issue, although not fully compliant with this Standard, because there were no CAs and CCAs during the pendency of the issue or thereafter, and because the issue lasted for four months, TRE_URE1 determined this issue presented a minimal risk to the BPS. | TRE_URE1_URE2 updated the RBAM for the facility at issue when a senior manager approved the RBAM. TRE_URE1 verified completion of these mitigating activities.
2012-07-31 | TRE_URE1liability Entity (TRE_URE1) | Unidentified Registered Entity 2 (TRE_URE2) | NCRXXXXX | TRE201100531 | CIP-002-2 | R2 | During a Spot-Check, TRE_URE1 concluded that TRE_URE1_URE2 did not develop a list of its identified Critical Assets (CAs) determined through an annual application of the risk-based assessment methodology (RBAM), as required by CIP-002-2 R2. TRE_URE1_URE2 conducted a high-level review of a newly acquired station shortly after purchasing the station and registering with NERC. TRE_URE1_URE2 used a RBAM that applied to other assets from its fleet to identify CAs and Critical Cyber Assets (CCAs) within its new station, determined that it had no CAs and CCAs but failed to document its findings. However, the list of identified CAs and CCAs created by the previous owner of the station was redacted and therefore unreadable, thus presenting an issue with CIP-002-2 R2. This noncompliant list was in place for four months until TRE_URE1_URE2 documented an updated RBAM for its newly acquired station, and used the RBAM to develop a list of its CAs, which addressed the requirements of CIP-002-2 R2. TRE_URE1 determined that the issue was from the date of TRE_URE1_URE2's registration with NERC to the date an updated RBAM was created and approved. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the issue was documentation in nature as TRE_URE1_URE2 realized that it needed to update its RBAM, that it had no CAs or CCAs, but failed to update the RBAM and the existing list of CAs and CCAs, as required by this Standard. Also, the duration of this issue was limited to four months. After applying the updated RBAM, TRE_URE1_URE2 determined that there were no Critical Assets at the facility at issue. Also, during the pendency of the issue, TRE_URE1_URE2 had a RBAM in place that was also applicable to other assets, and performed a high-level review of this particular facility, and correctly determined that it had no CAs or CCAs, thereby reducing the risk to the BPS to minimal. | TRE_URE1_URE2 updated the RBAM for the facility at issue and created a list of CAs applying the updated RBAM. The list indicated that there were no CAs or CCAs at this facility. TRE_URE1 verified completion of these mitigating activities.
2012-07-31 | TRE_URE1liability Entity (TRE_URE1) | Unidentified Registered Entity 2 (TRE_URE2) | NCRXXXXX | TRE201100532 | CIP-002-2 | R3 | During a Spot-Check, TRE_URE1 concluded that TRE_URE1_URE2 did not develop a list of associated Critical Cyber Assets (CCAs) essential to the operation of the Critical Assets (CAs), as required by CIP-002-2 R3. TRE_URE1_URE2 conducted a high-level review of a newly acquired station shortly after purchasing the station and registering with NERC. TRE_URE1_URE2 used a risk-based assessment methodology (RBAM) that applied to other assets from its fleet to identify CAs and CCAs within its new station, determined that it had no CAs and CCAs but failed to document its findings. However, the list of identified CAs and CCAs created by the previous owner of the station was redacted and therefore unreadable, thus presenting an issue with CIP-002-2 R2. This noncompliant list was in place for four months until TRE_URE1_URE2 documented an updated RBAM for its newly acquired station, and used the RBAM to develop a list of CCAs, which addressed the requirements of CIP-002-2 R3. TRE_URE1 determined that the issue was from the date of TRE_URE1_URE2's registration with NERC to the date an updated RBAM was created and approved. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the issue was documentation in nature as TRE_URE1_URE2 realized that it needed to update its RBAM, that it had no CAs or CCAs, but failed to update the RBAM and the existing list of CAs and CCAs, as required by this Standard. Also, the duration was limited to four months. After applying the updated RBAM, TRE_URE1_URE2 determined that there were no CAs and CCAs at the facility at issue. Also, during the pendency of the issue, TRE_URE1_URE2 had a RBAM in place that was also applicable to other assets, and performed a high-level review of this particular facility, and correctly determined that it had no CAs or CCAs, thereby reducing the risk to the BPS to minimal. | TRE_URE1_URE2 updated the RBAM for the facility at issue and created a list of CAs and CCAs applying the updated RBAM. The list indicated that there were no CAs or CCAs at this facility. TRE_URE1 verified completion of these mitigating activities.
2012-07-31 | TRE_URE1liability Entity (TRE_URE1) | Unidentified Registered Entity 2 (TRE_URE2) | NCRXXXXX | TRE201100533 | CIP-002-2 | R4 | During a Spot-Check, TRE_URE1 concluded that TRE_URE1_URE2 did not keep a signed and dated record of the senior manager or delegate(s)' annual approval of the risk-based assessment methodology (RBAM), the list of Critical Assets (CAs) and the list of Critical Cyber Assets (CCAs), as required by CIP-002-2 R4. TRE_URE1_URE2 conducted a high-level review of a newly acquired station shortly after purchasing the station and registering with NERC. TRE_URE1_URE2 used a RBAM that applied to other assets from its fleet to identify CAs and CCAs within its new station, determined that it had no CAs and CCAs but failed to document its findings. This RBAM was used for four months until TRE_URE1_URE2 documented an updated RBAM for its newly acquired station, and used the RBAM to develop lists of CAs and CCAs. The RBAM, and lists of CAs and CCAs was approved by the senior manager or delegates four months after TRE_URE1_URE2 purchased the station and registered with NERC. TRE_URE1 determined that the issue was from the date of TRE_URE1_URE2's registration with NERC to the date an updated RBAM and lists of CAs and CCAs were approved by the senior manager. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the issue was documentation in nature, as TRE_URE1_URE2 realized that it needed to update its RBAM, that it had no CAs or CCAs, but failed to update the RBAM and the existing list of CAs and CCAs and to keep a record of the senior manager's approval of these documents, as required. After applying the updated RBAM, TRE_URE1_URE2 determined that there were no CAs and CCAs at the facility at issue, and the senior manager or delegates approved the RBAM and the null lists of CCAs and CAs. Also, during the pendency of the issue, TRE_URE1_URE2 had a RBAM in place that was also applicable to other assets, performed a high-level review of this particular facility and correctly determined that it had no CAs or CCAs, thereby reducing the risk to the BPS to minimal. | TRE_URE1_URE2 updated the RBAM for the facility at issue and created a list of CAs and CCAs applying the updated RBAM. The list indicated that there were no CAs or CCAs at this facility. TRE_URE1_URE2's senior manager approved the RBAM and lists of CAs and CCAs. TRE_URE1 verified completion of these mitigating activities.
2012-07-31 | TRE_URE1liability Entity (TRE_URE1) | Unidentified Registered Entity 2 (TRE_URE2) | NCRXXXXX | TRE201100534 | CIP-003-2 | R2 | During a Spot-Check, TRE_URE1 concluded that TRE_URE1_URE2 did not assign a single manager with overall responsibility and authority for leading and managing TRE_URE1_URE2's implementation of, and adherence to, Standards CIP-002-2 through CIP-009-2, as required by CIP-003-2 R2. TRE_URE1 determined that when TRE_URE1_URE2 first registered with NERC, it properly assigned a single manager, as per CIP-003-2 R2. However another person, who was not the delegated single manager, approved TRE_URE1_URE2's updated risk-based assessment methodology (RBAM), the list of Critical Assets (CAs) and the list of Critical Cyber Assets (CCAs). TRE_URE1_URE2 realized the discrepancy and prepared documentation, stating that the person who approved the RBAM and the list of CAs and CCAs was in fact the proper, delegated manager and he had authority to approve these documents. TRE_URE1 determined that because a different person, other than the initially authorized single manager, signed the RBAM and list of CAs and CCAs, TRE_URE1_URE2 was noncompliant with CIP-003-2 R2. TRE_URE1 determined that the issue duration was a period of about three months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because TRE_URE1_URE2 had a senior manager with overall responsibility for compliance with CIP-002-2 through CIP-009-2 at all times. However, for the period of about three months the delegation of authority to a single senior manager with overall responsibility existed but was not documented. TRE_URE1 determined that this issue was documentation in nature, thereby reducing the risk to the BPS to minimal. | TRE_URE1_URE2 documented the delegation of authority to a single senior manager. TRE_URE1 verified completion of these mitigating activities.
2012-07-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2012009697 | CIP-006-3c | R5 | WECC_URE1 submitted a Self-Report indicating an issue with CIP-006-3c R5. A WECC_URE1 employee accessed one of WECC_URE1's Physical Security Perimeters (PSP) to perform a business function. The PSP the employee accessed is a cabinet containing one Critical Cyber Asset (CCA) used for a WECC_URE1 management system. WECC_URE1's procedures for this PSP require a hard key to open the cabinet and a card must be swiped to turn off the events being monitored at the security center. WECC_URE1’s procedures also require an employee to reactivate monitoring of the PSP after accessing the PSP by re-swiping their access card. In this case, after the employee involved was finished accessing the CCA, he failed to re-swipe the access card to reactivate monitoring of the PSP. The access system did not re-initiate monitoring of the cabinet until a security operator noticed that the cabinet was unmonitored. The security operator then force-armed the access system to once again begin monitoring the cabinet. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the PSP in scope is locked using a hard key. In addition, the room containing the PSP is staffed with operational personnel twenty-four hours and electronic controls are in place for the one CCA. Finally, in case the CCA was compromised, the monitoring system frequency and unit output would have alerted the operational personnel. | This issue was remediated when monitoring was reactivated.
2012-07-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2012009390 | CIP-006-3c | R1.6.2 | WECC_URE2 self-certified noncompliance with CIP-006-3c R1.6.2. This Standard requires continuous escorted access of visitors within the Physical Security Perimeter (PSP). WECC determined that WECC_URE2 had an issue of CIP-006-3c R1.6.2 because three individuals requiring escorted access within a (PSP) had unescorted access for a period of approximately three minutes. The three individuals were unescorted in a WECC_URE2 PSP, which contained two Critical Cyber Assets (CCAs). | This issue did not pose a serious or substantial risk and only posed minimal risk to the reliability of the bulk power system (BPS) the three individuals only had physical access to the PSP. Also, the PSP is monitored twenty-four hours a day and each access point door is configured to generate an alarm for unauthorized access. In addition, the PSP is manned twenty-four hours a day. | This issue was remediated when the three individuals were escorted after the three minute issue duration.
2012-07-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2012010272 | CIP-002-3 | R4 | WECC_URE3 self-reported noncompliance with CIP-002-3 R4. According to the Self-Report, WECC_URE3 failed to annually approve the risk-based assessment methodology (RBAM), the Critical Asset list, and the Critical Cyber Asset (CCA) list for a calendar year. WECC_URE3 stated that it did perform an annual risk based assessment as required by CIP-002 before the end of the calendar year, the assigned CIP senior manager did not approve the documentation until after the required date. WECC reviewed WECC_URE2’s Self-Report and its risk-based annual assessment. Specifically, WECC_URE3 performed its annual assessment of Critical Assets and CCAs prior to the end of the year and WECC_URE3 submitted its completed risk-based assessment and associated lists to the appropriate managers for approval. WECC_URE3’s risk-based annual approval process is more robust than industry standard, in that it requires approval by two supplementary managers in addition to the assigned CIP senior manager. Based on WECC_URE3’s document routing evidence, the annual approval process was initiated, reviewed, and approved by two WECC_URE3 managers, but not approved by the assigned CIP senior manager until 13 days late. This delay was a result of the CIP senior manager being out of the office for a holiday vacation. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because WECC_URE3’s annual assessment was initiated and completed except for the final approval of the CIP senior manager. The assessment was reviewed and approved by two of the three managers. The final approval was put on hold for 13 days until the assigned CIP senior manager returned from vacation. During the 13 days that the lists were not approved by the CIP senior manager, WECC_URE3’s associated Critical Assets and CCAs were thoroughly identified, reviewed and approved by two WECC_URE3 managers that signed off on the assessment prior to the end of the year. Additionally, WECC_URE3 documentation had previously been annually approved in the year proceeding the noncompliant year and the year following the noncompliant year. | WECC_URE3’s RBAM and updated Critical Asset and CCA lists were approved by the assigned CIP senior manager. WECC_URE3 moved its annual approval process to be performed earlier in the calendar to ensure the documentation is properly approved and recorded on an annual basis.
2012-07-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC2012010514 | CIP-007-1 | R4 | WECC_URE4 self-reported an issue of CIP-007-1 R4. WECC reviewed WECC_URE4's Self-Report. According to the WECC, WECC_URE4 failed to use anti-virus and malware protection tools on sixty of its non-Cyber Asset and Critical Cyber Assets located within an Electronic Security Perimeter (ESP), but had not filed Technical Feasibility Exceptions (TFEs) for these devices. Although TFEs were not filed timely according to the requirement, WECC approved the TFEs pertaining to these devices. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because WECC_URE4 submitted TFE Part A’s for these devices which are in the “Accepted” status at WECC. As compensating measures, these devices reside in a Physical Security Perimeter PSP and ESP which are highly secured environments. These devices have no keyboards, CD/DVD drives, USB ports, or internet access, and the operating system is proprietary to the equipment so it has minimal exposure to viruses and malware. | WECC_URE4 remediated this issue when it submitted TFEs for the devices in scope.
2012-07-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC2012010515 | CIP-007-1 | R5 | WECC_URE4 self-reported an issue of CIP-007-1 R5. WECC reviewed the Self-Report and determined that WECC_URE4 failed to ensure that eight devices located within an Electronic Security Perimeter (ESP) require and use strong passwords, as required by CIP-007-1 R5.3. WECC_URE5 filed Technical Feasibility Exceptions (TFEs) for these devices late. WECC approved the TFEs pertaining to these devices. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because TFE Part A’s for these devices were submitted and are in the “Accepted” status at WECC. WECC_URE4 stated that these devices reside in certain facilities and it is technically infeasible for these devices to have the protections of CIP-007-1 R5. As compensating measures these devices reside in a Physical Security Perimeter (PSP) and an ESP which are highly secured environments. These devices have no keyboards, CD/DVD drives, USB ports, or internet access, and the operating system is proprietary to the equipment so it has minimal exposure to viruses and malware. | WECC_URE4 remediated this issue when it submitted TFEs for the devices in scope.
2012-06-29 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC201100437 | CIP-003-3 | R6 | FRCC_URE1 self-reported that on one occasion, it implemented a change without documenting approval of the appropriate system control owner or manager, as required by FRCC_URE1's change control and configuration management procedure, which resulted in an issue with CIP-003-3 R6. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Even though the approval of the change was not documented prior to the change, verbal approval was acquired prior to implementation and all the Cyber Assets were tested pursuant to the requirements of CIP-007 R1 for any adverse effects to the existing cyber security control. | FRCC_URE1 completed mitigation activities by conducting an incident review with the FRCC_URE1 personnel responsible for compliance with the Standard and a review of the change management procedure with the energy management system team responsible for implementing the change.
2012-06-29 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2011007514 | CIP-002-3 | R2 | During a FRCC CIP Compliance Audit, it was determined that FRCC_URE1 failed to correctly apply its risk-based assessment methodology as required by CIP-002-3 R1. FRCC_URE1 failed to identify as Critical Assets all transmission facilities at a single station or substation location that are identified by the Reliability Coordinator (RC), Planning Authority, or Transmission Planner as critical to the derivation of Interconnection Reliability Operating Limits (IROLs) and their associated contingencies. Specifically, FRCC_URE1 failed to include one facility that was identified by its RC as an IROL derivative asset, resulting in an issue with CIP-002-3 R2. Thus, FRCC_URE1's Critical Asset list was incomplete for a period of less than three months. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because even though the asset was a Critical Asset, it had been determined in previous years' assessments that FRCC_URE1 had no Critical Cyber Assets. All the Cyber Assets at the identified Critical Asset used non-routable protocol (serial only) and hence no CIP Standards were applicable. | FRCC_URE1 completed mitigation activities by updating the Critical Asset list and Critical Cyber Asset list. The addition of the new Critical Asset did not result in any new Critical Cyber Assets.
2012-06-29 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2011007521 | CIP-007-2a | R7 | During a FRCC CIP Compliance Audit, it was determined that FRCC_URE1 failed to demonstrate that prior to redeployment of its dispatch training workstations, FRCC_URE1 erased the data storage media to prevent unauthorized retrieval of sensitive cyber security or reliability data. FRCC_URE1 redeployed the Cyber Assets outside the Electronic Security Perimeter (ESP) without ensuring that the data storage media were erased. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because most of the cyber security-related information and data was erased from the system using the multiple pass erase method. Additionally, systems were removed from the ESP but were protected by the same Physical Security Perimeter (PSP) and with identical access protection as that employed for Critical Cyber Assets (CCAs). Since these systems were not critical to reliable operation, they were deployed outside the ESP and still controlled and operated by the FRCC_URE1 control center staff. | FRCC_URE1 completed mitigation activities by reviewing the configuration of the assets that were redeployed and confirmed that no CCA-related information exists. FRCC_URE1 has also updated its procedure for allowing exceptions to the cyber security policy.
2012-06-29 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2011007522 | CIP-009-1 | R4 | During a FRCC CIP Compliance Audit, it was determined that FRCC_URE1 failed to demonstrate that its recovery plans included processes and procedures for the backup and storage of information required to successfully restore Critical Cyber Assets. There were no processes and procedures available that demonstrated the backup and storage of information for energy management system workstations, network switches and firewalls. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because although FRCC_URE1 did not document the location or process for storage and retrieval of the backup data, FRCC_URE1 provided sufficient evidence to demonstrate that all the required data was backed up for use in restoration. | FRCC_URE1 completed mitigation activities by documenting steps for backing up the data required for restoration.
2012-06-29 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO201100378 | CIP-006-1 | R1; R1.1 | During a Spot Check, MRO discovered that MRO_URE1 failed to establish a six-wall boundary for a server cabinet in a supervisory control and data acquisition room. The server cabinet resides within an identified Physical Security Perimeter (PSP), but it did not have a completely enclosed border and no alternative measures were documented. Specifically, the server cabinet did not have a solid bottom and it was not secured to the floor, failing to meet the six-wall criteria. The space between the cage door and the floor beneath the floor tile was at least 12 inches by 24 inches or 288 square inches. | MRO determined that this issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although the server cabinet was not bolted to the floor, creating a six-walled boundary, it was within an identified PSP. The cabinet was located within a secure room itself, it just needed to be bolted to the floor. | Upon discovery of the issue, the cabinet was bolted to the floor and the work was completed prior to audit staff departure from MRO_URE1. MRO verified that MRO_URE1 completed its mitigation activities.
2012-06-29 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO201100379 | CIP-006-1 | R3 | During a Spot Check, MRO discovered that MRO_URE1 failed to document and implement technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeter (PSP) twenty-four hours a day, seven days a week. Specifically, MRO_URE1 failed to monitor two access points. A security cabinet utilized to secure the physical access control system has two side panels that are hard key accessible, and both access points were not monitored. | MRO determined that this issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The physical access points in question were sealed access doors to equipment cabinets, within a secure perimeter. The access doors can only be opened with a key, which was destroyed by MRO_URE1 upon installation. In addition, the cabinet is within a restricted area accessible only by key cards and by personnel with proper CIP privileges, such as individuals with personnel risk assessments and relevant training. | MRO_URE1 implemented an alert system to detect unauthorized access through the security cabinet panels. MRO verified that MRO_URE1 completed its mitigation activities.
2012-06-29 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO201100380 | CIP-006-1 | R4 | MRO discovered that MRO_URE1 failed to implement and document the technical and procedural mechanisms for logging physical entry at all access points to the Physical Security Perimeter (PSP). Specifically, MRO_URE1 failed to monitor two access points. A security cabinet utilized to secure the physical access control system has two side panels that are hard key accessible, and both access points were not monitored or logged. | MRO determined that this issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The physical access points in question were sealed access doors to equipment cabinets, within a secure perimeter. The access doors can only be opened with a key, which was destroyed by MRO_URE1 upon installation. In addition, the cabinet is within a restricted area accessible only by key cards and by personnel with proper CIP privileges, such as individuals with personnel risk assessments and relevant training. | MRO_URE1 implemented manual logging and installed signage at the side panel to ensure log entries are made. For cases where someone may gain unauthorized access through a panel, an alert system was implemented. MRO verified that MRO_URE1 completed its mitigation activities.
2012-06-29 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 2 (MRO_URE2) | NCRXXXXX | MRO201100374 | CIP-007-3 | R3; R3.1 | MRO_URE2 self-reported noncompliance with CIP-007-3 R3 because it failed to review and document one security patch within thirty days. MRO_URE2 discovered that a security patch assessment had not been completed for one device for a three-month period. Although the vendor failed to notify MRO_URE2 that the security patch had been released, further investigation revealed that a patch had been released by the vendor in the previous year. Upon discovery, the patch was assessed and determined to be "not applicable" to the device. | MRO_URE2determined that this issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. MRO_URE2 has an account management system which restricts access to the device. Additionally, the single patch that was missed for the vendor device was a non-security patch that was not applicable to MRO_URE2's device type and configuration, and therefore did not require installation. | MRO_URE2 assessed the patch release with existing security patches for applicability. No installations were necessary because the patch was not applicable to MRO_URE2's systems. MRO_URE2verified that MRO_URE2 completed its mitigation activities.
2012-06-29 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 2 (MRO_URE2) | NCRXXXXX | MRO2012009747 | CIP-004-3 | R4; R4.1 | MRO_URE2 self-reported noncompliance with CIP-004-3 R4 because it failed to revoke physical access within seven calendar days for an intern who no longer required such access to Critical Cyber Assets. The intern's business need for the physical access to two locations ended. The intern's supervisor did not report to the same physical location as the intern, so the end of business need was not immediately visible to the supervisor. In advance of his termination, the intern's physical access to one of the two locations was removed by a local and informal supervisor. The other access type was not included in that request. The intern's supervisor was on vacation at the time the business need ended, and did not immediately enter the termination or contact the help desk directly to have the intern's access removed. The following month, the supervisor returned from vacation and removed access. | MRO_URE2determined that this issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although the security access was not revoked from the intern's badge, the intern left his badge at the security desk on his last day of work. Additionally, everyone at the facility was aware that the intern had returned to school and was no longer working. Also, the intern did not have cyber access privileges, and the physical access was removed 19 days after the individual's last day. Therefore, MRO_URE2 was 12 days late in removing the physical access for one location. Additionally, the individual did not use his physical access rights to the location after his need had expired. | MRO_URE2 removed access rights to the individual. MRO_URE2 initiated an access management internal audit in order to understand if more occurrences existed or if any process changes were necessary. At the completion of the internal audit, the NERC CIP team sent a letter and quick reference card to all MRO_URE2 NERC CIP supervisors and updated program documentation to send a letter and quick reference card to supervisors new to NERC CIP responsibilities at the time of their assignment to the area or group. MRO_URE2verified that MRO_URE2 completed its mitigation activities.
2012-06-29 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 2 (MRO_URE2) | NCRXXXXX | MRO201100384 | CIP-006-1 | R1; R1.1 | During a Spot Check, MRO_URE2discovered that MRO_URE2 failed to establish a six-wall boundary for a server cabinet in a supervisory control and data acquisition room. The server cabinet resides within an identified Physical Security Perimeter (PSP), but it did not have a completely enclosed border and no alternative measures were documented. Specifically, the server cabinet did not have a solid bottom and it was not secured to the floor, failing to meet the six-wall criteria. The space between the cage door and the floor beneath the floor tile was at least 12 inches by 24 inches or 288 square inches. | MRO_URE2determined that this issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although the server cabinet was not bolted to the floor, creating a six-walled boundary, it was within an identified PSP. The cabinet was located within a secure room itself, it just needed to be bolted to the floor. | Upon discovery of the issue, the cabinet was bolted to the floor and the work was completed prior to audit staff departure from MRO_URE2. MRO_URE2verified that MRO_URE2 completed its mitigation activities.
2012-06-29 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 2 (MRO_URE2) | NCRXXXXX | MRO201100385 | CIP-006-1 | R3; R3.1 | During a Spot Check, MRO_URE2discovered that MRO_URE2 failed to document and implement technical and procedural controls for monitoring physical access at all access points to the Physical Security Perimeter (PSP) twenty-four hours a day, seven days a week. Specifically, MRO_URE2 failed to monitor two access points. A security cabinet utilized to secure the physical access control system has two side panels that are hard key accessible, and both access points were not monitored. | MRO_URE2determined that this issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The physical access points in question were sealed access doors to equipment cabinets, within a secure perimeter. The access doors can only be opened with a key, which was destroyed by MRO_URE2 upon installation. In addition, the cabinet is within a restricted area accessible only by key cards and by personnel with proper CIP privileges, such as individuals with personnel risk assessments and relevant training. | MRO_URE2 implemented manual logging and installed signage at the side panel to ensure log entries are made. For cases where someone may gain unauthorized access through a panel, an alert system was implemented. MRO_URE2verified that MRO_URE2 completed its mitigation activities.
2012-06-29 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 2 (MRO_URE2) | NCRXXXXX | MRO201100386 | CIP-006-1 | R4; R4.1 | During a Spot Check, MRO_URE2discovered that MRO_URE2 failed to implement and document the technical and procedural mechanisms for logging physical entry at all access points to the Physical Security Perimeter (PSP). Specifically, MRO_URE2 failed to monitor two access points. A security cabinet utilized to secure the physical access control system has two side panels that are hard key accessible, and both access points were not monitored or logged. | MRO_URE2determined that this issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The physical access points in question were sealed access doors to equipment cabinets, within a secure perimeter. The access doors can only be opened with a key, which was destroyed by MRO_URE2 upon installation. In addition, the cabinet is within a restricted area accessible only by key cards and by personnel with proper CIP privileges, such as individuals with personnel risk assessments and relevant training. | MRO_URE2 implemented manual logging and installed signage at the side panel to ensure log entries are made. For cases where someone gains unauthorized access through the panel, an alert system was implemented. MRO_URE2verified that MRO_URE2 completed its mitigation activities on.
2012-06-29 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 2 (MRO_URE2) | NCRXXXXX | MRO201100387 | CIP-004-3 | R4; R4.1 | MRO_URE2 self-reported noncompliance with CIP-004-3 R4 because it failed to ensure access lists for contractors and service vendors are properly maintained. A request was submitted to the help desk to get access for an individual vendor. The ticket was submitted as an incident management ticket, instead of an access change ticket. The help desk routed the incident management ticket (which lacks steward approval, personnel risk assessment (PRA) verification, and cybersecurity training verification) for access configuration. The request was completed and physical access was configured to a NERC CIP location without documented approval by the designated steward for the area. The individual already met the PRA and training prerequisites, so when the lack of documented steward approval in the correct module was discovered within three calendar days, the correct ticket was submitted and the approval was documented. Additionally, an access request was submitted for another individual for unescorted physical access. The request was approved by the supervisor the same day and by the steward three days later; however, a security guard added the clearance code to the badge of a different individual with the same name. During the quarterly access review, MRO_URE2 discovered the inconsistency and access was revoked for the inappropriate individual. Therefore, the individual had unauthorized access for eight days. | MRO_URE2determined that this issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The first issue dealt with an internal routing error giving access to an individual with approval by the wrong manager. The individual already had the appropriate PRA and CIP training, and was properly approved three days after the access was granted. The second issue dealt with giving incorrect access to an individual because he had the same name as another employee. Procedurally, MRO_URE2 always required verification of employee identification numbers before adding or removing access, the issue was caused by an error in following procedure. The individual only had access for eight days. This was an isolated incident and the personnel followed procedure otherwise. Additionally, the individual was part of the CIP program, with an updated PRA and CIP training for access to other areas, although not approved for this subject restricted area. The individual was improperly given access to the to a station which is over 100 miles from the individual's job locale. This issue was discovered during a quarterly review and fixed. MRO_URE2 verified that the improper individual never actually accessed the area for which he was erroneously granted access. | When the lack of documented steward approval was discovered, a formal request was submitted to obtain that specific approval. Immediately upon discovery of the incorrect individual approval on the reports for authorized/actual access, the wrong individual's access was removed. The correct individual received access on his badge to the correct location. The guards have been retrained and the dual verification form updated to include an employee identification number column. The guards are now required to document the employee identification number of the person for which they are adding or removing access. Procedurally, the guards were always required to and are still required to verify the employee identification number before adding or removing access; however, now it is documented on the dual verification form. An updated form was implemented. MRO_URE2verified that MRO_URE2 completed its mitigating activities.
2012-06-29 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2011009039 | CIP-006-3a | R2.2 | During a NPCC CIP Compliance Audit, it was determined that NPCC_URE1 had an issue with CIP-006-3c R2.2. NPCC determined that NPCC_URE1 failed to timely perform a cyber vulnerability assessment for the servers that are involved with the physical access control system (PACS), as specified in CIP-007-3 R8. The cyber vulnerability assessment for the servers at issue was performed approximately six months late. NPCC_URE1's parent company performs vulnerability assessments on a corporate level. Failure to complete the vulnerability assessment, as described above, affected multiple registered entities, including NPCC_URE1. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the servers at issue are not used to monitor or control BPS assets. They control the card-reader system that is utilized to control the Physical Security Perimeter's (PSP) physical access points. In addition to the card-reader system, NPCC_URE1 utilizes security guards and video cameras to monitor access to the PSP. NPCC_URE1 also has strict controls in place for providing physical access to Critical Cyber Assets. NPCC took into account that NPCC_URE1 had previous violations of this Standard. NPCC determined that the instant facts and circumstances were distinguishable and did not represent recurring conduct. None of the prior violations involved cyber vulnerability assessments. Rather, the prior violations involved improper methods of accessing the PSP. Specifically, each of the prior violations involved personnel using a key, as opposed to a card key, to access the PSP. These individuals had been issued keys prior to the effective date of the Reliability Standards, but were not issued card keys for unescorted access to Critical Cyber Assets. In order to mitigate these violations, NPCC_URE1 installed devices that disable the key locks except to allow access by authorized individuals only at a time when the key card reader unit is inoperable. The keys to these new lock devices were issued only to authorized personnel and are used only during emergencies when the key card reader is inoperable. Because the instant issue involved a cyber vulnerability assessment which was performed late, NPCC determined that the issue did not represent recurring conduct by NPCC_URE1. | NPCC_URE1 completed the vulnerability assessment for the servers at issue and revised its compliance assessment process document.
2012-06-29 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 2 (NPCC_URE2) | NCRXXXXX | NPCC2011008448 | CIP-006-3a | R2.2 | NPCC_URE2 self-reported an issue with CIP-006-3a R2.2. During a NPCC CIP Compliance Audit, it was determined that NPCC_URE2 failed to timely perform a cyber vulnerability assessment for the servers that are involved with the physical access control system (PACS), as specified in CIP-007-3 R8. The cyber vulnerability assessment for the servers at issue was performed approximately six months late. NPCC_URE2 performs vulnerability assessments on a corporate level. Failure to complete the vulnerability assessment, as described above, affected multiple registered entities. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the servers at issue are not used to monitor or control BPS assets. They control the card-reader system that is utilized to control the Physical Security Perimeter's (PSP) physical access points. In addition to the card-reader system, NPCC_URE2 utilizes security guards and video cameras to monitor access to the PSP locations. NPCC_URE2 also has strict controls in place for providing physical access to Critical Cyber Assets. | NPCC_URE2 completed the vulnerability assessment for the servers at issue and revised its compliance assessment process document.
2012-06-29 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 3 (NPCC_URE3) | NCRXXXXX | NPCC2011008447 | CIP-006-3a | R2.2 | NPCC_URE3 self-reported an issue with CIP-006-3a R2.2. During a NPCC CIP Compliance Audit, it was determined that NPCC_URE3 failed to timely perform a cyber vulnerability assessment for the servers that are involved with the physical access control system (PACS), as specified in CIP-007-3 R8. The cyber vulnerability assessment for the servers at issue was performed approximately six months late. NPCC_URE3's parent company performs vulnerability assessments on a corporate level. Failure to complete the vulnerability assessment, as described above, affected multiple registered entities, including NPCC_URE3. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the servers at issue are not used to monitor or control BPS assets. They control the card-reader system that is utilized to control the Physical Security Perimeter's (PSP) physical access points. In addition to the card-reader system, NPCC_URE3 utilizes security guards and video cameras to monitor access to the PSP. NPCC_URE3 also has strict controls in place for providing physical access to Critical Cyber Assets. | NPCC_URE3 completed the vulnerability assessment for the servers at issue and revised its compliance assessment process document.
2012-06-29 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 4 (NPCC_URE4) | NCRXXXXX | NPCC2011009018 | CIP-007-3 | R5; R5.1; R5.1.2; R5.3 | NPCC_URE4 self-certified that there was an issue with the credentials window associated with a radio-frequency identification (RFID) system on certain terminals that can access the energy management system in NPCC_URE4's control room and backup control center. It was observed that if a user disregarded the credentials window, he or she could manipulate the other windows populating the desktop behind the credentials window. NPCC determined that NPCC_URE4 had an issue with CIP-007-3 R5.1 and R5.3, since effective controls were not in place for authentication and accountability for access and user activity. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because only control room personnel had access to the console on which the RFID readers were enabled. In addition, this system was used only for operator training, in a training room environment intended to simulate all aspects of the real-time systems. However, this training environment is on a separate network and completely isolated from the Electronic Security Perimeter (ESP). | NPCC_URE4 disabled the badge reader on systems not individually manned 24/7 and required users to enter a valid user name and password. This action was undertaken at both NPCC_URE4’s control room and backup control center. The system manufacturer sent a corrective patch and a supervisor tested the installation and verified that the patch did resolve the issue. All terminals using the RFID system have been patched and have been verified to be working as designed.
2012-06-29 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC201100792 | CIP-007-1 | R5.2.3 | RFC_URE1 self-reported an issue with CIP-007-1 R5.2.3 to ReliabilityFirst. RFC_URE1 discovered that it failed to maintain an audit trail of the account use for multiple shared accounts on its transmission management system and shared accounts in the substation network. Although there was a policy in place to minimize and manage the scope and acceptable use of administrator, shared, and other generic account privileges including factory default accounts, the program which runs the automated audit trails malfunctioned so the automated audit trails failed to function in this instance. | ReliabilityFirst determined that this issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk to the reliability of the BPS was mitigated by the following factors. The individuals who had access to the shared accounts during the relevant time period were properly authorized, had completed training, and had current personnel risk assessments. In addition, RFC_URE1 experienced no cybersecurity incidents during the relevant time period. | RFC_URE1 established manual audit trails for shared accounts on the substation networks and the transmission management system networks. RFC_URE1 tracked and reviewed these audit trails.
2012-06-29 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC201100802 | CIP-007-1 | R5.2.3 | RFC_URE2 self-reported an issue with CIP-007-1 R5.2.3 to ReliabilityFirst. RFC_URE2 discovered that it failed to maintain an audit trail of the account use for multiple shared accounts on its transmission management system and shared accounts in the substation network. Although there was a policy in place to minimize and manage the scope and acceptable use of administrator, shared, and other generic account privileges including factory default accounts, the program which runs the automated audit trails malfunctioned so the automated audit trails failed to function in this instance. | ReliabilityFirst determined that this issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk to the reliability of the BPS was mitigated by the following factors. The individuals who had access to the shared accounts during the relevant time period were properly authorized, had completed training, and had current personnel risk assessments. In addition, RFC_URE2 experienced no cybersecurity incidents during the relevant time period. | RFC_URE2 established manual audit trails for shared accounts on the substation networks and the transmission management system networks. RFC_URE2 tracked and reviewed these audit trails.
2012-06-29 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC201100811 | CIP-007-1 | R5.2.3 | RFC_URE3 self-reported an issue with CIP-007-1 R5.2.3 to ReliabilityFirst. RFC_URE3 discovered that it failed to maintain an audit trail of the account use for multiple shared accounts on its transmission management system and shared accounts in the substation network. Although there was a policy in place to minimize and manage the scope and acceptable use of administrator, shared, and other generic account privileges including factory default accounts, the program which runs the automated audit trails malfunctioned so the automated audit trails failed to function in this instance. | ReliabilityFirst determined that this issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk to the reliability of the BPS was mitigated by the following factors. The individuals who had access to the shared accounts during the relevant time period were properly authorized, had completed training, and had current personnel risk assessments. In addition, RFC_URE3 experienced no cybersecurity incidents during the relevant time period. | RFC_URE3 established manual audit trails for shared accounts on the substation networks and the transmission management system networks. RFC_URE3 tracked and reviewed these audit trails.
2012-06-29 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC201100793 | CIP-007-1 | R6.5 | RFC_URE1 self-reported an issue with CIP-007-1 R6.5 to ReliabilityFirst. RFC_URE1 maintained logs of system events related to cybersecurity but had no documentation to verify that it reviewed the security logs from its transmission management system. | ReliabilityFirst determined that this issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk to the reliability of the BPS was mitigated by the following factors. RFC_URE1 protects the transmission management system with layers of defenses beginning with physical security access controls that isolate the hosts from unauthorized access and any potential vulnerabilities. In addition, RFC_URE1's parent company corporate networks were protected by firewalls, virtual local area network constraints, and domain and local account security restrictions at all relevant times. These protections constitute a defense-in-depth strategy of protection that an intruder would have to overcome to gain access to RFC_URE1's transmission management system. In addition, although RFC_URE1 failed to review the security logs, the security logs for the transmission management system did exist. When RFC_URE1 subsequently reviewed these logs, it found no threatening anomalies. | RFC_URE1 implemented manual monthly security log reviews.
2012-06-29 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC201100803 | CIP-007-1 | R6.5 | RFC_URE2 self-reported an issue with CIP-007-1 R6.5 to ReliabilityFirst. RFC_URE2 maintained logs of system events related to cybersecurity had no documentation to verify that it reviewed the security logs from its transmission management system. | ReliabilityFirst determined that this issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk to the reliability of the BPS was mitigated by the following factors. RFC_URE2 protects the transmission management system with layers of defenses beginning with physical security access controls that isolate the hosts from unauthorized access and any potential vulnerabilities. In addition, RFC_URE2's parent company corporate networks were protected by firewalls, virtual local area network constraints, and domain and local account security restrictions at all relevant times. These protections constitute a defense-in-depth strategy of protection that an intruder would have to overcome to gain access to RFC_URE2's transmission management system. In addition, although RFC_URE2 failed to review the security logs, the security logs for the transmission management system did exist. When RFC_URE2 subsequently reviewed these logs, it found no threatening anomalies. | RFC_URE2 implemented manual monthly security log reviews.
2012-06-29 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC201100812 | CIP-007-1 | R6.5 | RFC_URE3 self-reported an issue with CIP-007-1 R6.5 to ReliabilityFirst. RFC_URE3 maintained logs of system events related to cybersecurity but had no documentation to verify that they reviewed the security logs from its transmission management system. | ReliabilityFirst determined that this issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk to the reliability of the BPS was mitigated by the following factors. RFC_URE3 protects its transmission management system with layers of defenses beginning with physical security access controls that isolate the hosts from unauthorized access and any potential vulnerabilities. In addition, RFC_URE3's parent company corporate networks were protected by firewalls, virtual local area network constraints, and domain and local account security restrictions at all relevant times. These protections constitute a defense-in-depth strategy of protection that an intruder would have to overcome to gain access to RFC_URE3's transmission management system. In addition, although RFC_URE3 failed to review the security logs, the security logs for the transmission management system did exist. When RFC_URE3 subsequently reviewed these logs, it found no threatening anomalies. | RFC_URE3 implemented manual monthly security log reviews.
2012-06-29 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC201100783 | CIP-004-1 | R4.1 | RFC_URE1 self-reported an issue with CIP-004-1 R4.1 to ReliabilityFirst. RFC_URE1 discovered that it failed to review all access lists of personnel who have authorized cyber or authorized unescorted physical access rights to Critical Cyber Assets (CCA). Specifically, RFC_URE1 failed to review the access list for a device at one substation. | ReliabilityFirst determined that this issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk to the reliability of the BPS was mitigated by the following factor. There were no individuals who should have been removed from the access list. All the personnel appropriately had authorized cyber or authorized unescorted physical access rights to CCAs. | RFC_URE1 began reviewing the CCA access lists for the device at issue and continued monitoring access rights to the device until the device was decommissioned. In addition, RFC_URE1 added the CCA access lists to the RFC_URE1 quarterly review of access rights until the device was decommissioned.
2012-06-29 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC201100784 | CIP-005-1 | R3.1 | RFC_URE1 self-reported an issue with CIP-005-1 R4.1 to ReliabilityFirst. RFC_URE1 discovered that it failed to document and implement a monitoring process at each access point to a dial-up device. RFC_URE1's device was a dial-up accessible Critical Cyber Assets (CCA) that used a non-routable protocol. RFC_URE1’s substations contained a device within an Electronic Security Perimeter, and due to oversight, RFC_URE1 failed to document and implement a process for monitoring access at this dial-up device. | ReliabilityFirst determined that this issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The risk to the reliability of the BPS was mitigated by the following factors. The individuals who had access to the device were properly authorized, had been trained, and had current personnel risk assessments. In addition, in order to access a device, an individual must have had a user identification and password that matched the user identification and password created solely for the device access. Further, although RFC_URE1 failed to monitor logs generated for this access point, it did generate the required logs for this access point to the dial-up device as of the compliance date. | RFC_URE1 documented the monitoring process for the security review and logging procedures for the device at issue. In addition, the device at issue was decommissioned.
2012-06-29 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC201100789 | CIP-007-1 | R1.1 | RFC_URE1 self-reported an issue with CIP-007-1 R1.1 to ReliabilityFirst. RFC_URE1’s relay access devices are identified as Critical Cyber Assets (CCA) and reside within the Electronic Security Perimeter (ESP). RFC_URE1 discovered that it had an issue with CIP-007-3 R1.1 for failing to have documentation or records to verify the initial testing that would ensure no adverse effects to existing security controls of the security configuration of the relay access devices. | ReliabilityFirst determined that this issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). However, the risk to the reliability of the BPS was mitigated by the following factors. Although RFC_URE1 failed to document the tests, RFC_URE1 did perform the tests to ensure that the new Cyber Assets did not adversely affect existing cybersecurity controls. Specifically, it utilized the same process for the devices during the installation process as they do for all CCAs, which includes reviewing the controls and testing the configuration of the Cyber Asset. In addition, RFC_URE1 performed a field test consisting of a remote verification of the correct functional configuration of the devices during the time of installation to confirm its standard configuration. Furthermore, the ports and services enabled on the relay access devices beyond those required were located within the ESP, further limiting access. | RFC_URE1 performed a scan of the relay access devices during its annual cyber vulnerability assessment. During that scan, RFC_URE1 compared required ports and services for the relay access devices with actual ports and services and performed testing to determine the necessary configuration changes. RFC_URE1’s change control tool now documents the final disposition of enabled and disabled ports and services. RFC_URE1 performed the required changes to the relay access devices.
2012-06-29 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC201100799 | CIP-007-1 | R1.1 | RFC_URE2 self-reported an issue with CIP-007- R1.1 to ReliabilityFirst. RFC_URE2’s relay access devices are identified as Critical Cyber Assets (CCA) and reside within the Electronic Security Perimeter (ESP). RFC_URE2 discovered that it had an issue with CIP-007-3 R1.1 for failing to have documentation or records to verify the initial testing that would ensure no adverse effects to existing security controls of the security configuration of the relay access devices. | ReliabilityFirst determined that this issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). However, the risk to the reliability of the BPS was mitigated by the following factors. Although RFC_URE2 failed to document the tests, RFC_URE2 did perform the tests to ensure that the new Cyber Assets did not adversely affect existing cybersecurity controls. Specifically, it utilized the same process for the devices during the installation process as they do for all CCAs, which includes reviewing the controls and testing the configuration of the Cyber Asset. In addition, RFC_URE2 performed a field test consisting of a remote verification of the correct functional configuration of the devices during the time of installation to confirm its standard configuration. Furthermore, the ports and services enabled on the relay access devices beyond those required were located within the ESP, further limiting access. | RFC_URE2 performed a scan of the relay access devices during its annual cyber vulnerability assessment. During that scan, RFC_URE2 compared required ports and services for the relay access devices with actual ports and services and performed testing to determine the necessary configuration changes. RFC_URE2's change control tool now documents the final disposition of enabled and disabled ports and services. RFC_URE2 performed the required changes to the relay access devices.
2012-06-29 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC201000533 | CIP-002-1 | R1 | The SERC CIP Spot-Check team reported that SERC_URE1 had an issue with CIP-002-1 R1, stating that historical versions of SERC_URE1’s risk-based assessment methodology (RBAM) did not consider the assets listed in R1.2.1 through R1.2.7. SERC staff reviewed SERC_URE1 historical versions of its RBAM and Critical Asset lists and determined that SERC_URE1 did not consider the assets listed in R1.2.1 through R1.2.7 in its RBAM. | SERC staff determined that the issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because: 1. SERC_URE1 has no Critical Assets and does not own or operate any facilities that would meet any of the Critical Asset Criteria set forth in CIP-002-4; and 2. SERC_URE1 is a partial requirements supplier. SERC_URE1 does not own any transmission or generation assets. | SERC staff verified that SERC_URE1 completed the following actions: SERC_URE1 revised its RBAM to specifically address the criteria listed in CIP-002-1 R1.
2012-06-29 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 2 (SERC_URE2) | NCRXXXXX | SERC201000742 | CIP-005-2 | R3 | SERC_URE2 self-reported an issue with CIP-005-2 R3.2, stating that it had failed to review access logs for attempts at or actual unauthorized access within ninety calendar days as required. SERC staff learned that SERC_URE2 completed a review of its access logs, but due to an error in data entry, the date of completion entered in its internal tracking mechanism was incorrect. Due to the error in data entry, SERC_URE2 actually completed its third quarter review one day late, 91 calendar days after the previous review. | SERC staff determined that the issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because: 1. SERC_URE2 conducted its review one day late and found no attempts at or actual unauthorized access in the access logs; and 2. SERC_URE2 had a process in place for reviewing access logs but was late in completing that review due to an error in entering the date of the previous access log review. | SERC staff verified that SERC_URE2 completed the following actions: 1. SERC_URE2 shortened the interval between access log reviews to 75 days to provide a 15 day buffer on the 90-day requirement. 2. SERC_URE2 revised and implemented enhancements to its manual access log review procedure, which add more detail to the following key steps in the process: (a) gathering access log data for review; (b) analyzing the access log data; (c) recording the results of the access log review; (d) calculating and tracking the next access log review milestone dates; and (e) independently reviewing access log evidence and calculated dates for the next review period. 3. The enhancements to the access log review procedure also ensure that the data obtained for access log reviews always overlap with the previous review period and all pertinent dates used to ensure compliance are individually tracked.
2012-06-29 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 3 (SERC_URE3) | NCRXXXXX | SERC201000741 | CIP-005-2 | R3 | SERC_URE3 self-reported an issue with CIP-005-2 R3.2, stating that it had failed to review access logs for attempts at or actual unauthorized access within ninety calendar days as required. SERC staff learned that SERC_URE3 completed a review of its access logs, but due to an error in data entry, the date of completion entered into its internal tracking mechanism was incorrect. Due to the error in data entry, SERC_URE3 actually completed its third quarter review one day late, 91 calendar days after the previous review. | SERC staff determined that the issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because: 1. SERC_URE3 conducted its review one day late and found no attempts at or actual unauthorized access in the access logs; and 2. SERC_URE3 had a process in place for reviewing access logs but was late in completing that review due to an error in entering the date of the previous access log review. | SERC staff verified that SERC_URE3 completed the following actions: 1. SERC_URE3 shortened the interval between access log reviews to 75 days to provide a 15 day buffer on the 90-day requirement; 2. SERC_URE3 revised and implemented enhancements to its manual access log review procedure, which add more detail to the following key steps in the process: (a) gathering access log data for review; (b) analyzing the access log data; (c) recording the results of the access log review; (d) calculating and tracking the next access log review milestone dates; and (e) independently reviewing access log evidence and calculated dates for the next review period. 3. The enhancements to the access log review procedure also ensure that the data obtained for access log reviews always overlap with the previous review period and all pertinent dates used to ensure compliance are individually tracked.
2012-06-29 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP201100626 | CIP-002-3 | R1.1 | During a CIP audit of SPPRE_URE1, the SPP RE CIP audit team discovered a possible issue with CIP-002-3 R1.1. The audit team found that while SPPRE_URE1 developed and maintained a risk-based methodology (RBAM) to identify Critical Assets (CAs), which included a defined procedure for performing its RBAM and included the considerations listed in CIP-002-3 R1.2, SPPRE_URE1 failed to fully describe its evaluation criteria for identifying CAs, thereby presenting an issue with CIP-002-3 R1.1. | SPP RE determined that the issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because although SPPRE_URE1 did not fully describe its evaluation criteria for identifying CAs in its RBAM, SPPRE_URE1 did have an RBAM that it documented and maintained. Furthermore, SPPRE_URE1 was able to apply its RBAM sufficiently to determine that it did not own any CAs or any Critical Cyber Assets (CCAs). The subsequent changes implemented by SPPRE_URE1 to fully describe its evaluation criteria in its RBAM did not result in the identification of any additional CAs. Therefore, SPP RE determined that SPPRE_URE1's procedure did not fully describe the evaluating criteria for identifying CAs, in accordance with the applicable Requirement. | SPPRE_URE1 implemented an addition to its RBAM that includes specific criteria for evaluating and identifying CAs. The specific criteria addresses the requirements of CIP-002-3 R1.1.
2012-06-29 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE201100473 | CIP-004-3 | R2 | Texas RE_URE1 self-reported a possible compliance issue with CIP-004-3 R2. Texas RE_URE1 stated that it hired a planning supervisor at one of its plants. Four days later, the supervisor was granted authorized unescorted physical access to Texas RE_URE1's Physical Security Perimeters (PSPs) containing Critical Cyber Assets (CCAs), although the supervisor had not completed Texas RE_URE1's cyber security training program yet. Texas RE also determined that this compliance issue was the result of a combination of (1) the two employees that were authorizing access and issuing the access badges were relatively new in their roles; and (2) the access request and authorization form did not require a confirmation of the date when cyber security training was completed. The supervisor's access was revoked approximately six months later, the same day Texas RE_URE1 discovered the compliance issue. Therefore, Texas RE determined that the issue was from when access was granted to the supervisor to when access was revoked. The supervisor completed the required training and access was given back to him a week after the access was revoked. | This compliance issue posed a minimal risk and did not pose a serious or substantial risk to the bulk power system (BPS) because the risk was mitigated by several factors. First, the supervisor had undergone partial training prior to receiving authorized unescorted physical access to Texas RE_URE1's PSPs containing CCAs. Texas RE_URE1's code of conduct and other corporate policies were provided to the supervisor in question prior to granting him such access. These corporate policies contain information that mirror many of the items included in Texas RE_URE1's Critical Infrastructure Protection (CIP) training, thereby reducing the risk to the BPS presented by the supervisor's lack of required cyber security training. Second, the supervisor's personnel risk assessment (PRA) was successfully completed the prior year, prior to granting him access to the PSPs. Third, the supervisor had physical access, but no cyber access to the CCAs for the period in question, and his job did not require any physical or cyber interaction with the CCAs. Also, Texas RE determined that there was only a limited possibility of granting access to Texas RE_URE1's PSPs containing CCAs prior to completing the required training because of the relatively small number of new applications for such access. Texas RE determined that the potential number of such improper access authorizations was reduced by the fact that the employees involved in authorizing access and issuing badges knew that cyber security training was required prior to granting authorization. Therefore, only one isolated incident of noncompliance with this Standard has occurred during the issue period. | Texas RE_URE1 revoked the supervisor's access the same day the violation was discovered and granted access again when the supervisor completed the required training. Additional training was completed for those individuals responsible for managing and granting access to NERC CIP protected areas at the plant in question. Texas RE_URE1's NERC CIP access authorization form was modified to include a verification of the date that cyber security training was complete and required that training was confirmed before access was granted. Additional cyber security training was conducted for other plant employees in order to increase awareness of NERC CIP cyber security requirements. Finally, Texas RE_URE1 completed a company-wide review of its NERC CIP access management and control procedures to avoid future instances of noncompliance with this Standard. Texas RE verified completion of these mitigation activities.
2012-06-29 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2012009958 | CIP-003-3 | R2 | During an internal review of its Compliance Program, WECC_URE1 self-reported a possible issue of CIP-003-3 R2. According to the Self-Report, WECC_URE1 failed to assign a single manager with overall responsibility and authority for leading and managing the entity’s implementation of, and adherence to, Standard CIP-002-3 through CIP-009-3 for approximately three months. Although WECC_URE1 did not assign a CIP senior manager, it has self-certified that it did not own any Critical Assets (CAs) or Critical Cyber Assets (CCAs). In the past, WECC_URE1 was not required to be compliant with CIP-003 through CIP-009 because it did not have CAs or CCAs. This was accurate until April 1, 2010, when CIP-003-2 became enforceable for WECC_URE1 due to changes in Section 4.2.3 of CIP-003-2. The change required in Version two was also required when Version three became enforceable on October 1, 2010. The change requires CIP-003-3 R2 to apply to all Responsible Entities, including Responsible Entities that have no CCAs. WECC_URE1 failed to notice this change in the Standard and as a result failed to assign a senior manager with overall responsibility and authority for leading and managing the entity's implementation of, and adherence to, Standards CIP-002-3 through CIP-009-3, as required by CIP-003-3 R2. | WECC determined this issue posed a minimal and not serious or substantial risk to the reliability of the bulk power system. Although WECC_URE1 failed to assign a senior manager as required by CIP-003-3 R2, WECC determined that the issues posed a minimal risk to the reliability of the bulk power system because WECC_URE1 has a null list of CAs or CCAs. Additionally, WECC_URE1 does not operate any facilities that would meet any of the Critical Asset identification criteria. | WECC verified that WECC_URE1 had completed the following mitigating activities: WECC_URE1 assigned a senior manager with the overall responsibility and authority for leading and managing the implementation of and adherence to CIP-002 through CIP-009. WECC_URE1’s general compliance manager was trained on CIP standards and his responsibilities to ensure that the Cyber Security Assignment is properly documented and stored.
2012-06-29 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2012009103 | CIP-005-1 | R1 | WECC_URE2 submitted a Self-Report addressing possible noncompliance with CIP-005 R1. WECC_URE2 failed to ensure it provided all the protections specified in CIP-005 R1.5 to two token servers used in the access control and monitoring of Electronic Security Perimeters (ESPs). Specifically, WECC_URE2 did not have a list of individuals with access to the token servers, thus, WECC_URE2 was not able to provide evidence of compliance for four sub-requirements of CIP-007 R5 (i.e., CIP-007 R5.1.1, CIP-007 R5.1.3, CIP-007 R5.2.2, CIP-007 R5.2.3). WECC_URE2 did provide CIP-007 R5.3 protections and additionally submitted an acceptable and applicable Technical Feasibility Exception for CIP-007 R5.3.2. WECC_URE2 did not conduct cyber vulnerability assessments on these devices (pursuant to CIP-007 R8), did not conduct an annual review pursuant to CIP-007 R9 and did not have or exercise a recovery plan nor test the devices backup media at least annually pursuant to CIP-009 R1, R2, and R5. Accordingly, WECC determined WECC_URE2 had a possible issue of CIP-005-1 R1.5. Although Enforcement determined WECC_URE2 did not apply the above-listed protections to two servers, the devices associated with the noncompliance support WECC_URE2’s multi-factor authentication security protocols and are limited to a single factor of the authentication protocol. Further, these devices are part of WECC_URE2’s defense-in-depth security architecture. Thus, if these token servers were compromised, a valid username and password would still be required to gain access into WECC_URE2. Therefore, the Cyber Assets inside the ESPs would remain protected. | WECC determined this issue posed a minimal and not serious or substantial risk to the reliability of the bulk power system. Despite not treated in accordance with the protective measures specified in CIP-005-1 R1.5, the devices in scope had malware prevention tools, restricted logical access with active directory, used tripwire file monitoring, and were located in a Physical Security Perimeter (PSP). Further, although WECC_URE2 did not have a recovery plan for the devices, it did maintain backups that could have been used to recover the token servers. The devices were located in a secure network and behind restrictive firewalls. Additionally, the devices were configured to send all syslogs to the entity’s system event monitoring servers; these servers are configured for automated alerting. Most importantly, the devices in scope were responsible for only one of the two factors required to gain access to the ESPs. To gain access into the ESPs, a user requires a valid user name and password from active directory, and a “token” from the devices in scope. Thus, if these token servers were compromised, a valid username and password would still be required to gain access into the ESPs. Therefore, the Cyber Assets inside the ESPs would remain protected, as access into the ESPs requires both factors. Additionally, all individuals with access to CCAs had current training and PRAs. | WECC_URE2 evaluated the assets to ensure WECC_URE2 afforded protective measures specified in CIP-003, CIP-004 R3, CIP-005 R2, R3, CIP-006 R3 to the devices. WECC_URE2 added the Cyber Assets to its list of Cyber Assets used for electronic access control and monitoring. WECC_URE2 completed its evaluation of the devices and the applicable protective measures. WECC_URE2 ensured it afforded these devices the protective measures specified in CIP-008 R1, R2, CIP-009 R1, R2, R3, R4, R5, and CIP-007 R1, R3, R4, R5, R6, R7, R8, R9.
2012-06-29 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2012009104 | CIP-005-1 | R2 | WECC_URE2 submitted a Self-Report addressing possible noncompliance with CIP-005 R2. WECC_URE2 did not ensure all its access control devices displayed an appropriate use banner, thus WECC determined WECC_URE2 was in noncompliance with CIP-005-1 R2. | WECC determined this issue posed a minimal and not serious or substantial risk to the reliability of the bulk power system. All Critical Cyber Assets (CCAs) inside the ESP displayed an appropriate use banner upon interactive access and were located in a Physical Security Perimeter and an Electronic Security Perimeter, and thus afforded the protections of CIP-005 and CIP-006. Further, if inappropriate use was suspected, WECC_URE2’s tripwire file monitoring is configured to detect any changed files on the CCAs. The devices were also configured to send all system logs to the entity’s system event monitoring server which is configured for automated alerting upon unauthorized access attempts. Additionally, all individuals with access to CCAs had current training and PRAs. | WECC_URE2 evaluated the assets to ensure WECC_URE2 afforded protective measures specified in CIP-003, CIP-004 R3, CIP-005 R2, R3, CIP-006 R3 to the devices. WECC_URE2 added the Cyber Assets to its list of Cyber Assets used for electronic access control and monitoring. WECC_URE2 completed its evaluation of the devices and the applicable protective measures. WECC_URE2 ensured it afforded these devices the protective measures specified in CIP-008 R1, R2, CIP-009 R1, R2, R3, R4, R5, and CIP-007 R1, R3, R4, R5, R6, R7, R8, R9.
2012-06-29 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2012009975 | CIP-005-1 | R2 | WECC conducted an onsite Compliance Audit (Audit) of WECC_URE3. During a site tour conducted by WECC of WECC_URE3's facilities, WECC identified three electronic access control devices that did not display an appropriate use banner on the screen upon all interactive access attempts. The three devices identified during the Audit were electronic access control devices required to display an appropriate use banner pursuant to R2.6. WECC_URE3’s failure to implement a use banner that displays upon all interactive access attempts constitutes an issue of CIP-005-1 R2. | WECC determined this issue posed a minimal and not serious or substantial risk to the reliability of the bulk power system. The risks posed by WECC_URE3 noncompliance are limited given compensating measures in place during the noncompliance period. WECC_URE3 has an in-depth defense structure to ensure electronic security. This includes network segmentation within ESPs. All Cyber Assets and Critical Cyber Assets are secured behind firewalls wherein access is controlled, logged and monitored. All personnel with access to each of the three devices have completed Cyber Security training and have completed personnel risk assessments. Each of the three devices is password protected. | WECC_URE3 installed an appropriate use banner on the three devices. The appropriate use banner is displayed on devices upon all interactive access attempts.
2012-06-29 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 5 (WECC_URE5) | NCRXXXXX | WECC2012009452 | CIP-005-3 | R2 | WECC_URE5 submitted a Self Certification citing possible noncompliance with CIP-005-3 R2. Specifically, WECC_URE5 reported that it commissioned three devices provisioning Electronic Security Perimeter (ESP) access control and monitoring without having filed a Technical Feasibility Exception (TFE) for CIP-005-3 R2.6. CIP-005-3 R2.6 requires entities to ensure that devices provisioning access control and monitoring to the ESP, where technically feasible, display an appropriate use banner upon all interactive attempts. In this case, WECC determined that WECC_URE5 failed to file a timely TFE for three devices on which it was not technically feasible to display an appropriate use banner as required by CIP-005-3 R2.6. | WECC determined this issue posed a minimal and not serious or substantial risk to the reliability of the bulk power system. The three devices were secured behind firewalls that did display the banner. The devices were secured within an ESP and a Physical Security Perimeter. Electronic and physical access thereto was, therefore, controlled and monitored. A limited number of personnel were granted electronic or physical access rights to the devices. These individuals all completed personnel risk assessments and cybersecurity training. | WECC_URE5 filed a TFE for each of the three devices identified herein. WECC reviewed WECC_URE5’s TFE and issued a notice of TFE acceptance.
2012-06-29 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 6 (WECC_URE6) | NCRXXXXX | WECC2011008670 | CIP-007-1 | R4 | CIP-007-1 R4 requires WECC_URE6 to use anti-virus software and other malicious software (malware) prevention tools, where technically feasible, to detect, prevent, deter, and mitigate the introduction, exposure, and propagation of malware on all Cyber Assets within the Electronic Security Perimeter(s). WECC_URE6 submitted a Self-Report for possible noncompliance with CIP-007-1 R4. WECC reviewed the Self-Report and determined that WECC_URE6 was in noncompliance with CIP-007-1 R4 for its failure to have anti-virus and other malware software installed. Related to this Self-Report, WECC_URE6 submitted Technical Feasibility Exception Requests (TFEs), addressing its technical infeasibility to install anti-virus and other malware software, to comply with CIP-007-1 R4. WECC approved the TFE requests. Based on the technically feasible language, WECC determined that WECC_URE6’s approved TFE requests satisfied the requirements of CIP-007-1 R4. However, as a result of the late filing date, WECC determined WECC_URE6 was in noncompliance with CIP-007-1 R4. | WECC determined this issue posed a minimal and not serious or substantial risk to the reliability of the bulk power system. All devices are located within an ESP and a Physical Security Perimeter (PSP) with no direct connection to the internet or the use of email. Also, anti-virus software is installed on all other devices in the ESP and there is 24/7 monitoring and logging of physical and cyber access to these devices. Additionally, the ESPs have intrusion protection system sensors to inspect network traffic at the access points. | WECC_URE6 filed the TFE, WECC approved the Part A and Part B TFE.
2012-06-29 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 7 (WECC_URE7) | NCRXXXXX | WECC201102981 | CIP-007-1 | R4 | WECC_URE7 self-certified a potential remediated issue of CIP-007-1 R4. WECC contacted WECC_URE7 to discuss its self-certification. WECC_URE7 stated that it failed to install anti-virus software and other malware prevention tools on twelve of its Critical Cyber Assets (CCAs). The CCAs are human-machine interfaces (HMI) that control gas compressors, analyzers, and facilitate programmable logic controllers that manage blackstart generators. The HMIs involved utilized operating systems that did not support anti-virus and malware prevention tools. As a result, it was technically infeasible for WECC_URE7 to install anti-virus and malware prevention tools on the devices involved. | WECC_URE7 provided WECC evidence from its vendor that substantiated the inability to install anti-virus and malware prevention tools on these devices. WECC determined this remediated issue posed a minimal risk to the reliability of the bulk power system. The devices were located inside of an Electronic Security Perimeter and the individuals who had access to the devices had personnel risk assessments (PRAs) and CIP training. | WECC_URE7 removed the routable connectivity of these devices and serially connected them to its Electronic Security Perimeter.
2012-06-29 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 8 (WECC_URE8) | NCRXXXXX | WECC2011008635 | CIP-005-1 | R2 | WECC audited the WECC_URE8's compliance with CIP-005-1 R2. At the Audit, WECC_URE8 produced an Electronic Security Perimeter (ESP) architectural diagram detailing the configurations of its ESP at its substations. The diagrams the entity produced exemplified separate ESPs at each substation. Based on a review of these diagrams and an evaluation of WECC_URE8's individual ESPs at each of its substations, the Audit Team concluded that WECC_URE8 failed to implement default restrictions to its substation ESP access points as required by CIP-005-1 R2. In addition, the Audit Team concluded that WECC_URE8 failed to restrict traffic to specified ports and services on the substations ESP access points to all Cyber Assets with the ESP. Although WECC_URE8’s architectural diagrams reflect individual substation ESPs and, as individual substation ESPs WECC_URE8 failed to implement appropriate access point controls, but it has in place a larger ESP that encompasses all the substations involved and does have appropriate access point controls. WECC_URE8 has implemented a security configuration on the larger ESP that ensures that all traffic to and from the substations involved are protected by a firewall with restrictive access controls. | Although WECC_URE8 failed to implement proper control as access points to an ESP which could allow unauthorized access to Critical Cyber Assets, WECC determined that the issue posed a minimal risk to the reliability of the bulk power system. In this instance, WECC_URE8 utilized a firewall at each substation. All traffic is decrypted and forced into a sub-interface on the firewall for rules processing. The firewall contains restrictive controls for each interface, thus ensuring only specific access is allowed based upon IP addresses and specific ports/services. In addition, WECC_URE8 has access control lists that deny access by default. | WECC_URE8 utilizes the firewall at each substation. All traffic is decrypted and forced into a sub-interface on the firewall for rules processing. The firewall contains restrictive controls for each interface, thus ensuring only specific access is allowed based upon IP addresses and specific ports/services. In addition, WECC_URE8 has implemented access control lists that deny access by default.
2012-05-30 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2012009741 | CIP-002-3 | R4 | FRCC_URE1 self-certified an issue with CIP-002-3 R4 using the Self-Certification form. FRCC_URE1 did not timely complete the annual Critical Asset (CA) and Critical Cyber Asset (CCA) list and risk-based assessment methodology (RBAM), with approval signed and dated by the senior manager. FRCC_URE1 did timely complete a RBAM application review as part of its response to the NERC survey and timely identified all its CAs and CCAs but did not document the signatures of the senior manager. FRCC_URE1 stated that the list has not changed in the prior two years. The signed RBAM approval and list of CAs and CCAs was completed 26 days past the required date. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). FRCC_URE1 did timely complete a RBAM application review as part of its response to the NERC survey and timely identified all its CAs and CCAs but did not document the signatures of the senior manager. FRCC_URE1 was only 26 days late in documenting the annual review, and the annual review and assessment identified no CCAs and no additional CAs. | FRCC_URE1 completed mitigation activities by obtaining the senior manager's signed and dated approval. Second, FRCC_URE1 scheduled its review(s) for the next two years. FRCC_URE1 also discussed the issue with the personnel responsible for RBAM application and emphasized timely completion of all required compliance activities.
2012-05-30 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 2 (FRCC_URE2) | NCRXXXXX | FRCC2012010064 | CIP-004-3 | R2; R2.3 | FRCC_URE2 self-reported an issue with CIP-004-3 R2.3 because one of its contractors did not complete his required annual cyber security training when his annual training expired. He had authorized logical access to Critical Cyber Assets and it was discovered 64 days later, when he accessed the systems after a long gap, that his training was expired. Upon discovery of the expired annual training, the contractor's access was revoked. The subject contractor completed a successful training the following day. Thus, the duration of the issue was 65 days. The concerned contractor was previously trained in prior years. FRCC_URE2 originally self-reported an issue with CIP-007-3 R5, but following FRCC review and guidance, FRCC_URE2 corrected and re-submitted the Self-Report for the correct CIP Standard and requirement, as described in the previous paragraph. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the subject contractor had previously completed training , and the last course had no significant updates. Further, the contractor was a trusted vendor with a valid long-term contract and a valid personnel risk assessment. The contractor promptly completed the training refresher with the resultant delay of two months. During that time, he had access to Cyber Assets only once. Although FRCC_URE2 has violated this Standard previously, the instant issue nonetheless does not represent recurring conduct. The prior violation involved an employee who only received partial training, whereas this issue relates to contractor training. Further, the previous instance was recorded in the early stages of CIP-004-2 R2 compliance for initial training. Following the prior violation, FRCC_URE2 updated many controls and imparted training to all responsible for controlling access. In the current instance, the training lapse resulted from the extended absence of the contractor. | FRCC_URE2 completed mitigation activities by having the contractor complete the required annual training. Additionally, FRCC_URE2 conducted activities including one-on-one discussion and additional awareness training for FRCC_URE2 personnel involved with handling of contractor engagements, in order to improve awareness of mandatory annual retraining requirements for those involved with the process.
2012-05-30 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO201100436 | CIP-007-3 | R3; R3.1 | MRO_URE1 self-reported noncompliance with Reliability Standard CIP-007-3 R3 because it failed to assess applicability of a security patch for a certain software within 30 days. The application security patch was assessed and installed 11 days after the 30-day time window required by CIP-007-3 R3.1. The entity’s Energy Management System (EMS) group utilizes two methods for identifying updates and security patches for applications installed on EMS Cyber Assets residing within the Electronic Security Perimeter (ESP). Most scheduled and out-of-cycle updates for another application are downloaded automatically consistent with the monthly patch release process. Patches and upgrades for other applications, such as the application at issue, are obtained from a number of software vendors, each with their own notification system and patch or upgrade release schedule. The downloading and assessment of patches to these applications is a manual process previously assigned to one of the EMS system administrators. The EMS system administrator to whom responsibility was assigned for monitoring and assessing application security patches and upgrades resigned from MRO_URE1. When transitioning his responsibilities to the other two EMS system administrators, the individual failed to transfer the contact information for the application patch release notification to his fellow system administrators. As a result, the security patch notification did not reach the two EMS system administrators. One of the EMS system administrators observed that he had not seen any change control tickets to update the application. He proceeded to log into the application's website to check for the most recent security patch releases. He found that a security update had been released 41 days prior. The system administrator was able to assess and install the security patch on the same day; however, he recognized the patch was assessed 11 days after the 30-day window required by CIP-007 R3.1 and reported the issue to his supervisor. | The issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because MRO_URE1 only missed one patch for a short period of time, and that patch dealt with document-reader software installed on machines without internet access. Additionally, the software was only enabled in the "Protected Mode," which prevents and restricts security vulnerabilities. | Upon discovering the missing security patch, the system administrator immediately proceeded to download, assess, test and install the security patch on the application. The system administrator then checked and confirmed that all applications installed on EMS Cyber Assets residing within the ESP were running the latest security patch releases. To mitigate the issue and preclude recurrence, MRO_URE1 revised its security patch management monitoring and assessment process for applications that are not downloaded automatically and are residing within the ESP as follows: (1) confirmed that correct EMS contact information was contained in all associated vendor patch release notification systems; (2) revised the EMS security patch management procedure for applications to require personnel to check with each vendor for security patch releases every 30 calendar days; and (3) added a list of the applications and their respective vendors to the procedure.
2012-05-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2011001252 | CIP-007-3 | R3; R3.1 | RFC_URE1 self-reported noncompliance with Reliability Standard CIP-007-3 R3 because it failed to assess applicability of a security patch for a certain software within 30 days. The application security patch was assessed and installed 11 days after the 30-day time window required by CIP-007-3 R3.1. The entity’s Energy Management System (EMS) group utilizes two methods for identifying updates and security patches for applications installed on EMS Cyber Assets residing within the Electronic Security Perimeter (ESP). Most scheduled and out-of-cycle updates for another application are downloaded automatically consistent with the monthly patch release process. Patches and upgrades for other applications, such as the application at issue, are obtained from a number of software vendors, each with their own notification system and patch or upgrade release schedule. The downloading and assessment of patches to these applications is a manual process previously assigned to one of the EMS system administrators. The EMS system administrator to whom responsibility was assigned for monitoring and assessing application security patches and upgrades resigned from RFC_URE1. When transitioning his responsibilities to the other two EMS system administrators, the individual failed to transfer the contact information for the application patch release notification to his fellow system administrators. As a result, the security patch notification did not reach the two EMS system administrators. One of the EMS system administrators observed that he had not seen any change control tickets to update the application. He proceeded to log into the application's website to check for the most recent security patch releases. He found that a security update had been released 41 days prior. The system administrator was able to assess and install the security patch on the same day; however, he recognized the patch was assessed 11 days after the 30-day window required by CIP-007 R3.1 and reported the issue to his supervisor. | The issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because RFC_URE1 only missed one patch for a short period of time, and that patch dealt with document-reader software installed on machines without internet access. Additionally, the software was only enabled in the "Protected Mode," which prevents and restricts security vulnerabilities. | Upon discovering the missing security patch, the system administrator immediately proceeded to download, assess, test and install the security patch on the application. The system administrator then checked and confirmed that all applications installed on EMS Cyber Assets residing within the ESP were running the latest security patch releases. To mitigate the issue and preclude recurrence, RFC_URE1 revised its security patch management monitoring and assessment process for applications that are not downloaded automatically and are residing within the ESP as follows: (1) confirmed that correct EMS contact information was contained in all associated vendor patch release notification systems; (2) revised the EMS security patch management procedure for applications to require personnel to check with each vendor for security patch releases every 30 calendar days; and (3) added a list of the applications and their respective vendors to the procedure.
2012-05-30 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 2 (MRO_URE2) | NCRXXXXX | MRO2012009154 | CIP-003-1 | R2 | MRO_URE1 self-certified noncompliance with CIP-003-1 R2 because it failed to assign a single senior manager with overall responsibility and authority for leading and managing the entity’s implementation of, and adherence to, Standards CIP-002-1 through CIP-009-1. | The issue posed a minimal risk and did not pose serious or substantial risk to the reliability of the bulk power system because although the entity failed to have a policy appointing a senior manager in charge of the responsibilities for CIP-002-3 through CIP-009-3, MRO_URE1 did have an unassigned senior manager in charge. This senior manager was ultimately assigned as the senior manager per the Standard. | MRO_URE1's general manger authorized and approved a policy that designates the electrical engineering manager as the single senior manager with overall responsibility and authority for leading and managing the entity’s adherence to CIP-002-3 through CIP-009-3. MRO_URE2verified that the entity completed its Mitigation Plan.
2012-05-30 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 3 (MRO_URE3) | NCRXXXXX | MRO201100437 | CIP-004-1 | R4; R4.1 | During a spot check, MRO determined that MRO_URE2 failed to perform quarterly reviews of physical and cyber access for a six-quarter period. The access rights of users were not reviewed quarterly for a installed system, which is used in performing backups of Critical Cyber Assets, as well as workstations at the backup control center. The backup system is only accessed by five individuals, all of whom were involved in the installation of the system and have proper access. The workstations have only two accounts on them - one for use by system operators in the event that MRO_URE2 would need to relocate to its backup center, and a single administrative account. This account is only accessible by one individual, a long-term employee that is the primary administrator for all CIP workstations and whose access was reviewed quarterly for CIP workstations that did not reside at the backup control center. | The issue posed a minimal risk and did not pose serious or substantial risk to the reliability of the bulk power system because the backup system is only accessed by five individuals, all of whom were involved in the installation of the system and have proper access. The workstations have only two accounts on them - one for use by system operators in the event that the entity would need to relocate to its backup center, and a single administrative account. This account is only accessible by one individual, a long-term employee that is the primary administrator for all CIP workstations and whose access was reviewed quarterly for CIP workstations that did not reside at the backup control center. Furthermore, these workstations reside on a separate network from the primary Energy Management System and are powered off except for periodic checks and patch installation. For both of the workstations and the backup system, accounts were reviewed annually as part of MRO_URE2's annual vulnerability assessment. Additionally, MRO_URE2 has not needed to operate its backup control center or use the workstations related to this issue, other than for the purpose of maintaining them, and MRO_URE2 did not have any reportable cyber incidents during the period. | MRO_URE2 performed the following actions to mitigate the issue: (1) identified missing devices and associated accounts on the quarterly access review reports; (2) updated the quarterly access review reports to include omitted information; and (3) conducted the quarterly access review and verified that objectives were met. MRO verified that MRO_URE2 completed its Mitigation Plan.
2012-05-30 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 3 (MRO_URE3) | NCRXXXXX | MRO201100438 | CIP-005-1 | R2; R2.5.3 | During a spot check, MRO determined that MRO_URE2 failed to perform quarterly reviews of the access rights of users for access point devices in accordance with CIP-005-1 R2.5.3. Specifically, MRO_URE2 was unable to provide evidence that it performed reviews of access point devices for a six-quarter period. The access point devices are only accessed by two employees. | The issue posed a minimal risk and did not pose serious or substantial risk to the reliability of the bulk power system because the access point devices are only accessed by two employees, and both employees are responsible for other CIP assets which did have quarterly access reviews performed. MRO_URE2 also has an intrusion detection system to alert it of unauthorized access to the Electronic Security Perimeter, and the accounts on all access point devices were reviewed annually as part of the entity's annual vulnerability assessment. Additionally, MRO_URE2 did not have any reportable cyber incidents during the period. | MRO_URE2 performed the following actions to mitigate the issue: (1) identified missing devices and associated accounts on the quarterly access review reports; (2) updated the quarterly access review reports to include omitted information; and (3) conducted the quarterly access review and verified that objectives were met MRO verified that the entity completed its Mitigation Plan.
2012-05-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2011001046 | CIP-006-1 | R1; R1.1 | RFC_URE1 self-reported an issue with CIP-006-1 R1 to ReliabilityFirst. RFC_URE1 did not enclose within conduit two sections of cable located outside a Physical Security Perimeter (PSP). The first section of unenclosed cable is approximately 36 feet long, and the second section of unenclosed cable is approximately 159 feet long. Both sections of cable are located in the same RFC_URE1 generating facility. | ReliabilityFirst determined that this issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The two sections of cable are located in the same RFC_URE1 generating facility which is protected by physical security measures including perimeter fencing, surveillance cameras, and security guards who remain on duty twenty-four hours a day, seven days a week. Further, access to the generating facility in which the cables reside is restricted to only those individuals with approved key card access. Additionally, the cables reside above a suspended ceiling thereby reducing access due to the height of the ceiling. Finally, the cables reside with a number of non-critical cables of the exact same type and color, thereby making identification of the cables difficult. | RFC_URE1 placed the 36 foot section of the cable at issue, as well as the 159 foot section of the other cable at issue, in conduit, thereby creating a complete “six-wall” border pursuant to CIP-006-1 R1.1.
2012-05-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2012009862 | CIP-002-1 | R1; R1.1 | ReliabilityFirst conducted a compliance audit to assess RFC_URE2’s compliance with applicable CIP Reliability Standards (Compliance Audit). During this Compliance Audit, ReliabilityFirst discovered that two versions of RFC_URE2’s risk-based assessment methodology (RBAM) were not in fact risk-based. These methodologies simply stated the types of facilities that RFC_URE2 would review annually. These methodologies also concluded that RFC_URE2 characteristics rendered it unable to “impact the Bulk Electric System.” RFC_URE2 stated that it would evaluate its ability to impact the bulk power system (BPS) annually. ReliabilityFirst determined that RFC_URE2 had an issue with the Standard as these versions of RFC_URE2’s RBAM did not document RFC_URE2's procedures and evaluation criteria. | ReliabilityFirst determined that this issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. While the RBAM was incomplete, it provided some indication of what types of assets to include, which was corroborated by the later finding of no assets. Although RFC_URE2’s RBAM was found to be deficient, ReliabilityFirst found that RFC_URE2’s determination that it had no Critical Assets, and therefore no Critical Cyber Assets, was correct. This determination was confirmed when RFC_URE2 implemented its updated RBAM. In addition, the RBAM took into consideration RFC_URE2’s interconnection points and load size. | RFC_URE2 submitted to ReliabilityFirst a Mitigation Plan to address the issue with of CIP-002-1 R1. In this Mitigation Plan, RFC_URE2 memorialized that it updated and implemented its revised RBAM. ReliabilityFirst verified this completion via evidence reviewed at RFC_URE2’s compliance audit.
2012-05-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2012009863 | CIP-002-3 | R2 | ReliabilityFirst conducted a compliance audit to assess RFC_URE2’s compliance with applicable CIP Reliability Standards (Compliance Audit). During ReliabilityFirst’s Compliance Audit of RFC_URE2, RFC_URE2 failed to provide evidence of its annual application of its risk-based assessment methodology (RBAM). Accordingly, RFC_URE2 failed to show that it developed a list of Critical Assets, as required by CIP-002-3 R2, and associated Critical Cyber Assets, as required by CIP-002-3 R3. RFC_URE2 also failed to show that its senior manager had approved its RBAM, its list of Critical Assets, and its list of Critical Cyber Assets, as required by CIP-002-3 R4. As a result, ReliabilityFirst identified an issue with CIP-002-3 R2. | ReliabilityFirst determined that this issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Throughout the time period of this issue, RFC_URE2 self-certified to ReliabilityFirst that it was in conformity with CIP-002-3 R2, R3 and R4. RFC_URE2's self-certifications were based on its own review of its RBAM and its lists of Critical Assets and associated Critical Cyber Assets. While the RBAM was incomplete, it provided some indication of what types of assets to include, which was corroborated by the later finding of no assets. Although RFC_URE2’s RBAM was found to be deficient, ReliabilityFirst determined that RFC_URE2’s determination that it had no Critical Assets, and therefore no Critical Cyber Assets was correct. In addition, the RBAM took into consideration RFC_URE2’s interconnection points and load size. | RFC_URE2 submitted to ReliabilityFirst a Mitigation Plan to address issue with CIP-002-3 R2. RFC_URE2’s Mitigation Plan addressing its issue with CIP-002-1 R1 memorialized that it updated and implemented its revised RBAM. These actions also mitigated the issue with CIP-002-3 R2. RFC_URE2’s Mitigation Plan addressing its issues with CIP-002-3 R2, R3 and R4 memorialized actions it took to revise its document retention policies to ensure that it retains evidence of the requisite annual reviews in the future.
2012-05-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2012009864 | CIP-002-3 | R3 | ReliabilityFirst conducted a compliance audit to assess RFC_URE2’s compliance with applicable CIP Reliability Standards (Compliance Audit). During ReliabilityFirst’s Compliance Audit of RFC_URE2, RFC_URE2 failed to provide evidence of its annual application of its risk-based assessment methodology (RBAM). Accordingly, RFC_URE2 failed to show that it developed a list of Critical Assets, as required by CIP-002-3 R2, and associated Critical Cyber Assets, as required by CIP-002-3 R3. RFC_URE2 also failed to show that its senior manager had approved its RBAM, its list of Critical Assets, and its list of Critical Cyber Assets, as required by CIP-002-3 R4. As a result, ReliabilityFirst identified an issue with CIP-002-3 R3. | ReliabilityFirst determined that this issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Throughout the time period of this issue, RFC_URE2 self-certified to ReliabilityFirst that it was in conformity with CIP-002-3 R2, R3 and R4. RFC_URE2's self-certifications were based on its own review of its RBAM and its lists of Critical Assets and associated Critical Cyber Assets. While the RBAM was incomplete, it provided some indication of what types of assets to include, which was corroborated by the later finding of no assets. Although RFC_URE2’s RBAM was found to be deficient, ReliabilityFirst determined that RFC_URE2’s determination that it had no Critical Assets, and therefore no Critical Cyber Assets was correct. In addition, the RBAM took into consideration RFC_URE2's interconnection points and load size. | RFC_URE2 submitted to ReliabilityFirst a Mitigation Plan to address issue with CIP-002-3 R3. RFC_URE2’s Mitigation Plan addressing its issue with CIP-002-1 R1 memorialized that it updated and implemented its revised RBAM. These actions also mitigated the issue with CIP-002-3 R3. RFC_URE2’s Mitigation Plan addressing its issues with CIP-002-3 R2, R3 and R4 memorialized actions it took to revise its document retention policies to ensure that it retains evidence of the requisite annual reviews in the future.
2012-05-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2012009865 | CIP-002-3 | R4 | ReliabilityFirst conducted a compliance audit to assess RFC_URE2’s compliance with applicable CIP Reliability Standards (Compliance Audit). During ReliabilityFirst’s Compliance Audit of RFC_URE2, RFC_URE2 failed to provide evidence of its annual application of its risk-based assessment methodology (RBAM). Accordingly, RFC_URE2 failed to show that it developed a list of Critical Assets, as required by CIP-002-3 R2, and associated Critical Cyber Assets, as required by CIP-002-3 R3. RFC_URE2 also failed to show that its senior manager had approved its RBAM, its list of Critical Assets, and its list of Critical Cyber Assets, as required by CIP-002-3 R4. As a result, ReliabilityFirst identified an issue with CIP-002-3 R4. | ReliabilityFirst determined that this issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Throughout the time period of this issue, RFC_URE2 self-certified to ReliabilityFirst that it was in conformity with CIP-002-3 R2, R3 and R4. RFC_URE2's self-certifications were based on its own review of its RBAM and its lists of Critical Assets and associated Critical Cyber Assets. While the RBAM was incomplete, it provided some indication of what types of assets to include, which was corroborated by the later finding of no assets. Although RFC_URE2’s RBAM was found to be deficient, ReliabilityFirst determined that RFC_URE2’s determination that it had no Critical Assets, and therefore no Critical Cyber Assets was correct. In addition, the RBAM took into consideration RFC_URE2's interconnection points and load size. | RFC_URE2 submitted to ReliabilityFirst a Mitigation Plan to address issue with CIP-002-3 R4. RFC_URE2’s Mitigation Plan addressing its issue with CIP-002-1 R1 memorialized that it updated and implemented its revised RBAM. These actions also mitigated the issue with CIP-002-3 R4. RFC_URE2’s Mitigation Plan addressing its issues with CIP-002-3 R2, R3 and R4 memorialized actions it took to revise its document retention policies to ensure that it retains evidence of the requisite annual reviews in the future.
2012-05-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC2012009869 | CIP-002-3 | R1 | ReliabilityFirst conducted a compliance audit of RFC_URE3 (Compliance Audit). During the Compliance Audit, ReliabilityFirst discovered an issue with CIP-002-3 R1. RFC_URE3 failed to maintain a risk-based assessment methodology (RBAM) as required by CIP-002-3 R1. RFC_URE3’s RBAM consisted of one question: "Does an asset, if destroyed, degraded, compromised or otherwise rendered unavailable, adversely impact the reliability or operability of the Bulk Electrical System (BES)?" The RBAM defined three possible impact determinations: "Low," "Medium," and "High," providing only minimal descriptions of the criteria for each category. The RBAM provided no additional guidance on how to choose a category for a particular asset, or how to determine whether the loss of the plant will fall into one of the categories. Since the RBAM did not provide sufficient guidance to a user, it was not effectively risk-based. | ReliabilityFirst determined that this issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. While the RBAM was incomplete, it provided some indication of what types of assets to include, which was corroborated by the later finding of no assets. In addition, RFC_URE3 has no Critical Assets and therefore inherently presents minimal risk to the BPS. Despite the described shortcomings of RFC_URE3’s RBAM, ReliabilityFirst’s audit team determined that RFC_URE3 had properly declared no Critical Assets. | RFC_URE3's operational responsibilities shifted from one company to another company. After the Compliance Audit, RFC_URE3 implemented a new RBAM based on the new company's standard methodology. RFC_URE3 provided the new RBAM to ReliabilityFirst and ReliabilityFirst verified that RFC_URE3 mitigated the issue as of that date.
2012-05-30 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2011008611 | CIP-002-1 | R4 | The SERC CIP audit team reported an issue with CIP-002 R4, stating that SERC_URE1, failed to provide evidence showing that the senior manager or delegate(s) annually approved the risk-based assessment methodology (RBAM), the list of Critical Assets, and the list of Critical Cyber Assets (CCAs). SERC staff determined that SERC_URE1 had failed to assign in writing a senior manager with responsibility for SERC_URE1's implementation of, and adherence to, the CIP standards until that responsibility was assigned in writing to a SERC_URE1 business manager. As a result, despite the fact that a SERC_URE1 manager had signed and approved RBAMs with null lists for Critical Assets and CCAs in two instances, the manager was not a valid signer because he or she had not been assigned responsibility in writing for SERC_URE1's compliance with the CIP standards. SERC_URE1 also had an RBAM with null lists for Critical Assets and CCAs but could not provide evidence that it had been signed. Therefore, the issue extends back to Version 1 of the Standard. | SERC staff determined that the issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because: 1. SERC_URE1 has no Critical Assets and does not own or operate any facilities that would meet any of the Critical Asset criteria set forth in CIP-002-4; and 2. Although a SERC_URE1 manager had not been properly delegated responsibility for SERC_URE1's compliance with the CIP standards, the manager reviewed and approved SERC_URE1's RBAMs with null lists for Critical Assets and CCAs in two instances indicating that SERC_URE1 did not acquire any Critical Assets or CCAs in 2010. | SERC staff verified that SERC_URE1 completed the following actions: SERC_URE1 revised its Internal Compliance Program (ICP) to clarify details of the annual Critical Asset Identification self-assessment. The ICP now requires the senior manager or delegate to sign the self-assessments and file at the facility.
2012-05-30 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2011008612 | CIP-003-1 | R2 | The SERC CIP audit team reported an issue with CIP-003-1 R2, stating that SERC_URE1 failed to provide evidence documenting the senior manager’s delegation of authority to a named delegate in the same manner as R2.1 and R2.2, and failed to provide evidence of the senior manager’s approval of the delegation of authority. SERC staff determined that SERC_URE1 was unable to provide evidence that it had assigned a senior manager with overall responsibility for leading and managing SERC_URE1's implementation of, and adherence to, Standards CIP-002 through CIP-009. Three months after the audit, a SERC_URE1's manager was assigned authority in writing to manage all aspects of the facility’s NERC compliance program, including the CIP standards. | SERC staff determined that the issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because: 1. SERC_URE1 has no Critical Assets and does not own or operate any facilities that would meet any of the Critical Asset criteria set forth in CIP-002-4; and 2. Although a SERC_URE1's manager had not been assigned responsibility in writing for SERC_URE1's compliance with the CIP standards, the manager was acting in that capacity. | SERC staff verified that SERC_URE1 completed the following actions: 1. SERC_URE1 assigned its manager authority in writing to manage all aspects of the facility's NERC compliance program, including the CIP standards; and 2. SERC_URE1 revised its Internal Compliance Program (ICP) to clarify details surrounding the CEO delegation, the senior manager delegation, delegations made by the senior manager and the requirement to document changes to the senior manager position within 30 days. The ICP now includes the designation of a single senior manager with overall responsibility and authority for leading and managing SERC_URE1's implementation of, and adherence to, Standards CIP-002-3 through CIP-009-3.
2012-05-30 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 2 (SERC_URE2) | NCRXXXXX | SERC2012009649 | CIP-003-1 | R2 | SERC_URE2 self-certified an issue with CIP-003-1 R2, stating that it did not have documentation of the assignment of a single senior manager with overall responsibility and authority for leading and managing SERC_URE2's implementation of, and adherence to, Standards CIP-002 through CIP-009. SERC staff reviewed documentation showing that SERC_URE2 assigned its general manager with overall responsibility and authority for leading and managing SERC_URE2's implementation of, and adherence to, Standards CIP-002 through CIP-009 and identified the general manager by name, title, and the date of designation. The same documentation showed a proper delegation of authority from the general manager to a different manager on the same day. | SERC staff determined that the issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because: 1. SERC_URE2 has no Critical Assets and does not own or operate any facilities that would meet any of the Critical Asset criteria set forth in CIP-002-4; and 2. SERC_URE2 is a minimal size utility. | SERC staff verified that SERC_URE2 completed the following action: SERC_URE2 established a corporate procedure, effective that met the requirements of CIP-003 R2 and identified the single senior manager with overall responsibility and authority for leading and managing implementation of, and adherence to, NERC Reliability Standards CIP-002 through CIP-009.
2012-05-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP201100554 | CIP-002-3 | R4 | SPP RE_URE1 self-reported an issue with CIP-002-3 R4 related to approval of its Critical Asset list and its Critical Cyber Asset (CCA) list by the senior manager or his or her delegate(s). As required by CIP-002-3 R3, SPP RE_URE1 had developed a list of CCAs essential to the operation of its Critical Assets. However, SPP RE_URE1's senior manager did not approve the list of CCAs. Instead, the list approved by the senior manager was a high level consolidated list describing the CCAs, rather than a detailed component level inventory. | SPP RE determined that the issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Although the CCAs list approved by the SPP RE_URE1's senior manager was not a detailed list of the CCA inventory, SPP RE_URE1 had developed a detailed list of CCAs. However, instead of approving the detailed list, the senior manager was approving a representative, high-level list of the CCAs. Further, the senior manager had approved SPP RE_URE1's Critical Asset list. | SPP RE_URE1 added the detailed list of CCAs to the annual approval document and has had the document approved by the senior manager or delegate.
2012-05-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPPRE_URE2) | NCRXXXXX | SPP201100565 | CIP-002-3 | R4 | SPPRE_URE2 self-reported an issue with CIP-002-3 R4 related to approval of its Critical Asset list and its Critical Cyber Asset (CCA) list by the senior manager or his or her delegate(s). As required by CIP-002-3 R3, SPPRE_URE2 had developed a list of CCAs essential to the operation of its Critical Assets. However, SPPRE_URE2's senior manager did not approve the list of CCAs. Instead, the list approved by the senior manager was a high level consolidated list describing the CCAs, rather than a detailed component level inventory. | SPP RE determined that the issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). Although the CCAs list approved by the SPPRE_URE2's senior manager was not a detailed list of the CCA inventory, SPPRE_URE2 had developed such a detailed list of CCAs. However, instead of approving the detailed list, the senior manager was approving a representative, high-level list of the CCAs. Furthermore, the senior manager had approved SPPRE_URE2's Critical Asset list. | SPPRE_URE2 added the list of CCAs to the annual approval document and has had the document approved by the senior manager or delegate.
2012-05-30 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE201100263 | CIP-005-1 | R1 | During an Audit, Texas RE found that Texas RE_URE1 failed to identify and document all access points to its Electronic Security Perimeter (ESP). Texas RE_URE1 had two system switches installed. The system switches unidirectionally transmit data outside the ESP via ports to the quality assurance system testing environment. Texas RE determined that Texas RE_URE1 has implemented technical controls to prevent incoming traffic; however, these ports, which transmitted outgoing traffic, were still considered access points and should have been identified as such. The start date of this issue is when Texas RE_URE1 failed to identify these access points to the ESP. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the ports at issue were still being afforded the same protective measures of all other access points on the system, including firewalls, intrusion protection systems, and antivirus software. These ports were not identified as access points due to Texas RE_URE1's incorrect understanding of the definition of the term. | Since the Audit, Texas RE_URE1 has reconfigured it's network, eliminating the ports at issue and only allowing traffic to pass in/out of its ESP via firewalls. These ports were eliminated and documented. Texas RE_URE1's current network diagrams confirm that all access points have been documented. Texas RE verified all mitigation activities were complete.
2012-05-30 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE201100266 | CIP-007-1 | R5; R5.2.1; R5.3.2; R5.3.3 | During an Audit, Texas RE found that Texas RE_URE1 was noncompliant with R5.2.1, R5.3.2 and R5.3.3. First, Texas RE_URE1 did not disable shared administrator accounts on eight Cyber Assets, as required by R5.2.1. Texas RE_URE1 had implemented procedural controls to minimize and manage the scope of the enabled shared accounts. The assets associated with this issue were commissioned prior to the beginning of the noncompliance period. The noncompliance period was for eight months, from the day Texas RE_URE1 was required to comply with CIP-007 R5 for these assets, until the day Texas RE_URE1 disabled the shared accounts. Second, all of Texas RE_URE1's Cyber Assets authenticated by active directory are not capable of implementing technical controls that enforce strict compliance with the password requirements listed in R5.3.2. At the time of the audit, Texas RE_URE1 had not filed a Technical Feasibility Exception (TFE) request regarding these Cyber Assets. The duration of this issue was for two years, until Texas RE accepted Texas RE_URE1's TFE. Third, all Cyber Assets deployed within Texas RE_URE1's ESPs are not capable of implementing technical controls to enforce password expiration, as required by R5.3.3. At the time of the audit, Texas RE_URE1 had not filed a TFE for these Cyber Assets. The duration of this issue was for two years, until Texas RE accepted Texas RE_URE1's TFE. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because Texas RE_URE1 had implemented procedural controls to minimize and manage the scope of the enabled shared accounts and passwords. Regarding subrequirement R5.2.1, Texas RE_URE1's procedure requires that users utilizing shared accounts manually record the tasks they perform and the date they were performed and that these logs be submitted to a Supervisory Control and Data Acquisition (SCADA) administrator. Regarding subrequirements R5.3.2.and R5.3.3, the risk was mitigated by the fact that during the noncompliance period, Texas RE_URE1 had administered training to its staff in order to ensure that passwords are created with the complexity required by R5.3.2 and are retired in accordance with R5.3.3. | Texas RE_URE1 had mitigated the issue associated with R5.2.1 by disabling shared accounts. Further, Texas RE_URE1 submitted TFEs addressing the issues associated with R5.3.2 and R5.3.3. These TFEs were accepted by Texas RE. Additionally, Texas RE_URE1 has implemented procedural controls in the form of a staff training to ensure that passwords are created with the complexity required by R5.3.2 and are retired in accordance with R5.3.3. Texas RE verified all mitigation activities were complete.
2012-05-30 | TRE_URE1liability Entity (TRE_URE1) | Unidentified Registered Entity 2 (TRE_URE2) | NCRXXXXX | TRE201100511 | CIP-003-3 | R2.2 | TRE_URE1_URE2 self-reported that its appointed single senior manager with overall responsibility and authority for leading and managing the TRE_URE1_URE2 implementation of, and adherence to, Standards CIP-002-3 through CIP-009-3, left the company. TRE_URE1_URE2 CIP procedure identifying this senior manager, was not updated within 30 days of his departure, which presented an issue with CIP-003-3 R2.2. TRE determined that the issue duration was approximately four months, 30 days after the manager left, until TRE_URE1_URE2's internal compliance procedure was updated. | This issue did not pose a serious or substantial risk and posed a minimal risk to the reliability of the bulk power system (BPS). TRE_URE1 determined that based on the administrative nature of this issue, the availability of responsible leadership throughout the period, and TRE_URE1_URE2 's lack of Critical Assets, the risk to the reliability of the BPS was minimal. First, the senior manager that left reported to the replacement senior manager. When the appointed senior manager left, the replacement senior manager had already been on staff and at no point during the duration of this issue was TRE_URE1_URE2's NERC internal compliance program (ICP) left without leadership. In addition, TRE_URE1_URE2 is a small entity and all of its employees involved in NERC compliance knew at all times who was responsible for TRE_URE1_URE2's NERC ICP. Also, TRE_URE1_URE2 submitted an attestation that it did not have any Critical Assets during the time period of this issue. | TRE_URE1_URE2's internal cyber security procedure was updated to include the new single senior manager. The manager at the facility location and the compliance employees are aware of the updated document and its location, and have access to the document.
2012-05-30 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 3 (TRE_URE3) | NCRXXXXX | TRE201100512 | CIP-003-3 | R2.2 | Texas RE_URE3 self-reported that its appointed single senior manager with overall responsibility and authority for leading and managing the Texas RE_URE3's implementation of, and adherence to, Standards CIP-002-3 through CIP-009-3, left the company. Texas RE_URE3's CIP procedure identifying this senior manager was not updated within 30 days of his departure, which presented an issue with CIP-003-3 R2.2. TRE determined that the issue duration was approximately four months, 30 days after the manager left, until Texas RE_URE3's internal compliance procedure was updated. | This issue did not pose a serious or substantial risk and posed a minimal risk to the reliability of the bulk power system (BPS). TRE determined that based on the administrative nature of this issue, the availability of responsible leadership throughout the period, and Texas RE_URE3's lack of Critical Assets, the risk to the reliability of the BPS was minimal. First, the senior manager that left reported to the replacement senior manager. When the appointed senior manager left, the replacement senior manager had already been on staff and at no point during the duration of this issue was Texas RE_URE3's NERC internal compliance program (ICP) left without leadership. In addition, Texas RE_URE3 is a small entity and all of its employees involved in NERC compliance knew at all times who was responsible for Texas RE_URE3's NERC ICP. Also, Texas RE_URE3 submitted an attestation that it did not have any Critical Assets during the time period of this issue. | Texas RE_URE3's internal cyber security procedure was updated to include the new single senior manager. The manager at the facility location and the compliance employees are aware of the updated document and its location, and have access to the document.
2012-05-30 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 4 (TRE_URE4) | NCRXXXXX | TRE201100522 | CIP-003-3 | R2.2 | Texas RE_URE4 self-reported that its appointed single senior manager with overall responsibility and authority for leading and managing Texas RE_URE4 implementation of, and adherence to, Standards CIP-002-3 through CIP-009-3, left the company. Texas RE_URE4's CIP procedure identifying this senior manager was not updated within 30 days of his departure, which presented an issue with CIP-003-3 R2.2. TRE determined that the issue duration was approximately four months, 30 days after the manager left, until Texas RE_URE4's internal compliance procedure was updated. | This issue did not pose a serious or substantial risk and posed a minimal risk to the reliability of the bulk power system (BPS). TRE determined that based on the administrative nature of this issue, the availability of responsible leadership throughout the period, and Texas RE_URE4's lack of Critical Assets, the risk to the reliability of the BPS was minimal. First, the senior manager that left reported to the replacement senior manager. When the appointed senior manager left, the replacement senior manager had already been on staff and at no point during the duration of this issue was Texas RE_URE4's NERC internal compliance program (ICP) left without leadership. In addition, Texas RE_URE4 is a small entity and all of its employees involved in NERC compliance knew at all times who was responsible for Texas RE_URE4's NERC ICP. Also, Texas RE_URE4 submitted an attestation that it did not have any Critical Assets during the time period of this issue. | Texas RE_URE4's internal cyber security procedure was updated to include the new single senior manager. The manager at the facility location and the compliance employees are aware of the updated document and its location, and have access to the document.
2012-05-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2011008650 | CIP-007-3 | R6 | WECC_URE1 submitted a Self-Report stating that non-critical Cyber Assets were added to an Electronic Security Perimeter (ESP). The Cyber Assets were not configured to send Security Status Monitoring alerts to the syslog server. WECC_URE1 reported that consequently, access logs were not maintained nor reviewed per CIP-007-3 R6. WECC reviewed WECC_URE1's Self-Report and determined that WECC_URE 1 expanded its ESP to include non-critical Cyber Assets. WECC determined that WECC_URE1 failed to ensure these non-critical Cyber Assets were configured to send syslogs to its centralized server. WECC, therefore, determined that WECC_URE1 failed to ensure all Cyber Assets within the ESP implemented automated tools to monitor system events after expanding the boundary of an ESP. | This issue posed a minimal and not serious or substantial risk to the reliability of the bulk power system. The scope of the issue is limited to 18% of the non-critical Cyber Assets within the ESP. All Cyber Assets including the non-critical Cyber Assets within scope of the issue addressed herein were secured behind a firewall through which electronic access was controlled, logged and monitored. Further, although the non-critical Cyber Assets were not configured to log system events with the centralized server, the non-critical Cyber Assets did maintain logs locally that could have been reviewed if a threat was detected. All Cyber Assets were located within a Physical Security Perimeter. Personnel with electronic or physical access to devices completed Personnel Risk Assessments and Cyber Security Training. | WECC_URE1 reconfigured the non-critical Cyber Assets devices within the ESP to ensure that cyber security event logs were centrally maintained and reviewed.
2012-05-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2012009098 | CIP-004-3 | R4 | WECC_URE2 submitted a Self-Report reporting one instance in which specific access rights to Critical Cyber Assets (CCAs) were not listed and, one instance in which access rights were not revoked within seven days for personnel who no longer required such access. The first issue reported by WECC_URE2 occurred after WECC_URE2 implemented a configuration change. After the configuration change was made, access lists reflected that one individual maintained electronic access to one CCA when, in fact, the individual maintained electronic access rights to a total of six CCAs. WECC_URE2 detected the problem and revised its access list to include all of the individual’s access rights to the six CCAs. WECC_URE2 access lists, therefore, failed to list specific access rights as required under CIP-004-3 R4 for one individual. The second issue reported by WECC_URE2 stemmed from its failure to revoke physical access within seven days for a single person who no longer required such access. The individual was an intern with physical access rights to CCAs located within the control center. The internship ended but the individual’s security badge, provisioning physical access to the control room, was not returned until ten days later. Because the badge was not turned in within seven days of the intern’s departure, WECC determined that WECC_URE2 failed to comply with CIP-004 R4.2 for a period of three days. | This issue posed a minimal risk and not serious or substantial risk to the reliability of the bulk power system. Each of the two individuals within scope of the issue described herein completed Personnel Risk Assessments and Cyber Security Training. Further, WECC_URE2 remediated both instances upon detection. WECC_URE2 revised access lists to include specific electronic access rights held by one individual and, WECC_URE2 revoked physical access within ten days of the other individual’s departure. All CCAs to which individuals had access were secured within Physical Security Perimeters and Electronic Security Perimeters. All electronic and physical access to these CCAs was logged and monitored. | WECC_URE2 has undertaken a number of mitigating activities to address immediate instances and to prevent future reoccurrence. WECC_URE2 revised access lists to include all electronic access rights maintained by the individual in scope of the issue. WECC_URE2 is base-lining the access management system for appropriate CIP devices and all user accounts. WECC_URE2 implemented a manual process whereby the current user accounts/access privileges can still be reviewed and validated each quarter. WECC_URE2 implemented the use of additional reports that highlight updates associated with adding/changing or removing CIP devices and/or accounts. WECC_URE2 revoked access rights for the intern. WECC_URE2 is implementing training requirements to ensure that managers revoke physical access within the timeframe prescribed under R4.2.
2012-04-30 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2011007977 | CIP-004-3 | R3 | FRCC_URE1 self-reported that it failed to conduct personnel risk assessments (PRAs) for one of its personnel with authorized cyber or authorized unescorted physical access to Critical Cyber Assets, as required by CIP-004-3 R3. FRCC_URE1 granted remote access to the contractor at issue but did not conduct a PRA and document the results prior to granting access. This issue involved only one person, a contractor who accessed Critical Cyber Assets (CCAs) on three separate occasions for very short durations. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the person accessed the systems for specific maintenance pursuant to a trusted vendor contract with complete direction from the plant system operator. The turbine tuning activities involved coordination of plant and vendor remote staff to acquire and analyze real-time dynamics data using locally-installed equipment. The remote user has no access to the local device so they have to coordinate in order to complete the exercise. Further, all recommendations are implemented after full consultation with the plant operations management. On all the three occasions, access was for short durations (less than 2 hours) and system access was monitored and all activities were performed with consultation and clear direction. Further, the vendor has performed this maintenance activity for the past six years for many large generating units and was used frequently as a trusted resource specializing in the activity. Although FRCC_URE1 has violated this Standard previously, the instant remediated issue is appropriate for FFT treatment because it does not represent a failure to mitigate a prior violation appropriately. The prior violations involved on-site personnel, whereas the instant issue involved contractors accessing the assets remotely. Additionally, unlike the prior violations, the instant issue did not involve any new access provisioning, but rather, involved a contractual obligation with an existing vendor . This access was not a planned exercise but an unplanned usage of an access path that was scarcely used. Further, this instance was related to different controls and a different compliance schedule than in the prior violations, which involved the control center. | FRCC_URE1 certified that it completed its mitigation activities by revoking access and creating a new procedure for on-boarding all new vendor contractors that access systems remotely, which requires FRCC_URE1 to conduct PRAs and training prior to granting access to any CCAs and training of all personnel responsible for granting access to CCAs.
2012-04-30 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2011008234 | CIP-005-1 | R1; R1.6 | During a NERC CIP Compliance Audit, it was determined that FRCC_URE1 failed to document one of the Cyber Assets that is used to configure the intrusion detection system and hence perform electronic access control and monitoring, as required by CIP-005-1 R1.6. The Cyber Asset was not included on the Cyber Assets inventory list for a period of approximately a year and a half. FRCC_URE1 continued to provide the required CIP protection but failed to document the devices on its list of Cyber Assets as an Electronic Access Control and Monitoring (EACM) System. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because even though the device was not documented on its Cyber Assets inventory list, it was within the Electronic Security Perimeter and afforded protective measures as required by CIP-005 R1.5. This issue occurred because prior to the Audit, FRCC_URE1 did not understand that devices used to configure EACMs were required to be considered EACMs for purposes of the Cyber Assets inventory list. Although FRCC_URE1 has violated this Standard previously, the instant remediated issue is appropriate for FFT treatment because it does not represent a failure to mitigate a prior violation appropriately. The prior violations involved identification of non-Critical Cyber Assets (R1.4), whereas this issue was related to protection of the EACM system (R1.6). Though both subrequirements are part of CIP-005 R1, they are distinct with separate security controls, control measures, and control owners. | FRCC_URE1 certified that it completed its mitigation activities by correcting the list of electronic access control and monitoring systems to include the intrusion detection system asset.
2012-04-30 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC201100429 | CIP-007-3 | R1 | FRCC_URE1 self-reported that it failed to perform the required testing when adding Cyber Assets, as required by CIP-007-3 R1. Specifically, a new server was added to FRCC_URE1's Electronic Security Perimeter (ESP) and appropriate testing controls were not performed. The server was accidentally installed and was removed six days later. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the untested Cyber Asset was detected within six days. Second, the server was accidently installed and was never configured to communicate with any other device within the ESP or outside the ESP. Further, the untested Cyber Asset was removed from the ESP and configured as a non-Critical Cyber Asset workstation with no BPS control and monitoring function. | FRCC_URE1 certified that it completed its mitigation activities by promptly (6 days) removing the accidently-installed server.
2012-04-30 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 2 (FRCC_URE2) | NCRXXXXX | FRCC2011007239 | CIP-002-1 | R2 | During a Compliance Spot Check, FRCC discovered that FRCC_URE2 failed to properly apply its risk-based assessment methodology (RBAM) to develop a list of identified Critical Assets, as required by CIP-002-1 R2. Specifically, the list of Critical Assets provided by FRCC_URE2 did not correlate to the set of identification criteria included in its RBAM. FRCC_URE2's RBAM included explanation and development of a risk-based assessment approach and a resultant list of identification criteria for Critical Assets. From this list of identification criteria, the entity created a list of Critical Assets. The risk-based assessment approach developed within FRCC_URE2's RBAM included assessment of a “transmission substation” with greater than 1,200 MW of generation connected. However, when the final statement of the identification criteria was made in FRCC_URE2's RBAM, it incorrectly stated that a “generation site” greater than 1,200 MW should be considered a Critical Asset. As a result of this incorrect wording, a single generation site which contained greater than 1,200 MW was not listed as a Critical Asset. The final identification criteria in FRCC_URE2's RBAM that addressed a generation site greater than 1,200 MW appears to have been a wording error. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the list of Critical Assets identified by FRCC_URE2 did correlate with all the correctly-stated criteria of FRCC_URE2's RBAM. | FRCC_URE2 certified that it completed its mitigation activities, which consisted of correcting the errors in the methodology to clearly articulate the generation impact that could occur related to a cyber event.
2012-04-30 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 2 (FRCC_URE2) | NCRXXXXX | FRCC2011007240 | CIP-005-1 | R1; R1.1; R1.5 | During a Compliance Spot Check, FRCC discovered that FRCC_URE2 failed to identify and document the Electronic Security Perimeters (ESPs) and all access points to the perimeters, as required by CIP-005-1 R1. Specifically, FRCC_URE2 failed to identify certain modems connected to the communication server for communicating and data acquisition from the substations, as required by R1.1. Further, FRCC_URE2 failed to maintain recovery plans for electronic access control and monitoring devices, as required by R1.5. Additionally, FRCC_URE2 removed one set of intrusion detection system (IDS) devices and replaced it with another vendor product with same functionality but did not update the recovery plan to address the recovery of these Cyber Assets used in electronic access control and monitoring, as required by R1.5. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because FRCC_URE2's access points that were not identified used serial-only communication. Even these access points were well-protected using appropriate communication controls and limited by configuration. Devices are only allowed to communicate to pre-configured remote terminal unit (RTU) and authentication between the access point device and the RTU is authenticated through a preconfigured code uniquely assigned to each RTU, and configured within the ESP access control device to allow communication to the designated RTU only. | FRCC_URE2 certified that it completed its mitigation activities by identifying and documenting the serial access points and updating the recovery plans to address the change in IDS devices.
2012-04-30 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 3 (FRCC_URE3) | NCRXXXXX | FRCC2011007585 | CIP-005-1 | R2; R2.6 | FRCC_URE3 self-reported that it failed to display a matching appropriate use banner and to document the content of the banner on all interactive attempts for all Electronic Security Perimeter (ESP) access point devices, as per its documented cyber security procedure. This condition existed for a period of approximately two years. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because FRCC_URE3 did display a banner but the banner text did not exactly match its own documented banner content. However, this was sufficient to notify and caution all those accessing the ESP without authorization. | FRCC_URE3 certified that it completed its mitigation activities by updating its risk-based assessment methodology (RBAM) and updating the text for the banners for all required ESP access point devices.
2012-04-30 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 3 (FRCC_URE3) | NCRXXXXX | FRCC2011007807 | CIP-006-2 | R1; R1.6 | During a Compliance Spot Check, FRCC discovered that FRCC_URE3 failed to ensure that continuous escorting and physical access logs were maintained for all visitors on one specific day and on one occasion, visitors' exit timings were not recorded. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). One instance of lack of recording the exit timings did not pose a significant security risk, as the records indicated that the visitor was from a trusted vendor and was continuously escorted. | FRCC_URE3 certified that it completed mitigation activities by updating its risk-based assessment methodology (RBAM), assessing all identified Physical Security Perimeters (PSPs), creating an awareness email for all appropriate staff and establishing a plan to review visitor logs on a weekly basis and follow up on any concerns with the appropriate party in a timely manner.
2012-04-30 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 3 (FRCC_URE3) | NCRXXXXX | FRCC2011007808 | CIP-006-2 | R2 | During a Compliance Spot Check, FRCC discovered that FRCC_URE3 failed to identify six of its physical access control system (PACS) Cyber Assets and to afford them the protection required by CIP-006 R2.2. This condition existed for a period of approximately two years. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) as the subject PACS Cyber Assets were protected as per FRCC_URE3's own corporate security standards restricting any unauthorized access. Pursuant to FRCC_URE3's corporate security standards, only authorized persons are allowed within FRCC_URE3 facilities that host these systems. These facilities are considered secured facilities and access is monitored using video feeds. FRCC_URE3's PACS was secured within designated Physical Security Perimeters (PSPs) and all the remote equipment that was not within designated PSPs was on its own isolated network which could only be accessed after gaining control of the designated PSPs. | FRCC_URE3 certified that it completed mitigation activities by updating its PACS as a result of revision of its risk-based assessment methodology (RBAM) and updating the PACS inventory.
2012-04-30 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 3 (FRCC_URE3) | NCRXXXXX | FRCC2011007806 | CIP-007-1 | R5 | During a Compliance Spot Check, FRCC discovered that FRCC_URE3 failed to modify at least annually the passwords of multiple network users. This condition existed for a period of approximately two years. | This issue posed a minimal risk and not a serious or substantial risk to the reliability of the bulk power system (BPS) because the network is always in a disabled state and procedural controls are used prior to any usage and authentication requires a security question response that is unique to each individual user. All of the network users at the time of the issue had completed a valid personnel risk assessment (PRA) and CIP training. Although FRCC_URE3 has a previous issue of noncompliance with this Standard, the instant remediated issue nonetheless does not represent recurring conduct by FRCC_URE3. The prior issue consists of a late-filed Technical Feasibility Exception regarding password complexity. | FRCC_URE3 certified that it completed mitigation activities by updating its network password and reviewing and updating the list of all network users.
2012-04-30 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO201100362 | CIP-006-2 | R1; R1.1 | MRO_URE1 self-reported an issue with CIP-006-1 R1.1 for failing to submit a timely Technical Feasibility Exception (TFE) request in accordance with NERC procedures. The TFE request was submitted approximately 15 months beyond the required TFE submission window. MRO_URE1 could not provide a "six-wall" border for network cabling running between two Physical Security Perimeters (PSPs) because it would require MRO_URE1 to make the entire building a single PSP; and that solution would negatively impact operations without adding additional security. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. MRO_URE1 uses cabling to connect two PSPs in a single facility to the Electronic Security Perimeter (ESP). The cabling connecting the PSPs to the ESP is located above the ceiling within a non-public building protected by multiple physical access control layers. | MRO_URE1 submitted a TFE, which was approved.
2012-04-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2011001105 | CIP-006-2 | R1; R1.1 | RFC_URE1 self-reported an issue with CIP-006-1 R1.1 for failing to submit a timely Technical Feasibility Exception (TFE) request in accordance with NERC procedures. The TFE request was submitted approximately 15 months beyond the required TFE submission window. RFC_URE1 could not provide a "six-wall" border for network cabling running between two Physical Security Perimeters (PSPs) because it would require RFC_URE1 to make the entire building a single PSP; and that solution would negatively impact operations without adding additional security. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. RFC_URE1 uses cabling to connect two PSPs in a single facility to the Electronic Security Perimeter (ESP). The cabling connecting the PSPs to the ESP is located above the ceiling within a non-public building protected by multiple physical access control layers. | RFC_URE1 submitted a TFE, which was approved.
2012-04-30 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO201100363 | CIP-005-1 | R2.6 | MRO_URE1self-reported an issue with CIP-005-1 R2.6 for failing to submit timely Technical Feasibility Exception (TFE) requests in accordance with NERC procedures. The two TFE requests were submitted approximately 17 months beyond the required TFE submission window. MRO_URE1 could not afford the protective measures specified in CIP-005-1 R2.6 for Cyber Assets that authorize and/or log access to the Physical Security Perimeter (PSP), exclusive of hardware at the PSP. Specifically, it was not technically feasible for the electronic access control devices MRO_URE1 utilizes to authorize and/or log access to designated PSPs, to display appropriate use banners. Additionally, several Electronic Security Perimeter (ESP) access control and/or monitoring devices were also incapable of presenting the appropriate use banner for all methods of interactive access. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The electronic access control devices are closed operating systems running on appliances; third-party software cannot be installed. Remote access to the electronic access control devices door controllers is protected by the use of a two‐factor authentication system, including an intrusion detection system and multiple firewalls, and the electronic access control devices door controllers are located in secure areas within the PSP. Additionally, the ESP access control and/or monitoring devices are protected by PSPs and local access ports protected by tamper proof seals with access warnings, and global and local passwords at each access point. | MRO_URE1 submitted TFEs, which were approved.
2012-04-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2011001106 | CIP-005-1 | R2.6 | RFC_URE1self-reported an issue with CIP-005-1 R2.6 for failing to submit timely Technical Feasibility Exception (TFE) requests in accordance with NERC procedures. The two TFE requests were submitted approximately 17 months beyond the required TFE submission window. RFC_URE1 could not afford the protective measures specified in CIP-005-1 R2.6 for Cyber Assets that authorize and/or log access to the Physical Security Perimeter (PSP), exclusive of hardware at the PSP. Specifically, it was not technically feasible for the electronic access control devices RFC_URE1 utilizes to authorize and/or log access to designated PSPs, to display appropriate use banners. Additionally, several Electronic Security Perimeter (ESP) access control and/or monitoring devices were also incapable of presenting the appropriate use banner for all methods of interactive access. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. The electronic access control devices are closed operating systems running on appliances; third-party software cannot be installed. Remote access to the electronic access control devices door controllers is protected by the use of a two‐factor authentication system, including an intrusion detection system and multiple firewalls, and the electronic access control devices door controllers are located in secure areas within the PSP. Additionally, the ESP access control and/or monitoring devices are protected by PSPs and local access ports protected by tamper proof seals with access warnings, and global and local passwords at each access point. | RFC_URE1 submitted TFEs, which were approved.
2012-04-30 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 2 (MRO_URE2) | NCRXXXXX | MRO201100390 | CIP-005-1 | R1; R1.5 | During a regularly scheduled Compliance Audit, MRO_URE2determined that MRO_URE1 failed to afford the measures afforded in CIP-007-3 R5 for Cyber Assets used in the control and monitoring of the Electronic Security Perimeter. Specifically, MRO_URE1 failed to implement and document technical and procedural controls as required by CIP-007-3 R5. For all affected firewalls, password complexity for local administrative accounts was subject only to procedural control, and not technical control. The devices were capable of enforcing password complexity via technical control. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. MRO_URE1's procedural controls required that passwords be a minimum of six characters, that each password consisted of a combination of alpha, numeric, and “special” characters, and that each password is changed at least annually, or more frequently based on risk. Additionally, MRO_URE1 provided evidence that all of the passwords met the procedural controls. | MRO_URE1 implemented technical controls. MRO_URE2has verified mitigation activities completion.
2012-04-30 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 3 (MRO_URE3) | NCRXXXXX | MRO201100393 | CIP-002-1 | R1; R1.2.1; R1.2.3 | During a Spot Check, conducted between June 16, 2011 through June 28, 2011, MRO determined that the MRO_URE2 failed to include adequate evaluation criteria for the assessment of control centers and generation resources in its risk-based assessment methodology (RBAM). Specifically, MRO_URE2's RBAM did not represent a stand alone methodology for control centers and generation resources and failed to define the criteria and steps it follows to identify these Critical Assets. Instead, criticality of the assets were predetermined with conclusory justifications. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. MRO_URE2 considered its control center a Critical Asset and provided it the protections in the CIP Reliability Standards. The protections were in place for all the Critical Cyber Assets (CCAs) both before and after the criteria were revised. Although MRO_URE2 did not include adequate evaluation criteria for the assessment of control centers or generation resources, after revising the evaluation criteria for control centers and generation resources, the generation resources were still not considered critical, and therefore, should not have been treated as Critical Assets. | MRO_URE2 revised its RBAM to include adequate evaluation criteria for the assessment of control centers and generation resources, and was verified by MRO.
2012-04-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2011009036 | CIP-003-2 | R2; R2.3 | During a NPCC CIP Compliance Audit, it was discovered that NPCC_URE1 had an issue with CIP-003-2 R2.3. NPCC determined that a letter from an executive manager of NPCC_URE1 and senior manager having full authority and responsibility for CIP-002 through CIP-009 compliance verified that she had delegated authority to two other executives. This delegation of authority was not documented within thirty calendar days, as required by CIP-003-2 R2.3. The letter is relied upon by multiple affiliated registered entities for compliance with CIP-003-2 R2.3, including NPCC_URE1. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because this was a matter of late documentation covering a span of only four calendar days. Also, there was no gap in senior management leadership, and no actions were taken pursuant to the changed delegations during the four-day period before the documentation was updated. | NPCC_URE1 documented the delegation of authority for specific actions to named delegates. The mitigation activity was verified complete by NPCC.
2012-04-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 2 (NPCC_URE2) | NCRXXXXX | NPCC2011008338 | CIP-003-2 | R2; R2.3 | NPCC_URE2 self-reported to NPCC an issue with CIP-003-2 R2.3. During a NPCC CIP Compliance Audit of its affiliate, it was discovered that both companies had an issue with CIP-003-2 R2.3. NPCC determined that a letter from the affiliate's executive manager and senior manager having full authority and responsibility for CIP-002 through CIP-009 compliance verified that she had delegated authority to two other executives. This delegation of authority was not documented within thirty calendar days, as required by CIP-003-2 R2.3. The letter is relied upon by multiple affiliated registered entities for compliance with CIP-003-2 R2.3, including NPCC_URE2. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because this was a matter of late documentation covering a span of only four calendar days. Also, there was no gap in senior management leadership, and no actions were taken pursuant to the changed delegations during the four-day period before the documentation was updated. | NPCC_URE2 documented the delegation of authority for specific actions to named delegates. The mitigation activity was verified complete by NPCC.
2012-04-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 3 (NPCC_URE3) | NCRXXXXX | NPCC2011008442 | CIP-003-2 | R2; R2.3 | NPCC_URE3 self-reported to NPCC an issue with CIP-003-2 R2.3. During a NPCC CIP Compliance Audit of its subsidiary, it was discovered that both companies had an issue with CIP-003-2 R2.3. NPCC determined that a letter from the subsidiary's executive manager and senior manager having full authority and responsibility for CIP-002 through CIP-009 compliance verified that she had delegated authority to two other executives. This delegation of authority was not documented within thirty days, as required by CIP-003-3 R2.3. The letter is relied upon by multiple affiliated registered entities for compliance with CIP-003-2 R2.3, including NPCC_URE3. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because this was a matter of late documentation covering a span of only four calendar days. Also, there was no gap in senior management leadership, and no actions were taken pursuant to the changed delegations during the four-day period before the documentation was updated. | NPCC_URE3 documented the delegation of authority for specific actions to named delegates. The mitigation activity was verified complete by NPCC.
2012-04-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2011009038 | CIP-006-1 | R1; R1.1 | During a NPCC CIP Compliance Audit, it was discovered that NPCC_URE1 had an issue with CIP-006-1 R1.1. NPCC determined that NPCC_URE1's Electronic Security Perimeter, which resides within a Physical Security Perimeter where a completely enclosed ("six-wall") border was compromised by the ability of a person to access those areas through a raised floor area that was approximately 18 inches high. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because while there was a gap in the “six-wall" border (approximately 18 inches), the Physical Security Perimeter had multiple layers of security that would minimize unauthorized access into the secure area. To access the area where the gap was located, it would require: (1) permission to enter at the perimeter gate that completely surrounds the building and is monitored constantly by security personnel or a badge reader; (2) permission to enter the special use building through a badge reader; and (3) permission to enter the secure area through a badge reader that is restricted to personnel who work in that area. Additionally, NPCC_URE1 conducts video surveillance on the access points to the secure area. | NPCC_URE1 installed barriers in the raised floor thereby eliminating the gap under the raised floor between two secure Physical Security Perimeter areas. The mitigation activity was verified complete by NPCC.
2012-04-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2011009037 | CIP-005-1 | R2; R2.3 | During a NPCC CIP Compliance Audit, it was discovered that NPCC_URE1 had an issue with CIP-005-1 R2.3. NPCC determined that NPCC_URE1's procedure for securing dial-up access to the Electronic Security Perimeters (ESPs) was created approximately three years after NPCC_URE1 was required to comply with the Standard. NPCC_URE1 could not demonstrate that there was a procedure in effect prior to that time. This procedure is relied upon by multiple affiliated registered entities for compliance with CIP-005-3 R2.3, including NPCC_URE1. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because NPCC_URE1 provided evidence that demonstrated its commitment to securing its dial-up access points. First, dial-up access into the ESP is controlled by a system which utilizes multiple authentication controls including usernames, passwords, and other user authentication functions. Second, NPCC_URE1 does not allow dial-up access to its Energy Management System ESPs. Third, a presentation outlines how to secure the devices which are used to secure dial-up access. This presentation is given to the technicians responsible for installing the devices. | NPCC_URE1 created a procedure for securing dial-up access to the ESPs. The mitigation activity was verified complete by NPCC.
2012-04-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 2 (NPCC_URE2) | NCRXXXXX | NPCC2011008339 | CIP-005-1 | R2; R2.3 | NPCC_URE2 self-reported to NPCC an issue with CIP-005-1 R2.3. During a NPCC CIP Compliance Audit of its affiliate, it was discovered that both companies had an issue with CIP-005-1 R2.3. NPCC determined that NPCC_URE2's parent company had a corporate procedure for securing dial-up access to the Electronic Security Perimeters (ESPs) which was created approximately three years after NPCC_URE2 was required to comply with the Standard. NPCC_URE2 could not demonstrate that there was a procedure in effect prior to that time. This procedure is relied upon by multiple affiliated registered entities for compliance with CIP-005-3 R2.3, including NPCC_URE2. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because NPCC_URE2 provided evidence that demonstrated its commitment to securing its dial-up access points. First, dial-up access into the ESP is controlled by a system which utilizes multiple authentication controls including usernames, passwords, and other user authentication functions. Second, NPCC_URE2 does not allow dial-up access to its Energy Management System ESPs. Third, a presentation outlines how to secure the devices which are used to secure dial-up access. This presentation is given to the technicians responsible for installing the devices. Although NPCC_URE2 has violated this Standard previously, the instant remediated issue nonetheless does not represent recurring corporate conduct. The prior violation involved incomplete documentation of ports and services for Critical Cyber Assets. | NPCC_URE2 created a procedure for securing dial-up access to the ESPs. The mitigation activity was verified complete by NPCC.
2012-04-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 3 (NPCC_URE3) | NCRXXXXX | NPCC2011008446 | CIP-005-1 | R2; R2.3 | NPCC_URE3 self-reported to NPCC an issue with CIP-005-1 R2.3. During a NPCC CIP Compliance Audit of its subsidiary, it was discovered that both companies had an issue with CIP-005-1 R2.3. NPCC determined that NPCC_URE3's corporate procedure for securing dial-up access to the Electronic Security Perimeters (ESPs) was created approximately three years after NPCC_URE3 was required to comply with the Standard. NPCC_URE3 could not demonstrate that there was a procedure in effect prior to that time. This procedure is relied upon by multiple affiliated registered entities for compliance with CIP-005-3 R2.3, including NPCC_URE3. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because NPCC_URE3 provided evidence that demonstrated its commitment to securing its dial-up access points. First, dial-up access into the ESP is controlled by a system which utilizes multiple authentication controls including usernames, passwords, and other user authentication functions. Second, NPCC_URE3 does not allow dial-up access to its Energy Management System ESPs. Third, a presentation outlines how to secure the devices which are used to secure dial-up access. This presentation is given to the technicians responsible for installing the devices. | NPCC_URE3 created a procedure for securing dial-up access to the ESPs. The mitigation activity was verified complete by NPCC.
2012-04-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC201100776 | CIP-005-3 | R4 | RFC_URE1 self-reported an issue with CIP-005-3 R4 to ReliabilityFirst. In the Self-Report, the entity stated it failed to conduct its annual cyber vulnerability assessment of the electronic access points to the Electronic Security Perimeter (ESP) and of the Cyber Assets within the ESP. RFC_URE1 scheduled its annual cyber vulnerability assessment to occur concurrently with a planned major hardware and software upgrade of its Energy Management System/Supervisory Control and Data Acquisition (EMS/SCADA) and automatic generation control (AGC) systems; however, the hardware and software upgrade was delayed almost one month later. Due to the delay, RFC_URE1 conducted the cyber vulnerability assessment on its upgraded EMS/SCADA and AGC systems. ReliabilityFirst determined that RFC_URE1 had an issue with CIP-005-3 R4 when it did not perform an annual cyber vulnerability assessment of the electronic access points to the ESP and an annual cyber vulnerability assessment of all Cyber Assets within the ESP. | ReliabilityFirst determined that this issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because the risk was mitigated by the following factors. RFC_URE1 performed the cyber vulnerability assessment 21 days after the scheduled date. When RFC_URE1 later performed its cyber vulnerability assessment, RFC_URE1 assessed the upgraded EMS/SCADA and AGC. Therefore, RFC_URE1 assessed possible vulnerabilities and weaknesses of the upgraded EMS/SCADA and AGC systems rather than assessing the vulnerabilities and weaknesses for systems that RFC_URE1 was about to modify with major hardware and software upgrades. | RFC_URE1 submitted to ReliabilityFirst a Mitigation Plan to address the remediated issue of CIP-005-3 R4. In this Mitigation Plan, RFC_URE1 stated that it completed all mitigating actions necessary to address the remediated issue of CIP-005-3 R4. Specifically, RFC_URE1 completed the requisite cyber vulnerability assessment. Additionally, RFC_URE1 set up a notice in its compliance system that sends two employees a reminder to perform its annual cyber vulnerability assessment 60 days in advance of the due date. This notice will help ensure RFC_URE1 is not delinquent in performing its annual cyber vulnerability assessment.
2012-04-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC201100777 | CIP-007-3 | R8 | RFC_URE1 self-reported an issue with CIP-007-3 R8 to ReliabilityFirst. In the Self-Report, RFC_URE1 stated it failed to conduct its annual cyber vulnerability assessment of the electronic access points to the Electronic Security Perimeter (ESP) and of the Cyber Assets within the ESP. RFC_URE1 scheduled its annual cyber vulnerability assessment to occur concurrently with a planned major hardware and software upgrade of its Energy Management System/Supervisory Control and Data Acquisition (EMS/SCADA) and automatic generation control (AGC) systems; however, the hardware and software upgrade was delayed almost one month later. Due to the delay, RFC_URE1 conducted the cyber vulnerability assessment on its upgraded EMS/SCADA and AGC systems. ReliabilityFirst determined that RFC_URE1 had an issue with CIP-007-3 R8 when it did not perform an annual cyber vulnerability assessment of the electronic access points to the ESP and an annual cyber vulnerability assessment of all Cyber Assets within the ESP. | ReliabilityFirst determined that this issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because the risk was mitigated by the following factors. RFC_URE1 performed the cyber vulnerability assessment 21 days after the scheduled date. Additionally, when RFC_URE1 performed its cyber vulnerability assessment, RFC_URE1 assessed the upgraded EMS/SCADA and AGC. Therefore, RFC_URE1 assessed possible vulnerabilities and weaknesses of the upgraded EMS/SCADA and AGC systems rather than assessing the vulnerabilities and weaknesses for systems that RFC_URE1 was about to modify with major hardware and software upgrades. | RFC_URE1 submitted to ReliabilityFirst a Mitigation Plan to address the remediated issue of CIP-007-3 R8. In this Mitigation Plan, RFC_URE1 stated that it completed all mitigating actions necessary to address the remediated issue of CIP-005-3 R4. Specifically, RFC_URE1 completed the requisite cyber vulnerability assessment. Additionally, RFC_URE1 set up a notice in its compliance system that sends two employees a reminder to perform its annual cyber vulnerability assessment 60 days in advance of the due date. This notice will help ensure the entity is not delinquent in performing its annual cyber vulnerability assessment.
2012-04-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2012001313 | CIP-007-3 | R1 | RFC_URE2 self-reported an issue with CIP-007-3 R1 to ReliabilityFirst, identifying an issue of CIP-007-3 R1. Pursuant to its procedure to test changes to Cyber Assets, RFC_URE2 documented test results for new Cyber Assets and significant changes to existing Cyber Assets within the Electronic Security Perimeter (ESP) utilizing two forms, Form 1 and Form 2. Form 1 documented testing for new Cyber Assets within the ESP, and Form 2 documented testing for changes to Cyber Assets within the ESP. Form 2 also contained documentation of certain tests performed for new Cyber Assets within the ESP. When RFC_URE2 installed new operator workstations on four occasions for a two year period, RFC_URE2 completed Form 1, but not Form 2. RFC_URE2 failed to submit Form 2 because the individual responsible for doing so did not submit Form 2 until 30 to 120 days after the installation of the new operator workstations. Therefore, ReliabilityFirst determined that RFC_URE2 had an issue with the Standard for failing to complete the required documentation of testing performed on new Cyber Assets in the ESP. | ReliabilityFirst determined that this issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. RFC_URE2 completed Form 1 in each instance, which contains substantially the same information as Form 2. In addition, RFC_URE2 completed Form 2 for each of the devices when performing testing due to operating system security patches, within 30 to 120 days after the initial installation. | In order to mitigate the issue, RFC_URE2 replaced Form 1 and Form 2 with a single form and revised its procedures to include this single form. ReliabilityFirst verified that RFC_URE2 completed the mitigating activities.
2012-04-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC201100873 | CIP-003-1 | R6 | RFC_URE3 self-reported that during an internal assessment of CIP compliance, it discovered that it failed to document its assessment and application of certain patches on five applications. Since RFC_URE3 failed to monitor these Cyber Assets pursuant to CIP-007-1, it also failed to comply with CIP-003-1 R6. ReliabilityFirst determined that RFC_URE3 had an issue with the Standard for failing to implement supporting configuration management activities. The duration of the issue spans versions 1 through 3 of the Standard. | ReliabilityFirst determined that this issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The affected applications are considered non-critical Cyber Assets, and only one of the five affected applications had been issued a security patch by its original manufacturer over the duration of the issue. Although RFC_URE3 failed to document its assessment and application of certain patches on five applications, it assessed and applied patches for 97.8% of the applications within its Electronic Security Perimeter. Additionally, RFC_URE3 otherwise has an established change management program that includes associated procedures and supporting technology for implementation. Lastly, the affected Cyber Assets are protected by RFC_URE3’s comprehensive “defense-in-depth” security strategy. | RFC_URE3 submitted to ReliabilityFirst its Mitigation Plan to address the issue of NERC Reliability Standard CIP-003-1 R6. In the Mitigation Plan, RFC_URE3 memorialized the actions it took to address the issue with NERC Reliability Standard CIP-003-1 R6 and committed to additional actions to prevent future risk to the BPS. RFC_URE3 documented the implementation of identified patches and is undertaking significant, multi-faceted efforts to develop and implement an improved patch management process, including revisions to associated, dependent processes, such as RFC_URE3’s established change management program. RFC_URE3 completed the Mitigation Plan.
2012-04-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC201100874 | CIP-006-1 | R2 | RFC_URE3 self-reported that it discovered an issue with NERC Reliability Standard CIP-006-1 R2. In response to its discovery of possible noncompliance with CIP-007-3 R3 and CIP-003-1 R6, RFC_URE3 reviewed the affected Cyber Assets to assess its compliance with CIP-006-1 R2. This assessment identified Cyber Assets used to authorize or log access to the Physical Security Perimeter that did not receive all applicable cyber security software patches. These Cyber Assets are desktop computers that were subject to a vendor maintenance contract. Although the desktop computers were patched according to the vendor’s security software application, they were not patched relative to the installed operating systems and software applications. Since RFC_URE3 failed to consistently implement patches on these desktop computers, they were not afforded the protections of CIP-007-1 R3 and CIP-003-1 R6, as required by CIP-006-1 R2. The duration of the issue spanned versions 1 through 3c of the Standard. | ReliabilityFirst determined that this issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The desktop computer Cyber Assets involved in this issue were properly patched six months before the Self-Report and had received some patches through the vendor’s security-related software application up until that time. In addition, RFC_URE3 has an established change management program that includes associated procedures and supporting technology for implementation. Lastly, the affected Cyber Assets are protected by RFC_URE3’s comprehensive “defense-in-depth” security strategy of the BPS. | RFC_URE3 submitted to ReliabilityFirst its Mitigation Plan to address the issue with NERC Reliability Standard CIP-006-1 R2. In this Mitigation Plan, RFC_URE3 memorialized the actions it took to address the issue with NERC Reliability Standard CIP-006-1 R2 and committed to additional actions to prevent future risk to the BPS. RFC_URE3 documented the implementation of identified patches and is undertaking significant, multi-faceted efforts to develop and implement an improved patch management process, including revisions to associated, dependent processes, such as RFC_URE3’s established change management program. RFC_URE3 completed the Mitigation Plan.
2012-04-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC201100875 | CIP-007-1 | R3 | RFC_URE3 self-reported that during an internal assessment of CIP compliance, it discovered an issue with NERC Reliability Standard CIP-007-1 R3. ReliabilityFirst determined that RFC_URE3 had an issue with NERC Reliability Standard CIP-007-1 R3 by failing to consistently implement and document its efforts related to the tracking, evaluating, testing, and installation of applicable security patches for certain applications that are considered non-critical Cyber Assets within the Electronic Security Perimeter (ESP). The duration of the issue spans versions 1 through 3 of the Standard. | ReliabilityFirst determined that this issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). All affected applications are considered non-critical Cyber Assets, and only one of the five affected applications had been issued a security patch by its original manufacturer over the duration of the issue. Although RFC_URE3 failed to document its assessment and application of certain patches on five applications, it assessed and applied patches for 97.8% of the applications within its ESP. Additionally, RFC_URE3 otherwise has an established change management program that includes associated procedures and supporting technology for implementation. Lastly, the affected Cyber Assets are protected by RFC_URE3’s comprehensive “defense-in-depth” security strategy. | RFC_URE3 submitted to ReliabilityFirst its Mitigation Plan to address the issue with CIP-007-3 R3. In this Mitigation Plan, RFC_URE3 memorialized the actions it took to address the issue with NERC Reliability Standard CIP-007-3 R3 and committed to additional actions to prevent future risk to the BPS. RFC_URE3 documented the implementation of identified patches and is undertaking significant, multi-faceted efforts to develop and implement an improved patch management process, including revisions to associated, dependent processes, such as RFC_URE3’s established change management program. RFC_URE3 completed this Mitigation Plan.
2012-04-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC201100949 | CIP-005-1 | R1 | RFC_URE3 self-reported an issue with CIP-005-1 R1. RFC_URE3 discovered certain non-critical software components installed on Cyber Assets within an Electronic Security Perimeter (ESP) had not been identified in RFC_URE3’s documentation of Cyber Assets in the ESP as required by NERC Reliability Standards CIP-005-1 R1.4 and R1.6. More specifically, RFC_URE3 failed to categorize certain software components as non-critical Cyber Assets and, as a result, did not include those software components in its CIP compliance efforts aimed at identification and documentation of Cyber Assets in the ESP. As a result of RFC_URE3’s failure to identify all non-critical Cyber Assets within a defined ESP, it also failed to comply with NERC Reliability Standard CIP-005-1 R5. The duration of the issue spans versions 1 through 3a of the Standard. | ReliabilityFirst determined that this issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The Cyber Assets on which the software components were installed were identified as non-critical Cyber Assets and were protected by the ESP itself and RFC_URE3’s established “defense-in-depth” security strategy. Furthermore, the software components were maintained in accordance with RFC_URE3’s corporate processes, policies, and procedures, including its change management process, which afforded additional protection such as: (a) a requirement for a change ticket whenever a production change or modification is implemented; (b) a requirement that change tickets must include a test plan, test results, any variances or exceptions, and approvals by affected internal stakeholders to execute the change (including Real-Time Operations, where applicable); (c) a requirement that both internal and external notifications of planned modifications be made to affected stakeholders; (d) corporate-level archival of change tickets and RFC_URE3 source code; and (e) corporate-level version-control of RFC_URE3 source code. | RFC_URE3 submitted to ReliabilityFirst its Mitigation Plan to address the issue with NERC Reliability Standard CIP-005-1 R1. In this Mitigation Plan, RFC_URE3 memorialized the actions it took to address the issue with NERC Reliability Standard CIP-005-1 R1 and committed to additional actions to prevent future risk to the BPS. RFC_URE3 finalized its list of installed, non-critical software components and documented a formal process for control and maintenance of these software components. RFC_URE3 also relocated applications for which ESP protection is not necessary, which facilitates compliance by appropriately concentrating protection and compliance efforts. RFC_URE3 completed the Mitigation Plan.
2012-04-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC201100950 | CIP-005-1 | R5 | RFC_URE3 self-reported an issue with CIP-005-1 R5. RFC_URE3 reported that it discovered certain non-critical software components installed on Cyber Assets within an Electronic Security Perimeter (ESP) had not been identified in RFC_URE3’s documentation of Cyber Assets in the ESP as required by NERC Reliability Standards CIP-005-1 R1.4 and R1.6. More specifically, RFC_URE3 failed to categorize certain software components as non-critical Cyber Assets and, as a result, did not include those software components in its CIP compliance efforts aimed at identification and documentation of Cyber Assets in the ESP. As a result of RFC_URE3’s failure to identify all non-critical Cyber Assets within a defined ESP, it also failed to comply with NERC Reliability Standard CIP-005-1 R5. The duration of the issue spans versions 1 through 3a of the Standard. | ReliabilityFirst determined that this issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The Cyber Assets on which the software components were installed were identified as non-critical Cyber Assets and were protected by the ESP itself and RFC_URE3’s established “defense-in-depth” security strategy. Furthermore, the software components were maintained in accordance with RFC_URE3’s corporate processes, policies, and procedures, including its change management process, which afforded additional protection such as: (a) a requirement for a change ticket whenever a production change or modification is implemented; (b) a requirement that change tickets must include a test plan, test results, any variances or exceptions, and approvals by affected internal stakeholders to execute the change (including Real-Time Operations, where applicable); (c) a requirement that both internal and external notifications of planned modifications be made to affected stakeholders; (d) corporate-level archival of change tickets and RFC_URE3 source code; and (e) corporate-level version-control of RFC_URE3 source code. | RFC_URE3 submitted to ReliabilityFirst its Mitigation Plan to address the issue with NERC Reliability Standard CIP-005-1 R5. In this Mitigation Plan, RFC_URE3 memorialized the actions it took to address the issue with NERC Reliability Standard CIP-005-1 R5 and committed to additional actions to prevent future risk to the BPS. RFC_URE3 finalized its list of installed, non-critical software components and documented a formal process for control and maintenance of these software components. RFC_URE3 also relocated applications for which ESP protection is not necessary, which facilitates compliance by appropriately concentrating protection and compliance efforts. RFC_URE3 completed the Mitigation Plan.
2012-04-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2012009232 | CIP-003-2 | R2 | During an internal review of the CIP Standards, WECC_URE1 self-certified that it did not own any Critical Assets (CAs) or Critical Cyber Assets (CCAs). In the past, WECC_URE1 was not required to be compliant with CIP-003 through CIP-009 because WECC_URE1 did not have CAs or CCAs. This was accurate until April 1, 2010 when CIP-003-2 became enforceable for WECC_URE1 due to changes to Section 4.2.3 of CIP-003-2. The change required CIP-003-2 R2 to apply to all Responsible Entities, including Responsible Entities that have no CCAs. WECC_URE1 failed to notice this change in the Standard and as a result failed to assign a senior manager with overall responsibility and authority for leading and managing the entity's implementation of, and adherence to, Standards CIP-002-2 through CIP-009-2, as required by CIP-003-2 R2. | Although WECC_URE1 failed to assign a senior manager as required by CIP-003-2 R2, WECC determined that the issue posed a minimal risk to the reliability of the bulk power system because: 1. The entity has no CAs or CCAs. 2. The entity does not own or operate any facilities that would meet any of the Critical Asset Identification Criteria. | WECC_URE1 assigned a senior manager with the overall responsibility and authority for leading and managing the implementation of and adherence to CIP-002 through CIP-009.
2012-04-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2012009097 | CIP-007-3 | R9 | WECC_URE2 submitted a Self-Report stating that it had failed to document changes made to CIP-007-3 R5 procedure/policy within 30 days, pursuant to CIP-007-3 R9. Specifically, WECC_URE2 reported that the department responsible for the support of the network devices in the Emergency Management System (EMS) environment created a process document to capture the procedures and policies for “account management” as specified by R5. It was discovered that while the document does address R5.3, the information listed related to the authentication password controls for access to Critical Cyber Assets (CCAs) was out of date and had not been updated when a new authentication solution was implemented a year earlier. The change to the CIP-007-3 R5 procedure/policy occurred a year earlier, WECC_URE2 did not detect the issue and revise documentation until a year later, therefore, WECC_URE2 failed to document revised procedure within 30 days as required by CIP-007-3 R9. | WECC determined this issue posed minimal risk to the reliability of the bulk power system (BPS) because WECC_URE2 implemented procedures consistent with CIP-007-3. As compensating measures, WECC_URE2 stated that new password controls are stricter, e.g. the new systems require a minimum password length of 12 characters. WECC_URE2 states that all password controls required by the CIP-007 R5 standard were implemented. WECC, therefore, determined the risk posed by this issue was minimal. | WECC_URE2 updated CIP-007-3 R5 documentation to reflect revised process.
2012-04-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2012009688 | CIP-002-3 | R4 | During an Audit, WECC found that WECC_URE3 was noncompliant with CIP-002-3 R4 because it did not maintain a signed and dated list of its Critical Cyber Assets (CCAs). The entity does not have any CCAs, thus making this list a null set. | WECC determined this issue posed a minimal risk to the reliability of the bulk power system because the entity did not have any CCAs in accordance with its risk-based assessment methodology (RBAM). Although the entity did not maintain a signed and dated list of its CCAs, it does have in place a RBAM and a list of Critical Assets (CAs). Both of these documents are signed and dated by the entity's manager of a delegate thereof. Additionally, WECC verified that the entity mitigated the violation when it created a list of CCAs and had it signed by a senior manager. | The entity mitigated the violation when it created a list of CCAs and had it signed by a senior manager.
2012-04-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC201102826 | CIP-007-1 | R6 | WECC_URE4 performed an in-depth inventory of the Cyber Assets contained within the Electronic Security Perimeters (ESPs) for its substations. As a result of that inventory, WECC_URE4 discovered Cyber Assets that require a Technical Feasibility Exception (TFE) for CIP-007-1 Requirement 6. In total, 138 Critical Cyber Assets and 18 non-critical Cyber Assets located within 12 ESPs lacked the capability to implement automated tools or organizational process controls to monitor system events that are related to cyber security. WECC_URE4 self-reported that it had an issue with the CIP Standards arising from the entity's failure to timely submit TFE Requests in accordance with NERC procedures. The Self-Report referenced all identified TFEs that should have been filed as of that point. Specifically, WECC_URE4 submitted 37 late TFE Requests for CIP-007-1 R6. | WECC reviewed and accepted the TFE and determined it is technically infeasible for the entity to comply with the Standard for the devices associated with the TFE Identification number. The compensating measures, described below, were in place prior to the due date on which all such TFE requests were to originally be submitted to WECC. The entity had an implemented intrusion detection system (IDS) which monitors all network traffic and sends automated alerts upon detecting suspicious traffic. All devices in scope are located in Physical Security Perimeters and ESPs and thus afforded the protections of CIP-005 and CIP-006. Additionally, all individuals with access to the devices have a valid Personnel Risk Assessment and training. For these reasons, WECC determined that this issue posed minimal risk to the reliability of the bulk power system. | Entity filed the TFEs, WECC approved the Part A and Part B TFE.
2012-04-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 5 (WECC_URE5) | NCRXXXXX | WECC2011008701 | CIP-004-3 | R4 | WECC_URE5 self-reported an issue of CIP-004-3 R4. A WECC subject matter expert (SME) contacted WECC_URE5 to discuss its Self Report. According to the WECC SME, during the conversation, WECC_URE5 stated that it failed to update its access list and revoke access for two former employees within seven days of their leaving WECC_URE5 employment. The first employee left on August 5, 2011, and that employee’s access should have been revoked by August 12, 2011 but was not revoked until August 30, 2011. The second employee left WECC_URE5 on August 12, 2011 and that employee’s access should have been revoked on August 19, 2011 but was not revoked until September 13, 2011. According to the WECC SME, WECC_URE5 stated that these employees’ manager failed to notify WECC_URE5’s compliance department that the employees had left WECC_URE5 employment and, as a result, their access was not timely revoked and WECC_URE5’s access list was not updated. | The employees in scope had physical access to a Physical Security Perimeter (PSP) that contains Critical Cyber Assets (CCAs), but did not have electronic access to the CCAs. The employees had personal risk assessments (PRA) and training prior to getting physical access the CCAs. The CCAs in scope are located in a locked cabinet that had monitoring and logging measures to detect any unauthorized activity. For these reasons, WECC determined that this issue posed a minimal risk to the bulk power system. | WECC_URE5 revoked the access of the individuals involved in the violation and distributed an email outlining WECC_URE5's process for revoking employee's access to CCAs.
2012-03-30 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2011007267 | CIP-004-3 | R2 | FRCC_URE1 self-reported an issue with CIP-004-3 R2. FRCC_URE1 did not provide the proper training to two employees granted access to Critical Cyber Assets. Specifically, two long-term employees were granted NERC CIP access without having completed the proper NERC training. The first employee did not complete the annual required training and upon discovery five months later, the annual training was completed promptly. This employee had successfully completed 2009 and 2010 annual training, but his 2011 annual training was delayed by five months and six days. The second employee was inadvertently given access and was not trained prior to having access. His excess access privileges to NERC CIP Physical Security Perimeters (PSP) were revoked within six days. He was not aware that he had access nor did he exercise access during these six days. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the employees involved were long-term FRCC_URE1 personnel with satisfactory personnel risk assessments (PRAs). For the first employee, the annual training was delayed by five months, whereupon he completed the training with satisfactory results. With respect to the second employee, an incorrect badge was issued to a new employee who was not authorized for access to the secured PSP. This employee's access privileges to NERC CIP PSPs were revoked within six days. He was not aware that he had access nor did he exercise access during these six days. Although FRCC_URE1 has violated this Standard previously, the instant remediated issue is appropriate for FFT treatment because it does not represent a failure to mitigate a prior violation appropriately. The systems that FRCC_URE1 put in place to prevent recurrence of the prior violation were implemented for its transmission-related functions. The generation-related functions are managed separately and are the subject of the instant remediated issues. | With respect to the first employee, FRCC_URE1 provided the required training, which the employee completed with satisfactory results. FRCC_URE1's information security department corrected the improper access for the second employee and conducted a coaching session to re-emphasize the importance of following established procedures with staff responsible for processing card keys. Additionally, FRCC_URE1 modified the desk level procedure and trained its employee groups involved in granting physical and cyber access to reinforce the importance of following access procedures. FRCC verified completion of the mitigation activities.
2012-03-30 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2011007978 | CIP-004-3 | R2 | FRCC_URE1 self-reported an issue with CIP-004-3 R2. FRCC_URE1 allowed access to Critical Cyber Assets (CCA) for two contractors who were not trained as per FRCC_URE1's training program, as required by the Standard. These contractors were employees of a trusted vendor with a service level agreement for tuning and maintaining generating plant equipment. Access was granted on two occasions for very short durations (1 day and 3 days) and access and activity was monitored by generating plant operating personnel. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the two contractors were employees of a very large generating plant turbine equipment manufacturer, were authorized for turbine tuning, and have experience and sufficient training to handle the plant equipment. The vendor is responsible for plant equipment support and is under an obligation to maintain the plant equipment. In all instances, the access was controlled and all activities, including modifications, were performed in complete consultation with and observation by the plant operations staff. Although FRCC_URE1 has violated this Standard previously, the instant remediated issue is appropriate for FFT treatment because it does not represent a failure to mitigate a prior violation appropriately. The systems that FRCC_URE1 put in place to prevent recurrence of the prior violation were implemented for its transmission-related functions. The generation-related functions are managed separately and are the subject of the instant remediated issues. | FRCC_URE1 validated cyber security training for all access granted through the use of a vendor service request and on-boarding process. FRCC_URE1 also reviewed all vendor contractors who have performed remote access vendor support. Additionally, FRCC_URE1 updated and communicated procedures to ensure that vendor contractors providing support follow the full on-boarding process for contractors and have a completed annual cyber security training. FRCC verified completion of the mitigation activities.
2012-03-30 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2011007929 | CIP-006-1 | R1 (R1.1) | FRCC_URE1 self-reported an issue with CIP-006-1 R1. FRCC_URE1 failed to maintain a complete "six-wall" perimeter for five identified Physical Security Perimeters (PSPs) and failed to submit a TFE request, as required by the Standard. A review determined that the openings at issue were not easily accessible, as they were obstructed by carpets, furniture and plant equipment. All of the openings were located in ceilings or floors and FRCC_URE1 self-reported and corrected these after receiving guidance from NERC and FRCC that any opening greater than 96 square inches is an access point. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because a review determined that the openings at issue were not easily accessible, as they were obstructed by carpets, furniture and plant equipments. | To correct the issues at the control center, FRCC_URE1 installed sub-floor panels and extended the wall above the ceiling to the roof decks. Additionally, FRCC_URE1 updated the physical security plan to include the more restrictive criteria and documented changes in the change log as per the 30-day requirement. Further, the facility services developed procedures for checking the adequacy of the "six-wall" perimeters for PSPs in the future. The procedures consist of a checklist to help ensure application of the NERC and FRCC guidance criteria. FRCC verified the completion of the mitigation activities.
2012-03-30 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC201000406 | CIP-006-2 | R1 (R1.2) | FRCC_URE1 self-reported an issue with CIP-006-2 R1. FRCC_URE1 documented, implemented, and maintained a physical security plan, approved by the senior manager or delegate. However, FRCC_URE1 failed to identify one physical access point through the Physical Security Perimeter (PSP) and failed to identify the measures to control entry at this access point. Although the physical access point was not documented, most appropriate security controls were effective. The access point in question was for a HVAC maintenance access point in a ceiling inside the PSP. The HVAC access had an unlocked latch. The latch was locked and the issue corrected 461 days after the issue began. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because although the access point and access control methods were not documented for one access point, the access point was in a secured facility and was under constant observation. This facility is also secured with a 12-foot fence, is monitored by armed security guards at the gate, and is monitored periodically by a roving armed security guard. Access to the facility is only allowed for appropriate individuals based on need and justification and all individuals are screened at the gates. | FRCC_URE1 completed the following mitigation activities: (1) Installed a compliance CIP-controlled lock at the attic hatchway access point and created control procedure for access and use of a key prior to entry. The keys to these controlled locks are maintained in a secure location; (2) Enhanced facility services internal procedure regarding construction at applicable CIP-designated locations to prevent future occurrence of the construction-related hatch issue; (3) Updated the PSP drawings to include the hatch access and applicable access controls; (4) Conducted refresher training for facility services and Corporate Security employees; (5) Completed a one-time physical inspection of all "six-wall" perimeters at all PSP locations above and beyond the annual physical walkthrough, and corrected any exceptions to the physical security plan identified as a result of the review; and (6) Updated the physical security plan and Physical Perimeters Verification Form for verification of annual walkthrough. FRCC verified completion of the mitigation activities.
2012-03-30 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2011007971 | CIP-006-2 | R2 | FRCC_URE1 self-reported an issue with CIP-006-2 R2. FRCC_URE1 failed to identify one of the Cyber Assets used in the authorization and logging of access to the Physical Security Perimeter (PSP) for a generating unit identified as a Critical Asset with designated PSPs. FRCC determined that one of the physical access controllers was not documented but was appropriately protected as required by CIP-006 R2.2. Additionally, certain TFEs were submitted late for the requirements where it was technically infeasible to maintain strict compliance. TFEs were accepted by the region. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the issue was the result of a lack of documentation. The subject physical access controller was afforded all the required security controls of CIP-006-2 R2.2 that were technically feasible and only lacked submission of TFEs for requirements with technical limitation for the subject device. All comparable compensating and mitigating measures were in effect from the time of commissioning of the device, including firewall protection, procedural controls for password complexity and annual change, and procedural controls for malware protection and patching. A TFE was submitted late and accepted by the FRCC. | FRCC_URE1 reviewed the physical access control system and ensured that all cardkey control panels that control access for PSPs appear on the Cyber Asset list. FRCC_URE1 submitted appropriate existing cardkey TFEs for correct asset count. FRCC verified completion of the mitigation activities.
2012-03-30 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2011008072 | CIP-006-3c | R1 (R1.6) | FRCC_URE1 self-reported an issue with CIP-006 R1.6. On one occasion, one visitor was allowed access to a designated Physical Security Perimeter (PSP) and FRCC_URE1 failed to document the departure time and escort name. FRCC_URE1 has self-reported even though these logs are outside the 90-day log retention window as required by CIP standards. FRCC_URE1 further provided corroborating evidence and supporting attestation demonstrating the escort’s identity and departure time. The evidence demonstrated that the visitor was continuously escorted during his brief stay in the PSP. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because this was an isolated event which was the result of lack of complete documentation. The subject visitor was continuously escorted by authorized personnel and stayed in the PSP for a very short duration. | FRCC_URE1 completed a review of PSP visitor records to determine whether there were any additional occurrences by reviewing electronic and manual logs. Since no additional instances were found, FRCC_URE1 trained identified escorts regarding the requirement to complete the visitor log in full. FRCC_URE1 also issued awareness reminders to affected personnel reinforcing its visitor escort procedures. FRCC verified completion of the mitigation activities.
2012-03-30 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2011007968 | CIP-007-1 | R4 (R4.2) | FRCC_URE1 self-reported an issue with CIP-007-1 R4. For a period of approximately two and a half years, FRCC_URE1 failed to implement its anti-virus update procedure for testing and installing anti-virus signatures for various corporate and generating Cyber Assets that were required to comply with the Standard. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because all signatures were released from reliable vendors involving a thorough evaluation of the anti-virus signatures. All signatures other than the those released on weekends were tested using days of test data. Corporate system updates preceded the updates for the weekend signatures, limiting any significant risk to the Critical Cyber Assets (CCA). The corporate Cyber Assets were dedicated for administration of physical access controllers and the risk was minimal, as any adverse impact to these systems as a result of a malware signature update could not have impacted the BPS control and monitoring function. Physical access controls would continue to operate effectively without the administrative workstations, which are utilized to modify and update configurations only. | FRCC_URE1 resolved the anti-virus signature propagation delay for the Cyber Assets by modifying the application configuration. For the assets where configuring delay was not technically feasible with the current anti-virus product, FRCC_URE1 upgraded the anti-virus application to a different product that allowed for such propagation delay. FRCC_URE1 also updated the procedure documents to reflect the new configuration. FRCC verified completion of the mitigation activities.
2012-03-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2011007268 | CIP-007-1 | R3 | NPCC_URE1 self-reported an issue with CIP-007-1 R3. NPCC_URE1 has a documented security patch management program (CIP Security Patch Management Program). NPCC_URE1's program did not include the specific database associated with the energy management system (EMS) for a seven-month period. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because NPCC_URE1 had already been analyzing and reviewing the patches at issue in accordance with the CIP Security Patch Management Program, despite the fact that the program did not specifically include it. | NPCC_URE1 provided documentation that the database was added to the corporate security patch management program. The mitigation activity was verified complete by NPCC.
2012-03-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2011007274 | CIP-005-1 | R2; R2.6 | NPCC_URE1 self-reported an issue with CIP-005-1 R2.6. NPCC_URE1 self-reported that, for a 17-month period, all firewalls associated with the three corporate Electronic Security Perimeters (ESPs) did not display the appropriate use banner upon interactive access attempts, as required by the Standard. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because NPCC_URE1 has account administration controls in effect and strict physical security controls in place that limited access to certain users. | NPCC_URE1 provided documentation that the appropriate banners were added to all firewalls. The mitigation activity was verified complete by NPCC.
2012-03-30 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2012009645 | CIP-003-2 | R2 | SERC_URE1 self-certified a possible issue with CIP-003-2 R2, stating that it had not assigned a single senior manager with overall responsibility and authority for leading and managing the entity’s implementation of, and adherence to, Standards CIP-002-2 through CIP-009-2. SERC staff determined that the issue did not extend back to CIP-003-1 R2 because SERC_URE1 had documented and used its risk-based assessment methodology in 2007 and determined that it had no Critical Assets and therefore no Critical Cyber Assets (CCAs). Pursuant to the applicability section of CIP-003-1, SERC_URE1 was not required to be compliant with CIP-003-1 R2 because it had no CCAs. Upon the effective date of CIP-003-2 R2, however, SERC_URE1 was required by the applicability section of CIP-003-2 to comply with CIP-003-2 R2 even if it found it had no CCAs when using its risk-based assessment methodology. SERC_URE1 still does not have any Critical Assets and therefore has no CCAs. This issue spans versions 2 and 3 of CIP-003. | SERC staff determined that the issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because: 1. SERC_URE1 has no Critical Assets and does not own or operate any facilities that would meet any of the Critical Asset criteria set forth in the proposed CIP-002-4; and 2. A SERC_URE1's director was responsible for SERC_URE1's compliance with all the NERC Reliability Standards, and SERC_URE1's risk-based assessment methodology was in place and implemented, and reviewed annually by the director with no additions of Critical Assets or CCAs. | SERC staff verified that SERC_URE1 completed the following actions: The SERC_URE1 board of directors passed a board resolution which identified in writing a director as the senior manager with overall responsibility and authority for leading and managing SERC_URE1's implementation of, and adherence to Standards CIP-002 through CIP-009.
2012-03-30 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 2 (SERC_URE2) | NCRXXXXX | SERC2011007431 | CIP-003-2 | R2 | SERC_URE2 self-reported a possible issue with CIP-003-2 R2, stating that it had not assigned in writing a single senior manager with overall responsibility for leading and managing SERC_URE2’s implementation of, and adherence to, Standards CIP-002-2 through CIP-009-2. SERC staff determined that the issue did not extend back to CIP-003-1 R2 because SERC_URE2 had documented and used its risk-based assessment methodology in 2008 and determined that it had no Critical Assets and therefore no Critical Cyber Assets (CCAs). Pursuant to the applicability section of CIP-003-1, SERC_URE2 was not required to be compliant with CIP-003-1 R2 because it had no CCAs. Upon the effective date of CIP-003-2 R2, however, SERC_URE2 was required by the applicability section of CIP-003-2 to comply with CIP-003-2 R2 even if it found it had no CCAs when using its risk-based assessment methodology. This issue spans versions 2 and 3 of CIP-003. | SERC staff determined that the issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because: 1. SERC_URE2 has no Critical Assets and does not own or operate any facilities that would meet any of the Critical Asset Criteria set forth in the proposed CIP-002-4; and 2. During the period of noncompliance, the senior manager was in the same position as now and was in fact responsible for, and had the authority for, leading and managing SERC_URE2’s implementation of, and adherence to, Standards CIP-002 through CIP-009, but had not been formally assigned those duties in writing. | SERC staff verified that SERC_URE2 completed the following actions: 1. SERC_URE2 assigned, in writing, a single senior manager with overall responsibility and authority for leading and managing SERC_URE2's implementation of, and adherence to, CIP-002 through CIP-009. 2. SERC_URE2 also developed and implemented a CIP-003 procedure to address the appropriate designation of a senior manager with overall responsibility and authority for leading and managing SERC_URE2's implementation of, and adherence to, CIP-002 through CIP-009.
2012-03-30 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 3 (SERC_URE3) | NCRXXXXX | SERC2011006618 | CIP-002-1 | R3 | The SERC CIP audit team reported a possible issue with CIP-002-1 R3 because SERC_URE3’s Critical Cyber Asset (CCA) list included Cyber Assets that were not essential to the operation of Critical Assets. SERC staff learned the Cyber Assets that SERC_URE3 erroneously included on the CCA list were one router and two firewalls. The router resided outside the Electronic Security Perimeter (ESP) and was mistakenly added to the CCA list. The firewalls are access points to the ESP, and were protected as such, but were inaccurately designated as CCAs by SERC_URE3 personnel. | SERC determined that the issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of bulk power system because the router and two firewalls were not CCAs. The firewalls were access points to the ESP and were being afforded the protective measures pursuant to the CIP Standards. The router never resided within the ESP, was not an access point to the ESP and was not used in the access control and/or monitoring of the ESP. | SERC staff verified that SERC_URE3 completed the following actions: 1. SERC_URE3 removed the three Cyber Assets that were erroneously included on the CCA list. 2. SERC_URE3 added a statement to its CIP cyber security policy that stating that SERC_URE3's list of CCAs will contain explanations for adding or removing assets and will identify the Physical Security Perimeter (PSP) and ESP where the CCA will reside. The CCA list has also been updated to include the additional information regarding the PSP and ESP of the CCA.
2012-03-30 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 4 (SERC_URE4) | NCRXXXXX | SERC2011008455 | CIP-007-3 | R4 | SERC_URE4 self-reported a possible issue with CIP-007-3 R4 after inadvertently allowing an approved Technical Feasibility Exception (TFE) to expire. SERC_URE4 had submitted a TFE with an open-ended expiration date for two Cyber Assets (switches), on which anti-virus software and malware prevention tools could not be installed. SERC staff rejected the TFE, requesting that SERC_URE4 revise its explanation for the need for a TFE. SERC_URE4 revised the TFE and resubmitted it as a closed-ended TFE with an expiration date. SERC staff approved the revised TFE. SERC staff determined that SERC_URE4 failed to use anti-virus software and malware prevention tools on two Cyber Assets within an Electronic Security Perimeter (ESP) and did not document compensating measures applied to mitigate risk exposure after allowing an approved TFE to expire. | SERC staff determined that the issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because although the two Cyber Assets involved are not capable of installing anti-virus software or malware prevention tools, they retained the protection of residing within a Physical Security Perimeter and ESP while not covered by an approved TFE. | SERC staff verified that SERC_URE4 completed the following actions: SERC_URE4 submitted a new TFE request with an open-ended expiration date for the two Cyber Assets on which anti-virus software and malware prevention tools could not be installed in order to prevent this issue from occurring again.
2012-03-30 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE2012009901 | CIP-003-3 | R2.1 | During a compliance audit, Texas RE determined that TRE_URE1 did not assign a single senior manager with overall responsibility and authority for leading and managing implementation of, and adherence to, Standards CIP-002-3 through CIP-009-3, as required by CIP-003-3 R2.1. Texas RE determined that the duration period of this issue was from the day the Standard became mandatory and enforceable for TRE_URE1 through the effective date of its updated procedure, assigning a single senior manager. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the risk was mitigated by several factors. First, during the period of noncompliance, TRE_URE1 did not possess any Critical Cyber Assets (CCAs), which would require adherence with Standards CIP-002-3 through CIP-009-3. Second, TRE_URE1 stated, and Texas RE confirmed, that a senior manager was in place prior to the date the Standard became mandatory and enforceable. However, this change was not documented within the 30 calendar days of the effective day, as required by CIP-003-3 R2.2. Finally, Texas RE determined that TRE_URE1 has minimal potential impact on the BPS because TRE_URE1's peak load is approximately 120 MW. | A document appointing a senior manager was reviewed by Texas RE and Texas RE determined that this document was valid evidence that TRE_URE1 addressed the requirements of CIP-003-3 R2.1. Texas RE received an attestation letter from TRE_URE1, showing that TRE_URE1 has appointed an individual to serve as a single senior manager previously although it was not documented at the time of the appointment. As a result, Texas RE determined that TRE_URE1 has addressed the requirements of CIP-003-3 R2.1. Completion of the mitigation activities was verified by Texas RE during the compliance audit.
2012-03-30 | TRE_URE1liability Entity (TRE_URE1) | Unidentified Registered Entity 2 (TRE_URE2) | NCRXXXXX | TRE201100460 | CIP-003-1 | R2.2; R2.3 | TRE_URE1 discovered, during a compliance audit, that TRE_URE2's record identifying the responsible senior manager, with overall responsibility and authority for leading and managing the TRE_URE2's implementation of, and adherence to compliance with CIP-002 through CIP-009, was not signed. TRE_URE1 examined all records that required the senior manager's approval and found that they were signed by a different individual. Also, there was no record to evidence that changes to the named senior manager were documented within 30 calendar days of the effective date of the change. TRE_URE1 determined that TRE_URE2 did not address the requirements of CIP-003-1 R2.2 and R2.3 from the date that CIP-003-2 became enforceable and the requirements for identification of the senior manager and delegate became enforceable for entities without Critical Assets, through the date that the senior manager and delegate were identified and documented. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the issue was documentation related only and the risk was mitigated by several factors. First, the senior manager was identified in an acceptable document that was not signed but was backed up by emails that lead up to the signing of the delegation letter authorizing the plant manager to sign on behalf of the senior manager. Before the CIP-003-1 R2 requirement to document and identify the delegated person became enforceable for TRE_URE2, the plant manager was verbally given delegated authority to sign documents on behalf of the senior manager. As a result, the plant manager did in fact sign documents, including TRE_URE2's risk-based assessment methodology and Critical Assets lists. TRE_URE2 produced an attestation related to TRE_URE2's attempt to document the delegation of authority to the plant manager but the result of that documentation effort could not be provided to TRE_URE1. TRE_URE2 did not have any Critical Assets or Critical Cyber Assets. | During TRE_URE1's compliance audit, TRE_URE2 produced a new document that that has been determined by TRE_URE1 to sufficiently address the requirements of CIP-003-2 R2.2 and R2.3. The document identified and designated the senior manager and identified and designated approval authority to the plant manager.
2012-02-29 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 2 (FRCC_URE2) | NCRXXXXX | FRCC2011007253 | CIP-005-2 | R5; R5.2 | During a spot check, FRCC determined that the entity had an issue with CIP-005-2 R5. The entity's evidence was not sufficient to demonstrate that the entity updated the documentation to reflect the modification of the network or controls within 90 calendar days of the change. The entity's restoration plan included back-up requirements for intrusion protection devices which were removed the year before the spot check. The documentation was updated less than two years after the devices were removed. | FRCC determined that this issue did not pose serious or substantial risk and posed minimal risk to the reliability of the bulk power system (BPS) because the lack of updated documentation was mitigated by the fact that all entity personnel were adequately trained in recovery of the newly installed intrusion protection devices which were appropriately configured. | The entity completed mitigation activities including modifying the Critical Cyber Asset change management process and including steps for updating documents within the required period.
2012-02-29 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 2 (FRCC_URE2) | NCRXXXXX | FRCC2011007258 | CIP-007-1 | R4; R4.2 | During a spot check, FRCC determined that the entity had an issue with CIP-007-1 R4. The entity's evidence was sufficient to demonstrate that the entity submitted Technical Feasibility Exceptions (TFEs) for some of its devices. The FRCC spot check team reviewed entity documents and concluded that additional devices needed TFEs. Thus, the entity failed to submit TFEs for 15% of devices requiring TFEs. For these additional devices, the entity could not demonstrate that it documented a process for the update of anti-virus and malware prevention signatures which would address testing and installing the signatures. | FRCC determined that this issue did not pose serious or substantial risk and posed minimal risk to the reliability of the bulk power system (BPS) because the entity submitted TFEs for 85% of devices requiring TFEs. The incorrect accounting of the devices was an oversight and comparable security measures were enabled for the complete set of devices. Further, the entity had implemented a process for the update of anti-virus and malware prevention signatures which addressed testing and installing the signatures and the issue relates only to the failure to document the process. | The entity completed mitigation activities and submitted a new TFE for the remaining devices. The entity also updated the compliance documentation to include a process for the update of anti-virus and malware prevention signatures which addresses testing and installing the signatures.
2012-02-29 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2011008445 | CIP-003-1 | R1; R1.3 | The entity self-reported to NPCC an issue with CIP-003-1 R1. During a NPCC CIP audit of the entity's affiliate, it was found that the entity's cyber security policy was not signed by the senior manager assigned pursuant to CIP-003-2 R2, as required by the Standard. The cyber security policy is a single corporate document that is relied upon by multiple affiliated registered entities for compliance with CIP-003-2, including the entity. | NPCC determined that this issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because although the cyber security policy was not signed by the senior manager assigned pursuant to CIP-003 R2, it was reviewed by another department, who performs an annual review covering all NERC CIP-related information security requirements, and signed by another officer. This other officer was designated by the senior manager as his/her delegate pursuant to CIP-003 R2.3. Although the entity's affiliate has had an issue with this Standard previously, which was submitted in a prior FFT Report, the instant remediated issue nonetheless does not represent recurring conduct by the registered entity. The instant remediated issue and the prior remediated issue arose from the same conduct and was therefore not considered to be an aggravating factor. | The entity completed mitigation activities including reviewing and receiving approval of the cyber security policy by the senior manager assigned pursuant to CIP-003 R2. NPCC verified completion of the mitigation activities.
2012-02-29 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2011009040 | CIP-007-2a | R9 | During a NPCC CIP compliance audit, it was found that the entity had an issue with CIP-007-2a R9. NPCC determined that two of the entity's information security standard documents were not corrected to change its 90-day requirement to a 30-day requirement as required by the change in CIP-007-2a R9. The entity's information security standard documents were not corrected to change its 90-day requirement to a 30-day requirement, as required by the change in CIP-007-2a R9; however, the annual procedure review was performed in conformity with the Standard and updated to reflect the changes in CIP-007-3. The entity's NERC CIP information security standard documents are single corporate documents that are relied upon by multiple affiliated registered entities for compliance with CIP-007-2, including the entity. | NPCC determined that this issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because there were no system or control changes that occurred during the 8-month period in which the plan used the incorrect 90-day requirement. In addition, the annual procedure review was performed in conformity with the Standard and updated to reflect the changes reflected in CIP-007-3. Although the entity's affiliate has had an issue with this Standard previously, which was submitted in a prior FFT Report, the instant remediated issue nonetheless does not represent recurring conduct by the registered entity. The instant remediated issue and the prior remediated issue arose from the same conduct and was therefore not considered to be an aggravating factor. | The entity completed mitigation activities including updating the entity's parent company's information security standard documents by changing the ninety calendar day update requirement to the thirty calendar day update requirement. NPCC verified completion of the mitigation activities.
2012-02-29 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2011009041 | CIP-008-2 | R1; R1.4 | During a NPCC CIP compliance audit, it was determined that the entity had an issue with CIP-008-2 R1. NPCC determined that the entity's information security standard incident management document was approved to require a process for updating the Cyber Security Incident response plan within thirty days of any changes, as required by the Standard. This was done seventy days after its obligation to meet the 30-day requirement. The entity's cyber security policy is a single corporate document that is relied upon by multiple affiliated registered entities for compliance with CIP-008-2 R1.4, including the entity. | NPCC determined that this issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the information security standard incident management document was updated within a short period of time - less than three months after the ninety calendar day update requirement changed to the thirty calendar day update requirement. No interim and future risks were identified. Although the entity's affiliate has had an issue with this Standard previously, which was submitted in a prior FFT Report, the instant remediated issue nonetheless does not represent recurring conduct by the registered entity. The instant remediated issue and the prior remediated issue arose from the same conduct and was therefore not considered to be an aggravating factor. | The entity completed mitigation activities including the entity's parent company's information security standard incident management document was approved with the update to require a process for updating the Cyber Security Incident response plan within thirty days of any changes. NPCC verified completion of the mitigation activities.
2012-02-29 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2011009042 | CIP-009-1 | R4 | During a NPCC CIP compliance audit, it was determined that the entity had an issue with CIP-009-1 R4. NPCC determined that there was no documentation in the entity's disaster recovery procedures that addressed a process for backing up and storing information required to successfully restore Critical Cyber Assets (CCAs). The entity's cyber security policy is a single corporate document that is relied upon by multiple affiliated registered entities for compliance with CIP-009-1 R4 including the entity. | NPCC determined that this issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because evidence was provided that although there was no documentation in the entity's disaster recovery procedures that addressed a process for backing up and storage of information required to successfully restore CCAs, the backup and storage of information required to successfully restore CCAs was taking place. Although the entity's affiliate has had an issue with this Standard previously, which was submitted in a prior FFT Report, the instant remediated issue nonetheless does not represent recurring conduct by the registered entity. The instant remediated issue and the prior remediated issue arose from the same conduct and was therefore not considered to be an aggravating factor. | The entity completed mitigation activities including revising its disaster recovery procedures to include references to its change control and configuration procedure. The entity also revised this change control and configuration procedure to address CIP-009 R4 backup and restore requirements. NPCC verified completion of the mitigation activities.
2012-02-29 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 2 (NPCC_URE2) | NCRXXXXX | NPCC2011008444 | CIP-003-1 | R1; R1.3 | The entity self-reported to NPCC an issue with CIP-003-1 R1. During a NPCC CIP audit of the entity's subsidiary, it was found that the entity's cyber security policy was not signed by the senior manager assigned pursuant to CIP-003-2 R2, as required by the Standard. The cyber security policy is a single corporate document that is relied upon by multiple affiliated registered entities for compliance with CIP-003-2, including the entity. | NPCC determined that this issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because although the cyber security policy was not signed by the senior manager assigned pursuant to CIP-003 R2, it was reviewed by another department, who performs an annual review covering all NERC CIP-related information security requirements, and signed by another officer. This other officer was designated by the senior manager as his/her delegate pursuant to CIP-003 R2.3. Although the entity's subsidiary has had an issue with this Standard previously, which was submitted in a prior FFT Report, the instant remediated issue nonetheless does not represent recurring conduct by the registered entity. The instant remediated issue and the prior remediated issue arose from the same conduct and was therefore not considered to be an aggravating factor. | The entity completed mitigation activities including reviewing and receiving approval of the cyber security policy by the senior manager assigned pursuant to CIP-003 R2. NPCC verified completion of the mitigation activities.
2012-02-29 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 2 (NPCC_URE2) | NCRXXXXX | NPCC2011008449 | CIP-007-2a | R9 | The entity self-reported to NPCC an issue with CIP-007-2a R9. During a CIP compliance audit of the entity's subsidiary, NPCC determined that the entity failed to correct two of its information security standard documents to change its 90-day requirement to a 30-day requirement, as required by the change in CIP-007-2a R9. The entity's information security standard documents were not corrected to change its 90-day requirement to a 30-day requirement as required by the change in CIP-007-2a R9; however, the annual procedure review was performed in conformity with the Standard and updated to reflect the changes in CIP-007-3. The entity's NERC CIP information security standard documents are single corporate documents that are relied upon by multiple affiliated registered entities for compliance with CIP-007-2, including the entity. | NPCC determined that this issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because there were no system or control changes that occurred during the 8-month period in which the plan used the incorrect 90-day requirement. In addition, the annual procedure review was performed in conformity with the Standard and updated to reflect the changes reflected in CIP-007-3. Although the entity's affiliate has had an issue with this Standard previously, which was submitted in a prior FFT Report, the instant remediated issue nonetheless does not represent recurring conduct by the registered entity. The instant remediated issue and the prior remediated issue arose from the same conduct and was therefore not considered to be an aggravating factor. | The entity completed mitigation activities including updating the entity's parent company's information security standard documents by changing the ninety calendar day update requirement to the thirty calendar day update requirement. NPCC verified completion of the mitigation activities.
2012-02-29 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 2 (NPCC_URE2) | NCRXXXXX | NPCC2011008452 | CIP-008-2 | R1; R1.4 | The entity self-reported to NPCC an issue with CIP-008-2 R1. During a NPCC CIP compliance audit of the entity's subsidiary it was found that the subsidiary's information security standard incident management document was approved to require a process for updating the Cyber Security Incident response plan within thirty days of any changes, as required by the Standard. This was done seventy days after its obligation to meet the 30-day requirement. The entity's cyber security policy is a single corporate document that is relied upon by multiple affiliated registered entities for compliance with CIP-008-2 R1.4, including the entity. | NPCC determined that this issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the information security standard incident management document was updated within a short period of time - less than three months after the ninety calendar day update requirement changed to the thirty calendar day update requirement. No interim and future risks were identified. Although the entity's subsidiary has had an issue with this Standard previously, which was submitted in a prior FFT Report, the instant remediated issue nonetheless does not represent recurring conduct by the registered entity. The instant remediated issue and the prior remediated issue arose from the same conduct and was therefore not considered to be an aggravating factor. | The entity completed mitigation activities including the entity's information security standard incident management document was approved with the update to require a process for updating the Cyber Security Incident response plan within thirty days of any changes. NPCC verified completion of the mitigation activities.
2012-02-29 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 2 (NPCC_URE2) | NCRXXXXX | NPCC2011008454 | CIP-009-1 | R4 | The entity self-reported to NPCC an issue with CIP-009-1 R4. During a NPCC CIP compliance audit of the entity's subsidiary it was found that there was no documentation in the entity's disaster recovery procedures that addressed a process for backing up and storing information required to successfully restore Critical Cyber Assets (CCAs). The entity's cyber security policy is a single corporate document that is relied upon by multiple affiliated registered entities for compliance with CIP-009-1 R4 including the entity. | NPCC determined that this issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because evidence was provided that although there was no documentation in the entity's disaster recovery procedures that addressed a process for backing up and storage of information required to successfully restore CCAs, the backup and storage of information required to successfully restore CCAs was taking place. Although the entity's subsidiary has had an issue with this Standard previously, which was submitted in a prior FFT Report, the instant remediated issue nonetheless does not represent recurring conduct by the registered entity. The instant remediated issue and the prior remediated issue arose from the same conduct and was therefore not considered to be an aggravating factor. | The entity completed mitigation activities including revising its disaster recovery procedures to include references to its change control and configuration procedure. The entity also revised this change control and configuration procedure to address CIP-009 R4 backup and restore requirements. NPCC verified completion of the mitigation activities.
2012-02-29 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 3 (NPCC_URE3) | NCRXXXXX | NPCC2011008337 | CIP-007-2a | R9 | The entity self-reported to NPCC an issue with CIP-007-2a R9. During a CIP compliance audit of the entity's affiliate, NPCC determined that the entity failed to correct two of its information security standard documents to change its 90-day requirement to a 30-day requirement, as required by the change in CIP-007-2a R9. The entity's information security standard documents were not corrected to change its 90-day requirement to a 30-day requirement as required by the change in CIP-007-2a R9; however, the annual procedure review was performed in conformity with the Standard and updated to reflect the changes in CIP-007-3. The entity's NERC CIP information security standard documents are single corporate documents that are relied upon by multiple affiliated registered entities for compliance with CIP-007-2, including the entity. | NPCC determined that this issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because there were no system or control changes that occurred during the 8-month period in which the plan used the incorrect 90-day requirement. In addition, the annual procedure review was performed in conformity with the Standard and updated to reflect the changes reflected in CIP-007-3. Although the entity's affiliate has had an issue with this Standard previously, which was submitted in a prior FFT Report, the instant remediated issue nonetheless does not represent recurring conduct by the registered entity. The instant remediated issue and the prior remediated issue arose from the same conduct and was therefore not considered to be an aggravating factor. | The entity completed mitigation activities including updating the entity's parent company's information security standard documents by changing the ninety calendar day update requirement to the thirty calendar day update requirement. NPCC verified completion of the mitigation activities.
2012-02-29 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 4 (NPCC_URE4) | NCRXXXXX | NPCC2011008443 | CIP-003-1 | R1; R1.3 | The entity self-reported to NPCC an issue with CIP-003-1 R1. During a NPCC CIP audit of the entity's affiliate, it was found that the entity's cyber security policy was not signed by the senior manager assigned pursuant to CIP-003-2 R2, as required by the Standard. The cyber security policy is a single corporate document that is relied upon by multiple affiliated registered entities for compliance with CIP-003-2, including the entity. | NPCC determined that this issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because although the cyber security policy was not signed by the senior manager assigned pursuant to CIP-003 R2, it was reviewed by another department, who performs an annual review covering all NERC CIP-related information security requirements, and signed by another officer. This other officer was designated by the senior manager as his/her delegate pursuant to CIP-003 R2.3. Although the entity's affiliate has had an issue with this Standard previously, which was submitted in a prior FFT Report, the instant remediated issue nonetheless does not represent recurring conduct by the registered entity. The instant remediated issue and the prior remediated issue arose from the same conduct and was therefore not considered to be an aggravating factor. | The entity completed mitigation activities including reviewing and receiving approval of the cyber security policy by the senior manager assigned pursuant to CIP-003 R2. NPCC verified completion of the mitigation activities.
2012-02-29 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 4 (NPCC_URE4) | NCRXXXXX | NPCC2011008451 | CIP-007-2a | R9 | The entity self-reported to NPCC an issue with CIP-007-2a R9. During a CIP compliance audit of the entity's affiliate, NPCC determined that the entity failed to correct two of its information security standard documents to change its 90-day requirement to a 30-day requirement, as required by the change in CIP-007-2a R9. The entity's information security standard documents were not corrected to change its 90-day requirement to a 30-day requirement as required by the change in CIP-007-2a R9; however, the annual procedure review was performed in conformity with the Standard and updated to reflect the changes in CIP-007-3. The entity's NERC CIP information security standard documents are single corporate documents that are relied upon by multiple affiliated registered entities for compliance with CIP-007-2, including the entity. | NPCC determined that this issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because there were no system or control changes that occurred during the 8-month period in which the plan used the incorrect 90-day requirement. In addition, the annual procedure review was performed in conformity with the Standard and updated to reflect the changes reflected in CIP-007-3. Although the entity's affiliate has had an issue with this Standard previously, which was submitted in a prior FFT Report, the instant remediated issue nonetheless does not represent recurring conduct by the registered entity. The instant remediated issue and the prior remediated issue arose from the same conduct and was therefore not considered to be an aggravating factor. | The entity completed mitigation activities including updating the entity's parent company's information security standard documents by changing the ninety calendar day update requirement to the thirty calendar day update requirement. NPCC verified completion of the mitigation activities.
2012-02-29 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 4 (NPCC_URE4) | NCRXXXXX | NPCC2011008453 | CIP-008-2 | R1; R1.4 | The entity self-reported to NPCC an issue with CIP-008-2 R1. During a NPCC CIP compliance audit of the entity's affiliate, it was found that the affiliate's information security standard incident management document was approved to require a process for updating the Cyber Security Incident response plan within thirty days of any changes, as required by the Standard. This was done seventy days after its obligation to meet the 30-day requirement. The entity's cyber security policy is a single corporate document that is relied upon by multiple affiliated registered entities for compliance with CIP-008-2 R1.4, including the entity. | NPCC determined that this issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the information security standard incident management document was updated within a short period of time - less than three months after the ninety calendar day update requirement changed to the thirty calendar day update requirement. No interim and future risks were identified. Although the entity's affiliate has had an issue with this Standard previously, which was submitted in a prior FFT Report, the instant remediated issue nonetheless does not represent recurring conduct by the registered entity. The instant remediated issue and the prior remediated issue arose from the same conduct and was therefore not considered to be an aggravating factor. | The entity completed mitigation activities including the entity's parent company's information security standard incident management document was approved with the update to require a process for updating the Cyber Security Incident response plan within thirty days of any changes. NPCC verified completion of the mitigation activities.
2012-02-29 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 5 (NPCC_URE5) | NCRXXXXX | NPCC2011008517 | CIP-005-1 | R4 | During a joint compliance audit conducted by NPCC and another region, NPCC determined that the entity failed to complete a cyber vulnerability assessment in accordance with CIP-005-1 R4. NPCC determined that the entity completed its first formal cyber vulnerability assessment of the electronic access points to the Electronic Security Perimeter (ESP) eleven months past the required compliance date. The other region also found that the same conduct gave rise to an issue for an affiliate of the entity. NPCC did not consider the affiliate's issue an aggravating factor, as the issues arose from the same conduct. | NPCC determined that this issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because although the entity did not complete the formal annual cyber vulnerability assessment by its required compliance date, it did complete most of the work required by CIP-005-1 R4.1 through R4.4, including continually reviewing and hardening its ESP firewalls. | The entity completed the cyber vulnerability assessment. NPCC verified completion of the mitigation activities.
2012-02-29 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 5 (NPCC_URE5) | NCRXXXXX | NPCC2011008520 | CIP-006-1 | R1; R1.1 | During a joint compliance audit conducted by NPCC and another region, NPCC determined that the entity had an issue with CIP-006-1 R1. CIP-006-1 R1.1 requires that all Cyber Assets within an Electronic Security Perimeter (ESP) also reside within an identified Physical Security Perimeter (PSP). The entity has two Critical Cyber Assets (CCA) in one PSP within its alternate control center that are connected to a network switch in another separate PSP within the alternate control center. Since all three devices are in the ESP, the network cables that connect these devices are required to be contained within a PSP. However, a section of the two network cables used to connect the CCA to the network switch ran outside the PSPs through the ceiling of a conference room and did not meet the requirement of CIP-006-1 R1.1. The other region also found that the same conduct gave rise to an issue for an affiliate of the entity. NPCC did not consider the affiliate's issue an aggravating factor, as the issues arose from the same conduct. | NPCC determined that this issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the network cables that were the cause of this issue were protected by several layers of physical security controls and were not in a public area. The room traversed by the cables was within two additional rings of security and utilized a defense in depth strategy that included fencing, card key access to the building itself, and both exterior and interior camera monitoring. The entire building is limited to employees of the entity and escorted visitors. | The entity completed mitigation activities by running new network cables through the existing conduit that connected the two PSPs. This was performed prior to the completion of the NPCC CIP compliance audit. NPCC verified completion of the mitigation activities.
2012-02-29 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 5 (NPCC_URE5) | NCRXXXXX | NPCC2011008519 | CIP-006-1 | R1; R1.8 | During a joint compliance audit conducted by NPCC and another region, NPCC determined that the entity had an issue with CIP-006-1 R1. CIP-006-1 R1.8 requires Cyber Assets used in the access control and monitoring of the Physical Security Perimeter to be afforded the protections required by various CIP standards, including a vulnerability assessment as required by CIP-007-1 R8. NPCC determined that the entity completed its first formal cyber vulnerability assessment pursuant to CIP-007-1 R8 eleven months past the required compliance date. The other region also found that the same conduct gave rise to an issue for an affiliate of the entity. NPCC did not consider the affiliate's issue an aggravating factor, as the issues arose from the same conduct. | NPCC determined that this issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because although the entity did not complete the cyber vulnerability assessment by its required compliance date, the entity provided examples of actions such as approved purchase orders and statements of work which showed that the elements of the vulnerability assessment were being exercised and documented before the compliant status due date. Further, the entity was not found to be out of compliance with other requirements of CIP-006-1 R1.8. | The entity completed the cyber vulnerability assessment. NPCC verified completion of the mitigation activities.
2012-02-29 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 5 (NPCC_URE5) | NCRXXXXX | NPCC2011008518 | CIP-007-1 | R8 | During a joint compliance audit conducted by NPCC and another region, NPCC determined that the entity failed to complete a cyber vulnerability assessment in accordance with CIP-007-1 R8. NPCC determined that the entity completed its first formal cyber vulnerability assessment of all Cyber Assets within the Electronic Security Perimeter (ESP) eleven months past the required compliance date. The other region also found that the same conduct gave rise to an issue for an affiliate of the entity. NPCC did not consider the affiliate's issue an aggravating factor, as the issues arose from the same conduct. | NPCC determined that this issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because although the entity did not complete the formal annual cyber vulnerability assessment by its required compliance date, it did complete most of the work required by CIP-007-1 R8.1 through R8.4, including continually reviewing and hardening its ESP firewalls. The entity also provided examples of actions such as approved purchase orders and statements of work which showed that the elements of the vulnerability assessment were being exercised and documented before the compliant status due date. | The entity completed the cyber vulnerability assessment. NPCC verified completion of the mitigation activities.
2012-02-29 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2011001103 | CIP-006-3c | R7 | The entity self-reported an issue with CIP-006-3c R7 to ReliabilityFirst and another region. The entity discovered that its access control system's file backup process corrupted data files associated with physical access logs. Specifically, the backup process corrupted approximately 75 hours of stored physical access log data. By recovering some of the corrupted computer data and utilizing video cameras at access points of its Physical Security Perimeters (PSPs), the entity was able to assemble physical entry logs for approximately 70 of the 75 hours of corrupted data. The entity was unable to recover the remaining five hours of corrupt data and therefore could not retain all physical access logs for at least 90 calendar days. ReliabilityFirst determined that the entity had an issue with the Standard as it did not retain all physical access logs for at least 90 calendar days. | ReliabilityFirst determined that this remediated issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because during the duration of the remediated issue the access control system operated properly at all PSP access points. Additionally, the entity found no evidence of a cyber attack on its access control system or unauthorized physical intrusion into its PSP. Finally, the five-hour gap in physical access logs is limited to only two PSP access points. | In its Self-Report, the entity states that it reconfigured its access control system's file backup process to preclude any subsequent data loss.
2012-02-29 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2011001246 | CIP-005-1 | R4 | During a joint compliance audit conducted by ReliabilityFirst and another region, ReliabilityFirst determined that the entity completed its formal cyber vulnerability assessment eleven months past the required compliance date. | ReliabilityFirst determined that the remediated issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because although the entity did not complete the formal annual cyber vulnerability assessment by the required date, it did complete most of the work required by CIP-005-1 R4.1 through R4.4, including continually reviewing and hardening its Electronic Security Perimeter firewalls. The same conduct gave rise to an issue for an affiliate of the entity in another region but was not considered an aggravating factor. | The entity completed the cyber vulnerability assessment as required by CIP-005-1 R4. The entity completed this mitigation activity as verified at the compliance audit by ReliabilityFirst.
2012-02-29 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2011001247 | CIP-006-1 | R1; R1.1 | During a joint compliance audit conducted by ReliabilityFirst and another region, ReliabilityFirst determined that the entity failed to maintain Critical Cyber Assets (CCAs) within an Electronic Security Perimeter (ESP) within an identified Physical Security Perimeter (PSP). The entity has two CCAs (operator workstations) in one PSP within its alternate control center that are connected to a network switch in another separate PSP within the alternate control center. Since all devices are in the ESP, the network cables that connect these devices are required to be contained within a PSP; however, a section of the two network cables used to connect the CCAs to the network switch ran outside the PSPs through the ceiling of a conference room and did not meet the requirement of CIP-006-1 R1.1. | ReliabilityFirst determined that the remediated issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the network cables that were the cause of the issue were protected by several layers of physical security controls and were not in a public area. The room traversed by the cables was within two additional rings of security and utilized a defense in depth strategy that included fencing, card key access to the building itself, and has both exterior and interior camera monitoring. The entire building is limited to employees of the entity and escorted visitors. The same conduct gave rise to an issue for an affiliate of the entity in another region but was not considered an aggravating factor. | The entity corrected this issue by running new network cables through an existing conduit that connected the two Physical Security Perimeters (PSPs). This was performed prior to the completion of the compliance audit. The entity completed its mitigation activity as verified by ReliabilityFirst.
2012-02-29 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2011001248 | CIP-006-1 | R1; R1.8 | During a joint compliance audit conducted by ReliabilityFirst and another region, ReliabilityFirst determined that the entity completed its formal cyber vulnerability assessment eleven months past the required compliance date. | ReliabilityFirst determined that the remediated issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because although the entity did not complete the cyber vulnerability assessment by the required date, the entity provided examples of actions, approved purchase orders/statement of work showing that the elements of the vulnerability assessment were being exercised and documented before the due date and were not found to be out of compliance with other requirements of CIP-006-1 R1. The same conduct gave rise to an issue for an affiliate of the entity in another region but was not considered an aggravating factor. | The entity completed the cyber vulnerability assessment as required by CIP-006-1 R1. The entity completed its mitigation activity as verified at the compliance audit by ReliabilityFirst.
2012-02-29 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2011001249 | CIP-007-1 | R8 | During a joint compliance audit conducted by ReliabilityFirst and another region, ReliabilityFirst determined that the entity completed its formal cyber vulnerability assessment eleven months past the required compliance date. | ReliabilityFirst determined that the remediated issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because although the entity did not complete the formal annual cyber vulnerability assessment by the required date, it did complete most of the work required by CIP-007-1 R8.1 through R8.4 including continually reviewing and hardening its ESP firewalls. The entity also provided examples of actions, approved purchase orders/statement of work showing that the elements of the vulnerability assessment were being exercised and documented before the compliant status due date. The same conduct gave rise to an issue for an affiliate of the entity in another region but was not considered an aggravating factor. | The entity completed the cyber vulnerability assessment as required by CIP-007-1 R8. The entity completed its mitigation activity as verified at the compliance audit by ReliabilityFirst.
2012-02-29 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP201000390 | CIP-003-1 | R4; R4.1 | During a Self-Certification, SPP RE_URE1 reported that it had an issue with CIP-003-1 R4 because it had not identified, classified, or protected information associated with Critical Cyber Assets (CCAs). Specifically, SPP RE_URE1failed to thoroughly inventory and protect all of its security configuration information such as system configurations, system rule sets, and critical security settings, as required by CIP-003-1 R1.4. | The SPP RE determined that this issue posed a minimal risk and did not pose a serious or substantial risk to the bulk power system (BPS). Although SPP RE_URE1 had not thoroughly inventoried and actively protect its security configuration information, SPP RE_URE1’s system rule sets, system configurations, and critical security settings comprising its cyber security information were actually stored on machines within SPP RE_URE1’s Electronic Security Perimeter (ESP), which were protected. Additionally, SPP RE_URE1 did provide evidence that it had identified and protected other information associated with its CCAs, including its network topology or similar diagrams, floor plans and computing centers that contain CCAs, equipment layouts of CCAs, disaster recovery plans and incident response plans. Further, SPP RE_URE1 had a written policy in place for the identification, classification and protection of information related to CCAs; however, the policy did not include the specific security configuration information. | To mitigate this issue, SPP RE_URE1 updated its current list of CCAs to ensure that all system security configuration information had been identified, classified and protected from unauthorized access. SPP RE_URE1 modified its existing policy to document the identification, classification and protection of CCA protected information and identified how SPP RE_URE1 personnel will be granted access to this information. The policy also included a change in the management process for incorporating new CCA information or changes to existing CCA information. SPP RE_URE1 trained all affected employees on the new policy. SPP RE_URE1 certified that mitigation was complete, and SPP RE verified completion.
2012-02-29 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP201000398 | CIP-005-1 | R5; R5.1; R5.3 | During a Self-Certification, SPP RE_URE1 reported that it had an issue with CIP-005-1 R5. SPP RE_URE1 reported that it did not have documentation that it had performed an annual review of the documents and procedures referenced in Standard CIP-005 (R5.1). Additionally, because SPP RE_URE1 had not configured all access logs, its access logs were not maintained for a minimum of 90 days as required by R5.3. | The SPP RE has determined that this issue posed a minimal risk and did not pose a serious or substantial risk to the bulk power system (BPS). In order for SPP RE_URE1 to be compliant with CIP-005-1 R5, it should have reviewed the documents and procedures referenced in Standard CIP-005 within the required one year time frame. Although SPP RE_URE1 did not have documentation that it had performed any review of its documents and procedures referenced in Standard CIP-005 within the required one year time frame. It is clear that SPP RE_URE1 had reviewed those documents and procedures, as evidenced by the record; however, that review was not within the annual timeframe. | To mitigate this issue, SPP RE_URE1 completed its Mitigation Plans and updated its CIP-005 procedures. Then, SPP RE_URE1 performed an annual review of its CIP-005 documentation. Additionally, SPP RE_URE1 developed a policy to review its CIP-005 documentation at least annually and included requirements to update its CIP-005 documentation to reflect modifications to the network controls within 90 calendar days of a change; retain electronic access logs for at least 90 calendar days; and keep logs related to reportable incidents in accordance with the requirements of CIP-008. SPP RE_URE1 certified that mitigation was complete, and SPP RE verified completion.
2012-02-29 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPPRE_URE2) | NCRXXXXX | SPP201100662 | CIP-007-1 | R2 | SPPRE_URE2 self reported an issue with CIP-007-1 R2. SPPRE_URE2 reported that, while conducting its vulnerability assessment under CIP-007-3 R8, it found that it did not have documented evidence justifying the enabled ports and services on assets within the Electronic Security Perimeter (ESP), which were essential to the normal or emergency operation of SPPRE_URE2’s Cyber Assets. Prior to the initial development of SPPRE_URE2’s CIP compliance program, SPPRE_URE2’s Cyber Assets underwent a “hardening” process where several ports and services were disabled to improve device security. This hardening process was not documented and did not generate sufficient evidence to justify each and every enabled port and service. The vulnerability assessment identified ports and services that were enabled on various devices that were not essential to the normal or emergency operation of SPPRE_URE2’s Cyber Assets. | SPP RE determined that this issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). SPPRE_URE2 did successfully document that the ports were enabled on specified assets in its previous vulnerability assessment. Furthermore, the ports and services identified in the vulnerability assessment at issue as candidates to be disabled, did not present an obvious threat to the assets as they are operated within an ESP. Prior to the vulnerability assessment at issue, SPPRE_URE2 implemented a system tool that monitors system activity and alerts administrators upon detection of anomalous or suspicious activity. This further reduces the potential impact that the identified problems with CIP-007-1 R2 could cause. Additionally, SPPRE_URE2 has deployed and runs anti-virus and anti-malware software on its Cyber Assets as per CIP-007-1 R4. This reduces the risk of system exploits using viral code recognized by commercial anti-virus solutions. When considering SPPRE_URE2’s other protective measures in place, the potential on the BPS was minimal. Following its vulnerability assessment, SPPRE_URE2 began the process of documenting and justifying the enabled ports and services on its Cyber Assets. | Using data from the vulnerability assessment, SPPRE_URE2 has developed a database recording each enabled port and service on every asset inside its ESPs. SPPRE_URE2 has subsequently ensured that this database is aligned with the actual status of each machine. Print outs from this database will be reviewed and signed on a per-machine basis. SPPRE_URE2 also configured its ports and services to conform with the approved ports and services reports. SPPRE_URE2 certified mitigation was complete, and SPP RE verified completion.
2012-02-29 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 3 (SPPRE_URE3) | NCRXXXXX | SPP201100665 | CIP-002-1 | R4 | During a compliance audit, SPP RE determined that SPP RE_URE3 had an issue with CIP-002-1 R4. SPP RE's CIP compliance audit team found that SPP RE_URE3's risk-based assessment methodology (RBAM) was not reviewed or approved by SPP RE_URE3's designated senior manager or a delegate of the senior manager. Instead, a SPP RE_URE3's compliance officer reviewed and approved the RBAM. Because this compliance officer was not also the senior manager, nor was he a delegate of the senior manager, his review and approval of SPP RE_URE3's RBAM did not comply with CIP-002-1 R4. | SPP RE has determined that this issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the issue was related to a documentation error. SPP RE_URE3 did review its RBAM; however, it did not have the correct person approve the RBAM. In addition, the RBAM for the previous year was approved by the correct individual. | SPP RE_URE3 changed the language of its review and approval certification to provide specifically that the RBAM was reviewed and approved separately from the approval of the list of Critical Assets. SPP RE_URE3 certified completion of all mitigating activities.
2012-02-29 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 4 (SPPRE_URE4) | NCRXXXXX | SPP201100666 | CIP-002-1 | R4 | During a compliance audit, SPP RE determined that SPPRE_URE4 had an issue with CIP-002-1 R4. SPP RE's CIP compliance audit team found that SPPRE_URE4's risk-based assessment methodology (RBAM) was not reviewed or approved by SPPRE_URE4's designated senior manager or a delegate of the senior manager. Instead SPPRE_URE4 compliance officer reviewed and approved the RBAM. Because the chief compliance officer was not also the senior manager, nor was he a delegate of the senior manager, his review and approval of SPPRE_URE4's RBAM did not comply with CIP-002-1 R4. | SPP RE has determined that this issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the issue was related to a documentation error. SPPRE_URE4 did review its RBAM; however, it did not have the correct person approve the RBAM. In addition, the RBAM for the previous year was approved by the correct individual. | SPPRE_URE4 changed the language of its review and approval certification to provide specifically that the RBAM was reviewed and approved separately from the approval of the list of Critical Assets. SPPRE_URE4 certified completion of all mitigating activities.
2012-02-29 | TRE_URE1liability Entity (TRE_URE1) | Unidentified Registered Entity 2 (TRE_URE2) | NCRXXXXX | TRE201000175 | CIP-003-1 | R1.1 | The entity self-reported that its cyber security policy did not address all of the requirements in Standards CIP-002-2 through CIP-009-2, as required by CIP-003-2 R1.1. TRE_URE1 found the policy presented by the entity failed to adequately address the following two requirements: CIP-007-2 R5 and CIP-003-2 R5, as required by this Standard. | This issue did not pose a serious or substantial risk to the bulk power system (BPS) but posed a moderate risk to the BPS. TRE_URE1 determined that the risk was substantially mitigated by the fact that the entity's plan has been in place prior to the mandatory compliance date, and was annually reviewed and updated according to its internal document control procedures, and adequately addressed the vast majority of the requirements in Standards CIP-002-2 thorough CIP-009-2. Yet, a TRE_URE1 review of the entity's cyber security policy revealed that the policy failed to thoroughly address CIP-007-2 R5 and CIP-003-2 R5. TRE_URE1 determined that the entity's more recent version of its cyber security policy is more reflective of the Standards intent, mitigates the issue, and minimizes the risk to the reliability of the BPS. | TRE_URE1 received the entity's updated cyber security plan. The updated policy addresses each applicable CIP standard and requirement. Under each requirement there is a brief description of how the entity meets that requirement. The updated policy mitigates the issue with CIP-003-2 R1.1. The entity revised its policy to mitigate the issue.
2012-02-29 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 3 (TRE_URE3) | NCRXXXXX | TRE201000142 | CIP-004-1 | R4.1 | The entity self-reported that it did not adequately perform a review of the list(s) of its personnel who have access to Critical Cyber Assets (CCAs) on quarterly basis. The entity lacked sufficient evidence to demonstrate that reviews of access lists were done comprehensively and timely by all affected operational organizations. The affected organizations stated that they had timely performed the reviews, but lacked sufficient evidence to demonstrate satisfactory compliance with this Standard. | This issue did not pose a serious or substantial risk and posed a minimal risk to the bulk power system (BPS) because this was a documentation issue, which was mitigated by the entity's ongoing security program and its additional methods of determining misuse and threats to its systems, which include card-key access, security cards and/or video surveillance at access locations. | The entity completed its Mitigation Plan, which included training and spot checking of the entity's personnel compliance with the newly revised policies and procedures. The entity also installed and began using a new tracking software to further ensure compliance.
2012-02-29 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 3 (TRE_URE3) | NCRXXXXX | TRE201100382 | CIP-005-1 | R3 | The entity self-reported that it did not address the requirements of this Standard and that it was not technically feasible for the devices (relays that were considered CCAs) at issue to detect and alert attempts for or actual unauthorized accesses to its Electronic Security Perimeter(s), as required by this Standard. | This issue did not pose a serious or substantial risk and posed a minimal risk to the bulk power system (BPS) because the devices were in the family of devices that could not support logging. However, the entity controls access to the devices by keycard logging entry and also uses a video camera. | The entity filed a Technical Feasibility Exception (TFE) for this issue. To mitigate the issue, the entity installed a password protected lockbox. Also, maintenance personnel must call security for the password to open the lockbox.
2012-02-29 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 3 (TRE_URE3) | NCRXXXXX | TRE201100383 | CIP-007-1 | R4 | The entity self-reported that it did not address all requirements of this Standard. The entity stated that it was not technically feasible for the devices at issue (firewall service modules, relays, remote terminal units and switches) to use anti-virus and other malicious software prevention tools to detect, prevent, deter, and mitigate the introduction, exposure, and propagation of malware on all Cyber Assets within the Electronic Security Perimeter(s). | This issue did not pose a serious or substantial risk and posed a minimal risk to the bulk power system (BPS) because the entity restricts administrative access to the devices and does not allow establishing connections with indiscriminate and unknown Internet hosts and devices. Additionally, malware cannot be transferred from one embedded device to another, as the embedded devices are designed not to run any third-party applications. | The entity filed a Technical Feasibility Exception (TFE) for this issue.
2012-02-29 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 3 (TRE_URE3) | NCRXXXXX | TRE201000145 | CIP-007-1 | R6 | The entity self-reported that its Critical Cyber Asset (CCA) systems all provide for sending automated alerts to appropriate personnel when Cyber Security Incidents occur and that these alerts are sent to its employees. However, the entity determined that it has not adequately documented the fact that such log reviews have taken place and, as such, did not maintain records documenting review of logs. Based on the record, Texas RE determined that there was an issue with this Standard. | This issue did not pose a serious or substantial risk and posed a minimal risk to the bulk power system because this is a documentation issue, which was mitigated by the entity's ongoing security program and its other methods of determining misuse and threats to its systems the entity was maintaining and reviewing logs of system events. Texas RE determined that this was a documentation issue because the entity had not adequately document the fact that log reviews were being done. | The entity completed its Mitigation Plan, which included training and spot checking of its personnel's compliance with the newly revised policies and procedures to eliminate a reoccurrence of this issue. The entity also installed and began using new tracking software to further insure compliance. The entity also uses automated reports and quarterly reviews, which are documented on a form document.
2012-02-29 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 5 (TRE_URE5) | NCRXXXXX | TRE201100138 | CIP-007-1 | R5.1.2 | Texas RE_URE5 self-reported noncompliance with CIP-007-1 R5. Based on the Self-Report, Texas RE determined that while preparing to transition to a new generation management system (GMS) in accordance with ERCOT ISO’s transition to Nodal Market, legacy Texas RE_URE5's GMS was not capable of complying with R5.1.2. The legacy GMS system was not configured to track and log the shared accounts running on it at any given time. Texas RE_URE5 was notified, by a consultant, that the legacy GMS was infeasible and it would take longer to update the older system to comply with CIP-007 R5.1.2 then to begin using the new GMS with the new Nodal Market. | Texas RE determined this issue posed a minimal risk and did not pose a serious or substantial risk to the bulk power system (BPS) because during the short duration of noncompliance, Texas RE_URE5 worked to minimize any changes to its legacy GMS. Any changes that were made to this system were being tracked on a day-to-day basis. Furthermore, at each generation facility, a control room is in place to monitor the status of the plant in real time. Were a signal to arise from the GMS to indicate an anomaly (i.e. something that is not in line with standard operating metrics), the facility is removed from automatic voltage control until the anomaly is rectified. Lastly, Texas RE_URE5 stated that all anti-virus definitions are current, that all employees requiring physical and cyber access have completed background checks, and that these employees have completed training and are approved for the appropriate access. | Texas RE_URE5 mitigated this issue by acquiring the necessary equipment, installing the new network and hardware, implementing a new management system and initiating all required access control, logging and monitoring controls. The issue was mitigated once the transition to the new Nodal Market was completed and the new management system were in place.
2012-02-29 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC201102824 | CIP-007-1 | R4 | WECC_URE3 performed an in-depth inventory of the Cyber Assets contained within the Electronic Security Perimeters (ESPs) for its substations. As a result of that inventory, WECC_URE3 discovered Cyber Assets that required a Technical Feasibility Exception (TFE) for CIP-007-1 R4 because they lacked a capability for the installation of malicious software prevention tools. WECC_URE3 self-reported an issue with the CIP Standards arising from WECC_URE3's failure to timely submit TFE requests in accordance with NERC procedures. The Self-Report referenced all identified TFEs that should have been filed as of that point. WECC_URE3's TFE requests were submitted approximately 16 to 20 months late. Specifically, WECC_URE3 submitted 37 late TFE requests for CIP-007-1 R4. WECC reviewed and accepted the TFE and determined it is technically infeasible for WECC_URE3 to comply with the Standard for the devices associated with the TFE Identification number. | All devices in scope are located in Physical Security Perimeters (PSPs) and ESPs and thus afforded the protections of CIP-005 and CIP-006. Additionally, all individuals with access to the devices have a valid personnel risk assessment and training. For these reasons, WECC determined that this issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. | WECC_URE3 filed the TFEs with WECC and WECC approved the Part A and Part B TFE. WECC_URE3 has implemented an intrusion detection system (IDS) which monitors all network traffic and sends automated alerts upon detecting suspicious traffic. All devices in scope are located in PSPs and ESPs and thus afforded the protections of CIP-005 and CIP-006. Additionally, all individuals with access to the devices have a valid personnel risk assessment and training.
2012-01-31 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC201000311 | CIP-004-1 | R3 | During a spot check, FRCC determined that the entity failed to conduct personnel risk assessments (PRAs) in accordance with CIP-004-1 R3. PRAs for five entity personnel with access to entity's Critical Cyber Assets were not conducted within 30 days of personnel being granted access, as required by the Standard. PRAs were delayed between 1 and 5 days. All the risk assessments were completed with no negative results. | FRCC determined that this issue did not pose serious or substantial risk to the reliability of the bulk power system and only posed minimal risk because these PRAs for five long-term entity personnel were delayed between 1 and 5 days. The responsible entity completed the PRAs with satisfactory results. In addition, the personnel had already been submitted to a background check upon hiring. Background checks are performed for all long-term employees at the time of hiring and this background check is similar to one required by the Standard. | The entity completed the mitigation activities for correcting the gaps in the process of conducting PRAs. All late PRAs were conducted with satisfactory results prior to FRCC discovery and FRCC verified the completion of all mitigation activities.
2012-01-31 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC201000313 | CIP-008-1 | R1: R1.4 | During a spot check, FRCC determined that the entity failed to maintain a Cyber Security Incident response plan (CSIRP) in accordance with CIP-008-1 R1.4. Specifically, the entity's CSIRP did not include a process for updating the CSIRP within ninety calendar days of any changes, as required by the Standard. | FRCC determined that this issue did not pose serious or substantial risk to the reliability of the bulk power system and only posed minimal risk because during the relevant period there were no changes to the CSIRP. This remediated issue occurred in the very early stages of compliance and was corrected within six months from the compliance date. During this period, no changes were made that could have impacted the CSIRP. Further, the entity promptly mitigated the gap upon discovery. | The entity completed the mitigation activities for correcting the gaps in its CSIRP and included required steps for updating of CSIRP with 90 days from any changes. The issue was resolved prior to FRCC discovery and FRCC verified the completion of all mitigation activities.
2012-01-31 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 2 (FRCC_URE2) | NCRXXXXX | FRCC201000411 | CIP-004-3 | R4; R4.1 | The entity self-reported an issue with CIP-004-3 R4.1. The entity self-reported that it did not update the list(s) of personnel with authorized access to Critical Cyber Assets (CCAs) within seven calendar days after the change in access of the personnel with access to CCAs. One staff member was transferred and no longer required access to the CCA, and though his access was revoked, the list of authorized users was not updated within the required seven calendar days. The list was updated six days beyond the required compliance date. The employee was transferred one day before access was revoked, and the database was updated twelve days after the transfer. | FRCC determined that this issue did not pose serious or substantial risk to the reliability of the bulk power system and only posed minimal risk because the entity did not update the list(s) within seven calendar days of the change in personnel with access to CCAs. Since the concerned personnel's access was revoked in a timely manner as required by CIP-004-3 R4.2 and given the fact that this was merely a lack of timely documentation, FRCC concluded that the risk of impact to reliability was minimal. Although the entity has violated this Standard previously, the instant remediated issue nonetheless does not represent recurring conduct by the registered entity. The entity has four prior violations of CIP-004, three of which involve different requirements and are therefore distinguishable. The prior CIP-004 R4 violation occurred nearly three years prior to the issue at hand. Following the prior violation, the entity developed a database for use in tracking and recording training dates and access privileges, reviewed and updated the list of personnel with access to CCAs; reviewed its database; modified its training attendance sheet with a block to indicate database updated for each attendee; created calendar reminders at four weeks prior to end of the quarter to trigger review process, created a memorandum of understanding for contractors to notify the entity of all terminations within 12 hours, reviewed and updated the process for documenting that training has occurred, created a process for Human Resources to notify the energy control center of all employee terminations, and developed queries in the database to facilitate reviews of access lists on a routine basis. The instant remediated issue is distinguishable in that the prior violation involved a lack of documentation of the personnel list review, but the entity did create and maintain the list of authorized users with access to CCAs in accordance with the Standard. The instant issue involves the entity not updating the personnel list within the required time period. | The entity promptly completed mitigation activities including updating the list of authorized personnel with access to CCAs, adding another layer of notification from Human Resources and training all personnel responsible for employee access authorization and status change notification process. The entity completed the mitigation activities and FRCC verified completion.
2012-01-31 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO201100369 | CIP-003-1 | R2 | During a compliance audit, MRO determined that the entity had an issue with CIP-003-1 R2 for failing to assign a senior manager with overall responsibility for leading and managing the entity’s implementation of, and adherence to, Standards CIP-002 through CIP-009. | The remediated issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because failure to assign a senior manager did not change the implementation of the entity's cyber security policy, or the senior manager overseeing the implementation of the policy. Although the entity lacked a formal documented assignment, the senior manager did sign the policy. Additionally, the entity is summer peaking with an all time peak of less than 100 MW in July 2007, and has less than 20 miles of transmission line. | The entity designated a senior manager with the authority and responsibility for leading and managing the implementation of CIP-002 through CIP-009 compliance. The entity completed its mitigation activities, as verified by MRO.
2012-01-31 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 2 (MRO_URE2) | NCRXXXXX | MRO201100302 | CIP-007-1 | R1 | The entity self-reported an issue with CIP-007-1 R1 because it failed to document test results which indicate whether initial testing of new Cyber Assets within the Electronic Security Perimeter adversely affect existing cyber security controls, including a scan of open/enabled ports and services. Specifically, the entity did not have any documentation to verify the initial testing of the security configuration of the relay access devices, identified as Critical Cyber Assets (CCAs), at the substations to ensure no adverse effects to existing security controls. | The remediated issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because during the installation process, the devices were commissioned employing the same controls as other CCAs. Additionally, the devices were field-tested at the time of installation to confirm their standard configuration. The deficiency was in the absence of documentation of the baseline standard configuration test. | The entity conducted a scan of the relay access devices in which the baseline of required ports and services was compared to actual ports and services discovered during that scan. Also, further testing was performed to determine the necessary configuration changes. As a result, the required changes to CCAs to enable only required ports and services were defined, deployed and completed at all relevant locations
2012-01-31 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 3 (MRO_URE3) | NCRXXXXX | MRO201100294 | CIP-007-2 | R3 | The entity self-reported an issue with Reliability Standard CIP-007-2 R3 because it failed to document the assessment of security patches for applicability within thirty calendar days of availability of the patches. The entity conducted a search of the National Institute of Standards and Technology National Vulnerability Database (NIST NVD) for Common Vulnerabilities and Exposures (CVEs) to identify security patches or upgrades, but no results were returned for the particular identified software; however, there was a new security patch. The entity subsequently learned that the NIST NVD CVE summary application names were not identical to the vendor's application names registered on the Cyber Assets, and therefore did not identify the security patch in its search. | The remediated issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because in order to exploit the vulnerability, users have to access a malicious website. The Electronic Security Perimeter (ESP) access point protecting the Cyber Assets with this identified software prohibits users from accessing websites outside the ESP. | The entity performed the following actions to mitigate the issue: (1) assessed patches; (2) modified the manual NIST NVD search criteria; (3) expanded its configuration management system to include specific software; (4) developed and implemented an in-house NIST NVD search tool; and (5) updated the CIP security patch management job aid with detailed instructions for the new in-house NIST NVD search tool. The entity completed its mitigation activities, as verified by MRO.
2012-01-31 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 4 (MRO_URE4) | NCRXXXXX | MRO201000179 | CIP-003-1 | R4 | During a CIP spot check, MRO determined that the entity had an issue with CIP-003-1 R4 for failing to label the entity's disaster recovery plans and Critical Asset lists according to the entity's energy information security classifications policy. | The remediated issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the entity has a document software package which facilitates secure content management and limits electronic access to authorized users. The documents not marked in accordance with the energy information security classifications policy were within a restricted area of the system. Only a limited number of authorized users were able to access the documents. | The entity performed the following actions to mitigate the issue: (1) conducted a comprehensive CIP review; and (2) marked the disaster recovery plans and Critical Asset lists documents in accordance with its energy information security classifications policy.
2012-01-31 | NERC Compliance Enforcement Authority (NCEA) | Unidentified Registered Entity 1 (NCEA_URE1) | NCRXXXXX | NCEA200900043 | CIP-002-1 | R1 | The entity did not include in its methodology or assessment the CIP assets of other third party entities that were performing tasks on its behalf. Due to different compliance schedules, there was a gap in timing for compliance with respect to those assets. NCEA also found that: (i) One third party entity had a risk-based assessment methodology that was flawed in that it was not reliability-based, but instead had business criteria considered in the calculations to determine the Critical Asset (CA) List. The entity still had substations and control centers on its CA List. (ii) Another third party entity eliminated assets from consideration for the CA List based upon setting risk at various levels less than unity. The methodology had a primary control center declared as a “high criticality asset” initially but it was eliminated by setting the vulnerability and likelihood of compromise at significantly less than unity. | This issue posed a moderate and not serious or substantial risk to the reliability of the bulk power system (BPS) because NCEA considered that, over the period of the issue, the third party entities were preparing for compliance with the CIP standards, as required by the Approved Implementation Plan. There was no actual impact to reliability of the BPS as a result of the subject issue. | Coordinated Functional Registration agreements were put in place to address respective responsibilities. The methodologies and assessments were corrected and the respective third party entities were certified for the applicable function and had to demonstrate compliance at that time with this requirement.
2012-01-31 | NERC Compliance Enforcement Authority (NCEA) | Unidentified Registered Entity 1 (NCEA_URE1) | NCRXXXXX | NCEA200900044 | CIP-002-1 | R2 | The entity did not include in its methodology or assessment the CIP assets of other third party entities that were performing tasks on its behalf. Due to different compliance schedules, there was a gap in timing for compliance with respect to those assets. NCEA also found that one third party entity's policy had insufficient references to the requirements in Standards CIP-002 through CIP-009 related to emergency situations. Another third party entity did not provide evidence that its policy was available to all personnel who have access to, or are responsible for, Critical Cyber Assets. | This issue posed a moderate and not serious or substantial risk to the reliability of the bulk power system (BPS) because NCEA considered that, over the period of the issue, the third party entities were preparing for compliance with the CIP standards, as required by the Approved Implementation Plan. There was no actual impact to reliability of the BPS as a result of the subject issue. | Coordinated Functional Registration agreements were put in place to address respective responsibilities. The methodologies and assessments were corrected and the respective third party entities were certified for the applicable function and had to demonstrate compliance at that time with this requirement.
2012-01-31 | NERC Compliance Enforcement Authority (NCEA) | Unidentified Registered Entity 1 (NCEA_URE1) | NCRXXXXX | NCEA200900045 | CIP-002-1 | R3 | The entity did not include in its methodology or assessment the CIP assets of other third party entities that were performing tasks on its behalf. Due to different compliance schedules, there was a gap in timing for compliance with respect to those assets. NERC found that third party entities failed to provide information or did not provide information sufficient to indicate that they met the requirement as of July 1, 2008. Furthermore NERC found that third party entities failed to provide information or did not provide information sufficient to indicate that they met the requirement at the time of their spot check. | This issue posed a moderate and not serious or substantial risk to the reliability of the bulk power system (BPS) because NCEA considered that, over the period of the issue, the third party entities were preparing for compliance with the CIP standards, as required by the Approved Implementation Plan. There was no actual impact to reliability of the BPS as a result of the subject issue. | Coordinated Functional Registration agreements were put in place to address respective responsibilities. The methodologies and assessments were corrected and the respective third party entities were certified for the applicable function and had to demonstrate compliance at that time with this requirement.
2012-01-31 | NERC Compliance Enforcement Authority (NCEA) | Unidentified Registered Entity 1 (NCEA_URE1) | NCRXXXXX | NCEA200900046 | CIP-003-1 | R1 | The entity did not include in its methodology or assessment the CIP assets of other third party entities that were performing tasks on its behalf. Due to different compliance schedules, there was a gap in timing for compliance with respect to those assets. Specifically, a third party entity's evidence did not demonstrate the policy was available to all employees who had access to CCAs and another third party entity’s policy had insufficient references to the requirements in Standards CIP-002 through CIP-009 related to emergency situations. | This issue posed a moderate and not serious or substantial risk to the reliability of the bulk power system (BPS) because NCEA considered that, over the period of the issue, the third party entities were preparing for compliance with the CIP standards, as required by the Approved Implementation Plan. There was no actual impact to reliability of the BPS as a result of the subject issue. | Coordinated Functional Registration agreements were put in place to address respective responsibilities. The methodologies and assessments were corrected and the respective third party entities were certified for the applicable function and had to demonstrate compliance at that time with this requirement.
2012-01-31 | NERC Compliance Enforcement Authority (NCEA) | Unidentified Registered Entity 1 (NCEA_URE1) | NCRXXXXX | NCEA200900047 | CIP-003-1 | R2 | The entity did not include in its methodology or assessment the CIP assets of other third party entities that were performing tasks on its behalf. Due to different compliance schedules, there was a gap in timing for compliance with respect to those assets. Specifically, a third party entity's evidence did not show that it had developed a list of its identified Critical Assets determined through an annual application of the risk-based assessment methodology required in R1. | This issue posed a moderate and not serious or substantial risk to the reliability of the bulk power system (BPS) because NCEA considered that, over the period of the issue, the third party entities were preparing for compliance with the CIP standards, as required by the Approved Implementation Plan. There was no actual impact to reliability of the BPS as a result of the subject issue. | Coordinated Functional Registration agreements were put in place to address respective responsibilities. The methodologies and assessments were corrected and the respective third party entities were certified for the applicable function and had to demonstrate compliance at that time with this requirement.
2012-01-31 | NERC Compliance Enforcement Authority (NCEA) | Unidentified Registered Entity 1 (NCEA_URE1) | NCRXXXXX | NCEA200900048 | CIP-003-1 | R3 | The entity did not include in its methodology or assessment the CIP assets of other third party entities that were performing tasks on its behalf. Due to different compliance schedules, there was a gap in timing for compliance with respect to those assets. Specifically, a third party entity's evidence did not demonstrate it used a list of Critical Assets developed pursuant to R2, nor that it developed a list of associated Critical Cyber Assets essential to the operation of the Critical Asset. | This issue posed a moderate and not serious or substantial risk to the reliability of the bulk power system (BPS) because NCEA considered that, over the period of the issue, the third party entities were preparing for compliance with the CIP standards, as required by the Approved Implementation Plan. There was no actual impact to reliability of the BPS as a result of the subject issue. | Coordinated Functional Registration agreements were put in place to address respective responsibilities. The methodologies and assessments were corrected and the respective third party entities were certified for the applicable function and had to demonstrate compliance at that time with this requirement.
2012-01-31 | NERC Compliance Enforcement Authority (NCEA) | Unidentified Registered Entity 1 (NCEA_URE1) | NCRXXXXX | NCEA200900049 | CIP-004-1 | R2 | The entity did not include in its methodology or assessment the CIP assets of other third party entities that were performing tasks on its behalf. Due to different compliance schedules, there was a gap in timing for compliance with respect to those assets. Specifically, two third party entities did not provide evidence that their security training program was reviewed annually or that it was updated as necessary. | This issue posed a moderate and not serious or substantial risk to the reliability of the bulk power system (BPS) because NCEA considered that, over the period of the issue, the third party entities were preparing for compliance with the CIP standards, as required by the Approved Implementation Plan. There was no actual impact to reliability of the BPS as a result of the subject issue. | Coordinated Functional Registration agreements were put in place to address respective responsibilities. The methodologies and assessments were corrected and the respective third party entities were certified for the applicable function and had to demonstrate compliance at that time with this requirement.
2012-01-31 | NERC Compliance Enforcement Authority (NCEA) | Unidentified Registered Entity 1 (NCEA_URE1) | NCRXXXXX | NCEA200900050 | CIP-004-1 | R3 | The entity did not include in its methodology or assessment the CIP assets of other third party entities that were performing tasks on its behalf. Due to different compliance schedules, there was a gap in timing for compliance with respect to those assets. Specifically, two third party entities provided no evidence that personnel risk assessments (PRAs) had been conducted for all employees, contractors, and service vendor personnel with authorized cyber access or unescorted physical access; the evidence provided by two third party entities did not indicate that PRAs were updated every 7 years and/or for cause; four third party entities provided no evidence of PRA results. | This issue posed a moderate and not serious or substantial risk to the reliability of the bulk power system (BPS) because NCEA considered that, over the period of the issue, the third party entities were preparing for compliance with the CIP standards, as required by the Approved Implementation Plan. There was no actual impact to reliability of the BPS as a result of the subject issue. | Coordinated Functional Registration agreements were put in place to address respective responsibilities. The methodologies and assessments were corrected and the respective third party entities were certified for the applicable function and had to demonstrate compliance at that time with this requirement.
2012-01-31 | NERC Compliance Enforcement Authority (NCEA) | Unidentified Registered Entity 1 (NCEA_URE1) | NCRXXXXX | NCEA200900051 | CIP-004-1 | R4 | The entity did not include in its methodology or assessment the CIP assets of other third party entities that were performing tasks on its behalf. Due to different compliance schedules, there was a gap in timing for compliance with respect to those assets. After all evidence was reviewed, it was discovered that for one third party entity, no evidence was provided listing employees with authorized cyber access and/or unescorted physical access. For four third party entities, no evidence was provided listing contractors and service vendors with authorized cyber access and/or unescorted physical access. For three third party entities, there was no evidence that access list(s) are reviewed quarterly. For three third party entities, there was no evidence that access list(s) are updated within 7 days of any change in access rights. For two third party entities, there was no evidence that access list(s) for contractors and service vendors were properly maintained. For two third party entities, there was no evidence that access was revoked within 24 hours for personnel terminated for cause. Finally, for three third party entities, there was no evidence that access was revoked within 7 calendar days for personnel who no longer required access. | This issue posed a moderate and not serious or substantial risk to the reliability of the bulk power system (BPS) because NCEA considered that, over the period of the issue, the third party entities were preparing for compliance with the CIP standards, as required by the Approved Implementation Plan. There was no actual impact to reliability of the BPS as a result of the subject issue. . | Coordinated Functional Registration agreements were put in place to address respective responsibilities. The methodologies and assessments were corrected and the respective third party entities were certified for the applicable function and had to demonstrate compliance at that time with this requirement.
2012-01-31 | NERC Compliance Enforcement Authority (NCEA) | Unidentified Registered Entity 1 (NCEA_URE1) | NCRXXXXX | NCEA200900052 | CIP-007-1 | R1 | The entity did not include in its methodology or assessment the CIP assets of other third party entities that were performing tasks on its behalf. Due to different compliance schedules, there was a gap in timing for compliance with respect to those assets. Specifically, for one third party entity, several requirements listed in the standard were not included in the documentation provided. | This issue posed a moderate and not serious or substantial risk to the reliability of the bulk power system (BPS) because NCEA considered that, over the period of the issue, the third party entities were preparing for compliance with the CIP standards, as required by the Approved Implementation Plan. There was no actual impact to reliability of the BPS as a result of the subject issue. | Coordinated Functional Registration agreements were put in place to address respective responsibilities. The methodologies and assessments were corrected and the respective third party entities were certified for the applicable function and had to demonstrate compliance at that time with this requirement.
2012-01-31 | NERC Compliance Enforcement Authority (NCEA) | Unidentified Registered Entity 1 (NCEA_URE1) | NCRXXXXX | NCEA200900053 | CIP-008-1 | R1 | The entity did not include in its methodology or assessment the CIP assets of other third party entities that were performing tasks on its behalf. Due to different compliance schedules, there was a gap in timing for compliance with respect to those assets. Specifically, one third party entity did not address several requirements listed in the standard; another third party entity's evidence did not indicate what procedures were used to characterize and classify events as reportable Cyber Security Incidents; yet another third party entity's evidence did not indicate a process for ensuring that its Cyber Security Incident response plan was tested at least annually. | This issue posed a moderate and not serious or substantial risk to the reliability of the bulk power system (BPS) because NCEA considered that, over the period of the issue, the third party entities were preparing for compliance with the CIP standards, as required by the Approved Implementation Plan. There was no actual impact to reliability of the BPS as a result of the subject issue. | Coordinated Functional Registration agreements were put in place to address respective responsibilities. The methodologies and assessments were corrected and the respective third party entities were certified for the applicable function and had to demonstrate compliance at that time with this requirement.
2012-01-31 | NERC Compliance Enforcement Authority (NCEA) | Unidentified Registered Entity 1 (NCEA_URE1) | NCRXXXXX | NCEA200900054 | CIP-009-1 | R1 | The entity did not include in its methodology or assessment the CIP assets of other third party entities that were performing tasks on its behalf. Due to different compliance schedules, there was a gap in timing for compliance with respect to those assets. Specifically, one third party entity's evidence did not adequately support compliance with the standard; another third party entity’s recovery plan did not fully specify the appropriate actions for responding to situations of varying duration and severity. | This issue posed a moderate and not serious or substantial risk to the reliability of the bulk power system (BPS) because NCEA considered that, over the period of the issue, the third party entities were preparing for compliance with the CIP standards, as required by the Approved Implementation Plan. There was no actual impact to reliability of the BPS as a result of the subject issue. | Coordinated Functional Registration agreements were put in place to address respective responsibilities. The methodologies and assessments were corrected and the respective third party entities were certified for the applicable function and had to demonstrate compliance at that time with this requirement.
2012-01-31 | NERC Compliance Enforcement Authority (NCEA) | Unidentified Registered Entity 1 (NCEA_URE1) | NCRXXXXX | NCEA200900055 | CIP-009-1 | R2 | The entity did not include in its methodology or assessment the CIP assets of other third party entities that were performing tasks on its behalf. Due to different compliance schedules, there was a gap in timing for compliance with respect to those assets. Specifically, one third party entity's evidence did not clearly indicate how the sample test report pertains to the recovery of Critical Cyber Assets (CCAs) and another third party entity's test evidence for failover did not specifically address CCA recovery, as is necessary per the standard purpose statement, so they did not have a valid annual exercise. | This issue posed a moderate and not serious or substantial risk to the reliability of the bulk power system (BPS) because NCEA considered that, over the period of the issue, the third party entities were preparing for compliance with the CIP standards, as required by the Approved Implementation Plan. There was no actual impact to reliability of the BPS as a result of the subject issue. | Coordinated Functional Registration agreements were put in place to address respective responsibilities. The methodologies and assessments were corrected and the respective third party entities were certified for the applicable function and had to demonstrate compliance at that time with this requirement.
2012-01-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 10 (RFC_URE10) | NCRXXXXX | RFC2011001076 | CIP-005-3 | R1; R1.1 | ReliabilityFirst conducted a compliance audit of the entity, during which ReliabilityFirst discovered that the entity had a possible issue with the Standard. ReliabilityFirst discovered that the entity did not identify certain third-party vendor security device appliances as access points to Electronic Security Perimeters (ESPs). These appliances allow the third-party vendor to monitor activity on the entity's network and identify any unauthorized activities. These appliances are directly connected to mirrored ports on routers within the ESP. This issue involved nine of the entity's devices. The entity failed to identify these devices as access points to the ESP, as required by CIP-005-3 R1.1. | ReliabilityFirst determined that this issue posed a minimal risk to the reliability of the bulk power system (BPS). The risk to the reliability of the BPS was mitigated by the following factors. The entity included these appliances on its network diagrams, although it did not identify the appliances as access points to the ESP. The entity also afforded the same protections to the appliances as it provides to all access points to the ESP. Therefore, the entity merely failed to document the appliances as access points to the ESP and at all relevant times provided the requisite protections to the appliances. In addition, due to their being connected via mirrored ports, the appliances are only configured for monitoring traffic and for reporting anomalies out of the ESP. These appliances are not configured to carry information into the ESP. Furthermore, the appliances are located within Physical Security Perimeters. | In order to mitigate the issue, during the compliance audit, the entity, revised its network topology diagrams to identify the appliances as access points to the ESP. The entity completed its mitigation activities, which was verified by ReliabilityFirst.
2012-01-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 11 (RFC_URE11) | NCRXXXXX | RFC2011001253 | CIP-005-3 | R1; R1.1 | ReliabilityFirst conducted a compliance audit of the entity, during which ReliabilityFirst discovered that the entity had a possible issue with the Standard. ReliabilityFirst determined that the facts and circumstances of an issue with the entity's affiliate also constituted a possible issue for the entity (RFC2011001076). ReliabilityFirst discovered that the entity did not identify certain third-party vendor security device appliances as access points to Electronic Security Perimeters (ESPs). These appliances allow the third-party vendor, to monitor activity on the entity's network and identify any unauthorized activities. These appliances are directly connected to mirrored ports on routers within the ESP. This issue involved nine of the entity's devices. The entity failed to identify these devices as access points to the ESP, as required by CIP-005-3 R1.1. | ReliabilityFirst determined that this issue posed a minimal risk to the reliability of the bulk power system (BPS). The risk to the reliability of the BPS was mitigated by the following factors. The entity included these appliances on its network diagrams, although it did not identify the appliances as access points to the ESP. The entity also afforded the same protections to the appliances as it provides to all access points to the ESP. Therefore, the entity merely failed to document the appliances as access points to the ESP and at all relevant times provided the requisite protections to the appliances. In addition, due to their being connected via mirrored ports, the appliances are only configured for monitoring traffic and for reporting anomalies out of the ESP. These appliances are not configured to carry information into the ESP. Furthermore, the appliances are located within Physical Security Perimeters. | In order to mitigate the issue, the entity, during the compliance audit, revised its network topology diagrams to identify the appliances as access points to the ESP. The entity completed its mitigation activities, which was verified by ReliabilityFirst.
2012-01-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 12 (RFC_URE12) | NCRXXXXX | RFC201100930 | CIP-004-3 | R3 | The entity submitted a Self-Report for CIP-004-3 R3 to ReliabilityFirst. A month earlier, the entity’s NERC compliance team notified the entity’s security services team that they identified an unexpected individual on the daily physical access report. Upon further investigation, the entity discovered that it granted physical access to Critical Cyber Assets to the wrong individual. Specifically, a contractor performing fire alarm system work requested and was granted, access to the entity’s headquarters building, which contains four Physical Security Perimeters (PSPs); however, the entity erroneously granted the access to the four PSPs to another contractor with another company, a credit union employee whose office is located in a different city. The other contractor did not have a background check on file, and therefore did not receive a personnel risk assessment as required by CIP-004-3 R3. The erroneous grant of access to the other contractor resulted from two issues in the entity’s access request process. First, an entity employee failed to issue a user identification for the other contractor while creating the other contractor’s employee record, which resulted in a null value for the other contractor in the employee database. Second, the access request submitted for the correct contractor was corrupted and did not have user identification, which also resulted in a null value for the correct contractor in the employee database. Since the null values matched, the system granted the correct contractor’s access request to the other contractor. | ReliabilityFirst determined that this issue posed a minimal risk to the reliability of the bulk power system (BPS). The risk to the BPS posed by the foregoing facts and circumstances was mitigated by the following factors. The entity's daily physical access reports quickly pinpointed the erroneous grant of access to the other contractor, and as a result, the issue lasted less than one day. Additionally, the other contractor was unaware that the entity granted her access to the headquarters facility, and she did not attempt to use this access during the time period of the issue. Moreover, the other contractor worked in a separate physical facility in a different city from the location of the CCAs. Of the four PSPs to which the entity granted the other contractor access, two of the PSPs would have been inaccessible as a result of biometric security features installed in those PSPs. Additionally, the remaining two PSPs are small rooms in the entity’s headquarters and would be difficult for an unauthorized individual to find and access. | In its mitigation plan, the entity memorialized the actions it took to address the issue of CIP-004-3 R3. The entity removed the access rights from the other contractor, reminded the other contractor's company of the proper data entry standards, and checked for additional null entries in the employee records database. The entity also updated its database forms to enforce proper data entry for the user identification field, and worked with its software vendor to implement similar error checking in its security badge management product. The entity completed its mitigation activities, which was verified by ReliabilityFirst.
2012-01-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 13 (RFC_URE13) | NCRXXXXX | RFC2011001242 | CIP-007-3 | R5.3 | The entity submitted a Self-Report to ReliabilityFirst, identifying an issue with CIP-007-3 R5. The entity implemented a process to automate monitoring and alerts related to password age in order to improve its prior manual password review process. During this process, the entity discovered two local accounts on two of its servers within the Electronic Security Perimeter (ESP) with passwords that had not been changed annually. The entity had not changed the passwords on the accounts since their creation. ReliabilityFirst determined that the entity had an issue with CIP-007-3 R5 by failing to annually change the password on two of its local accounts. | ReliabilityFirst determined that this issue posed a minimal risk to the reliability of the bulk power system (BPS). The risk to the reliability of the BPS was mitigated by the following factors. Although located within the ESP, the two servers were not Critical Cyber Assets. The entity’s other utility utilized the servers for historic data archiving, and the servers were logically isolated from the Energy Management System servers. Therefore, the servers at issue were not configured to affect BPS elements. In addition, the entity verified that the local accounts have never been accessed since their creation. Only a small group of information technology individuals with CIP cybersecurity training and current background checks had access to the local accounts. The local accounts were only accessible inside the ESP, for which the requisite protections were in place. | In order to mitigate the issue the entity deleted the two local accounts at issue. The entity completed its mitigation activities as verified by ReliabilityFirst.
2012-01-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 15 (RFC_URE15) | NCRXXXXX | RFC2011001228 | CIP-006-3c | R1 | ReliabilityFirst determined, during a compliance audit, that the entity had an issue with CIP-006-3c R1. The entity failed to maintain a six-wall border around the control room of one of its facilities, which contains Critical Cyber Assets. Specifically, a 12-inch gap exists between the tops of the walls and the ceiling. ReliabilityFirst determined that the entity had an issue with CIP-006-3c R1 by failing to maintain a six-wall border around all Cyber Assets within an Electronic Security Perimeter (ESP). The entity filed a late Technical Feasibility Exception (TFE) request with ReliabilityFirst stating that the operational limitations of its heating, ventilation, and air conditioning system required the 12-inch gap, and modifications could affect air circulation in the facility. | ReliabilityFirst determined that this issue posed a minimal risk to the reliability of the bulk power system (BPS). The risk to the BPS was mitigated by the following factors. The entity used motion sensors to monitor the 12-inch gap in the six-wall border and this mitigating measure has been fully implemented and approved by ReliabilityFirst. The facility in question is also secured by security fencing and a guarded single access gate. Additionally, both the building that contains the main control center and the control center itself restrict access via card-reader equipment with monitoring and alarming features. All compensating measures were in place for the duration of the issue. | ReliabilityFirst accepted and approved the entity's late TFE request.
2012-01-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 15 (RFC_URE15) | NCRXXXXX | RFC2011001233 | CIP-007-3 | R4 | ReliabilityFirst found, during a compliance audit, that the entity had an issue with CIP-007-3 R4. ReliabilityFirst determined that the entity had an issue with CIP-007-3 R4 by failing to use anti-virus software and other malware prevention tools on all Cyber Assets within the Electronic Security Perimeter. The entity submitted two late Technical Feasibility Exception (TFE) requests related to Cyber Assets for which there were no available malware prevention tools. Specifically, the entity stated that both affected devices run proprietary operating systems for which no manufacturer or third-party malware prevention tools exist. The entity filed the two TFE requests with ReliabilityFirst. ReliabilityFirst accepted the TFE requests and approved them on. | ReliabilityFirst determined that this issue posed a minimal risk to the reliability of the bulk power system (BPS). The risk to the BPS was mitigated by the following factors, which the entity provided as compensating measures for the TFEs. Both Cyber Assets run on proprietary operating systems on which malware development is unlikely. The Cyber Assets are located behind firewalls that restrict traffic, and remote access to them requires two-factor authentication. The entity also protects the Cyber Assets with video surveillance. These compensating measures were in place for the duration of the issue. | ReliabilityFirst accepted and approved the entity's two late TFE request.
2012-01-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 15 (RFC_URE15) | NCRXXXXX | RFC2011001238 | CIP-008-3 | R1.6 | ReliabilityFirst found, during a compliance audit, that the entity had an issue with CIP-008-3 R1.6. Although the entity was able to provide a Cyber Security Incident response plan (Plan), it failed to include within the Plan a process for ensuring that it was tested at least annually. Although it failed to have a documented process within the Plan, the entity was able to provide evidence that it did test the Plan annually. ReliabilityFirst determined that the entity had an issue with CIP-008-3 R1 by failing to include within its Plan a process for ensuring that the Plan is tested at least annually. | ReliabilityFirst determined that this issue posed a minimal risk to the reliability of the bulk power system (BPS). The risk posed to BPS was mitigated by the fact that the issue was a documentation error because although the entity did not document a process within the Plan to ensure that it tests the Plan annually, the entity did test the Plan annually. | The entity provided evidence that it updated its Plan to include a process for annual testing as required by CIP-008-3 R1.6. The entity completed its mitigation activities as verified by ReliabilityFirst.
2012-01-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 9 (RFC_URE9) | NCRXXXXX | RFC201100856 | CIP-006-2 | R1; R1.4 | The entity submitted a Self-Report to ReliabilityFirst indicating a possible issue CIP-006-2 R1. Specifically, the entity's physical security plan did not address response to loss and prohibition of inappropriate use of physical access controls pursuant to CIP-006-2 R1.4. The entity's training and corporate policies addressed response to loss and prohibition of inappropriate use, but those policies were not part of the physical security plan and were not approved by senior management, as required by CIP-006-2 R1.4. Additionally, the entity included a provision in its physical security plan which stated that the entity would update the physical security plan within 90 calendar days of the completion of any physical security system redesign or reconfiguration. Although Version 1 of CIP-006 R1.7 allowed for a 90-day period to update a physical security plan, on April 1, 2010, Version 2 of CIP-006 took effect, which required a shorter 30-day update period. Therefore, from the effective date of CIP-006-2, the entity did not include a requirement in its physical security plan to update the physical security plan within 30 days of a physical security system design or configuration change. | ReliabilityFirst determined that this issue posed a minimal risk to the reliability of the bulk power system (BPS). The risk to the reliability of the BPS was mitigated by the fact that the issue is the result of a documentation error. It is a documentation error because although the entity’s physical security plan did not address response to loss or a prohibition of inappropriate use of physical access controls, the entity addressed these topics in corporate policies and trained its employees on these topics. Additionally, although the entity’s physical security plan stated that it must update the physical security plan within 90 days of any changes rather than within 30 days, the entity made no changes during the duration of the issue, and therefore, did not need to make any updates. | In its mitigation plan, the entity outlined the actions it took to mitigate the issue. The entity revised its physical security plan to address response to loss and prohibition of inappropriate use of physical access controls. The entity also included a requirement to update the physical security plan within 30 days of a physical security system design or configuration change. The entity completed its mitigation activities, which was verified by ReliabilityFirst.
2012-01-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 9 (RFC_URE9) | NCRXXXXX | RFC201100855 | CIP-008-2 | R1 | The entity submitted a Self-Report to ReliabilityFirst indicating that it had a possible issue with CIP-008-2 R1. The entity's Cyber Security Incident response plan (Response Plan) did not include a process for updating the Response Plan within 30 calendar days of any changes. Rather, the entity's Response Plan included a process for updating the Response Plan within 90 calendar days of any changes. Although Version 1 of CIP-008 allowed for a 90-day period to update the Response Plan, on April 1, 2010, Version 2 of CIP-008 took effect, which required registered entities to update their respective response plans within a shorter 30-day period. Therefore, from the effective date of CIP-008-2, the entity had an issue with CIP-008-2 R1.4. | ReliabilityFirst determined that this issue posed a minimal risk to the reliability of the bulk power system (BPS). The risk to the reliability of the BPS was mitigated by the fact that the issue is the result of a documentation error. It is a documentation error because although the entity's Response Plan stated that it must update the Response Plan within 90 days of any changes rather than within 30 days, the entity made no changes during the duration of the issue, and therefore, did not need to make any updates to the Response Plan. | In its mitigation plan, the entity outlined the actions it took to mitigate the issue. The entity revised its Response Plan to include a process for updating the Response Plan within 30 calendar days of any changes. The entity completed its mitigation activities, which was verified by ReliabilityFirst.
2012-01-31 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP201000301 | CIP-003-1 | R1; R1.1 | SPP RE discovered an issue with CIP-003-1 R1.1 during a spot check. The entity's Cyber Security Policy (CSP), during the period which entity was required to comply with CIP-003-1 R1, failed to address all of the requirements of CIP-002-1 through CIP-009-1, as required by CIP-003-1 R1.1. On the date on which version two of the CIP standards went into effect, the entity enacted a new CSP, which addressed all of the requirements of CIP-002-2 through CIP-009-2, as required by CIP-003-2 R1.1. SPP RE determined that the entity’s CSP under CIP version one failed to address the following: CIP-004-1 R2.1, R2.1; CIP-005-1 R1.5, R2.1, R2.6; CIP-006-1 R1.1 through R1.7; CIP-007-1 R1.1, R1.2, R4.2, R5.2.2, R5.2.3, R5.3.2; CIP-008-1 R1.1, R1.4. | SPP RE determined that the issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The entity had a CSP in place and on the date version two of the CIP standards went into effect, and prior to the spot check, entity enacted a new CSP that addressed the requirements of CIP-003-2 R1. Although the entity’s prior CSP for CIP did not address every requirement, it did address each of the main level requirements of all of the CIP standards. In paraphrasing the requirements of CIP-002 through CIP-009, the entity omitted some of the included requirements. The CSP, however, still served the purpose of conveying management’s commitment and ability to secure the entity’s Critical Cyber Assets. | The entity, prior to the spot check, had implemented a new CSP in order to comply with version two of the CIP standards. The entity certified that mitigation was complete, and SPP RE verified completion.
2012-01-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2011008712 | CIP-005-3 | R2 | WECC_URE1 submitted one late-filed Technical Feasibility Exception (TFE) addressing infeasibility with CIP-005-3 R2 for an electronic access control system. The entity stated the device does not support the display of an appropriate use banner prior to an interactive access attempt (login and password prompt) for a system administrator account on the device. | WECC determined that this issue posed a minimal risk and not a serious or substantial risk to the reliability of the bulk power system (BPS). WECC reviewed and accepted the TFE and determined it is technically infeasible for the entity to comply with the Standard for the device associated with the TFE Identification number. The compensating measures, described below, were in place prior to the due date on which all such TFE requests were to originally be submitted to WECC. The entity stated the appropriate use banner is displayed after successful entry of a valid user ID, PIN and two factor authentication key for system administrative access to the device. Further, security events from the device and the network intrusion detection system are logged. | Entity filed the TFEs, WECC approved the Part A and Part B TFE. Two factor authentication is implemented for remote interactive access through the firewalls. A Physical Security Perimeter was implemented.
2012-01-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC2011008711 | CIP-007-2 | R4 | WECC_URE1 submitted two late-filed Technical Feasibility Exceptions (TFEs) addressing infeasibility with CIP-007-2 R4 for firewalls. The entity stated that the devices are incapable of running anti-malware software on its firewall appliance in its supported configuration. | WECC determined that this issue posed a minimal risk and not a serious or substantial risk to the reliability of the bulk power system (BPS). WECC reviewed and accepted the TFE and determined it is technically infeasible for the entity to comply with the Standard for the devices associated with the TFE Identification number. The compensating measures, described below, were in place prior to the due date on which all such TFE requests were to originally be submitted to WECC. The entity has implemented a two-factor authentication for external interactive access, also any firmware (memory location) change on the device requires a reboot for the device to take effect. A network intrusion detection system (NIDS) monitors for threats on the local area network within the Electronic Security Perimeter(s), any security events from the device and NIDS are logged to a central security event monitoring console. Further, the Physical Security Perimeter and restricted access to only authorized personnel deters local misuse and introduction of malware. | Entity filed the TFEs, WECC approved the Part A and Part B TFE. The vendor hardened the cyber asset. A separate security monitoring appliance is used to detect anomalous behavior on the network.
2012-01-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC2011008713 | CIP-007-1 | R4 | WECC_URE2 submitted one late-filed Technical Feasibility Exception (TFE) addressing infeasibility with CIP-007-1 R4 for a control system. The entity stated that anti-virus software was installed on the device which resulted in failure of the device after a couple of days. Upon further investigation, it was discovered that the server failed due to a memory leak from a communication protocol system process. Although the memory leak already existed prior to the antivirus being installed, the support staff believed the anti-virus software exasperated the issue based on continuous scanning of the system. The entity has since uninstalled the anti-virus software. | WECC determined that this issue posed a minimal risk and not a serious or substantial risk to the reliability of the bulk power system (BPS). WECC reviewed and accepted the TFE and determined it is technically infeasible for the entity to comply with the Standard for the device associated with the TFE Identification number. The compensating measures, described below, were in place prior to the due date on which all such TFE requests were to originally be submitted to WECC. The entity stated that the device is on a local area network only with internet connectivity, the device's secure configuration disables/removes software such as email clients that could make the server vulnerable to a virus. Further, the device is within a Physical Security Perimeter(s) and Electronic Security Perimeter(s). | Entity filed the TFEs, WECC approved the Part A and Part B TFE. Compensating measures were applied to limit exposure, such as no direct Internet connections or e-mail accounts are allowed on the system, and disabling of the auto run/auto play feature was performed. Anti-malware will be evaluated for compatibility if it becomes available.
2012-01-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC2011008714 | CIP-007-1 | R6 | WECC_URE3 submitted one late-filed Technical Feasibility Exception (TFE) addressing infeasibility with CIP-007-1 R6 for peripheral devices (e.g. printers). The entity stated that these devices are incapable of employing security access monitoring. | WECC determined that this issue posed a minimal risk and a not serious or substantial risk to the reliability of the bulk power system (BPS). WECC reviewed and accepted the TFE and determined it is technically infeasible for the entity to comply with the Standard for the devices associated with the TFE Identification number. The compensating measures, described below, were in place prior to the due date on which all such TFE requests were to originally be submitted to WECC. The entity implemented all available security measures supported by the device (e.g. strong passwords and disabling of used ports and services). Neighboring networked devices that do employ all security features are fully monitored for usual activity to provide visibility and will provide periphery notification in the event that the device begins exhibiting unusual or suspicious behavior. Further, strong Physical Security Perimeter(s) boundaries are enforced to reduce the risk of a physical compromise to the device. | Entity filed the TFEs, WECC approved the Part A and Part B TFE. All available security measures supported by the devices are implemented. Neighboring networked devices that do employ all security features are fully monitored for unusual activity to provide visibility.
2012-01-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC2011008715 | CIP-005-2 | R2 | WECC_URE4 submitted two late-filed Technical Feasibility Exceptions (TFEs) addressing infeasibility with CIP-005-2 R2 for an electronic access control system. The entity stated that client application used for administration of devices does not support the deployment of appropriate use banners on all of its interfaces. The web user and the command line interfaces only allow configuration changes to be made to the firewalls and do not provide full administration capabilities of the firewall, including changes to firewall access control lists. | WECC determined that this issue posed a minimal risk and not a serious or substantial risk to the reliability of the bulk power system (BPS). WECC reviewed and accepted the TFE and determined it is technically infeasible for the entity to comply with the Standard for the devices associated with the TFE Identification number. The compensating measures, described below, were in place prior to the due date on which all such TFE requests were to originally be submitted to WECC. To compensate for the lack of an acceptable use banner, WECC_URE4 has placed these two instances of the application behind two factor authentication (which contains the appropriate use banner) to restrict and control access. Access has been further restricted by limiting permitted network connections to a small number of dedicated IP address reservations which are locked to the individual firewall administrators’ domain accounts. Additionally, all firewall administrators have undergone background checks, and administrators must first acknowledge an acceptable use banner on their workstation computers before they are able to instantiate and operate any instance of the software. Further, accounts on the application are limited to the minimum privilege level necessary to administer the systems. WECC_URE4 has also implemented strong passwords for all administrative accounts to minimize the possibility of unauthorized access. The strong passwords meet WECC_URE4 and CIP complexity requirements, and are changed at least annually. Procedures are also in place to ensure passwords are changed should any of the administrators leave WECC_URE4 or no longer have responsibility for the devices. | Entity filed the TFEs, WECC approved the Part A and Part B TFE. Access to the application was restricted using two factor authentication (which contains appropriate use banner) and network connections were limited to dedicated IP addresses locked to individual domain accounts of firewall and VPN administrators exceeding CIP access standards.
2011-12-30 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2011008543 | CIP-007-1 | R2; R2.3 | The entity self-reported an issue with CIP-007-1 R2. This issue is a result of the entity's failure to timely submit Technical Feasibility Exception (TFE) requests in accordance with NERC procedures. The entity installed eight vibration monitors, eight micro controllers and two terminals where it was technically infeasible to stop/disable ports and services that were enabled on the devices. The entity implemented compensating measures at the time of implementation but submitted late TFEs 220 days after the safe harbor date. | FRCC determined this issue posed a minimal and not serious or substantial risk to the reliability of the bulk power system, because this issue was due to late submission of the TFE and all mitigation and compensating measure to provide comparable security were in place at the time of implementation of these Cyber Assets. The entity implemented the following compensating measures. The entity implemented technical controls such as network/VLAN separation and only allowed the required communication through the network. The network is protected by the firewall in a designated Electronic Security Perimeter. Further, the entity utilizes intrusion detection systems to perform network packet/traffic scan and alerting for malware signatures. | The entity submitted one Technical Feasibility Exception (TFE) that was accepted by FRCC.
2011-12-30 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2011008544 | CIP-007-1 | R6; R6.3 | The entity self-reported an issue with CIP-007-1 R6. This issue is a result of the entity's failure to timely submit Technical Feasibility Exception (TFE) requests in accordance with NERC procedures. The entity installed 66 switches, two routers, 56 micro controllers, 22 vibration sensors and 13 servers where it was not technically possible to meet CIP-007-3 R6 and R6.2. The entity implemented compensating measures at the time of implementation but submitted late TFE requests were submitted 408 days after the safe harbor date. | FRCC determined this issue posed a minimal and not serious or substantial risk to the reliability of the bulk power system, because this issue was due to late submission of the TFE and all mitigation and compensating measures to provide comparable security were in place at the time of implementation of these Cyber Assets. The entity implemented the following compensating measures. The entity implemented technical controls such as network/VLAN separation and only allowed the required communication through the network. The network is protected by the firewall in a designated Electronic Security Perimeter. Further, the entity utilizes intrusion detection systems to perform network packet/traffic scan and alerting for malware signatures. | The entity submitted 12 Technical Feasibility Exceptions that were accepted by FRCC.
2011-12-30 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2011008541 | CIP-007-1 | R4 | The entity self-reported an issue with CIP-007-1 R4. This issue is a result of the entity's failure to timely submit Technical Feasibility Exception (TFE) requests in accordance with NERC procedures. The entity installed two network switches and ten vibration monitoring systems for which it was technically infeasible to install anti-malware. The entity installed comparable compensating and mitigating measures by implementing procedural controls to require review for authenticity prior to installation of any application or firmware. The TFE submittals were 65 and 306 days late. | FRCC determined this issue posed a minimal and not serious or substantial risk to the reliability of the bulk power system, because this issue was due to late submission of the TFE and all mitigation and compensating measure to provide comparable security were in place at the time of implementation of these Cyber Assets. The entity implemented the following compensating measures. The entity implemented technical controls such as network separation and only allowed the required communication through the network. The network is protected by firewall in a designated Electronic Security Perimeter. The entity also implemented manual controls to perform review of all new installation of patches and firmware to ensure source and integrity validation. This process also includes vendor certification and hash value integrity check. Further, the entity is utilizing intrusion detection systems to perform network packet/traffic scan and alerting for malware signatures. | The entity submitted two Technical Feasibility Exceptions (TFEs) that were accepted by FRCC.
2011-12-30 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC2011008542 | CIP-007-1 | R5; R5.3; R5.3.2 | The entity self-reported an issue with CIP-007-1 R5. This issue is a result of the entity's failure to timely submit Technical Feasibility Exception (TFE) requests in accordance with NERC procedures. The entity installed one terminal server, four printers, 32 network switches, 26 micro controllers, seven routers, 168 servers and desktops, and ten vibration monitoring devices, where it was technically infeasible to enforce compliance with the password requirements of R5.3 and password complexity requirements of R5.3.2. The entity implemented compensating measures at the time of implementation but submitted late TFEs 37 to 306 days after the safe harbor date. | FRCC determined this issue posed a minimal and not serious or substantial risk to the reliability of the bulk power system, because this issue was due to late submission of the TFE and all mitigation and compensating measure to provide comparable security were in place at the time of implementation of these Cyber Assets. The entity implemented the following compensating measures. The entity implemented technical controls such as network separation and only allowed the required communication through the network. The network is protected by the firewall in a designated Electronic Security Perimeter. The entity has also implemented manual controls designed to increase user awareness for password compliance requirements, perform manual review of all password for complexity, created annual schedule of required password change. Further, where the passwords cannot meet the CIP requirements for complexity and character length, the entity manual controls require the user to ensure that passwords are created to apply the maximum technically feasible complexity and the length. | The entity submitted seven Technical Feasibility Exceptions (TFEs) that were accepted by FRCC.
2011-12-30 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 2 (FRCC_URE2) | NCRXXXXX | FRCC2011008531 | CIP-007-1 | R5; R5.3 | The entity self-reported an issue with CIP-007-1 R5. This issue is a result of the entity's failure to timely submit Technical Feasibility Exception (TFE) requests in accordance with NERC procedures. The entity's TFE for the ten firewalls was submitted 397 days after installation of the devices. These firewalls do not have the capability to enforce password complexity as required by CIP-007 R5.3. While the devices do support acceptable passwords there is no technical mechanism to enforce it. This TFE includes ten firewalls and was late by 397 days. | This issue posed a minimal risk and not a serious or substantial risk to the reliability of the bulk power system because even though the TFE request was submitted late, the following compensating and mitigating measures were implemented at the time of device installation. The firewalls are on a private network as the separation point between the general business traffic and the control center network. Additionally, all network traffic to these devices is monitored by the entity’s intrusion detection system. The entity also implemented procedural controls to ensure that all passwords comply to highest technically feasible complexity. | The entity has submitted one Technical Feasibility Exception that was accepted and approved by FRCC.
2011-12-30 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 3 (FRCC_URE3) | NCRXXXXX | FRCC2011008528 | CIP-007-1 | R2; R2.3 | The entity self-reported an issue with CIP-007-1 R2. This issue is a result of the entity's failure to timely submit Technical Feasibility Exception (TFE) requests in accordance with NERC procedures. The entity has two micro controllers where it is technically infeasible to disable unused ports and services as required by the Standard. The entity implemented comparable security measures but failed to submit the TFE before the safe harbor date. The TFE was late by 188 days. | FRCC determined this issue posed a minimal and not serious or substantial risk to the reliability of the bulk power system, because this issue was due to late submission of the TFE and all mitigation and compensating measure to provide comparable security were in place at the time of implementation of these Cyber Assets. The entity implemented the following compensating measures. The entity implemented technical controls such as network/VLAN separation and only allowed the required communication through the network. The network is protected by the firewall in a designated ESP. Further, the Responsible Entity is utilizing intrusion detection systems to perform network packet/traffic scan and alerting for malware signatures. | The entity has submitted one Technical Feasibility Exception that was accepted and approved by FRCC.
2011-12-30 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 3 (FRCC_URE3) | NCRXXXXX | FRCC2011008529 | CIP-007-1 | R5; R5.3.2 | The entity self-reported an issue with CIP-007-1 R5. This issue is a result of the entity's failure to timely submit Technical Feasibility Exception (TFE) requests in accordance with NERC procedures. The entity has 20 operating systems where enforcing a combination of alpha, numeric and "special" characters for passwords as required by CIP-007 R5.3.2 is not technically feasible. The entity implemented comparable security measures but failed to submit the TFE before the safe harbor date for 20 of these systems. The TFE was late by 188 days. | FRCC determined this issue posed a minimal and not serious or substantial risk to the reliability of the bulk power system, because this issue was due to late submission of the TFE and all mitigation and compensating measure to provide comparable security were in place at the time of implementation of these Cyber Assets. The entity implemented the following compensating measures. The entity implemented technical controls such as network separation and only allowed the required communication through the network. The network is protected by the firewall in a designated Electronic Security Perimeter. The entity also implemented manual controls designed to increase user awareness for password compliance requirements, perform manual review of all password for complexity, created annual schedule of required password change. Further, where the passwords cannot meet the CIP requirements for complexity and character length, the entity manual controls require the user to ensure that passwords are created to apply the maximum technically feasible complexity and the length. | The entity has submitted one Technical Feasibility Exception that was accepted and approved by FRCC.
2011-12-30 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 4 (FRCC_URE4) | NCRXXXXX | FRCC2011008526 | CIP-006-1 | R1; R1.1 | The entity self-reported an issue with CIP-006-1 R1. This issue is a result of the entity's failure to timely submit Technical Feasibility Exception (TFE) requests in accordance with NERC procedures. The entity submitted three late TFEs for three of its Physical Security Perimeters (PSPs) that could not implement a complete six-walled perimeter due to excessive cost implications. While the entity submitted the TFE later than the safe harbor date, it did implement comparable security measures. The TFE was late by 113 days. | FRCC determined this issue posed a minimal risk and not a serious or substantial risk to the reliability of the bulk power system because this issue was due to late submission of the TFE. In addition, all mitigating and compensating measures to provide comparable security were in place at the time of implementation of the PSPs. The following compensating and mitigating measures were implemented prior to TFE acceptance/approval by FRCC. The PSPs are within a facility that is guarded 24 hours a day, seven days a week, and only authorized entity personnel have access to the facility. All PSPs have access controls including locked doors and card readers with alarms. In order to compensate the lack of complete six-wall boundary due to use of raised floors and false ceilings in some areas, the entity has implemented mesh of bars that limit access. Further, all the Cyber Assets are inside locked cabinets and only authorized personnel have access to these locked cabinets. | The entity submitted one late Technical Feasibility Exception that was approved by FRCC.
2011-12-30 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 4 (FRCC_URE4) | NCRXXXXX | FRCC2011008527 | CIP-007-1 | R6; R6.3 | The entity self-reported an issue with CIP-007-1 R6. This issue is a result of the entity's failure to timely submit Technical Feasibility Exception (TFE) requests in accordance with NERC procedures. The entity has a single GPS clock source that is not able to comply with CIP-007-1 R6 due to technical limitations. The entity implemented comparable security measures but submitted the TFE later than the safe harbor date. The TFE was late by 113 days. | FRCC determined this issue posed a minimal risk and not a serious or substantial risk to the reliability of the bulk power system because this issue was due to late submission of the TFE. In addition, all mitigating and compensating measures to provide comparable security were in place at the time of implementation of these Cyber Assets. The following compensating and mitigating measures were completed prior to the TFE approval. The entity implemented technical controls such as network/VLAN separation and only allowed the required communication through the network. The network is protected by the firewall in a designated Electronic Security Perimeter. Further, the entity utilizes intrusion detection systems to perform network packet/traffic scan and alerting for malware signatures. | The entity submitted one late Technical Feasibility Exceptions that was approved by FRCC.
2011-12-30 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 5 (FRCC_URE5) | NCRXXXXX | FRCC2011008530 | CIP-007-1 | R4 | The entity self-reported an issue with CIP-007-1 R4. This issue is on account of entity's failure to timely submit a Technical Feasibility Exception (TFE) request in accordance with NERC procedures. The entity installed three physical access control system microcontrollers for which no anti-malware is available. The TFE was submitted late by 274 days. | FRCC determined this issue posed a minimal risk and not a serious or substantial risk to the reliability of the bulk power system because this issue was due to late submission of the TFE. In addition, all mitigating and compensating measures to provide comparable security were in place at the time of implementation of these Cyber Assets. The entity implemented technical controls such as network separation and only allowed the required communication through the network. The network is protected by firewall in a designated Electronic Security Perimeter. The entity also implemented manual controls to perform review of all new installation of patches and firmware to ensure source and integrity validation. | The entity submitted one late Technical Feasibility Exceptions that was approved by FRCC.
2011-12-30 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO201100406 | CIP-005-1 | R3; R3.2 | The entity failed to submit a timely Technical Feasibility Exception (TFE) request in accordance with NERC procedures for CIP-005-1 R3. The TFE request was submitted approximately two months beyond the required TFE submission window. The entity requested the TFE because the Cyber Assets used to control and monitor physical access to the entity's Physical Security Perimeter do not support security monitoring processes that alert for attempts at or actual unauthorized accesses. | The remediated issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the entity implemented the following compensating measures: (1) located the Cyber Assets within a Physical Security Perimeter; (2) manually reviewed access logs; and (3) isolated Cyber Assets from the corporate network, Supervisory Control and Data Acquisition (SCADA) system and the internet. The only logical access to the system is in the data center and is protected by strong passwords. Additionally, these compensating measures were in place prior to the date on which the TFE request was originally due to MRO. | The entity performed a new analysis of its risk-based assessment methodology and subsequently declared no Critical Assets or Critical Cyber Assets. The devices were covered by appropriate compensating security measures while in service and declared as Critical Cyber Assets. MRO terminated the TFE.
2011-12-30 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO201100407 | CIP-007-1 | R2; R2.3 | The entity failed to submit a timely Technical Feasibility Exception (TFE) request in accordance with NERC procedures for CIP-007-1 R2. The TFE request was submitted approximately two months beyond the required TFE submission window. The entity requested the TFE because several Cyber Assets do not support the disabling of unused ports and services. The system is not vendor-supported due to system age, and attempts to disable ports and services will have adverse operational effects. | The remediated issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the following compensating measures were in place: (1) the Cyber Assets are located in a Physical Security Perimeter; and (2) the Cyber Assets are isolated from the corporate network, SCADA system and the internet. The only logical access to the system is in the data center and is protected by strong passwords. Additionally, these compensating measures were in place prior to the date on which the TFE request was originally due to MRO. | The entity performed a new analysis of its risk-based assessment methodology and subsequently declared no Critical Assets or Critical Cyber Assets (CCAs). The devices were covered by appropriate compensating security measures while in service and declared as CCAs. MRO terminated the TFE.
2011-12-30 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO201100408 | CIP-007-1 | R4 | The entity failed to submit a timely Technical Feasibility Exception (TFE) request in accordance with NERC procedures for CIP-007-1 R4. The TFE request was submitted approximately two months beyond the required TFE submission window. The entity requested the TFE because several physical access control systems did not support the installation of anti-virus or malware prevention software. Additionally, the system is not vendor supported due to system age, and an attempt to install anti-virus software would have an adverse operational affect. | The remediated issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the following compensating measures were in place: (1) the Cyber Assets covered by this TFE are located within the Physical Security Perimeter; (2) the Cyber Assets are isolated from the corporate network, Supervisory Control and Data Acquisition (SCADA) system and the internet; the only logical access to the system is in the data center and is protected by strong passwords; and (3) all devices used for maintenance activities are scanned for viruses and malware prior to connection to these covered Cyber Assets. | The entity performed a new analysis of its risk-based assessment methodology and subsequently declared no Critical Assets or Critical Cyber Assets (CCAs). The devices were covered by appropriate compensating security measures while in service and declared as CCAs. MRO terminated the TFE.
2011-12-30 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO201100409 | CIP-007-1 | R6 | The entity failed to submit a timely Technical Feasibility Exception (TFE) request in accordance with NERC procedures for CIP-007-1 R6. The TFE request was submitted approximately two months beyond the required TFE submission window. The entity requested the TFE because several of the entity's devices did not support automated tools to monitor system events related to cyber security. Attempts to install automated monitoring would have an adverse operation effect on system configurations. | The remediated issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the entity has the following compensating measures in place: (1) the Cyber Assets covered are located within a Physical Security Perimeter; (2) the Cyber Assets are isolated from the corporate network, Supervisory Control and Data Acquisition (SCADA) system and the internet; the only logical access is through the data center which is protected by strong passwords; and (3) logs and system events are reviewed annually. | The entity performed a new analysis of its risk-based assessment methodology and subsequently declared no Critical Assets or Critical Cyber Assets (CCAs). The devices were covered by appropriate compensating security measures while in service and declared as CCAs. MRO terminated the TFE.
2011-12-30 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 2 (MRO_URE2) | NCRXXXXX | MRO201100410 | CIP-007-1 | R2; R2.3 | The entity failed to submit a timely Technical Feasibility Exception (TFE) request in accordance with NERC procedures for CIP-007-1 R2. The TFE request was submitted approximately one year beyond the required TFE submission window. The entity requested the TFE because several substation meters and card reader access controls have unused ports and services which cannot be disabled. | The remediated issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the TFE was approved by MRO_URE2and the entity has the following compensating measures: (1) The substation meter is connected to the substation Electronic Security Perimeter (ESP) switch that is in a locked cabinet. The switch enforces that all connecting devices are authorized by media access control address, and restricts connections between pre-defined source and destination switch ports only; (2) remote access into the substation WAN is only allowed from designated support stations in Physical Security Perimeters (PSP), and the vulnerable IP ports are restricted by policy; (3) the ESP firewall logs remote access events and policy violations to a central log server; (4) the substation LAN is monitored by an intrusion detection system that detects protocol anomalies; (5) access logs are manually reviewed typically every business day, but never more than 30 days later; (6) all controller devices are isolated as the sole network device in an ESP behind a firewall. The firewall policy allows remote access only by the card access server on the authorized port. The firewall restricts the controller device from initiating any outbound connection, only communicating with establish incoming communications; (7) for controller devices on the central card access LAN ESP, no external hosts are allowed to communicate with these devices via configuration; and (8) the controllers and firewalls are always inside of a PSP. | The entity mitigated the issue by submitting all acceptable TFE requests and has continuously performed all of the compensating measures as discussed in the TFE requests.
2011-12-30 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 2 (MRO_URE2) | NCRXXXXX | MRO201100411 | CIP-007-1 | R5; R5.3 | The entity failed to submit a timely Technical Feasibility Exception (TFE) request in accordance with NERC procedures for CIP-007-1 R5. The TFE request was submitted one year beyond the required TFE submission window. The entity requested the TFE because a legacy Inter-Control Center Protocol (ICCP) application server has user accounts and passwords embedded in the software that cannot be changed because the vendor no longer supports the system. | The remediated issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the TFE was approved by MRO_URE2and the entity has the following compensating measures: (1) pre-defined external connections allowed with peer hosts communicating on the port have been removed. The only remaining data links are to other internal systems in the same Physical Security Perimeter as these servers; (2) a new firewall and perimeter network has been implemented, and direct incoming access to this host is no longer allowed; and (3) external support access from authorized hosts must use indirect access, after establishing a session to an allowed host. | The entity mitigated the issue by submitting all acceptable TFE requests and has continuously performed all of the compensating measures as discussed in the TFE requests.
2011-12-30 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 3 (MRO_URE3) | NCRXXXXX | MRO201100415 | CIP-007-1 | R4 | The entity failed to submit timely Technical Feasibility Exception (TFE) requests in accordance with NERC procedures for CIP-007-1 R4. The TFE requests were submitted approximately four months and fourteen months beyond the required TFE submission window. The entity requested the TFE because Cyber Assets detailed in the TFE are network firewalls that do not support the use or running of anti-virus or malware prevention tools. Per the manufacturer attestation and documentation, the devices are not susceptible to malware or viruses. The entity has provided a document attesting to the fact that the systems do not support the use of anti-virus or other malware prevention tools. Additionally, the TFE covers network routers, switches and telecommunications devices that that do not support the use or running of anti-virus or malware prevention tools. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the entity has the following compensating measures: (1) access is protected by Electronic Security Perimeter (ESP) and login access control; (2) the Cyber Assets reside within a second tier Physical Security Perimeter controlled by cyber locks to intentionally reduce and control log access to the device; (3) logical and electronic access is controlled and restricted to personnel with the “need to know” job criteria; (4) anti-virus and malware prevention tools are implemented on all other Cyber Assets within the ESP(s) where capable; and (5) hardware, firmware and software for the Cyber Assets are frozen; the covered assets are to conform to their corresponding frozen versions in order to be in the system. | The entity mitigated the issue by submitting all acceptable TFE requests and has continuously performed all of the compensating measures as discussed in the TFE requests.
2011-12-30 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 3 (MRO_URE3) | NCRXXXXX | MRO201100417 | CIP-007-1 | R5; R5.3 | The entity failed to submit a timely Technical Feasibility Exception (TFE) request in accordance with NERC procedures for CIP-007-1 R5. The TFE was submitted approximately 10 months beyond the required TFE submission window. The entity requested the TFE because the devices detailed in this TFE are network servers running databases that are tightly coupled to the entity's transmission management system (TMS) application. A small number of administrative accounts are utilized by the TMS application for database access and currently cannot be changed without impact on the functioning of that application. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the entity has the following compensating measures: (1) the covered Cyber Asset is protected by an Electronic Security Perimeter; (2) the covered asset is a purpose built device with a hardened operating system; and (3) access to the covered asset is via user identification and password login access control. | The entity mitigated the issue by submitting all acceptable TFE requests and has continuously performed all of the compensating measures as discussed in the TFE requests.
2011-12-30 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 4 (MRO_URE4) | NCRXXXXX | MRO201100419 | CIP-005-1 | R2; R2.6 | The entity failed to submit a timely Technical Feasibility Exception (TFE) request in accordance with NERC procedures for CIP-005-1 R2. The TFE request for the entity was submitted approximately eight months late. The entity requested the TFE because the devices detailed in this TFE are LAN controllers for the physical access control system that do not support the use of or installation of appropriate use banners. | MRO determined that the issue posed a minimal risk to the reliability of the bulk power system (BPS) because the issue resulted from failures by the entity to comply with the administrative process for the submission of a formal TFE request. MRO considered that the LAN controllers reside within defined Physical Security Perimeters (PSPs); interactive management access to the LAN controllers is restricted to only connections originating at the access control system server; and there is real-time logging of all connections to the LAN controllers. | The entity mitigated the issue by submitting all acceptable TFE requests and has continuously performed all of the compensating measures as discussed in the TFE requests.
2011-12-30 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 4 (MRO_URE4) | NCRXXXXX | MRO201100418 | CIP-007-1 | R2; R2.3 | The entity failed to submit a timely Technical Feasibility Exception (TFE) request in accordance with NERC procedures for CIP-007-1 R2. The TFE request for the entity was submitted approximately three months late. The entity requested the TFE because the devices detailed in this TFE are two application servers where the entity has not been able to disable unused ports and services declaring that it is currently infeasible and would introduce operational risk to the Energy Management System (EMS). To the extent possible, the entity has worked with EMS vendor to define and document all ports and services for these covered Cyber Assets. To date, a complete list has not been attainable and this is the basis for the TFE. | MRO determined that the issue posed a minimal risk to the reliability of the bulk power system (BPS) because the issue resulted from failures by the entity to comply with the administrative process for the submission of a formal TFE request. MRO considered that the vendor has performed system hardening on all operating systems that are part of the Energy Management System and network during the last EMS upgrade completed in April 2008, enabling only ports and services that at that time were known to be necessary for normal and emergency operations. Host-based intrusion detection systems (HIDS) agents are running on all EMS systems providing host-based firewall and anti-virus/malware protection services. The entity has configured host-to-host connection restrictions within the Electronic Security Perimeter (ESP) enforced by the HIDS. Access to EMS host systems within the ESP is provided by multiple levels of host-based and network based authentication. Remote access into the ESP is managed through secure virtual private network (VPN) appliances using two-factor authentication. | The entity mitigated the issue by submitting all acceptable TFE requests and has continuously performed all of the compensating measures as discussed in the TFE requests.
2011-12-30 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 4 (MRO_URE4) | NCRXXXXX | MRO201100420 | CIP-007-1 | R4 | The entity failed to submit a timely Technical Feasibility Exception (TFE) request in accordance with NERC procedures for CIP-007-1 R4. The TFE request for the entity was submitted approximately eight months late. The entity requested the TFE because the devices detailed in this TFE are LAN controllers for the access control system that do not support the use of or installation of anti-virus or malware prevention tools. The entity provided vendor attestation that these devices cannot deploy anti-virus and malware prevention tools. | MRO determined that the issue posed a minimal risk to the reliability of the bulk power system (BPS) because the issue resulted from failures by the entity to comply with the administrative process for the submission of a formal TFE request. MRO considered that the LAN controllers reside within defined Physical Security Perimeters (PSPs); interactive management access to the LAN controllers is restricted to only connections originating at the access control system server; and there is real-time logging of all connections to the LAN controllers. | The entity mitigated the issue by submitting all acceptable TFE requests and has continuously performed all of the compensating measures as discussed in the TFE requests.
2011-12-30 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 5 (MRO_URE5) | NCRXXXXX | MRO201100421 | CIP-007-1 | R3 | The entity failed to submit timely Technical Feasibility Exception (TFE) requests in accordance with NERC procedures for CIP-007-1 R3. The TFE requests for the entity were submitted between two months and seven months late. The entity requested the TFE because the devices detailed in these TFE requests are a security information management system, a server running proprietary load management software, two modems, a remote access server providing dial-in access and data storage appliances that cannot support the installation of security patches or updates. | MRO determined that the issue posed a minimal risk to the reliability of the bulk power system (BPS) because the issue resulted from failures by the entity to comply with the administrative process for the submission of a formal TFE request. MRO considered that the security information management system resides within a defined Electronic Security Perimeter (ESP) with limited access to the system, resides within a defined Physical Security Perimeters (PSPs), has a hardened operating system with no administrative access to the system or software for the users, and devices communicating with the security information management system are regularly patched per the entity's security patch management program. MRO considered that the data storage appliances reside within a defined ESP and PSP. MRO considered that the modems connect to a Cyber Asset that has security patches and updates deployed per the entity's security patch management program and communication to and from the devices uses a non-routable protocol. MRO considered that the remote access server connects to a Cyber Asset that has security patches and updates deployed per the security patch management program; external communication to/from the device uses a non-routable protocol; access and use of the modem is controlled through the use of a password authentication and remote controlled relay switch. The switch allows a system operator to remotely enable the modem for a requested period of time for an authorized user. Also, an alert is sent to the Energy Management System (EMS) analyst whenever the modem is connected. Additionally, all communication with devices within the ESP is monitored by a security information and event management system and controlled via firewall access point policy. | The entity mitigated the issue by submitting all acceptable TFE requests and has continuously performed all of the compensating measures as discussed in the TFE requests. The entity has installed a new server which allows application of security patches and updates. MRO approved termination of the TFE related to the first identified server. The entity removed the remote access dial-in server and a modem from the EMS network. MRO approved termination of the TFEs related to the remote access server and one modem. The entity removed the data storage appliances from the EMS network. MRO approved termination of the TFE related to the data storage appliances.
2011-12-30 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 5 (MRO_URE5) | NCRXXXXX | MRO201100422 | CIP-007-1 | R4 | The entity failed to submit timely Technical Feasibility Exception (TFE) requests in accordance with NERC procedures for CIP-007-1 R4. The TFE requests for the entity were submitted between four months and nine months late. The entity requested the TFEs because the devices detailed in these TFEs are a security information management system, extreme network switches, and a virtual private network (VPN) appliance that do not support the use or running of anti-virus or malware prevention tools. | MRO determined that the issue posed a minimal risk to the reliability of the bulk power system (BPS) because the issue resulted from failures by the entity to comply with the administrative process for the submission of a formal TFE request. MRO considered that the security information and event management (SIEM) system resides within a defined Electronic Security Perimeter (ESP) with limited access to the system, resides within a defined Physical Security Perimeter (PSP), has a hardened operating system with no administrative access to the system or software for the users, and devices communicating with the security management information system are regularly patched per the security patch management program. MRO considered that the extreme network switches reside within a defined ESP and PSP, and all Cyber Assets connected to the network switch that are capable of running anti-virus and malware prevention tools have those services installed and running. MRO considered that remote access sessions initiated by the VPN appliance are directed to firewall access points for network and host access control; only identified users are configured in and allowed access via the VPN appliance; and all ESP data traffic and the VPN appliance are monitored by SIEM. | The entity mitigated the issue by submitting all acceptable TFE requests and has continuously performed all of the compensating measures as discussed in the TFE requests.
2011-12-30 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 6 (MRO_URE6) | NCRXXXXX | MRO201100423 | CIP-007-1 | R4 | The entity failed to submit a timely Technical Feasibility Exception (TFE) request in accordance with NERC procedures for CIP-007-1 R4. The TFE request for the entity was submitted approximately three months late. The entity requested the TFE because the devices detailed in this TFE are network switches, encryption devices and remote terminal units (RTUs) that do not run anti-virus software or services. The entity has provided vendor documentation and attestation that the devices cannot use anti-virus software or other malware prevention tools. | MRO determined that the issue posed a minimal risk to the reliability of the bulk power system (BPS) because the issue resulted from failure by the entity to comply with the administrative process for the submission of a formal TFE request. The devices reside within a defined Electronic Security Perimeter (ESP) and are protected by firewalls with appropriate policies blocking access to these devices. Remaining Critical Cyber Assets and Cyber Assets within the ESP that are capable of using and running anti-virus software and malware prevention tools have those services implemented. | The entity mitigated the issue by submitting all acceptable TFE requests and has continuously performed all of the compensating measures as discussed in the TFE requests.
2011-12-30 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 6 (MRO_URE6) | NCRXXXXX | MRO201100424 | CIP-007-1 | R6 | The entity failed to submit a timely Technical Feasibility Exception (TFE) request in accordance with NERC procedures for CIP-007-1 R6. The TFE request for the entity was submitted approximately three months late. The entity requested the TFE because it has provided vendor documentation and attestation that the remote terminal units (RTU) devices cannot implement automated tools or organizational process controls to monitor system events that are related to cyber security. | MRO determined that the issue posed a minimal risk to the reliability of the bulk power system (BPS) because the issue resulted from failure by the entity to comply with the administrative process for the submission of a formal TFE request. The devices reside within a defined Electronic Security Perimeter (ESP) and are protected by firewalls with appropriate policies blocking access to these devices. Remaining Critical Cyber Assets and Cyber Assets within the ESP that are capable of using and running anti-virus software and malware prevention tools have those services implemented. | The entity mitigated the issue by submitting all acceptable TFE requests and has continuously performed all of the compensating measures as discussed in the TFE requests.
2011-12-30 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 7 (MRO_URE7) | NCRXXXXX | MRO201100291 | CIP-007-1 | R4 | The entity self-reported an issue with CIP-007-1 R4 because it failed to submit a timely Technical Feasibility Exception (TFE) request in accordance with NERC procedures. The TFE request for the entity was submitted approximately ten months late. The entity requested the TFE because it utilizes anti-virus software on all non-Energy Management System (EMS) equipment located within the defined Electronic Security Perimeter, however anti-virus software was not installed on any communication front end device because the EMS vendor did not have an anti-virus product certified for use with the software release currently running on the system. The critical performance of communication for Supervisory Control and Data Acquisition (SCADA) would not afford the necessary resource to run virus scanning while performing the real-time SCADA function. | MRO determined that the issue posed a minimal risk to the reliability of the bulk power system (BPS) because the issue resulted from failure by the entity to comply with the administrative process for the submission of a formal TFE request. During the duration of the TFE, the entity did not allow direct internet connections or email accounts on the Energy Management System (EMS). Additionally for all EMS equipment, the autorun and autoplay features were disabled. | The entity mitigated the issue by submitting all acceptable TFE requests and has continuously performed all of the compensating measures as discussed in the TFE requests. This TFE has been terminated because the entity completed the installation of anti-virus software on the covered Cyber Assets.
2011-12-30 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 8 (MRO_URE8) | NCRXXXXX | MRO201100426 | CIP-007-1 | R4 | The entity failed to submit timely Technical Feasibility Exception (TFE) requests in accordance with NERC procedures for CIP-007-1 R4. The TFE requests for the entity were submitted approximately four months late. The entity requested the TFE because the devices detailed in these TFE requests are network switches, fiber channel switches, data storage components, network security appliances and firewalls, terminal servers that provide serial-to-ethernet conversion, protocol converters, splitter panels used for sharing modem connections between front-end processors (FEPs), and a printer that do not run anti-virus software or services. The entity has provided vendor documentation that the devices do not use or run anti-virus software or other malware prevention tools. | MRO determined that the issue posed a minimal risk to the reliability of the bulk power system (BPS) because the issue resulted from failures by the entity to comply with the administrative process for the submission of a formal TFE request. MRO determined that the hardened design of the devices, redundancy of critical components, use of intrusion detection software and a monitoring, analysis and response system to detect malicious activity and administrator notifications of potential security events minimize risk, to the extent possible, of adverse impact to the covered Cyber Assets. | The entity mitigated the issue by submitting all acceptable TFE requests and has continuously performed all of the compensating measures as discussed in the TFE requests.
2011-12-30 | NERC Compliance Enforcement Authority (NCEA) | Unidentified Registered Entity 1 (NCEA_URE1) | NCRXXXXX | NCEA201100125, NCEA201100126 | CIP-007-1 | R4, R4.1, R4.2 | NCEA_URE1 submitted a Self-Report to NCEA stating that its Hewlett-Packard (HP) Printers and Multi Function Printers (MFPs) do not have the capabilities to install anti-virus or malicious software prevention tools. Such software is neither provided by HP nor is it available from third parties. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because all files including software updates are scanned for anti-virus and anti-malware on other systems prior to entering the Electronic Security Perimeter (ESP). Software updates are also verified by comparing to the manufacturer's (hash) files when available. These printers were not included on the initial list of TFEs submitted by NCEA_URE1. | The TFE was submitted to NCEA and approved. NCEA_URE1 is unaware of similar devices that have anti-virus or anti-malware capabilities. NCEA_URE1 will continue to research the market for similar devices that will meet these requirements of these devices. All files including software updates are scanned for anti-virus and anti-malware on other systems prior to entering the ESP. Software updates are also verified by comparing to the manufacturer's (hash) files when available.
2011-12-30 | NERC Compliance Enforcement Authority (NCEA) | Unidentified Registered Entity 1 (NCEA_URE1) | NCRXXXXX | NCEA201100125, NCEA201100126 | CIP-007-1 | R4, R4.1, R4.2 | NCEA_URE1 submitted a Self-Report to NCEA stating that its Hewlett-Packard (HP) Printers and Multi Function Printers (MFPs) do not have the capabilities to install anti-virus or malicious software prevention tools. Such software is neither provided by HP nor is it available from third parties. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because all files including software updates are scanned for anti-virus and anti-malware on other systems prior to entering the Electronic Security Perimeter (ESP). Software updates are also verified by comparing to the manufacturer's (hash) files when available. These printers were not included on the initial list of TFEs submitted by NCEA_URE1. | The TFE was submitted to NCEA and approved. NCEA_URE1 is unaware of similar devices that have anti-virus or anti-malware capabilities. NCEA_URE1 will continue to research the market for similar devices that will meet these requirements of these devices. All files including software updates are scanned for anti-virus and anti-malware on other systems prior to entering the ESP. Software updates are also verified by comparing to the manufacturer's (hash) files when available.
2011-12-30 | NERC Compliance Enforcement Authority (NCEA) | Unidentified Registered Entity 1 (NCEA_URE1) | NCRXXXXX | NCEA201100127 | CIP-007-1 | R5.3 | NCEA_URE1 submitted a Self-Report to NCEA stating that its Hewlett-Packard (HP) Printers and Multi Function Printers (MFPs) are not capable of implementing password controls for Administrator accounts as required by NERC standards. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because access to the printers is only available to users on the administrative network which is strictly controlled. These printers were not included on the initial list of TFEs submitted by NCEA_URE1. | The TFE was submitted to NCEA and approved. Access to the printers is only available to users on the administrative network which is strictly controlled. The compensating and/or mitigating measures have been fully implemented.
2011-12-30 | NERC Compliance Enforcement Authority (NCEA) | Unidentified Registered Entity 1 (NCEA_URE1) | NCRXXXXX | NCEA201100128 | CIP-007-3 | R6.3 | NCEA_URE1 submitted a Self-Report to NCEA stating that the Event Logging in Hewlett-Packard (HP) LaserJet printers T610 plotters is limited to device and printing errors. It does not provide security event logging for authentication errors, setting changes, or other security related events. This issue was discovered as part of NCEA_URE1's ongoing process to review its compliance with applicable Reliability Standards, it was discovered that these printers did not meet the Requirements for security event logging as required. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because meeting this Requirement is not technically feasible for this entity and NCEA_URE1 has submitted a TFE. | The HP LaserJet printers T610 plotters were disconnected from the Electronic Security Perimeter (ESP) and moved to a secured area network outside of the ESP, where real-time plant data can be amassed on a server that sits between the process and general networks, allowing general users to get any necessary data without having to directly access the system itself. For prevention of future risk, connection to the secured area containing the printers is limited. Firewall policy only allows administration connections to the printers from the administrator's management workstations. All connections to the printers are logged in the firewall.
2011-12-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC2011001051 | CIP-004-3 | R2 | The entity self-reported a possible issue with CIP-004-3 R2 to ReliabilityFirst. The entity discovered that it granted an employee who had not completed the entity’s CIP training unescorted physical access to one Physical Security Perimeter (PSP) containing Critical Cyber Assets (CCAs). The entity revoked the employee’s access after it discovered the issue through its daily reconciliation of employee access rights. ReliabilityFirst determined that the entity had an issue with the Standard as it failed to ensure that the employee received CIP training prior to granting that employee unescorted physical access to the PSP containing CCAs. | The risk to the reliability of the bulk power system was mitigated by the following factors. The employee to whom the entity granted unescorted physical access had successfully completed similar initial and annual CIP training required by the entity's affiliates. Also, the employee at issue had been subject to a personnel risk assessment prior to the issue. In light of the nature of the issue, offset by the aforementioned mitigating factor, ReliabilityFirst determined that this issue posed a minimal and not a serious or substantial risk to the reliability of the bulk power system. | The entity submitted a mitigation plan, in which it memorialized the actions it took to address the issue, to ReliabilityFirst. The entity revised its procedure for granting physical access to require a supervisor to approve and implement all requests for access to PSPs. The entity also conducted training on the revised procedure for all relevant employees. In this mitigation plan, the entity represented that it completed the mitigating actions.
2011-12-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 4 (RFC_URE4) | NCRXXXXX | RFC2011001092 | CIP-003-1 | R2; R2.2; R2.3 | ReliabilityFirst conducted a compliance audit of the entity, during which ReliabilityFirst discovered that the entity had a possible issue with CIP-003-1 R2. The CIP senior manager for the entity and its affiliates delegated the authority to perform the CIP senior manager functions that are necessary to ensure compliance with CIP-002 R4 to another individual. The entity's parent company changed the delegated senior manager authority to a different individual. Pursuant to CIP-003-1 R2.2 and R2.3, the entity was required to document that change within thirty calendar days; however, the entity did not document that change until approximately 3 months later. ReliabilityFirst determined that the entity had an issue with the Standard by failing to document evidence of its senior management delegation change within thirty calendar days of the effective date of the change. | In light of the nature of the issue, offset by the mitigating factors, ReliabilityFirst determined that this issue posed a minimal, not serious or substantial, risk to the reliability of the bulk power system. The risk posed by the foregoing facts and circumstances was mitigated by the following factors. The issue is a documentation error because although the entity did not document the senior manager delegation change within 30 calendar days, the senior manager delegate did begin performing all delegated senior manager functions. In addition, the entity has no Critical Cyber Assets. | In order to mitigate the issue, the entity documented the senior manager delegation change. During the compliance audit, ReliabilityFirst verified the completion of the entity's mitigating actions.
2011-12-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 5 (RFC_URE5) | NCRXXXXX | RFC2011001093 | CIP-003-1 | R2; R2.2; R2.3 | ReliabilityFirst conducted a compliance audit of the entity, during which ReliabilityFirst discovered that the entity had a possible issue with CIP-003-1 R2. The CIP senior manager for the entity and its affiliates delegated the authority to perform the CIP senior manager functions that are necessary to ensure compliance with CIP-002 R4 to another individual. Subsequently, the entity's parent company changed the delegated senior manager authority to a different individual. Pursuant to CIP-003-1 R2.2 and R2.3, the entity was required to document that change within thirty calendar days; however, the entity did not document that change until approximately 3 months later. ReliabilityFirst determined that the entity had an issue with the Standard by failing to document evidence of its senior management delegation change within thirty calendar days of the effective date of the change. | In light of the nature of the issue, offset by the mitigating factors, ReliabilityFirst determined that this issue posed a minimal, not serious or substantial, risk to the reliability of the bulk power system. The risk posed by the foregoing facts and circumstances was mitigated by the following factors. The issue is a documentation error because although the entity did not document the senior manager delegation change within 30 calendar days, the senior manager delegate did begin performing all delegated senior manager functions. In addition, the entity has no Critical Cyber Assets. | In order to mitigate the issue, the entity documented the senior manager delegation change. During the compliance audit, ReliabilityFirst verified the completion of the entity's mitigating actions.
2011-12-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 6 (RFC_URE6) | NCRXXXXX | RFC2011001123 | CIP-004-3 | R2 | The entity self-reported to ReliabilityFirst a possible issue of CIP-004-3 R2. In the Self-Report, the entity stated that it granted unescorted physical access to Critical Cyber Assets (CCAs) to an employee prior to conducting a personnel risk assessment for that employee and prior to that employee’s completion of the entity's cyber security training. ReliabilityFirst determined that the entity had an issue with CIP-004-3 R2 by failing to train an employee having unescorted physical access to CCAs prior to granting such access to the employee. | In light of the nature of the issue, offset by the mitigating factors, ReliabilityFirst determined that this issue posed a minimal, not serious or substantial, risk to the reliability of the bulk power system. The risk posed by the foregoing facts and circumstances was mitigated by the following factors. Although the entity granted the employee with unescorted physical access, the employee was stationed at a remote site and was not aware that the entity had granted this access. The employee made no attempt to nor did the employee enter any Physical Security Perimeters. Additionally, the entity performed a personnel risk assessment for the employee after granting the access and discovered no issues. Finally, the elapsed time from the entity granting access to the entity’s discovery and revocation of such access was less than two business days. | The entity submitted a mitigation plan, in which it memorialized the actions it took to address the issue, to ReliabilityFirst. The entity updated its access request database to prevent future accidental approvals for authorized cyber or authorized unescorted physical access to CCAs.
2011-12-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 6 (RFC_URE6) | NCRXXXXX | RFC2011001124 | CIP-004-3 | R3 | The entity self-reported to ReliabilityFirst a possible issue of CIP-004-3 R3. In the Self-Report, the entity stated that it granted unescorted physical access to Critical Cyber Assets (CCAs) to an employee prior to conducting a personnel risk assessment for that employee and prior to that employee’s completion of the entity's cyber security training. ReliabilityFirst determined that the entity had an issue with CIP-004-3 R3 by failing to conduct a personnel risk assessment for an employee, prior to granting the employee authorized unescorted physical access to CCAs. | In light of the nature of the issue, offset by the mitigating factors, ReliabilityFirst determined that this issue posed a minimal, not serious or substantial, risk to the reliability of the bulk power system. The risk posed by the foregoing facts and circumstances was mitigated by the following factors. Although the entity granted the employee with unescorted physical access, the employee was stationed at a remote site and was not aware that the entity had granted this access. The employee made no attempt to nor did the employee enter any Physical Security Perimeters. Additionally, the entity performed a personnel risk assessment for the employee after granting the access and discovered no issues. Finally, the elapsed time from the entity granting access to the entity’s discovery and revocation of such access was less than two business days. | The entity submitted a mitigation plan, in which it memorialized the actions it took to address the issue, to ReliabilityFirst. The entity updated its access request database to prevent future accidental approvals for authorized cyber or authorized unescorted physical access to CCAs.
2011-12-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 8 (RFC_URE8) | NCRXXXXX | RFC2011001188 | CIP-002-1 | R3 | ReliabilityFirst conducted a compliance audit and discovered a possible issue with CIP-002-1 R3 for the entity. The entity determined, through annual application of its risk-based assessment methodology (RBAM), that it had no Critical Assets, and developed a null list reflecting that fact as required by CIP-002-1 R2; however, the entity did not create a null list to reflect the fact that it had no Critical Cyber Assets (CCAs), as required by CIP-002-1 R3. | In light of the nature of the issue, offset by the mitigating factors, ReliabilityFirst determined that this issue posed a minimal, not serious or substantial, risk to the reliability of the bulk power system (BPS). The risk to the reliability of the BPS was mitigated by the following factors. The entity determined through the annual application of its RBAM that it had no Cyber Assets and no CCAs. The issue is a documentation errors because the entity did not create a null list of CCAs, in addition to the null list it created for Cyber Assets. | The entity submitted a letter certifying that it completed the necessary mitigating activities, along with evidence of completion, to ReliabilityFirst. Specifically, the entity provided ReliabilityFirst with a copy of its null list of CCAs, which documents that it has no CCAs.
2011-12-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 8 (RFC_URE8) | NCRXXXXX | RFC2011001189 | CIP-002-1 | R4 | ReliabilityFirst conducted a compliance audit of the entity and discovered a possible issue with CIP-002-1 R4. The entity did not annually approve its Critical Cyber Assets (CCAs) list (even if the list is null) as required by CIP-002-1 R4, because it never developed a null list of CCAs pursuant to CIP-002-1 R3. | In light of the nature of the issue, offset by the mitigating factors, ReliabilityFirst determined that this issue posed a minimal, not serious or substantial, risk to the reliability of the bulk power system (BPS). The risk to the reliability of the BPS was mitigated by the following factors. The entity determined through the annual application of its RBAM that it has no Cyber Assets and no CCAs. This issue is a documentation error because the entity did not create a null list of CCAs, in addition to the null list it created for Cyber Assets, therefore, the entity could not annually approve a null list of CCAs. | The entity submitted a letter certifying that it completed the necessary mitigating activities, along with evidence of completion, to ReliabilityFirst. Specifically, the entity provided ReliabilityFirst with a copy of its null list of CCAs, which the entity will approve annually. ReliabilityFirst reviewed the evidence the entity submitted, and determined that the entity successfully completed all mitigating actions necessary to resolve the issue of CIP-002-1 R4.
2011-12-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 9 (RFC_URE9) | NCRXXXXX | RFC2011001190 | CIP-002-1 | R3 | ReliabilityFirst conducted a compliance audit and discovered a possible issue with CIP-002-1 R3 for the entity. The entity determined, through annual application of its risk-based assessment methodology (RBAM), that they have no Critical Assets, and developed a null list reflecting that fact as required by CIP-002-1 R2; however, the entity did not create a null list to reflect the fact that it has no Critical Cyber Assets (CCAs), as required by CIP-002-1 R3. | In light of the nature of the issue, offset by the mitigating factors, ReliabilityFirst determined that this issue posed a minimal, not serious or substantial, risk to the reliability of the bulk power system (BPS). The risk to the reliability of the BPS was mitigated by the following factors. The entity determined through the annual application of its RBAM that it has no Cyber Assets and no CCAs. This issue is a documentation error because the entity did not create a null list of CCAs, in addition to the null list it created for Cyber Assets. | The entity submitted a letter certifying that they completed the necessary mitigating activities, along with evidence of completion, to ReliabilityFirst. Specifically, the entity provided ReliabilityFirst with a copy of its null list of CCAs, which documents that the entity has no CCAs.
2011-12-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 9 (RFC_URE9) | NCRXXXXX | RFC2011001191 | CIP-002-1 | R4 | ReliabilityFirst conducted a compliance audit of the entity and discovered a possible issue with CIP-002-1 R4. The entity did not annually approve its Critical Cyber Assets (CCAs) list (even if the list is null) as required by CIP-002-1 R4, because it never developed a null list of CCAs pursuant to CIP-002-1 R3. | In light of the nature of the issue, offset by the mitigating factors, ReliabilityFirst determined that this issue posed a minimal, not serious or substantial, risk to the reliability of the bulk power system (BPS). The risk to the reliability of the BPS was mitigated by the following factors. The entity determined through the annual application of its RBAM that it has no Cyber Assets and no Critical Cyber Assets (CCAs). This issue is a documentation error because the entity did not create a null list of CCAs, in addition to the null list it created for Cyber Assets, therefore, the entity could not annually approve a null list of CCAs. | The entity submitted a letter certifying that it completed the necessary mitigating activities, along with evidence of completion, to ReliabilityFirst. Specifically, the entity provided ReliabilityFirst with a copy of its null list of CCAs, which the entity will approve annually. ReliabilityFirst reviewed the evidence the entity submitted, and determined that the entity successfully completed all mitigating actions necessary to resolve the issue of CIP-002-1 R4.
2011-12-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP201000235 | CIP-002-1 | R3 | During a Spot Check, SPP RE’s CIP audit team discovered that SPP RE_URE1's Critical Cyber Asset (CCA) list contained substantive errors, indicating an issue with this Standard. SPP RE_URE1 had incorrectly classified a host integration server as a CCA. In addition, several systems that were shown to be out-of-service on the prior year's CCA list were shown back in service on the next year's CCA list, even though those systems remained out of service. | SPP RE determined that SPP RE_URE1’s issue with CIP-002-1 R3 did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) and posed only a minimal risk to the BPS. SPP RE_URE1’s error to the CCA list was that it included an additional asset rather than omitted an asset that should have been deemed a CCA. Additionally, no “out of service” CCAs listed on the CCA “in-service” list was ever actually put back into service between the two years. SPP RE determined that this was a documentation issue only. As such, there were no CCAs that were left unprotected, and the risk to the BPS was minimal. | SPP RE_URE1 re-assessed its CCA list and removed the host integration server and other systems shown as out-of-service on the prior year's CCA list and had its chief security officer approve the new list. This issue was assigned NERC Mitigation Plan ID MIT-08-2747. SPP RE_URE1 certified that mitigation was complete, and SPP RE verified completion.
2011-12-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPPRE_URE2) | NCRXXXXX | SPP201000327 | CIP-004-1 | R2 (R2.1, R2.2.1) | During a Spot Check, SPP RE determined that SPPRE_URE2 had an issue with CIP-004-1 R2.1 and R2.2.1. Regarding R2.1, 3.2% of randomly sampled personnel with authorized cyber or authorized unescorted physical access to Critical Cyber Assets (CCAs) were not trained within 90 days of such authorization. An SPP RE Enforcement’s subsequent survey of 100% of SPPRE_URE2’s employees with authorized cyber or authorized unescorted physical access revealed that a total of 4% of SPPRE_URE2’s entire company had not received training within 90 days of being granted access. Regarding R2.2.1, although SPPRE_URE2's EMS/SCADA vendor conducted its own cyber security training for its support personnel, two year's of annual training did not include the proper use of CCAs, as required by this Standard. | SPP RE has determined that SPPRE_URE2’s issue with CIP-004-1 R2 posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System. Regarding R2.1, the 4% of individuals who had not received training within 90 days from authorized access were trusted employees with no disciplinary actions who had received the required cyber security training by early in 2010. This was confirmed by Personnel Risk Assessments (PRAs) that were being conducted during this time by SPPRE_URE2. Regarding R2.2.1, while the EMS/SCADA vendor was not trained on the proper uses of SPPRE_URE2's CCAs, the small group of vendor support personnel received comprehensive training on CIP Standards and work in a position that requires technical knowledge inclusive of cyber security best practices. As such, they fully understood the implications of their access to SPPRE_URE2's CCAs. | Regarding R2.1, as early in 2010, SPPRE_URE2 had trained all personnel with authorized cyber or authorized unescorted physical access to CCAs. SPPRE_URE2 also implemented a NERC CIP flag in its HR system that keeps track of all personnel with authorized access to SPPRE_URE2's CCAs. This new system allows SPPRE_URE2 to cross reference training records in order to verify that all affected personnel has received cyber security training within required intervals. Regarding R2.2.1, SPPRE_URE2 issued its EMS/SCADA vendor that addresses the proper use of its CCAs. Vendors support personnel must now acknowledge reading and understanding this summary before being granted cyber access. This issue was assigned NERC Mitigation Plan ID MIT-08-3014. SPPRE_URE2 certified that mitigation was complete, and SPP RE verified completion.
2011-12-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 3 (SPPRE_URE3) | NCRXXXXX | SPP201100664 | CIP-007-3 | R5.3 | SPP RE_URE3 Self-Reported an issue with CIP-007-1 R5.3. SPP RE_URE3 submitted three Technical Feasibility Exception (TFE) requests, regarding its Oracle database server and compliance with CIP-007-1 R5.3.1, R5.3.2, and R5.3.3. SPP RE approved the TFE requests. The TFEs were necessary because the Oracle database server had a hardcoded password that made it operationally infeasible to comply with CIP-007-1 R5.3. SPP RE_URE3 had anticipated that it would resolve its issues with the database password before its TFEs expired, with the resolution having the ability to comply with all requirements of CIP-007-3 R5.3. However, in mid-2011, SPP RE_URE3 had not yet resolved its database password issue, and the three TFEs pertaining to CIP-007-3 R5.3 expired. SPP RE_URE3 filed new TFEs for CIP-007-3 R5.3. | SPP RE has determined that SPP RE_URE3’s issue with CIP-007-3 R5.3 posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). Although SPP RE_URE3 allowed the three TFEs pertaining to CIP-007-3 R5.3 to expire, SPP RE_URE3 continued the compensating and mitigating measures described in its TFEs. Namely, SPP RE_URE3's database user password is only accessible to personnel with a “need to know” status, and all personnel with a “need to know” status have attended security awareness training and have had background checks performed. Additionally, all scripts containing the password are within a secured ESP. Furthermore, the gap between the expiration of the TFEs that were filed and the date that SPP RE_URE3 resubmitted TFEs for the Oracle database password lasted only about one month. Lastly, SPP RE_URE3’s resubmitted TFEs with the same compensating and mitigating measures that it had in place with the TFEs filed and the same measures it had continued to perform during the one-month gap in which it did not have valid TFEs. | SPP RE_URE3 filed another TFE to cover the period between the newly filed TFE request and the date of implementation of its new SCADA system and historian server. This issue was assigned NERC Mitigation Plan ID SPPMIT005948. SPP RE_URE3 certified that mitigation was complete.
2011-12-30 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE201100381 | CIP-002-3 | R1 | This issue was discovered through an Audit. Texas RE determined that for the audit period, Texas RE_URE1's Risk-Based Assessment Methodology did not consider applicable assets of its Qualified Scheduling Entity. The Qualified Scheduling Entity was under contract to perform communications with the Reliability Coordinator and the Balancing Authority on behalf of Texas RE_URE1. | This issue did not pose a serious or substantial risk and posed a minimal risk to the bulk power system because Texas RE_URE1 did not have any Critical Assets. Further, Texas RE_URE1 found no Critical Assets after it modified and implemented its Risk-Based Asset Methodology to address this issue. Texas RE_URE1's Risk-Based Asset Methodology was very thorough and the exclusion of the Qualified Scheduling Entity communications was based on the inability of those communications to directly control Texas RE_URE1's generation assets because their control resides within Texas RE_URE1's control rooms. | Texas RE_URE1 mitigated the issue by modifying, approving and implementing its Risk-Based Assessment Methodology to specifically consider the control room functions contracted away to its Qualified Scheduling Entity.
2011-12-30 | TRE_URE1liability Entity (TRE_URE1) | Unidentified Registered Entity 2 (TRE_URE2) | NCRXXXXX | TRE201100350 | CIP-002-2 | R3 | During an Audit, TRE_URE1 found four devices on TRE_URE1_URE2's Critical Cyber Asset (CCA) list to be outside of the Physical Security Perimeter (PSP). TRE_URE1 further determined that the four devices did not belong to the CCA list but were mistakenly added to the list, in violation of this Standard. | This issue did not pose a serious or substantial risk and posed a minimal risk to the bulk power system because the four devices in question were part of a test platform that was not part of any Electronic Security Perimeter (ESP). The devices were mistakenly added to the CCA list and the annual review of the CCA list had not yet occurred for that year. | The CCA list was reviewed and the test platform devices were removed from it.
2011-12-30 | TRE_URE1liability Entity (TRE_URE1) | Unidentified Registered Entity 2 (TRE_URE2) | NCRXXXXX | TRE201100352 | CIP-003-2 | R3 | A Self-Report addressing this issue was submitted to TRE_URE1, after a notification of TRE_URE1's Audit was sent to TRE_URE1_URE2. TRE_URE1_URE2 reported that it did not properly document an exception to its Cyber Security Policy and that the exception was related to the failure to perform monthly ports and services checks according to TRE_URE1_URE2's Desk Procedures and CIP-007. TRE_URE1 determined that the discovery method for this issue was an Audit. | This issue did not pose a serious or substantial risk and posed a minimal risk to the bulk power system because the check of the ports and services that was not performed according to CIP-007, is also required to be performed annually by the Reliability Standards. TRE_URE1_URE2's Desk Procedures require more frequent checks than the annual check required by the Standard. TRE_URE1_URE2 restarted its monthly checks, which are required by its Desk Procedures, before the annual check would have been due. | The required exception document has been completed and approved. Additionally, the management of the responsible department provided additional awareness education and strengthened the language in the TRE_URE1_URE2's procedure documents regarding the process for obtaining an exception when TRE_URE1_URE2 is unable to conform to its Cyber Security Policy.
2011-12-30 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 3 (TRE_URE3) | NCRXXXXX | TRE201000226 | CIP-006-1 | R4.3 | Texas RE_URE3 Self-Reported that it had an issue with CIP-006-1 R4.3 on two specific incidents because Texas RE_URE3 failed to implement manual logging controls for personnel that were granted escorted access to established Physical Security Perimeters (PSPs). | The First Instance: This issue did not pose a serious or substantial risk and had a moderate risk to the bulk power system (BPS) because although there was an issue with proper logging, the employee who entered the PSP of the transmission dispatch center had previously completed background checks. The Second Instance: This issue did not pose a serious or substantial risk and posed a moderate risk to the BPS because although there was an issue with proper logging, on the Second Instance, an IT contractor entering the telecommunications room at the system operator building without having been properly logged into the facility had completed required cyber security training, had a clear background check, and had been granted authorized physical access to the telecommunications room at the same system operator's building. Further, the contractor was escorted by an employee during the entire period. | Email communication was issued to remind Texas RE_URE3 staff of the visitor physical access requirements and processes. In addition, CIP Facility Visitor Log requirements training material and discussion guide were given to staff.
2011-12-30 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 4 (TRE_URE4) | NCRXXXXX | TRE201100268 | CIP-009-2 | R1.1 | Texas RE discovered an issue with this Standard during a Spot Check. Texas RE_URE4’s Recovery Plans did not specifically address varying duration and severity levels that would activate the recovery plan(s). Texas RE found that Texas RE_URE4's recovery plan discusses all exercises and procedures to recover specific Critical Cyber Assets (CCAs) including steps to follow in an event of emergency. The procedure specified that failed cyber assets be replaced immediately and all relevant contact information of personnel necessary for recover specific failures was also included in the procedure. Texas RE_URE4 modified its procedure to include varying duration and severity after Texas RE_URE4 was notified of this finding during a certification process. | This issue did not pose a serious or substantial risk and posed a minimal risk to the bulk power system because Texas RE_URE4's CCA recovery plan was in place and was being annually reviewed. Moreover, specific CCA device failures and the procedure to recover them was specified in detail in the recovery plan. It was specified that the failed device will be repaired or replaced immediately and brought back to service. The notification procedure and contact information of personnel to contact for specific failures was also mentioned in the procedures. | This issue was mitigated in a later recovery plan document once Texas RE_URE4 was notified of the limitations during the certification process. The new Recovery Plans for CCAs address varying duration and severity that would activate the recovery plan(s).
2011-12-30 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 5 (TRE_URE5) | NCRXXXXX | TRE201100338 | CIP-002-3 | R2 | Texas RE discovered this issue during a Spot Check. Texas RE_URE5's current risk-based assessment methodology included a Critical Asset (CA) and Critical Cyber Asset (CCA) list that addressed the current requirement. Texas RE requested an earlier version of the risk-based assessment, CA and CCA list. Texas RE_URE5 failed to provide these documents, indicating an issue with this Standard but Texas RE_URE5’s procedure and CIP Assessment Methodology required an annual review and assessment of CA and CCA's. | This issue did not pose a serious or substantial risk and posed a minimal risk to the bulk power system because Texas RE_URE5 did not and still does not have any CAs and CCAs following the compliance date. | This issue was mitigated when Texas RE_URE5's Critical Asset Methodology (RBAM), CA and CCA list were approved by the senior manager and the application of RBAM resulted in no CA or CCA identification.
2011-12-30 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 5 (TRE_URE5) | NCRXXXXX | TRE201100339 | CIP-002-3 | R3 | Texas RE discovered this issue during a Spot Check. Texas RE_URE5's current risk-based assessment included a Critical Asset (CA) and Critical Cyber Asset (CCA) list that addressed this Standard's requirement. Texas RE requested an earlier version of Texas RE_URE5's risk-based assessment, and CA and CCA lists but Texas RE_URE5 did not provide any, indicating an issue with this Standard. However, Texas RE_URE5’s procedure and CIP Assessment Methodology required an annual review and assessment of CA and CCA's. | This issue did not pose a serious or substantial risk and posed a minimal risk to the bulk power system because Texas RE_URE5 did not and still does not have any CAs or any CCAs following the compliance date. | This issue was mitigated when Texas RE_URE5's Critical Asset Methodology (RBAM), CA and CCA list were approved by the senior manager and the application of RBAM resulted in no CA or CCA identification.
2011-12-30 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 5 (TRE_URE5) | NCRXXXXX | TRE20100340 | CIP-002-3 | R4 | Texas RE discovered this issue at a Spot Check. Texas RE determined that Texas RE_URE5 had an issue with CIP-002-3 R4 because Texas RE_URE5's Critical Asset Methodology (RBAM) was not approved by the Senior Manager nor it was delegated to anyone else to approve it. CA and CCA list were approved by the Senior Manager. | This issue did not pose a serious or substantial risk and posed a minimal risk to the bulk power system because Texas RE_URE5 did not and does not have any Critical Assets or any Critical Cyber Assets. Moreover, RBAM existed but was not officially signed off by the Senior Manager. The RBAM, CA and CCA list were approved by Senior Manager within the Standard's annual requirement. | This issue was mitigated when RBAM, CA and CCA list were approved by the Senior Manager and the application of RBAM resulted in no CA or CCA identification.
2011-12-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201103030 | CIP-004-3 | R4 | WECC_URE1 submitted a Self-Report to WECC. A WECC Subject Matter (SME) contacted WECC_URE1 to discuss its Self-Report. According to the WECC SME, during the discussion WECC_URE1 stated that it failed to review one out of its five access list types in the first quarter of 2011. WECC_URE1’s five access lists are Physical Card key, Physical hard key, electronic supervisory control and data acquisition (SCADA), Physical Access Control Systems, and Access Database. The access list WECC_URE1 failed to review is the "Electronic SCADA" access list. | WECC determined this issue posed minimal risk and not a serious or substantial risk to the reliability of the bulk power system (BPS). While failure to maintain a list of personnel with logical and/or physical access to Critical Cyber Assets (CCAs) could allow malicious logical and/or physical access to CCAs which could compromise the security of such assets essential to the BPS, thereby disrupting the reliable operation of the BPS, in this instance, WECC_URE1 stated that all individuals with access to CCAs had current personnel risk assessments and CIP training, and all CCAs were located in a Physical Security Perimeter and Electronic Security Perimeter and provided the protections of CIP-006 and CIP-005. | WECC_URE1 performed the second and third quarter reviews of 2011.
2011-12-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC201103036 | CIP-004-3 | R4 | WECC_URE2 submitted a Self-Report to WECC. A WECC Subject Matter (SME) contacted WECC_URE2 to discuss its Self-Report. According to the WECC SME, during the discussion WECC_URE2 stated that it failed to review one out of its five access list types in the first quarter of 2011. WECC_URE2’s five access lists are Physical Card key, Physical hard key, electronic supervisory control and data acquisition (SCADA), Physical Access Control Systems, and Access Database. The access list WECC_URE2 failed to review is the "Electronic SCADA" access list. In addition, WECC_URE2 stated that on one occasion it failed to update its access list within seven days of an individual no longer requiring authorized access and failed to revoke access and update is access list for a contractor who no longer required access to Critical Cyber Assets. | WECC determined this issue posed minimal risk and not a serious or substantial risk to the reliability of the bulk power system (BPS). While failure to maintain a list of personnel with logical and/or physical access to Critical Cyber Assets (CCAs) could allow malicious logical and/or physical access to CCAs which could compromise the security of such assets essential to the BPS, thereby disrupting the reliable operation of the BPS, in this instance, WECC_URE2 stated that all individuals with access to CCAs had current personnel risk assessments and CIP training, and all CCAs were located in a Physical Security Perimeter and Electronic Security Perimeter and provided the protections of CIP-006 and CIP-005. | WECC_URE2 performed the second and third quarter reviews of 2011.
2011-11-30 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 2 (FRCC_URE2) | NCRXXXXX | FRCC2011007254 | CIP-006-3c | R1 | During a spot check, FRCC determined that the entity is subject to the Standard. On two separate occasions, when a visitor was granted access to the Physical Security Perimeter (PSP), the entity failed to document that name of the personnel responsible for providing continuous escorting to the visitor as required by its visitor control program for visitors procedure (R1.6). | The remediated issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because the concerned PSP is manned 24 hours a day and seven days a week and on the two instances of the issue the operator did escort the visitor but failed to document the logs. | This issue has been mitigated by the entity by documenting the logs and the mitigation plan includes additional milestones to prevent recurrence by revising its visitor control program for visitors procedure documentation and providing training to all staff responsible for escorting visitors. The entity completed its mitigation plan, as verified by FRCC.
2011-11-30 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO201100262 | CIP-009-1 | R4 | During a Spot Check, MRO discovered that the entity failed to provide backup records of network switches which are classified as Critical Cyber Assets (CCAs) for the previous full calendar year in its recovery plan for CCAs. Due to the “First In First Out” (FIFO) storage method utilized by the entity's backup system, previous switch configurations are “rolled off” after a certain number of new configuration versions are backed up. Furthermore, the entity’s backup solution only retains the data for 90 days once it has been removed from the actual server. While the entity could demonstrate that its backup system was performing its intended function throughout the time period covered by the Spot Check, the system’s design could not produce evidence that a backup was performed on a specific date and time. | The remediated issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because all of the appropriate backups of information required to successfully restore the entity's CCAs were being performed, even though documentation was found to be inadequate. | The entity established and documented a process to record and retain documentation demonstrating the successful archival of network switches data backup. To confirm the backup is being performed as required the system automatically issues a change control ticket when the backup is completed. The ticket is assigned to a member of the network team who will verify the archival process was successful. The entity completed its mitigation plan, as verified by MRO.
2011-11-30 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 3 (MRO_URE3) | NCRXXXXX | MRO201100251 | CIP-006-1 | R1; R1.1 | During a CIP Spot Check, conducted between August 16, 2010 through August 26, 2010, MRO determined that the entity, as a Responsible Entity registered as a Balancing Authority, Generator Operator, Generator Owner, Load-Serving Entity, Transmission Operator and Transmission Owner, failed to have a completely enclosed Physical Security Perimeter (PSP) with a completely enclosed (“six-wall”) border as part of its physical security plan. The extent of the undefined border was at least the length of the door and about 1.5 feet in depth. The entity mitigated the PSP gap during the Spot Check and MRO reviewed and verified the mitigating measures. | The remediated issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because multiple layers of security would need to be penetrated before gaining access to the PSPs. One of the PSPs is manned 24 hours per day, seven days per week. Both facilities contain Cyber Assets that have strong electronic protective measures in place. Specifically, at one PSP, there are at least ten security control types, including combinations of card readers, bio readers, mantrap, door status switches, human observer, proprietary keys, high security fence, padlocks, cameras and anti-tailgating devices. All paths have at least four security layers and at least three different types of security controls within those layers. At the other PSP, there are at least five security control types, including combinations of card readers, mantraps, door status switches, human observer and proprietary keys. All paths have at least four security layers to infiltrate before gaining access to the PSPs. | The entity performed the following to mitigate the remediated issue: (1) placed heavy wire mesh over the opening; (2) replaced the flexible ducts with rigid duct work; (3) developed a guide document for its staff to assist with the identification of “six-wall" borders and access points. The entity completed its mitigation plan, as verified by MRO.
2011-11-30 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 4 (MRO_URE4) | NCRXXXXX | MRO201000200 | CIP-004-1 | R2; R2.1; R2.3 | During a CIP Spot Check, MRO determined that the entity had established, documented and maintained an annual cyber security training (CST) program for personnel having authorized cyber or authorized unescorted physical access to Critical Cyber Assets (CCAs); however, the entity's documentation was not sufficient to demonstrate that all personnel having authorized cyber or authorized unescorted physical access to CCAs had completed the training. Although the entity maintains that the training was provided prior to granting access to those individuals, who were provided paper copies of the training, the entity's records did not clearly identify that those individuals had received the training within ninety calendar days of such authorization (R2.1) and conducted at least annually, including the date the training was completed and attendance records (R2.3). | The remediated issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because this was a documentation deficiency where the entity's process did not clearly identify the individuals receiving the training. The entity provided annual training to all personnel with authorized cyber or authorized unescorted physical access to CCAs in 2010 and again in 2011. | The entity performed the following actions to mitigate the remediated issue: (1) updated its CIP personnel system to automatically read computer based testing results and track the completion date; (2) updated the CIP personnel system to automatically send an email out to employees and their supervisors when retraining is required; (3) retrained all employees with security access via the computer-based training (CBT) method; (4) retrained and proctored all contractors with access to CCAs; and (5) updated its CIP-004 R2 corporate document with the new training processes for employees and contractors. The entity completed its mitigation plan, as verified by MRO.
2011-11-30 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 4 (MRO_URE4) | NCRXXXXX | MRO201000201 | CIP-004-1 | R3 | During a CIP Spot Check, MRO determined that the entity had an incomplete personnel risk assessment for one employee and could not corroborate statements that personnel risk assessments had been conducted within thirty days of such personnel being granted authorized cyber or authorized unescorted physical access to Critical Cyber Assets and updated at least every seven years or for cause, pursuant to the program required in R3 for three contractors. The entity had relied upon unverified attestations from the contractors. | The remediated issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because although only a partial record was available, the personnel risk assessment for the employee had been completed. The entity conducted a new personnel risk assessment for the employee and found no issues with it. Additionally, the entity verified the personnel risk assessments for the three contractors and found no issues with them. | The entity performed the following actions to mitigate the remediated issue: (1) updated personnel risk assessments from 2004 and 2005 to address the seven-year criminal background issue and provide a list of employees with access and associated background check dates; (2) updated its contract language to assure that background check requirements meeting the relevant CIP standards for contractors and vendors are clearly set forth in the contract; (3) audited all personnel risk assessment records for contractors and provided a list of contractors with unescorted access and dates of completed and verified background check dates; and (4) updated its CIP-004 R3 corporate document with the background check verification processes for employees and contractors. The entity completed its mitigation plan, as verified by MRO.
2011-11-30 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 4 (MRO_URE4) | NCRXXXXX | MRO201000202 | CIP-004-1 | R4; R4.1; R4.2 | During a CIP Spot Check, MRO determined that although the entity maintains a list of individuals with physical and cyber access to Critical Cyber Assets (CCAs) via its CIP personnel program, the entity failed to demonstrate that it had a process in place to be notified by its vendors when an individual has been terminated by the vendor, either with or without cause and update and maintain the access list accordingly within seven calendar days of any personnel change as required by CIP-004-1 R4.1. As a result, access was not revoked for three contractors who no longer required access within seven calendar days as required by CIP-004-1 R4.2. | The remediated issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because none of the contractors had any access to the entity's facilities after they were terminated. In addition, none of the contractors had electronic access to the entity's CCAs. In addition, the failure of the vendor to report the employees' dismissal did not account for any security-related events. | The entity performed the following actions to mitigate the remediated issue: (1) the criminal background screening requirements section of the entity's contract service agreement was revised to include provisions for notifying the entity when unescorted access is no longer required or contractor’s employee is terminated for cause; (2) CIP corporate annual training was updated with access removal requirements for employees and contractors and vendors and all employees and contractors and vendors were retrained to receive the updated training; and (3) contractors and vendors and their entity sponsors will be notified of the requirements for authorized unescorted access removal on a semi-annual basis. The entity completed its mitigation plan, as verified by MRO.
2011-11-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2011007276 | CIP-004-1 | R2; R2.1 | After reviewing a Self-Report submitted by the entity for a possible violation of CIP-007-1 R4, NPCC, in its investigation, determined that the entity was noncompliant with CIP-004-1 R2 because personnel having access to Critical Cyber Assets (CCAs), including contractors and service vendors, were not trained prior to the CIP Implementation Table date on the entity's annual cyber security training program. The entity discovered that three employees continued to have physical access to CCAs for a time after the compliance enforcement date without having completed cyber security training. At the time of the Self-Report, the cyber security training had already been completed for the three employees. The duration of physical access past the compliance enforcement date without having completed the cyber security training was 101 days, 105 days and 111 days for the three employees. | NPCC determined that there was a minimal risk to the reliability of the bulk power system (BPS), and the issue did not pose a serious or substantial risk. There was no actual impact to the BPS as there were no intentional or unintentional actions committed by any of the three employees as a result of not completing cyber security training before having physical access granted. There was minimal potential impact because the employees accessed areas that were staffed 24 hours a day, seven days a week. These areas were also monitored by cameras while access to those areas was logged. | 1. The entity provided NPCC with various documents and spreadsheets showing that it had performed a full review of all PRA, cyber training and access list records going back to the compliance enforcement date. 2. The entity provided NPCC with revised policies associated with termination of employment and the protection of critical energy infrastructure and information. 3. The entity provided NPCC with documentation that the revised policies and future expectations had been shared with the relevant business units. The mitigation activities were completed as verified by NPCC.
2011-11-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2011007277 | CIP-004-1 | R3 | After reviewing a Self-Report submitted by the entity for a possible violation of CIP-007-1 R4, NPCC, in its investigation, determined that the entity was noncompliant with CIP-004-1 R3 because a personnel risk assessment (PRA) was not conducted prior to the CIP Implementation Table date for personnel that had already been granted access to Critical Cyber Assets. The entity discovered that two employees continued to have physical access to CCA for a time after the compliance enforcement date without a completed PRA. At the time of the Self-Report, the PRA had already been completed for the two employees. The two employees continued to have physical access to Critical Cyber Assets after the compliance enforcement date for differing durations (8 months and 7.75 months) until the required PRAs were completed. | NPCC determined that there was a minimal risk to the reliability of the bulk power system (BPS), and the issue did not pose a serious or substantial risk. There was no actual impact to the BPS as there were no intentional or unintentional actions committed by the two identified employees as a result of a PRA not being completed before having physical access granted. There was minimal potential impact because both employees accessed areas that were staffed 24 hours a day, seven days a week and monitored by cameras and access to those areas was logged. | 1. The entity provided NPCC with various documents and spreadsheets showing that it had performed a full review of all PRA, cyber training and access list records going back to the compliance enforcement date. 2. The entity provided NPCC with revised policies associated with termination of employment and the protection of critical energy infrastructure and information. 3. The entity provided NPCC with documentation that the revised policies and future expectations had been shared with the relevant business units. The mitigation activities were completed as verified by NPCC.
2011-11-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2011007278 | CIP-004-1 | R4; R4.1; R4.2 | The entity self-reported noncompliance with CIP-004-1 R4. The entity discovered that reviews of Physical Security Perimeter/Electronic Security Perimeter (PSP/ESP) access rights list did not occur in such fashion after the compliance enforcement date to ensure that revocation of access rights were completed as per R4.1. The entity is a CIP Implementation Table 4 entity with a 12/5/09 due date for becoming compliant. The entity did not review the list(s) of its personnel who have access to Critical Cyber Assets quarterly, and update the list(s) within seven calendar days of any change of personnel with such access to CCAs, or any change in the access rights of such personnel, nor ensure access list(s) for contractors and service vendors were properly maintained. As a result of not reviewing access rights within a regular fashion after the compliance enforcement date, three instances were found that exceeded the 7-day revocation limit for personnel who no longer require such access to CCAs as per R4.2. The duration of the three instances were 2 days, 27 days and 14 months. | NPCC determined that there was a minimal risk to the reliability of the bulk power system (BPS), and the issue did not pose a serious or substantial risk. There was no actual impact to the BPS as there were no access attempts made by the employees after the date that rights were no longer needed. There was minimal potential impact related to the first identified employee as the entity was only 2 days late revoking access. There was minimal potential impact related to the second identified employee. Although SCADA access for this employee still existed, he would have had to have an escort into the control room (his physical access had already been revoked) and remain there unsupervised to log onto an operating console. There was minimal potential impact related to the third identified employee because physical access rights were revoked in 2008 and would have required an escort into the entity's facilities before gaining access to use the unrevoked Windows administrative rights. | 1. The entity provided NPCC with various documents and spreadsheets showing that it had performed a full review of all PRA, cyber training and access list records going back to the compliance enforcement date. 2. The entity provided NPCC with revised policies associated with termination of employment and the protection of critical energy infrastructure and information. 3. The entity provided NPCC with documentation that the revised policies and future expectations had been shared with the relevant business units. The mitigation activities were completed as verified by NPCC.
2011-11-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC2011007273 | CIP-007-1 | R4 | The entity self-reported non-compliance with CIP-007-1 R4 stemming from the entity’s failure to timely submit Technical Feasibility Exception (TFE) requests in accordance with NERC procedures. The TFE was requested because malware and anti-virus software cannot be installed on several assets. There were 15 late TFE requests of which 14 were filed 45 days late. The TFE Part A approval for all was granted by NPCC 4 days later. | NPCC determined that there was a minimal risk to the reliability of the bulk power system, and the issue did not pose a serious or substantial risk. The entity's system is structured with intrusion prevention sensors at the network and host level, hardened operating systems, strong account management, logging for system configuration changes, and periodic vulnerability scans which are run on the devices in question. These compensating measures were in place well before the past due date for TFE request submittals to NPCC. | The TFE Part A approval was granted by NPCC. The approved TFE requests are open-ended because the hardened operating system in question does not support third party software.
2011-11-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 2 (NPCC_URE2) | NCRXXXXX | NPCC2011007730 | CIP-004-1 | R4; R4.1 | The entity self-reported non-compliance with CIP-004-1 R4. The entity, in correspondence with its service company affiliate IT compliance office, discovered that Critical Cyber Asset access lists associated with privileged users in the affiliate IT group were reviewed on an annual basis instead of a quarterly basis as required by R4.1. The affiliate's IT group documents the approved access to the server, Human Machine Interface (HMI) PCs, and network switches. The duration of this issue is 21 months which concluded with the verified end date of mitigation activities. | NPCC determined that there was a minimal risk to the reliability of the bulk power system (BPS), and the issue did not pose a serious or substantial risk. There was no actual impact to the BPS as there were no intentional or unintentional actions committed by the privileged users in the affiliate IT group due to the lack of quarterly access review. There was minimal potential impact because system logs are generated on a continual basis and reviewed every 90 days. Such log review includes validation of users who accessed or attempted access to the server, HMI PCs and network switches. In addition, user access can only be granted via an IT request form and is rescinded upon termination or change of duties. The HMI PCs require physical access to be used. Each PC is located within a defined PSP which requires authorized unescorted PSP access which is reviewed on a monthly basis. | 1. The entity provided documentation that the IT compliance office was established. 2. The entity provided documentation from the responsible managers that the quarterly access review process had been documented and was completed for first quarter of the year for the server, the HMI PCs, and the network switches. The mitigation activities were completed as verified by NPCC.
2011-11-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 3 (NPCC_URE3) | NCRXXXXX | NPCC2011007728 | CIP-004-1 | R4; R4.1 | The entity self-reported non-compliance with CIP-004-1 R4. The entity, in correspondence with its service company affiliate IT compliance office, discovered that Critical Cyber Asset access lists associated with privileged users in the affiliate IT group were reviewed on an annual basis instead of a quarterly basis as required by R4.1. The affiliate's IT group documents the approved access to the server and network switches. The duration of this issue is 15 months which concluded with the verified end date of mitigation activities. | NPCC determined that there was a minimal risk to the reliability of the bulk power system (BPS), and the issue did not pose a serious or substantial risk. There was no actual impact to the BPS as there were no intentional or unintentional actions committed by the privileged users in the affiliate IT group due to the lack of quarterly access review. There was minimal potential impact because system logs are generated on a continual basis and reviewed every 90 days. Such log review includes validation of users who accessed or attempted access to the server and network switches. In addition, user access can only be granted access via an IT request form which is rescinded upon termination or change of duties. | 1. The entity provided documentation that the IT compliance office was established. 2. The entity provided documentation from the responsible managers that the quarterly access review process had been documented and was completed for first quarter of the year for the server and the network switches. The mitigation activities were completed as verified by NPCC.
2011-11-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 4 (NPCC_URE4) | NCRXXXXX | NPCC2011007729 | CIP-004-1 | R4; R4.1 | The entity self-reported non-compliance with CIP-004-1 R4. The entity, in correspondence with its service company affiliate IT compliance office, discovered that Critical Cyber Asset access lists associated with privileged users in the affiliate IT group were reviewed on an annual basis instead of a quarterly basis as required by R4.1. The affiliate's IT group documents the approved access to the server and network switches. The duration of this issue is 15 months which concluded with the verified end date of mitigation activities. | NPCC determined that there was a minimal risk to the reliability of the bulk power system (BPS), and the issue did not pose a serious or substantial risk. There was no actual impact to the BPS as there were no intentional or unintentional actions committed by the privileged users in the affiliate IT group due to the lack of quarterly access review. There was minimal potential impact because system logs are generated on a continual basis and reviewed every 90 days. Such log review includes validation of users who accessed or attempted access to the server and network switches. In addition, user access can only be granted access via an IT request form which is rescinded upon termination or change of duties. | 1. The entity provided documentation that the IT compliance office was established. 2. The entity provided documentation from the responsible managers that the quarterly access review process had been documented and was completed for first quarter of the year for the server and the network switches. The mitigation activities were completed as verified by NPCC.
2011-11-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC2011001000 | CIP-007-3 | R4 | The entity is subject to compliance with CIP-007-3 R4. The entity submitted a Self-Report to ReliabilityFirst identifying an issue with CIP-007-3 R4. The entity did not use anti-virus software and other malware prevention software for eight Critical Cyber Assets (CCAs), as required by CIP-007-3 R4. The entity believed the eight CCAs were integrated components of the servers on which they reside and, therefore, did not require separate anti-virus software or other malware prevention tools; however, six of these CCAs were self-contained modules within the server that provide a separate network connection for personnel to remotely manage the server under emergency conditions. The remaining two CCAs run directly on server hardware without requiring an additional underlying operating system. These characteristics of the eight CCAs necessitated that they have anti-virus software and other malware prevention tools. According to the entity, these eight CCAs were incapable of using anti-virus software and other malware prevention tools but the entity did not request a Technical Feasibility Exception (TFE) from ReliabilityFirst for the eight CCAs. ReliabilityFirst determined the entity failed to use anti-virus software and other malware prevention tools pursuant to CIP-007-3 R4 and did not submit TFE requests until 13 months after the compliance enforcement date. | In light of the nature of the issue, offset by the mitigating factors, ReliabilityFirst determined that this issue posed a minimal risk to the reliability of the bulk power system (BPS), and did not pose a serious or substantial risk. The risk to the reliability of the BPS was mitigated by the fact that the entity had compensating measures in place to meet the intent of CIP-007 R4 prior to the mandatory compliance date. Specifically, the entity installed firewalls at the perimeter of the Electronic Security Perimeter with an intrusion prevention system that can detect and prevent many types of malware from propagating. The entity also installed virus protection on workstations and servers as well as firewall software on its workstations. Passwords for the CCAs are stored securely in a server password database that is restricted to authorized personnel only. Finally, administrative access to the CCAs is limited to a small group of support personnel to further minimize risk exposure. | The entity mitigated the issue by submitting TFE requests concerning the eight Critical Cyber Assets (CCAs) at issue to ReliabilityFirst, which were subsequently accepted and approved by ReliabilityFirst. The entity completed mitigation activities for the issue.
2011-11-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC201100937 | CIP-002-2 | R1; R1.1 | The entity is subject to compliance with CIP-002-2 R1. The entity self-reported an issue with CIP-002-2 R1.1 to ReliabilityFirst. The entity determined it did not include evaluation criteria in its risk-based methodology (RBAM). The entity’s evaluation criteria included engineering studies and discussions with subject matter experts. The entity made references in its RBAM to engineering study procedures, but did not include the actual evaluation criteria in its RBAM. ReliabilityFirst determined that the entity failed to include evaluation criteria in its RBAM, pursuant to CIP-002-2 R1.1. | In light of the nature of the issue, offset by the mitigating factors, ReliabilityFirst determined that this issue posed a minimal risk to the reliability of the bulk power system (BPS), and did not pose a serious or substantial risk. The risk to the reliability of the BPS was mitigated by the fact that the issue was administrative in nature. It was administrative because although the entity failed to document its evaluation criteria in its RBAM, it did evaluate all its assets according to engineering studies and discussions with subject matter experts. Further, the entity did not identify any new facilities or change the designation of previously identified facilities from Critical Assets after it included the evaluation criteria required by CIP-002-2 R1.1 in its RBAM. | The entity performed the following mitigating activities. The entity documented the evaluation criteria in its RBAM pursuant to CIP-002-2 R1.1. The entity also notified all personnel involved in managing and using the RBAM of the updates. The entity completed mitigation activities for the issue.
2011-11-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 4 (RFC_URE4) | NCRXXXXX | RFC201100938 | CIP-002-2 | R1; R1.1 | The entity is subject to compliance with CIP-002-2 R1. The entity self-reported an issue with CIP-002-2 R1 to ReliabilityFirst. The entity determined that it did not include evaluation criteria in its risk-based methodology (RBAM). The entity’s evaluation criteria included engineering studies and discussions with subject matter experts. The entity made references in its RBAM to engineering study procedures, but did not include the actual evaluation criteria in its RBAM. ReliabilityFirst determined that the entity failed to include evaluation criteria in its RBAM pursuant to CIP-002-2 R1.1. | In light of the nature of the issue, offset by the mitigating factors, ReliabilityFirst determined that this issue posed a minimal risk to the reliability of the bulk power system (BPS), and did not pose a serious or substantial risk. The risk to the reliability of the BPS was mitigated by the fact that the issue was administrative in nature. It was administrative because although the entity failed to document its evaluation criteria in its RBAM, it did evaluate all its assets according to engineering studies and discussions with subject matter experts. Further, the entity did not identify any new facilities or change the designation of previously identified facilities from Critical Assets after it included the evaluation criteria required by CIP-002-2 R1.1 in its RBAM. | The entity performed the following mitigating activities. The entity documented the evaluation criteria in its RBAM pursuant to CIP-002-2 R1.1. The entity also notified all personnel involved in managing and using the RBAM of the updates. The entity completed mitigation activities for the issue.
2011-11-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 5 (RFC_URE5) | NCRXXXXX | RFC201100910 | CIP-002-2 | R1 | The entity is subject to compliance with CIP-002-2 R1. The entity self-certified non-compliance with CIP-002-2 R1 to ReliabilityFirst. The entity determined it did not include evaluation criteria in its risk-based methodology (RBAM). The entity’s evaluation criteria included engineering studies and discussions with subject matter experts. The entity made references in its RBAM to engineering study procedures, but did not include the actual evaluation criteria in its RBAM. ReliabilityFirst determined that the entity failed to include evaluation criteria in its RBAM pursuant to CIP-002-2 R1.1. | In light of the nature of the issue offset by the mitigating factors, ReliabilityFirst determined that this issue posed a minimal risk to the reliability of the bulk power system (BPS), and did not pose a serious or substantial risk. The risk to the reliability of the BPS was mitigated by the fact that the issue is the result of a documentation error. It is a documentation error because the entity did evaluate all its assets according to engineering studies and discussions with subject matter experts, but failed to document this evaluation. Further, the entity did not identify any new facilities or change the designation of previously identified facilities from Critical Assets after it included the evaluation criteria required by CIP-002-2 R1.1 in its RBAM. | The entity performed the following mitigating activities. The entity documented the evaluation criteria in its RBAM pursuant to CIP-002-2 R1.1. The entity also notified all personnel involved in managing and using the RBAM of the updates. The entity completed mitigation activities for the issue.
2011-11-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 5 (RFC_URE5) | NCRXXXXX | RFC201100911 | CIP-003-2 | R5 | The entity is subject to compliance with CIP-003-2 R5. The entity self-certified non-compliance with CIP-003-2 R5 to ReliabilityFirst. The entity determined it did not document its program for managing access to protected Critical Cyber Asset (CCA) information pursuant to CIP-003-2 R5. Additionally, the entity did not maintain a list of designated personnel responsible for authorizing logical or physical access to protected information pursuant to CIP-003-2 R5.1. ReliabilityFirst determined that the entity failed to document a program for managing access to protected CCA information and failed to maintain a list of designated personnel responsible for authorizing logical or physical access to protected information. | In light of the nature of the issue, offset by the mitigating factors, ReliabilityFirst determined that this issue posed a minimal risk to the reliability of the bulk power system (BPS), and did not pose a serious or substantial risk. The risk to the reliability of the BPS was mitigated by the fact that the issue was a result of the entity’s failure to document its program for managing access to CCAs information. It was a documentation failure because the entity had access controls in place during the duration of the issue which limited individuals’ access to information regarding CCAs. The entity had physical and electronic access controls surrounding all information regarding CCAs that limited access to only authorized personnel. This included electronic access control lists as well as limiting physical access to badge access rooms only to individuals who had completed CIP training and a personnel risk assessment (PRA) in accordance with the entity's procedures. Also, the entity delegated authorizing responsibility to designated personnel; however, the entity failed to document a list of those responsible personnel. | The entity performed the following mitigating activities. The entity developed a list of designated personnel responsible for authorizing logical and physical access to protected CCAs information. The entity also made changes to its procedures in order to include procedures to manage access to protected CCA information. The entity communicated all updates to its procedures on managing protected CCA information with relevant personnel. The entity completed mitigation activities for the issue.
2011-11-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 5 (RFC_URE5) | NCRXXXXX | RFC201100921 | CIP-003-2 | R1 | The entity is subject to compliance with CIP-003-2 R1. The entity self-certified non-compliance with Reliability Standard CIP-007-2 R5 to ReliabilityFirst; however, upon further review, ReliabilityFirst determined the appropriate Reliability Standard implicated in the issue was CIP-003-2 R1. The entity failed to implement its cyber security policy. Specifically, the entity’s cyber security policy requires the entity to change its passwords every 90 days. The entity did not implement the 90-day password policy to address any particular risk, but rather the entity based the 90-day password policy on generally accepted good practice. According to its cyber security policy, the entity should have changed its passwords no later than 90 days from the date the entity had to comply with CIP-003-2 R1; however, the entity did not change its passwords until eight months later. ReliabilityFirst determined that the entity failed to implement its cyber security policy by not changing its passwords every 90 days. | In light of the nature of the issue, offset by the mitigating factors, ReliabilityFirst determined that this issue posed a minimal risk to the reliability of the bulk power system (BPS), and did not pose a serious or substantial risk. The risk to the reliability of the BPS was mitigated by the fact that the entity's cyber security policy is more stringent than that required by CIP-007-2 R5.3.3, which requires that a registered entity change its passwords at least annually. The entity did change its passwords annually, but failed to implement its internal cyber security policy, which mandated it change its passwords every 90 days. | The entity mitigated the issue by changing its passwords and updating its password management process to align with CIP-007 R5. The entity completed mitigation activities for the issue.
2011-11-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 5 (RFC_URE5) | NCRXXXXX | RFC201100912 | CIP-004-2 | R4 | The entity is subject to compliance with CIP-004-2 R4. The entity self-certified non-compliance with Reliability Standard CIP-004-2 R4 to ReliabilityFirst. The entity discovered it had not maintained its access list of personnel with cyber or unauthorized physical access to Critical Cyber Assets (CCAs). The entity also discovered it had not included, in its access list, the specific electronic access rights for individuals with access rights to CCAs. Specifically, after two employees received CIP training and completed a personnel risk assessment (PRA) in accordance with the entity’s procedure, the entity granted them access to CCAs but failed to include their names and access rights on its access list. Additionally, the entity included a compliance specialist on the access list even though the entity did not grant the compliance specialist access rights. ReliabilityFirst found that the entity failed to maintain its list of personnel with authorized cyber or authorized unescorted physical access to CCAs when it failed to timely to include two individuals with access rights and mistakenly included one individual on the list without access rights. Further, ReliabilityFirst determined that the entity failed to include, in its access list, the specific electronic access rights it granted to the two employees. | In light of the nature of the issue, offset by the mitigating factors, ReliabilityFirst determined this issue posed a minimal risk to the reliability of the bulk power system (BPS), and did not pose a serious or substantial risk. The risk to the reliability of the BPS was mitigated by the fact that the issue was a result of a documentation error. It was a documentation error because, although the access lists were incomplete, actual physical and electronic access rights were accurate and up to date. All individuals with cyber or unescorted physical access to CCAs had received CIP training, and completed PRAs in accordance with the entity’s procedure prior to the entity granting those individuals access rights. Additionally, there were no occurrences of access, physical or electronic, that were not properly authorized and documented by the entity. | The entity performed the following mitigating activities. The entity updated its access list to reflect all individuals with physical and electronic access rights and included detailed electronic access rights for each individual with electronic access rights. The entity also developed an improved documentation process to help ensure the access lists reflect the most up to date information concerning electronic and physical access rights to CCAs. The entity completed mitigation activities for the issue.
2011-11-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 5 (RFC_URE5) | NCRXXXXX | RFC201100914 | CIP-006-2 | R1 | The entity is subject to compliance with CIP-006-2 R1. The entity self-certified non-compliance with CIP-006-2 R1 to ReliabilityFirst. The entity determined it did not document all sub-requirements of CIP-006-2 R1 in its physical security plan. Specifically, the entity did not document sub-requirement CIP-006 R1.1, that all Cyber Assets within an Electronic Security Perimeter did not reside within an identified Physical Security Perimeter, and where a completely enclosed (“six-wall”) border cannot be established, the entity did not deploy and document alternative measures to control physical access to such Cyber Assets; R1.4, that an appropriate use of physical access controls as described in R4 including visitor pass management, response to loss and prohibition of inappropriate use of physical access controls were addressed; R1.5, that a review of access authorization requests and revocation of access authorization, in accordance with CIP-004-2 R4 were addressed; and R1.6, that continuous escorted access within the Physical Security Perimeter of personnel not authorized for unescorted access were addressed in its physical security plan. ReliabilityFirst determined that the entity failed to document sub-requirements of CIP-006-2 R1.1, R1.4, R1.5 and R1.6 in its physical security plan. | In light of the nature of the issue offset by the mitigating factors, ReliabilityFirst determined that this issue posed a minimal risk to the reliability of the bulk power system (BPS), and did not pose a serious or substantial risk. The risk to the reliability of the BPS was mitigated by the fact that the issue was the result of a documentation error. It was a documentation error because, although the entity’s physical security plan lacked proper documentation of the sub-requirements of CIP-006-2 R1, the entity implemented all the physical security controls required by CIP-006-2 R1. | The entity performed the following mitigating activities. The entity documented the sub-requirements of CIP-006-2 R1 at issue in its physical security plan. Additionally, the entity scheduled and performed training, highlighting the addition of the sub-requirements to its physical security plan, for all of its personnel. The entity completed mitigation activities for the issue.
2011-11-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 9 (RFC_URE9) | NCRXXXXX | RFC201100998 | CIP-007-3 | R4 | The entity is subject to compliance with CIP-007-3 R4. The entity submitted a Self-Report to ReliabilityFirst identifying a possible issue with CIP-007-3 R4. The entity determined it had not used anti-virus software and other malware prevention software for 135 Critical Cyber Assets (CCAs), pursuant to CIP-007-3 R4, and did not request a Technical Feasibility Exception (TFE) for this issue. The entity believed the 135 CCAs were integrated components of the servers on which they reside, therefore did not require separate anti-virus software or other malware prevention tool; however, 133 of these CCAs were self-contained modules within the server that provide a separate network connection for IT personnel to remotely manage the server under emergency conditions. The remaining two CCAs run directly on server hardware without requiring an additional underlying operating system. These characteristics of the 135 CCAs necessitated that they have anti-virus software and other malware prevention tools. The 135 CCAs are subject to CIP-007-3 R4, for which the entity should have complied or, alternatively, submitted a TFE request to ReliabilityFirst. According to the entity, these 135 CCAs were incapable of using anti-virus software and other malware prevention tools; however, the entity did not request a TFE from ReliabilityFirst concerning this issue until seven months after the compliance enforcement date. ReliabilityFirst determined that the entity failed to use anti-virus software and other malware prevention tools to mitigate risk exposure to the 135 CCAs pursuant to CIP-007-3 R4. | In light of the nature of the issue, offset by the mitigating factors, ReliabilityFirst determined that this issue posed a minimal risk to the reliability of the bulk power system (BPS), and did not pose a serious or substantial risk. The risk to the reliability of the BPS was mitigated by the fact that the entity had compensating measures in place prior to the mandatory compliance date. These compensating measures were ultimately approved by ReliabilityFirst. Specifically, the entity installed firewalls at the perimeter of the Electronic Security Perimeter (ESP) with an intrusion prevention system that can detect and prevent many types of malware from propagating. The entity also installed virus protection on workstations and servers as well as firewall software on its workstations. The entity stores the passwords for the CCAs securely in a server password database that is restricted to authorized personnel. Finally, the entity limits administrative access to the CCAs to a small group of support personnel to further minimize risk exposure. These compensating measures were in place for the entire time period of the issue. | The entity mitigated this issue by submitting its TFE requests for the CCAs at issue. ReliabilityFirst subsequently accepted and approved the entity's TFE requests. The entity completed mitigation activities for the issue.
2011-11-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 9 (RFC_URE9) | NCRXXXXX | RFC201000373 | CIP-008-1 | R1 | The entity is subject to compliance with CIP-008-1 R1. ReliabilityFirst conducted a CIP Spot Check of the entity. ReliabilityFirst reviewed the entity’s emergency incident and disturbance reporting procedure (Emergency Procedure Version 1) and determined it had not included roles and responsibilities of the incident response teams in the Emergency Procedure Version 1, pursuant to CIP-008-1 R1.2. The entity updated the Emergency Procedure Version 1 to define the roles and responsibilities of its response team (Emergency Procedure Version 2). ReliabilityFirst also reviewed the entity’s Emergency Procedure Version 2 and determined it did not contain a provision for the entity to review the Emergency Procedure Version 2 at least annually, pursuant to CIP-008-1 R1.5. Rather than conducting, at minimum, an annual review of its Cyber Security Incident response plan, the entity stated it would “periodically” conduct a review of the Emergency Procedure Version 2. ReliabilityFirst determined that the entity had an issue with CIP-008-1 R1.2 by failing to include the roles and responsibilities of its response teams within Emergency Procedure Version 1. Additionally, ReliabilityFirst determined that the entity had an issue with CIP-008-1, R1.5 by failing to include a provision within Emergency Procedure 2 requiring, at minimum, an annual review. | In light of the nature of the issue, offset by the mitigating factors, ReliabilityFirst determined that this issue posed a minimal risk to the reliability of the bulk power system (BPS), and did not pose a serious or substantial risk. The risk to the reliability of the BPS was mitigated by the fact that this was a documentation error. It was a documentation error because the entity had a procedure in place prior to the compliance enforcement date, that provided roles and responsibilities in the event of Cyber Security Incidents; however, the entity inadvertently referenced the incorrect procedure in its Emergency Procedure Version 1. The entity defined roles and responsibilities of response teams when it updated Emergency Procedure Version 1, almost a year before ReliabilityFirst’s Spot Check. Also while, the entity’s Emergency Procedure Version 2 called for periodic, rather than annual, review of the plan, the entity represents that the periodic review of Emergency Procedure Version 2 would include an annual review. | The entity performed the following mitigating activities. The entity updated its Cyber Security Incident response plan to define the roles and responsibilities of its response team, and thereby corrected the issue with CIP-008-1 R1.2. The entity updated its Emergency Procedure Version 1 to include specific roles and responsibilities for its response team pursuant to CIP-008-1 R1.2. The entity also revised Emergency Procedure Version 2 to provide for, at minimum, an annual review. The entity completed mitigation activities for the issue.
2011-11-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201103046 | CIP-003-2 | R5 | WECC_URE1 self-reported that it had failed to implement its access control program pursuant to CIP-003-2 R5. As part of WECC_URE1's access controls related to accessing Critical Cyber Asset (CCA) information, WECC_URE1 maintains a list of individuals that WECC_URE1 authorized to access such information. In this case, a WECC_URE1 engineer had a business need to view CCA information. An individual that WECC_URE1 designated to grant access to such information invited the engineer into a meeting where CCA information was displayed (projected) on a wall. Although the power production engineer had a business need to view this information, had the appropriate training to properly utilize this information, and was intentionally granted access by a an individual responsible for granting access to this information, WECC_URE1 did not implement its documented program for managing access to protected CCA information. Specifically, WECC_URE1's documented program establishes that WECC_URE1 will place individuals on a list prior to being granted such access. In this case, WECC_URE1 place the engineer on the list after the meeting. The person who manages access (as required in CIP-003 R5.1) to the protected information in scope invited the power production engineer to attend the meetings before the engineer was placed on WECC_URE1's list as an individual authorized to view protected information. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because even though allowing access to an information related to an entity's CCAs could allow such information to be unintentionally misused or used with malicious intent, in this case WECC_URE1 provided significant protections to such information. There is no evidence to suggest WECC_URE1 allowed access to such information without taking appropriate precautions to protect the information and guard against possible misuse of the information. An individual responsible for granting access to the information invited a long-time employee with a business need to view the information to a meeting where the individual could view the information. This individual had a personnel risk assessment, CIP training, and had a legitimate business need to access the information, but was not on WECC_URE1's authorized list to view such information. WECC_URE1 added the individual to the authorized list following the meeting. Additionally, the individual in scope was only able to view information related to Critical Assets while at the meeting and only viewed the information projected on a wall. The individual did not have electronic or physical access to the information, could not remove the information from the room, and remains an employee in good standing. | WECC_URE1 placed the engineer on the list of individuals authorized to view protected information.
2011-10-31 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 10 (FRCC_URE10) | NCRXXXXX | FRCC201000361 | CIP-004-1 | R2.1 | The entity self-reported that one of its employees was not trained prior to being granted physical and logical access to the entity's Critical Cyber Assets (CCAs). | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the training was delayed by five days only and the concerned person was in the control room environment and was being trained under constant supervision of his/her peers. During the initial training the identified person did not operate the CCA (BPS control) independently without supervision. All his/her activities were supervised and under the guidance of experienced peers who were training under the CIP program. | Mitigation milestones included completion of pending training for one person and revision of procedures for granting authorized access to the CCA and to include exact code of the required training modules to limit any confusion with completion of other NERC and FERC related training which was recognized as the original root cause of the remediated issue. Mitigation was completed by the entity and verified by FRCC.
2011-10-31 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 10 (FRCC_URE10) | NCRXXXXX | FRCC201000305 | CIP-004-1 | R3 | The entity self-reported that one of its employees who was granted access to Critical Cyber Assets (CCAs) did not undergo a personnel risk assessment (PRA) within 30 days of being granted such access as required by CIP-004 R3. The required PRA was completed 43 days after the required date. | This issue posed a minimal risk and did not pose serious or substantial risk to the reliability of the BPS because the employee whose PRA was delayed was a longtime employee who already had access to the CCAs. The employee underwent a PRA within 73 days instead of 30, with satisfactory results. Since the employee already had access, delay in undergoing a PRA did not increase any potential risk to the BPS reliability. CIP-004-1 R3 allowed 30 days for conducting a PRA. The additional 43 days would not have added significant risk for an employee of long term standing who has been with the organization for 8 years. | Mitigation milestones included completion of pending PRA for one person, training for all concerned personnel who are involved in granting access to the Physical Security Perimeter (PSP) and revision of procedures for granting unescorted physical access to the PSP. Further, the entity modified technical controls in the physical access control systems to ensure that PRA and training dates are entered for verification prior to granting authorized physical access to the PSP. Mitigation was completed by the entity and verified by FRCC.
2011-10-31 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 10 (FRCC_URE10) | NCRXXXXX | FRCC201100426 | CIP-004-3 | R4.1 | The entity self-reported that it did not update the list of all authorized users with electronic or unescorted physical access within seven days from date of change as required by CIP-004 R4.1. One duplicate entry for a person who had retired was erroneously left on the list because the concerned person was listed twice on the list with one entry stating that access had been disabled. The record with correct access status was removed during the seven day update window, but the other entry was not removed due to oversight. The error was recognized during a quarterly review 50 days after the required date and the list was corrected immediately. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because all access cards were physically destroyed and access was revoked timely but only the list was not updated. The identified person could not have gained access without completing the complete process for gaining authorized access with an access card, which would involve a control check by a supervisor and the Critical Cyber Asset access control department. | Mitigation included steps to review all user profile on the list and remove any duplicate entries. Further, the entity modified the procedure to ensure that any new access or lost card badge requests are treated as new user access request and all controls and verification are applied. Mitigation also included further training of the staff involved with the verification and access provisioning process. The identified person's duplicate entry was removed from the list. Mitigation was completed by the entity and verified by FRCC.
2011-10-31 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO201000242 | CIP-007-2 | R5.1.1; R5.1.2 | The entity self-reported noncompliance with CIP-007-2 R5 because it failed to ensure that user accounts were implemented as required by R5.1.1, and did not maintain logs for 90 days as required by R5.1.2. During a quarterly personnel access review, the entity discovered that access for one individual (<1%) was granted without documented authorization in accordance with CIP-007 R5.1. One of the entity's administrators discovered that during that quarter, operator system level user activity logs had not been capturing failed authentication attempts. Since successful authentications were still being captured, more than 90 calendar days of logs were available for review. The issue was resolved on the same day it was discovered and failed authentication attempts were captured again. The total number of days for which failed authentication was not logged was 40 calendar days. | The remediated issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the entity had the following protective measures in place: (1) system access configuration logs were verified for the duration of the lapse and no suspicious account setups were present; (2) the number of accounts with logon rights to the servers is limited; (3) group policy object limits the number of failed logons before the account is locked; (4) firewall rules and ports are locked to only allow necessary communication; (5) the anti-virus monitors and corrects malicious events on the servers; (6) the intrusion detection system monitors and corrects malicious events on the network; (7) a system manager monitors server connectivity to network and detects and reports any changes to the hardware on the server; and (8) the entity's physical security limits physical access to the servers. | The entity performed the following actions to mitigate the remediated issue: (1) added servers back to program which limits number of failed logons before account is locked out; (2) fixed the script; and (3) tested to ensure logs were sent, received, and that monitoring and alerting functionality were operational. Mitigation has been completed and verified by MRO.
2011-10-31 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 2 (MRO_URE2) | NCRXXXXX | MRO201000244 | CIP-007-1 | R5.1.1 | The entity self-reported noncompliance with CIP-007-1 R5.1.1 because it failed to ensure that user accounts were implemented as approved by designated personnel. A cyber access account was created and access was allowed to critical facilities for 59 days without documented approval and authorization as required in CIP-007-1 R5.1.1. The entity reported that this issue occurred because an individual failed to follow the corporate procedure for CIP access when transferring from one job function to another within the entity. | The remediated issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the access was appropriate for the affected individual and the access remained configured in the servers. Additionally, the steward gave verbal approval, and the individual had personnel risk assessment (PRA) and cyber security training as required by CIP-004-1 R2 and R3. | The entity performed the following actions to mitigate the remediated issue: (1) verified that NERC CIP training and PRA prerequisites were met; and (2) ensured that subject matter experts understood the requirements for formal, documented approval of NERC CIP cyber access. Mitigation has been completed and verified by MRO.
2011-10-31 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 4 (MRO_URE4) | NCRXXXXX | MRO201100296 | CIP-004-1 | R4 | The entity self-reported noncompliance with CIP-004-1 R4 because it failed to review a Critical Cyber Asset (CCA) access list during the first quarter in which the entity was required to comply under the CIP Implementation Table. The CCA access list was reviewed starting in the next quarter. | The remediated issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because only one CCA access list was not reviewed for one quarter. Additionally, upon review, the entity did not identify any individuals that had access during that time that should have been removed from the list. | This remediated issue was mitigated when the entity reviewed the CCA access list for the second quarter of 2010.
2011-10-31 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 4 (MRO_URE4) | NCRXXXXX | MRO201100299 | CIP-005-1 | R3 | The entity self-reported noncompliance with CIP-005-1 R3 because it did not have a monitoring process documented or implemented for one category of Critical Cyber Asset (CCA) access devices. Logs were generated as of the date the entity was required to comply with the Standard under the CIP Implementation Table; however, they were not being monitored until three months later. The security review and logging procedures for these devices were formally documented and published six months after the compliance date. | The remediated issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the individuals with access to the devices were properly authorized, trained and had current personnel risk assessments. The deficiency was in the maintenance of the activity log for the category of devices for slightly longer than 90 days; however, authentication methods existed during the time of the issue. | The security review and logging procedures for the CCA devices were formally documented and published.
2011-10-31 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 4 (MRO_URE4) | NCRXXXXX | MRO201100306 | CIP-007-1 | R6 | The entity self-reported noncompliance with CIP-007-1 R6.5 because it failed to document reviewing logs for all system events for Cyber Assets within the Electronic Security Perimeter (ESP). Specifically, the entity failed to review the security logs from the transmission management system (TMS) for a two month period. The security logs for these systems existed but they were not reviewed. | The remediated issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because at all times, including this period of time, the entity was continuing to monitor all Cyber Assets with the ESP for security events. Automated and manual alerts were available to be issued on the detection of any such event. Subsequent review of those logs revealed there were no threatening anomalies during the period of time in question. | The entity completed review of its security logs and implemented procedures to ensure regular security log review.
2011-10-31 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 4 (MRO_URE4) | NCRXXXXX | MRO201100305 | CIP-007-1 | R5 | The entity self-reported noncompliance with CIP-007-1 R5 because it failed to have an audit trail of the shared account use. Specifically, the audit trails of the account use of shared accounts on the transmission management system (TMS), and two accounts in the substation network were not maintained as of the date of mandatory compliance, for one month for the TMS accounts and for three months for the substation accounts. | The remediated issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the individuals with access to the shared accounts were properly authorized, trained and had current personnel risk assessments. The deficiency was in the maintenance of the activity log and no incidents occurred during the period of deficiency. | The entity now maintains audit trails for shared account use for all required accounts.
2011-10-31 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 5 (MRO_URE5) | NCRXXXXX | MRO201100370 | CIP-004-3 | R4; R4.2 | The entity self-reported noncompliance with CIP-004-3 R4.2 because it failed to update its Critical Cyber Assets (CCAs) access list for a contractor within 7 days from when the contractor no longer required access. The entity's janitorial service company notified the entity building and grounds supervisor late in the day that one of its employees assigned to clean within the Physical Security Perimeter (PSP) was no longer employed with the janitorial services company as of that date. The building and grounds supervisor notified the entity system operator on duty, and left a telephone voice message for the entity electric compliance manager regarding this change at 4:46 p.m. CST; however, the electric compliance manager was on vacation, and the telephone voice message was not attended. The building and grounds supervisor also immediately revoked building access for the employee at that time. Additionally, the system operator on duty made note of this change in the logbook, kept within the control room, which lists the janitorial service employees that are allowed access to the PSP. At no time did the terminated janitorial service employee have physical access to the entity general office building or the control room. The electric compliance manager returned from vacation ten days later, and learned of the change at that time. | The remediated issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the deficiency related to updating the access list was promptly corrected and the actual physical access had been revoked. Access to the general office building is needed before any attempt could be made to request or gain access to the defined PSP. | The entity performed the following actions to mitigate the remediated issue: (1) revoked limited unescorted physical access and will no longer consider contractor personnel as having limited physical access to certain areas within the designated PSP. They are now considered escorted visitors whenever they are within the PSP; (2) because contractors no longer have limited physical access to certain areas within the designated security perimeter, these specific people were removed from the entity’s CCAs access list; (3) for additional security, the entity installed a keyed lock on a side door within the control room restroom that could possibly be used to access an area within the PSP that contains CCAs. This door will remain locked, and only be unlocked when the door is needed by personnel having unescorted physical or logical access to the entity’s CCAs; (4) installed an alarm on the door, that when opened, generates an Energy Management System (EMS) alarm to alert the system operator; and (5) when notified of any changes in contractor personnel, the entity building and grounds personnel have been instructed to make actual voice contact with either the entity NERC compliance analyst, electric compliance manager, or the manager of electric system operations and planning. These people are responsible for maintaining the CCAs access list, along with access to the logical or PSP. Mitigation has been completed and verified by MRO.
2011-10-31 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC201100239 | CIP-003-1 | R1; R1.3 | During an NPCC CIP compliance audit it was found that the entity was in noncompliance with CIP-003-1 R1. NPCC determined that the entity had a NERC cyber security policy and statement of management commitment not signed by the senior manager assigned pursuant to CIP-003 R2. | The remediated issue posed a minimal risk to the reliability of the bulk power system because although the policy was not signed by the senior manager assigned pursuant to CIP-003 R2, the policy was reviewed by the digital risk and security group, who performs annual review covering all NERC CIP-related information security requirements, and signed by the chief information security officer. The chief information security officer was designated by the senior manager as his/her delegate pursuant of CIP-003 R2.3. | The entity reviewed and received approval of the cyber security policy by the senior manager assigned pursuant to CIP-003 R2. The entity completed its mitigation activity as verified by NPCC.
2011-10-31 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC201100240 | CIP-007-2a | R9 | During a NPCC CIP compliance audit it was found that, the entity was in noncompliance with CIP-007-2a R9. NPCC determined that the entity's parent company's information security standard testing document was not corrected to change its 90-day requirement to a 30-day requirement as required by the change in CIP-007-2a R9; however, the annual procedure review was performed in conformity with the Standard and updated to reflect the changes reflected in CIP-007-3. | The remediated issue posed a minimal risk to the reliability of the bulk power system because there were no Cyber Security Incidents that required action pursuant to the Cyber Security Incident response plan during the 8-month period until the plan was updated to reflect the 30-day update period in accordance with CIP-007-2. In addition, the annual procedure review was performed in conformity with the Standard and updated to reflect the changes reflected in CIP-007-3 | The entity's parent company's information security standard testing document was updated, changing the ninety calendar day update requirement to the thirty calendar day update requirement. The entity completed its mitigation activity as verified by NPCC.
2011-10-31 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC201100241 | CIP-008-2 | R1; R1.4 | During a NPCC CIP compliance audit it was found that the entity was in noncompliance with CIP-008-2 R1. NPCC determined that the entity's parent company's information security standard incident management document was approved to require a process for updating the Cyber Security Incident response plan within 30 days of any changes as per CIP-008-3 R1.4. This was done 70 days after its obligation to meet the 30-day requirement. | The remediated issue posed a minimal risk to the reliability of the bulk power system because the information security standard incident management document was updated within a short period of time - only 2 months after the 30-day criteria went into effect, changing the ninety calendar day update requirement to the thirty calendar day update requirement. No interim and future risks were identified. | The entity's parent company's information security standard incident management document was approved with the update to require a process for updating the Cyber Security Incident response plan within 30 days of any changes as per CIP-008 R1.4 prior to the CIP audit. No further action to mitigate this violation was necessary. The entity completed its mitigation activity as verified by NPCC.
2011-10-31 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 1 (NPCC_URE1) | NCRXXXXX | NPCC201100243 | CIP-009-1 | R4 | During a NPCC CIP compliance audit it was found that the entity was in noncompliance with CIP-009-1 R4. NPCC determined that there was no documentation in the entity's disaster recovery procedures that addressed a process for backing up and storage of information required to successfully restore Critical Cyber Assets (CCAs). | The remediated issue posed a minimal risk to the reliability of the bulk power system because evidence was provided that although there was no documentation in the entity's disaster recovery procedures that addressed a process for backing up and storage of information required to successfully restore CCAs, the backup and storage of information required to successfully restore CCAs was taking place. | The entity revised its disaster recovery procedures to include references to its change control and configuration procedure. The entity also revised this change control and configuration procedure to address CIP-009 R4 backup and restore requirements. The entity completed its mitigation activity as verified by NPCC.
2011-10-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC200900297 | CIP-004-1 | R2; R2.1 | During a Spot Check ReliabilityFirst identified an issue concerning CIP-004-1 R2.1. The entity failed to address in its training program, in effect from July 1, 2008 to July 5, 2009, the proper use of Critical Cyber Assets (CCAs) as required by CIP-004-1 R2.2.1, or the action plans and procedures to recover CCAs following a Cyber Security Incident, as required by CIP-004-1 R2.2.4. | In light of the nature of the issue, offset by the mitigating factors, ReliabilityFirst determined that this issue posed a minimal risk to the reliability of the bulk power system (BPS). The risk to the BPS was mitigated by the fact that although the prior training program did not directly address the proper use of CCAs or action plans and procedures to recover CCAs following a Cyber Security Incident, it contained references to the entity policies and procedures that govern the proper use of CCAs and action plans and procedures to recover CCAs following a Cyber Security Incident. | The entity revised its cyber security training program to include training material about the proper use of CCAs and to include action plans and procedures to recover or re-establish CCAs and access thereto following a Cyber Security Incident. The entity mitigated the issue as verified by ReliabilityFirst.
2011-10-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC201000458 | CIP-003-1 | R1 | The entity submitted a Self-Report identifying an issue with CIP-003-1 R1. Due to security software incompatibility, the entity could not access certain Critical Cyber Assets (CCAs) to change passwords every 60 days as required by the entity's cyber security policy. The entity drafted its cyber security policy to comply with Reliability Standard CIP-007 R5. The entity’s policy to change passwords every 60 days is more stringent than CIP-007 R5, which requires an entity change its password “at least annually or more frequently based on risk." Under the entity's cyber security policy the entity should have changed the user account passwords on its identified CCAs but did not do so until approximately six months after the expected date. | ReliabilityFirst found that the issue posed a minimal risk to the reliability of the bulk power system (BPS) as the entity was adhering to the password requirements pursuant to CIP-007 R5, but had established a more stringent 60 day time frame for changing passwords associated with CCAs. The entity’s more stringent 60-day password change requirement was not established to address any heightened risk, but rather to ensure consistency with a general corporate information assurance practice of changing all IT system passwords every 60 days. Accordingly, the entity’s failure to act in strict accordance with the 60 day password policy does not represent a failure to address any known potential cyber risk. Moreover, the security software incompatibility that contributed to the entity’s password change delay within its internal 60-day timeframe effectively prevented anyone from gaining access to the identified CCAs for those six months. The entity has confirmed that there was no access to the identified CCAs during this time period. Furthermore, the entity has also confirmed that there were no personnel changes during the time period in question involving those individuals authorized to access these CCAs. | The entity installed a separate terminal within the entity’s Electronic Security Perimeter. This terminal gave the entity man-to-machine access to the identified CCAs and thus allowed it to change all user account passwords on the them. Pursuant to an extension requested by the entity and a subsequent approval of that request granted by ReliabilityFirst, the entity completed mitigation.
2011-10-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 2 (RFC_URE2) | NCRXXXXX | RFC201000436 | CIP-003-1 | R4 | The entity submitted a Self-Report to ReliabilityFirst indicating an issue with CIP-003-1 R4. The entity has a documented information protection program to identify, classify, and protect information associated with Critical Cyber Assets (CCAs). This program requires that the entity encrypt all information associated with CCAs before digitally transferring that information outside of the company. The entity, contrary to this program, submitted an unencrypted Technical Feasibility Exception (TFE) request, which included information associated with a CCA, to ReliabilityFirst. | In light of the nature of the issue, offset by the mitigating factors, ReliabilityFirst determined that this issue posed a minimal risk to the reliability of the bulk power system (BPS). At the time of the incident, the entity verbally confirmed that ReliabilityFirst received the unencrypted transmission. ReliabilityFirst was the only external addressee on the email and, to the entity’s knowledge the only external recipient of the unencrypted email. Moreover, the entity has confirmed that the entity’s internal email system is protected by controls which effectively prevent unauthorized access to the email in question. The entity also claims that only authorized individuals have had access to the email in question. | The entity trained two employees to be responsible for externally transmitting all CCA related information via encryption. The entity has implemented a technical control to quarantine messages labeled for encryption. The entity will also develop and distribute awareness materials to stress conformity with procedures to use email encryption prior to electronically transmitting information concerning CCAs. Pursuant to an extension requested by the entity, and a subsequent approval of that request granted by ReliabilityFirst, the entity completed mitigation.
2011-10-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC201000411 | CIP-005-1 | R2; R2.6 | The entity self-reported an issue with the CIP Standards arising from the entity's failure to timely submit Technical Feasibility Exception (TFE) Requests in accordance with NERC procedures. The Self-Reports referenced all identified TFEs that should have been filed as of that point. The entity subsequently conducted an extent-of-condition investigation and identified four additional needed TFEs. The TFE Requests for the entity were submitted between approximately five and fifteen months late. Specifically, the entity submitted one late TFE Request for CIP-005-1 R2.6. | ReliabilityFirst determined that the issue posed a minimal risk to the reliability of the bulk power system (BPS) because the issue resulted from failures by the entity to comply with the administrative process for the submission of formal TFE Requests. ReliabilityFirst determined that the entity's system is structured with many firewall and other security controls. As of the effective date of the CIP Standards, there were compensating measures in place, such as using two-factor authentication and firewall rules that minimize exposure of devices. Many of these compensating measures were in place well before the effective date of the CIP Standards. Therefore, although the entity submitted untimely TFE Requests, the entity was performing compensating measures to ensure the basic security of its system throughout the duration of the issue. ReliabilityFirst accepted and approved the TFE Requests’ compensating measures because they “achieve at least a comparable level of security for the Bulk Electric System as would Strict Compliance with the [CIP Standards].” Moreover, after the submission of the TFE Requests, the entity also identified and implemented additional measures, which exceeded the required compensating measures and further reduced any potential risk. For example, the entity identified a vendor solution that provides a method of implementing acceptable use banners. | The entity mitigated the issue by submitting all acceptable TFE Requests and has continuously performed all of the compensating measures as discussed in the TFE Requests.
2011-10-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC201000412 | CIP-007-1 | R3 | The entity self-reported an issue with the CIP Standards arising from the entity's failure to timely submit Technical Feasibility Exception (TFE) Requests in accordance with NERC procedures. The Self-Reports referenced all identified TFEs that should have been filed as of that point. The entity subsequently conducted an extent-of-condition investigation and identified four additional needed TFEs. The TFE Requests for the entity were submitted between approximately five and fifteen months late. Specifically, the entity submitted three late TFE Requests for CIP-007-1 R3. | ReliabilityFirst determined that the issue posed a minimal risk to the reliability of the bulk power system (BPS) because the issue resulted from failures by the entity to comply with the administrative process for the submission of formal TFE Requests. ReliabilityFirst determined that entity's system is structured with many firewall and other security controls. As of the effective date of the CIP Standards, there were compensating measures in place, such as performing vulnerability scans on the network and monitoring network traffic. Many of the compensating measures were in place well before the effective date of the CIP Standards. The systems also reside within a Physical Security Perimeter and an Electronic Security Perimeter. Therefore, although the entity submitted untimely TFE Requests, the entity was performing compensating measures to ensure the basic security of its system throughout the duration of the issue. ReliabilityFirst accepted and approved the TFE Requests’ compensating measures because they “achieve at least a comparable level of security for the Bulk Electric System as would Strict Compliance with the [CIP Standards].” | The entity mitigated the issue by submitting all acceptable TFE Requests and has continuously performed all of the compensating measures as discussed in the TFE Requests.
2011-10-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC201000413 | CIP-007-1 | R4 | The entity self-reported an issue with the CIP Standards arising from the entity's failure to timely submit Technical Feasibility Exception (TFE) Requests in accordance with NERC procedures. The Self-Reports referenced all identified TFEs that should have been filed as of that point. The entity subsequently conducted an extent-of-condition investigation and identified four additional needed TFEs. The TFE Requests for the entity were submitted between approximately five and fifteen months late. Specifically, the entity submitted three late TFE Requests for CIP-007-1 R4. | ReliabilityFirst determined that the issue posed a minimal risk to the reliability of the bulk power system (BPS) because the issue resulted from failures by the entity to comply with the administrative process for the submission of formal TFE Requests. ReliabilityFirst determined that entity's system is structured with many firewall and other security controls. As of the effective date of the CIP Standards, there were compensating measures in place, such as preventing the system from connecting to the internet through firewall restrictions and preventing users from directly installing software on the system. Many of these compensating measures were in place well before the effective date of the CIP Standards. Therefore, although the entity submitted untimely TFE Requests, the entity was performing compensating measures to ensure the basic security of the entity’s system throughout the duration of the issue. ReliabilityFirst accepted and approved the TFE Requests’ compensating measures because they “achieve at least a comparable level of security for the Bulk Electric System as would Strict Compliance with the [CIP Standards].” | The entity mitigated the issue by submitting all acceptable TFE Requests and has continuously performed all of the compensating measures as discussed in the TFE Requests.
2011-10-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC201000414 | CIP-007-1 | R5 | The entity self-reported an issue with the CIP Standards arising from the entity's failure to timely submit Technical Feasibility Exception (TFE) Requests in accordance with NERC procedures. The Self-Reports referenced all identified TFEs that should have been filed as of that point. The entity subsequently conducted an extent-of-condition investigation and identified four additional needed TFEs. The TFE Requests for the entity were submitted between approximately five and fifteen months late. Specifically, the entity submitted nine late TFE Requests for CIP-007-1 R5. | ReliabilityFirst determined that the issue posed a minimal risk to the reliability of the bulk power system (BPS) because the issue resulted from failures by the entity to comply with the administrative process for the submission of formal TFE Requests. ReliabilityFirst determined that entity's system is structured with many firewall and other security controls. As of the effective date of the CIP Standards, there were compensating measures in place, such as requiring frequent password changes through policies and procedural requirements for password length and complexity. The entity also monitors and tracks system log files for unusual user activity, performs background checks on all users, and users connect through a network protocol for secure remote login and other secure network services over an insecure network, which encrypts passwords. Many of the compensating measures were in place well before the effective date of the CIP Standards. Therefore, although the entity submitted untimely TFE Requests, the entity was performing compensating measures to ensure the basic security of the entity’s system throughout the duration of the issue. ReliabilityFirst accepted and approved the TFE Requests’ compensating measures because they “achieve at least a comparable level of security for the Bulk Electric System as would Strict Compliance with the [CIP Standards].” | The entity mitigated the issue by submitting all acceptable TFE Requests and has continuously performed all of the compensating measures as discussed in the TFE Requests.
2011-10-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 4 (RFC_URE4) | NCRXXXXX | RFC201000415 | CIP-005-1 | R2; R2.6 | The entity self-reported an issue with the CIP Standards arising from the entity's failure to timely submit Technical Feasibility Exception (TFE) Requests in accordance with NERC procedures. The Self-Reports referenced all identified TFEs that should have been filed as of that point. The entity subsequently conducted an extent-of-condition investigation and identified four additional needed TFEs. The TFE Requests for the entity were submitted between approximately five and fifteen months late. Specifically, the entity submitted one late TFE Request for CIP-005-1 R2.6. | ReliabilityFirst determined that the issue posed a minimal risk to the reliability of the bulk power system (BPS) because the issue resulted from failures by the entity to comply with the administrative process for the submission of formal TFE Requests. ReliabilityFirst determined that entity's system is structured with many firewall and other security controls. As of the effective date of the CIP Standards, there were compensating measures in place, such as using two-factor authentication and firewall rules that minimize exposure of devices. Many of these compensating measures were in place well before the effective date of the CIP Standards. Therefore, although the entity submitted untimely TFE Requests, the entity was performing compensating measures to ensure the basic security of the entity’s system throughout the duration of the issue. ReliabilityFirst accepted and approved the TFE Requests’ compensating measures because they “achieve at least a comparable level of security for the Bulk Electric System as would Strict Compliance with the [CIP Standards].” Moreover, the entity also identified and implemented additional measures after the submission of the TFE Requests, which exceed the required compensating measures and further reduced any potential risk. For example, the entity identified a vendor solution that provides a method of implementing acceptable use banners. | The entity mitigated the issue by submitting all acceptable TFE Requests and has continuously performed all of the compensating measures as discussed in the TFE Requests.
2011-10-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 4 (RFC_URE4) | NCRXXXXX | RFC201000417 | CIP-007-1 | R3 | The entity self-reported an issue with the CIP Standards arising from the entity's failure to timely submit Technical Feasibility Exception (TFE) Requests in accordance with NERC procedures. The Self-Reports referenced all identified TFEs that should have been filed as of that point. The entity subsequently conducted an extent-of-condition investigation and identified four additional needed TFEs. The TFE Requests for the entity were submitted between approximately five and fifteen months late. Specifically, the entity submitted two late TFE Request for CIP-007-1 R3. | ReliabilityFirst determined that the issue posed a minimal risk to the reliability of the bulk power system (BPS) because the issue resulted from failures by the entity to comply with the administrative process for the submission of formal TFE Requests. ReliabilityFirst determined that entity's system is structured with many firewall and other security controls. As of the effective date of the CIP Standards, there were compensating measures in place, such as performing vulnerability scans on the network and monitoring network traffic. The systems also reside within a Physical Security Perimeter and an Electronic Security Perimeter. Many of these compensating measures were in place well before the effective date of the CIP Standards. Therefore, although the entity submitted untimely TFE Requests, the entity was performing compensating measures to ensure the basic security of the entity’s system throughout the duration of the issue. ReliabilityFirst accepted and approved the TFE Requests’ compensating measures because they “achieve at least a comparable level of security for the Bulk Electric System as would Strict Compliance with the [CIP Standards].” | The entity mitigated the issue by submitting all acceptable TFE Requests and has continuously performed all of the compensating measures as discussed in the TFE Requests.
2011-10-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 4 (RFC_URE4) | NCRXXXXX | RFC201000418 | CIP-007-1 | R4 | The entity self-reported an issue with the CIP Standards arising from the entity's failure to timely submit Technical Feasibility Exception (TFE) Requests in accordance with NERC procedures. The Self-Reports referenced all identified TFEs that should have been filed as of that point. The entity subsequently conducted an extent-of-condition investigation and identified four additional needed TFEs. The TFE Requests for the entity were submitted between approximately five and fifteen months late. Specifically, the entity submitted three late TFE Requests for CIP-007-1 R4. | ReliabilityFirst determined that the issue posed a minimal risk to the reliability of the bulk power system (BPS) because the issue resulted from failures by the entity to comply with the administrative process for the submission of formal TFE Requests. ReliabilityFirst determined that entity's system is structured with many firewall and other security controls. As of the effective date of the CIP Standards, there were compensating measures in place, such as preventing the system from connecting to the internet through firewall restrictions and preventing users from directly installing software on the system. Therefore, although the entity submitted untimely TFE Requests, the entity was performing compensating measures to ensure the basic security of the entity’s system throughout the duration of the issue. ReliabilityFirst accepted and approved the TFE Requests’ compensating measures because they “achieve at least a comparable level of security for the Bulk Electric System as would Strict Compliance with the [CIP Standards].” | The entity mitigated the issue by submitting all acceptable TFE Requests and has continuously performed all of the compensating measures as discussed in the TFE Requests.
2011-10-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 4 (RFC_URE4) | NCRXXXXX | RFC201000419 | CIP-007-1 | R5 | The entity self-reported an issue with the CIP Standards arising from the entity's failure to timely submit Technical Feasibility Exception (TFE) Requests in accordance with NERC procedures. The Self Reports referenced all identified TFEs that should have been filed as of that point. The entity subsequently conducted an extent-of-condition investigation and identified four additional needed TFEs. The TFE Requests for the entity were submitted between approximately five and fifteen months late. Specifically, the entity submitted 11 late TFE Requests for CIP-007-1 R5. | ReliabilityFirst determined that the issue posed a minimal risk to the reliability of the bulk power system (BPS) because the issue resulted from failures by the entity to comply with the administrative process for the submission of formal TFE Requests. ReliabilityFirst determined that entity's system is structured with many firewall and other security controls. As of the effective date of the CIP Standards, there were compensating measures in place, such as requiring frequent password changes through policies and procedural requirements for password length and complexity. The entity also monitors and tracks system log files for unusual user activity, performs background checks on all users, and users connect through a network protocol for secure remote login and other secure network services over an insecure network, which encrypts passwords. Many of these compensating measures were in place well before the effective date of the CIP Standards. Therefore, although the entity submitted untimely TFE Requests, the entity was performing compensating measures to ensure the basic security of the entity’s system throughout the duration of the issue. ReliabilityFirst accepted and approved the TFE Requests’ compensating measures because they “achieve at least a comparable level of security for the Bulk Electric System as would Strict Compliance with the [CIP Standards].” | The entity mitigated the issue by submitting all acceptable TFE Requests and has continuously performed all of the compensating measures as discussed in the TFE Requests.
2011-10-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 5 (RFC_URE5) | NCRXXXXX | RFC201000420 | CIP-005-1 | R2; R2.6 | The entity self-reported an issue with the CIP Standards arising from the entity's failure to timely submit Technical Feasibility Exception (TFE) Requests in accordance with NERC procedures. The Self-Reports referenced all identified TFEs that should have been filed as of that point. The entity subsequently conducted an extent-of-condition investigation and identified four additional needed TFEs. The TFE Requests for the entity were submitted between approximately five and fifteen months late. Specifically the entity submitted one late TFE Request for CIP-005-1 R2.6. | ReliabilityFirst determined that the issue posed a minimal risk to the reliability of the bulk power system (BPS) because the issue resulted from failures by the entity to comply with the administrative process for the submission of formal TFE Requests. ReliabilityFirst determined that the entity's system is structured with many firewall and other security controls. As of the effective date of the CIP Standards, there were compensating measures in place, such as using two-factor authentication and firewall rules that minimize exposure of devices. Many of the compensating measures were in place well before the effective date of the CIP Standards. Therefore, although the entity submitted untimely TFE Requests, the entity was performing compensating measures to ensure the basic security of its system throughout the duration of the issue. ReliabilityFirst accepted and approved the TFE Requests’ compensating measures because they “achieve at least a comparable level of security for the Bulk Electric System as would Strict Compliance with the [CIP Standards].” Moreover, after the submission of the TFE Requests, the entity also identified and implemented additional measures which exceeded the required compensating measures and further reduced any potential risk. For example, the entity identified a vendor solution that provides a method of implementing acceptable use banners. | The entity mitigated the issue by submitting all acceptable TFE Requests and has continuously performed all of the compensating measures as discussed in the TFE Requests.
2011-10-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 5 (RFC_URE5) | NCRXXXXX | RFC201000421 | CIP-007-1 | R3 | The entity self-reported an issue with the CIP Standards arising from the entity's failure to timely submit Technical Feasibility Exception (TFE) Requests in accordance with NERC procedures. The Self-Reports referenced all identified TFEs that should have been filed as of that point. The entity subsequently conducted an extent-of-condition investigation and identified four additional needed TFEs. The TFE Requests for the entity were submitted between approximately five and fifteen months late. Specifically, the entity submitted one late TFE Request for CIP-007-1 R3. | ReliabilityFirst determined that the issue posed a minimal risk to the reliability of the bulk power system (BPS) because the issue resulted from failures by the entity to comply with the administrative process for the submission of formal TFE Requests. ReliabilityFirst determined that entity's system is structured with many firewall and other security controls. As of the effective date of the CIP Standards, there were compensating measures in place such as performing vulnerability scans on the network and monitoring network traffic. Many of these compensating measures were in place well before the effective date of the CIP Standards. The systems also reside within a Physical Security Perimeter and an Electronic Security Perimeter. Therefore, although the entity submitted untimely TFE Requests, the entity was performing compensating measures to ensure the basic security of its system throughout the duration of the issue. ReliabilityFirst accepted and approved the TFE Requests’ compensating measures because they “achieve at least a comparable level of security for the Bulk Electric System as would Strict Compliance with the [CIP Standards].” | The entity mitigated the issue by submitting all acceptable TFE Requests and has continuously performed all of the compensating measures as discussed in the TFE Requests.
2011-10-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 5 (RFC_URE5) | NCRXXXXX | RFC201000422 | CIP-007-1 | R4 | The entity self-reported an issue with the CIP Standards arising from the entity's failure to timely submit Technical Feasibility Exception (TFE) Requests in accordance with NERC procedures. The Self-Reports referenced all identified TFEs that should have been filed as of that point. The entity subsequently conducted an extent-of-condition investigation and identified four additional needed TFEs. The TFE Requests for the entity were submitted between approximately five and fifteen months late. Specifically, the entity submitted four late TFE Requests for CIP-007-1 R4. | ReliabilityFirst determined that the issue posed a minimal risk to the reliability of the bulk power system (BPS) because the issue resulted from failures by the entity to comply with the administrative process for the submission of formal TFE Requests. ReliabilityFirst determined that entity's system is structured with many firewall and other security controls. As of the effective date of the CIP Standards, there were compensating measures in place, such as preventing the system from connecting to the internet through firewall restrictions and preventing users from directly installing software on the system. Therefore, although the entity submitted untimely TFE Requests, the entity was performing compensating measures to ensure the basic security of the entity’s system throughout the duration of the issue. ReliabilityFirst accepted and approved the TFE Requests’ compensating measures because they “achieve at least a comparable level of security for the Bulk Electric System as would Strict Compliance with the [CIP Standards].” | The entity mitigated the issue by submitting all acceptable TFE Requests and has continuously performed all of the compensating measures as discussed in the TFE Requests.
2011-10-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 5 (RFC_URE5) | NCRXXXXX | RFC201000423 | CIP-007-1 | R5 | The entity self-reported an issue with the CIP Standards arising from the entity's failure to timely submit Technical Feasibility Exception (TFE) Requests in accordance with NERC procedures. The Self-Reports referenced all identified TFEs that should have been filed as of that point. The entity subsequently conducted an extent-of-condition investigation and identified four additional needed TFEs. The TFE Requests for the entity were submitted between approximately five and fifteen months late. Specifically, the entity submitted 18 late TFE Requests for CIP-007-1 R5. | ReliabilityFirst determined that the issue posed a minimal risk to the reliability of the bulk power system (BPS) because the issue resulted from failures by the entity to comply with the administrative process for the submission of formal TFE Requests. ReliabilityFirst determined that entity's system is structured with many firewall and other security controls. As of the effective date of the CIP Standards, there were compensating measures in place, such as requiring frequent password changes through policies and procedural requirements for password length and complexity. The entity also monitors and tracks system log files for unusual user activity, performs background checks on all users, and users connect through a network protocol for secure remote login and other secure network services over an insecure network, which encrypts passwords. Therefore, although the entity submitted untimely TFE Requests, the entity was performing compensating measures to ensure the basic security of the entity’s system throughout the duration of the issue. ReliabilityFirst accepted and approved the TFE Requests’ compensating measures because they “achieve at least a comparable level of security for the Bulk Electric System as would Strict Compliance with the [CIP Standards].” | The entity mitigated the issue by submitting all acceptable TFE Requests and has continuously performed all of the compensating measures as discussed in the TFE Requests.
2011-10-31 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 1 (SERC_URE1) | NCRXXXXX | SERC2011007287 | CIP-003-2 | R2 | During an Off-Site Audit conducted by SERC, SERC_URE1 failed to provide evidence that a single senior manager had been assigned with overall responsibility and authority for CIP-002 through CIP-009, as required. SERC_URE1 designated overall responsibility and authority to a senior manager on April 4, 2011, and identified the senior manager by name, title, and date of designation. | SERC determined that the issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because: 1. SERC_URE1 has no Critical Assets. 2. SERC_URE1 does not own or operate any facilities that would meet any of the Critical Asset Criteria set forth in the proposed CIP-002-4. | SERC_URE1 completed the following action: Assigned a senior manager with the overall responsibility and authority for leading and managing the implementation of and adherence to CIP-002 through CIP-009 on April 4, 2011. SERC staff verified completion of the mitigation activity.
2011-10-31 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP201000325 | CIP-002-1 | R3 | During a spot check, SPP RE determined that SPPRE_URE1 was noncompliant with CIP-002-1 R3 for incorrectly identifying ten network switches located within SPPRE_URE1’s Electronic Security Perimeter (ESP). Specifically, the switches were identified as Protected Cyber Assets (PCAs) but they should have been identified as CCAs because they are the communication interface between the operator consoles and the some of SPPRE_URE1's systems and essential to the reliable operation of SPPRE_URE1’s control center. | SPP RE has determined that this issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). In SPPRE_URE1’s cyber environment, PCAs and CCAs are afforded the same cyber security protection measures. Therefore, although the network switches were incorrectly identified, in practice, the switches were treated as CCAs. Consequently, the misclassification of the network switches had no actual impact to the reliability of the BPS, and there was no increased risk to the reliability of the BPS. | SPPRE_URE1 applied its Control Center CCA process to the network switches, changed the identification of the switches from PCAs to CCAs, and updated its CCA identification list to reflect the change. SPPRE_URE1 certified that mitigation was complete, and SPP RE verified completion.
2011-10-31 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP201000326 | CIP-003-1 | R1; R1.1; R1.2 | During a spot check, SPP RE determined that SPPRE_URE1 was noncompliant with CIP-003-1 R1.1 and R1.2. Regarding R1.1, SPPRE_URE1’s 2008 version of its Cyber Security Policy did not include any provisions for emergency situations. This issue was remediated in a subsequent version of the policy, which became effective on June 30, 2009. Regarding R1.2, SPPRE_URE1 was unable to demonstrate that it provided the Cyber Security Policy to its vendor personnel who had access to, or was responsible for, CCAs prior to April 13, 2010. | SPP RE has determined that this issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System. Regarding R1.1, although SPPRE_URE1 failed to include provisions for emergency situations in its 2008 version of its Cyber Security Policy, it did have a robust Cyber Security Policy demonstrating management’s commitment to implementing a program for compliance with the CIP Standards. Additionally, its 2009 version of the Cyber Security Policy provided provisions for emergency situations. Regarding R1.2, the Cyber Security Policy was uploaded on SPPRE_URE1’s intranet and made available to SPPRE_URE1's systems vendor upon request. While the systems vendor support personnel did not receive a copy of SPPRE_URE1's Cyber Security Policy, they received comprehensive training on CIP Standards and work in a position that requires technical knowledge inclusive of cyber security best practices. As such, they fully understood the implications of their access to SPPRE_URE1's CCAs. | Regarding R1.1, SPPRE_URE1 revised its Cyber Security Policy to include provisions for emergency situations. Regarding R1.2, SPPRE_URE1 provided its Cyber Security Policy to its systems vendor. Additionally, SPPRE_URE1 developed and implemented a new process for making its Cyber Security Policy readily available to its system vendor. The process requires SPPRE_URE1 to provide its Cyber Security Policy to its vendor on an annual basis, when a change of the policy occurs, or upon request by the vendor. SPPRE_URE1 certified that mitigation was complete, and SPP RE verified completion.
2011-10-31 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP201000232 | CIP-004-1 | R3; R3.1; R3.3 | SPPRE_URE1 submitted a Self-Report to the SPP RE stating that it had an issue with this Reliability Standard. Upon further investigation of the facts and circumstances, including a subsequent Spot Check, SPP RE determined that SPPRE_URE1 was noncompliant with CIP-004-1 R3.1 and R3.3. CIP-004-1 R3.1 During an internal compliance assessment, SPPRE_URE1 discovered that although it documented and implemented its Personnel Risk Assessment (PRA) program by the date the Standard became effective (July 1, 2008), PRAs for current employees that were conducted prior to the effective date of the Standard were based on a five-year criminal background rather than a seven-year time interval and as a result SPPRE_URE1 failed to conduct the PRAs within the seven-year timeframe after the Standard became effective. All new PRAs conducted after the effective date of the Standard were based on a seven-year time period. CIP-004-1 R3.3 SPPRE_URE1 also discovered, during its internal assessment, that it was unable to locate PRAs for six individuals with unescorted physical access to CCAs. These individuals gained authorized access on July 1, 2008. On January 13, 2010, background checks with a seven-year time interval were requested on all six individuals, and the PRAs were completed on January 27, 2010. During a Spot Check, SPP RE discovered an additional instance where a SPPRE_URE1 security integrator contractor with unescorted physical access rights did not have a PRA. The contractor was previously given access in July 2008 to unrestricted areas within SPPRE_URE1’s main office. Therefore, a PRA was neither required nor conducted. However, on July 1, 2008, SPPRE_URE1 expanded its physical security perimeter (PSP) to include a stairwell door that leads to a secured access door to its Control Center but failed to remove the contractor's access rights to the stairwell door until August 27, 2008, the date the oversight was discovered. The access logs show that the contractor never used his credentials to access the stairwell door. | SPP RE has determined that this issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). Although the background checks did not strictly adhere to the Standard, they were conducted, and the five-year interval covered a significant portion of the required seven-year time period. Additionally, regarding the six individuals in which no PRAs could be located, all were long-term trusted employees with no disciplinary actions who had received the required cyber security training. With respect to the contractor who was inadvertently granted access to a newly identified restricted area without a PRA, the oversight was discovered and corrected less than two months (58 days) after access was granted, and the contractor never attempted to use his credentials to enter the PSP. Even if the contractor had used his credentials to open the stairwell door, his credentials would not have allowed him to open the secured door to the control center. Additionally, after PRAs had been conducted on the six individuals having authorized cyber or authorized unescorted physical access to CCAs, no PRA came back as having failed. | SPPRE_URE1 revised its PRA procedures to clarify the roles for personnel responsible for implementing its PRA program. Additionally, on January 13, 2010, SPPRE_URE1 requested new PRAs with seven-year background checks for the six individuals whom PRAs could not be located, which were completed on January 27, 2010. SPPRE_URE1 also conducted new PRAs for all remaining personnel having authorized cyber or authorized unescorted physical access to CCAs. All PRAs were completed on March 30, 2010. Regarding the contractor with inadvertent unescorted physical access to an access point to SPPRE_URE1’s PSP, SPPRE_URE1 revoked such access on August 27, 2008. SPPRE_URE1 revised its PSP to require all changes that may impact physical security measure to first be sent in writing to a security manager prior to changes being made. This allows preplanning and discovery of any potential logging or monitoring changes that will need to be addressed after approval of such changes. SPPRE_URE1 certified that mitigation was complete, and SPP RE verified completion.
2011-10-31 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP201000329 | CIP-004-1 | R4.1 | During a spot check, SPP RE determined that SPPRE_URE1 was noncompliant with CIP-004-1 R4.1. Specifically, although SPPRE_URE1 was reviewing its systems vendor access list annually, it was not reviewing the list quarterly as required by the Standard. | SPP RE has determined that this issue did not pose a serious or substantial risk to the reliability of the Bulk Power System. Although the systems vendor list was not being reviewed quarterly, it was being reviewed annually. Additionally, there is no evidence of any known unauthorized access attempts from any vendor identified on any of SPPRE_URE1’s vendor access lists. | SPPRE_URE1 updated its process for reviewing its systems vendor access list to include quarterly assessments. As of October 14, 2010, SPPRE_URE1 reviews all unescorted access rights to Critical Cyber Assets on a quarterly basis. SPPRE_URE1 certified that mitigation was complete, and SPP RE verified completion.
2011-10-31 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP201000293 | CIP-006-1 | R1.8 | SPPRE_URE1 self-reported an issue with this Standard. Specifically, during an internal compliance assessment, SPPRE_URE1 discovered that it was unable to locate personnel risk assessments (PRAs) for five SPPRE_URE1 IT technicians and one SPPRE_URE1 security contractor who had access to one of its servers, which is a Cyber Asset (CA) used to control and monitor access of SPPRE_URE1's physical security perimeters (PSPs). These individuals gained authorized access on July 1, 2008. Background checks were requested for all individuals and completed PRAs were received on April 14, 2010. | SPP RE has determined that this issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System. The five IT technicians were long-term trusted employees with no disciplinary actions who had received the required cyber security training. Additionally, the contractor was a trusted vendor, who had been vetted for his employment. Additionally, after PRAs had been conducted on these six individuals, no PRA came back as having failed. | PRAs were completed as of April 14, 2010. To prevent reoccurrence of this issue, SPPRE_URE1 revised its Cyber Security Policy to restrict physical access to the server to only those with a business need. The policy now requires physical access to the server be requested and approved through SPPRE_URE1's facilities access request process, which incorporates the management authorization of the access, training prerequisites, or PRAs needed in order to be granted access. SPPRE_URE1 implemented additional security measures to its server room to further secure the server. For instance, SPPRE_URE1 installed a server rack with secured doors that can only be opened by a newly installed card reader that is attached to the rack. Moreover, unauthorized attempts to the server will now sound an alarm to SPPRE_URE1 personnel who remain located inside the facility where the server room is located 24 hours a day, 7 days a week. Access to the server remains monitored by security personnel 24 hours a day, 7 days a week with a camera that is installed in the server room. SPPRE_URE1 certified that mitigation was complete, and SPP RE verified completion.
2011-10-31 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 1 (SPPRE_URE1) | NCRXXXXX | SPP201000333 | CIP-009-1 | R2 | During a spot check, SPP RE determined that SPPRE_URE1 was noncompliant with CIP-009-1 R2. Specifically, SPPRE_URE1 was required to conduct an exercise of its Critical Cyber Asset Recovery Plan by July 1, 2008, but the exercise was not conducted until April 15, 2009. | SPP RE has determined that this issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System. Although SPPRE_URE1 had not exercised its CCA Recovery Plan on the date required, SPPRE_URE1 did have a recovery plan in place. Further, SPPRE_URE1's support staff had received comprehensive training on CIP Standards and is very experienced in the support of Critical Cyber Assets and can be reasonably expected to perform the appropriate recovery steps for a wide variety of incidents. Moreover, there have been no events to date requiring activation of the recovery plan. | SPPRE_URE1's CCA Recovery Plan requires an annual exercise of the plan, which was conducted on April 15, 2009 and prior to the Spot Check. SPPRE_URE1 certified that mitigation was complete, and SPP RE verified completion.
2011-10-31 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 3 (SPPRE_URE3) | NCRXXXXX | SPP201000392 | CIP-003-1 | R6 | SPP_URE3 reported in its Self Certification that it was not in full compliance with CIP-003-2 R6 because it did not have a formal change control policy for all Critical Cyber Asset (CCA) hardware, software, and security configurations. Specifically, SPP_URE3 had not established and documented a process for change control and configuration management for adding, modifying, replacing, or removing all CCA hardware or software and it had not implemented supporting configuration management activities. | The SPP RE has determined that this issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System. Although SPP_URE3 had not established or documented a process for change control and configuration management for adding, modifying, replacing, or removing all CCA hardware or software, SPP_URE3 did have a Change Control program that it used for changes to its systems hardware and application/database components that were controlled by its vendor. Any changes, additions or upgrades to SPP_URE3 equipment were provided by the vendor to SPP_URE3 and included detailed procedures and configuration changes that explained the effects the new equipment would have on the SPP_URE3's system. Also, SPP_URE3 had been using a spreadsheet to document changes that occurred to its system software, but the procedure of how and when to document changes was not included in SPP_URE3’s policy. While the change control program SPP_URE3 used on its SCADA system was not a formal process, it, nonetheless, did document changes in software and hardware that affected an important component in SPP_URE3's system. | To mitigate this issue, SPP_URE3 documented a process and supporting policy for a new change control methodology. This new process and supporting policy considered different types of infrastructure and types of changes (i.e. emergency, low risk, levels of approvals, patches, etc) for CCAs. SPP_URE3 developed applicable templates, forms and change systems to be utilized to support the change control process. Lastly, SPP_URE3 trained all affected SPP_URE3 employees on the new supporting process and policy to ensure that CCA information is identified, protected and classified. SPP_URE3 certified that mitigation was complete, and SPP RE verified completion.
2011-10-31 | TRE_URE1liability Entity (TRE_URE1) | Unidentified Registered Entity 2 (TRE_URE2) | NCRXXXXX | TRE201100150 | CIP-006-1 | R1 | TRE_URE2 should have timely filed TFEs for some card reader controllers because it did not use anti-virus software and other malicious software prevention tools, where technically feasible, to detect, prevent, deter, and mitigate the introduction, exposure, and propagation of malware on all Cyber Assets within the Electronic Security Perimeters. TRE_URE2 failed to file TFEs until May 17, 2010. This issue was discovered through a Self-Report. | This violation does not pose a serious or substantial risk and posed a minimal potential and actual risk to the bulk power system. Although, some card reader controllers did not use anti-virus software and other malicious software prevention tools, the devices were behind multiple physical security protection boundaries that include at a minimum an outer layer of physical security, at least one CIP compliant card reader system and at least one set of keyed locks. | Mitigation plan was completed and verified. Filing of TFEs on May 17, 2010 addressed the issue.
2011-10-31 | TRE_URE1liability Entity (TRE_URE1) | Unidentified Registered Entity 2 (TRE_URE2) | NCRXXXXX | TRE201100151 | CIP-006-1 | R1 | TRE_URE2 should have timely filed TFEs for some card reader controllers because it did not use anti-virus software and other malicious software prevention tools, where technically feasible, to detect, prevent, deter, and mitigate the introduction, exposure, and propagation of malware on all Cyber Assets within the Electronic Security Perimeters. TRE_URE2 failed to file TFEs until May 17, 2010. This issue was discovered through a Self-Report. | This violation does not pose a serious or substantial risk and posed a minimal potential and actual risk to the bulk power system. Although, some card reader controllers did not use anti-virus software and other malicious software prevention tools, the devices were behind multiple physical security protection boundaries that include at a minimum an outer layer of physical security, at least one CIP compliant card reader system and at least one set of keyed locks. | Mitigation plan was completed and verified. Filing of TFEs on May 17, 2010 addressed the issue.
2011-10-31 | TRE_URE1liability Entity (TRE_URE1) | Unidentified Registered Entity 2 (TRE_URE2) | NCRXXXXX | TRE201000318 | CIP-007-1 | R4 | TRE_URE2 should have timely filed TFEs for some card reader controllers because it did not use anti-virus software and other malicious software prevention tools, where technically feasible, to detect, prevent, deter, and mitigate the introduction, exposure, and propagation of malware on all Cyber Assets within the Electronic Security Perimeters. TRE_URE2 failed to file TFEs until May 17, 2010. This issue was discovered through a Self-Report. | This violation does not pose a serious or substantial risk and posed a minimal potential and actual risk to the bulk power system. The Cyber Assets which do not have an anti-virus and other malicious software prevention tools also do not have operating systems installed on the devices. The lack of an operating system not only prevents anti-virus software from being loaded onto the devices, this also prevents any virus and/or malware from infecting the devices. Without the ability to become infected by a virus or malware, there is no actual risk to the bulk power system. | Mitigation plan was completed and verified. Filing of TFEs on May 17, 2010 addressed the issue.
2011-10-31 | TRE_URE1liability Entity (TRE_URE1) | Unidentified Registered Entity 2 (TRE_URE2) | NCRXXXXX | TRE201000357 | CIP-007-1 | R4 | TRE_URE2 should have timely filed TFEs on card reader controllers because it did not use anti-virus software and other malicious software prevention tools, where technically feasible, to detect, prevent, deter, and mitigate the introduction, exposure, and propagation of malware on all Cyber Assets within the Electronic Security Perimeters. TRE_URE2 failed to file TFEs until May 17, 2010. This issue was discovered through a Self-Report. | This violation does not pose a serious or substantial risk and posed a minimal potential and actual risk to the bulk power system. The Cyber Assets which do not have an anti-virus and other malicious software prevention tools also do not have operating systems installed on the devices. The lack of an operating system not only prevents anti-virus software from being loaded onto the devices, this also prevents any virus and/or malware from infecting the devices. Without the ability to become infected by a virus or malware, there is no actual risk to the bulk power system. | Mitigation plan was completed and verified. Filing of TFEs on May 17, 2010 addressed the issue.
2011-10-31 | TRE_URE1liability Entity (TRE_URE1) | Unidentified Registered Entity 2 (TRE_URE2) | NCRXXXXX | TRE201000319 | CIP-007-1 | R5 | TRE_URE2 should have timely filed TFEs on card reader controllers because the devices do not have the ability to enforce the password length; alpha, numeric and special characters; and the annual password change. TRE_URE2 failed to file TFEs until May 17, 2010. This issue was discovered through a Self-Report. | This violation does not pose a serious or substantial risk and posed a minimal potential and actual risk to the bulk power system. The Cyber Assets which do not enforce passwords length, complexity or require annual change also do not have the ability to allow users to log into the devices. The CIP standard’s requirement to use passwords is intended to prevent unauthorized system access. Therefore there is no risk to bulk power system from an unauthorized system access, due to the systems inability to grant system access. | Mitigation plan was completed and verified. Filing of TFEs on May 17, 2010 addressed the issue.
2011-10-31 | TRE_URE1liability Entity (TRE_URE1) | Unidentified Registered Entity 2 (TRE_URE2) | NCRXXXXX | TRE201000358 | CIP-007-1 | R5 | TRE_URE2 should have timely filed TFEs on card reader controllers because the devices do not have the ability to enforce the password length; alpha, numeric and special characters; and the annual password change. TRE_URE2 failed to file TFEs until May 17, 2010. This issue was discovered through a Self-Report. | This violation does not pose a serious or substantial risk and posed a minimal potential and actual risk to the bulk power system. The Cyber Assets which do not enforce passwords length, complexity or require annual change also do not have the ability to allow users to log into the devices. The CIP standard’s requirement to use passwords is intended to prevent unauthorized system access. Therefore there is no risk to bulk power system from an unauthorized system access, due to the systems inability to grant system access. | Mitigation plan was completed and verified. Filing of TFEs on May 17, 2010 addressed the issue.
2011-10-31 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 5 (TRE_URE5) | NCRXXXXX | TRE201100351 | CIP-003-2 | R2.3 | As a result of an Audit, Texas RE determined that TRE_URE5's delegation of authority for specific actions to a named delegate, specifically approval of exceptions to its security policy did not include the name of the delegate, only the title and date of designation. | This issue did not pose a serious or substantial risk and posed a minimal potential and actual risk to the bulk power system because although the document did not explicitly list the name, the title was listed. During the compliance period, that title/position was held by the same person. Although that person changed official job titles, the entity presented other documents and emails that demonstrated that that person was the person being referred to in the delegation of authority. | TRE_URE5 revised the designation of authority so that it was consolidated into one document and includes delegate’s name, title, and date of designation. TRE_URE5 also revised the ‘Exceptions’ form to include the name of the authorized delegate, as well as their title. This will cause any change of authorized delegate to require a change to the forms as well.
2011-10-31 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201102908 | CIP-002-3 | R4 | During an annual internal review of the CIP Standards, WECC_URE1 found a discrepancy in its procedures. Specifically, WECC_URE1's senior manager failed to review the Risk Based Assessment Methodology (RBAM) for the 2010 calendar year. WECC_URE1 notes that versions 1 and 2 of the standard required an entity to approve annually the list of Critical Assets and the list of Critical Cyber Assets. However, when Version 3 of the standard became effective, the requirement included an annual review and approval of the RBAM in addition to annually approving the list of Critical Assets and the list of Critical Cyber Assets. | Although WECC_URE1 did not have a signed and dated record of the senior manager or delegate(s)’s annual approval of its 2010 Risk Based Assessment Methodology (RBAM), WECC_URE1's CIP Senior Manager had approved the Critical Asset and Critical Cyber Asset lists for calendar year 2010. While WECC_URE1 failed to review the RBAM in the calendar year 2010, WECC_URE1 created its RBAM in 2009, and annually approved the RBAM in 2009 and again in 2011. Additionally, WECC_URE1's list of Critical Assets and Critical Cyber Assets is null, which had not changed from years prior. Therefore, WECC_URE1's failure to update its procedure to include the annual approval of the RBAM did not negatively impact the BPS because the lists of Critical Assets and Critical Cyber Assets for WECC_URE1 were and remained null for the year. For these reasons, WECC determined this issue posed a minimal risk to the reliability of the BPS. | WECC_URE1 updated the annual approval procedure to include an annual review and approval of its RBAM by the CIP Senior Manager. Additionally, WECC_URE1 has hired a third-party consultant to validate the RBAM.
2011-09-30 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 1 (FRCC_URE1) | NCRXXXXX | FRCC201000339 | CIP-002-1 | R1 | The entity self-reported that the entity's risk-based assessment methodology as required by CIP-002-1 R1 was not in effect as of the date in which the entity was required to be in compliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the entity using its own risk-based assessment methodology, determined that it had no Critical Assets that could impact BPS reliability. In addition, the entity is relatively small. | The entity created a risk-based assessment methodology and Critical Asset list.
2011-09-30 | Florida Reliability Coordinating Council (FRCC) | Unidentified Registered Entity 4 (FRCC_URE4) | NCRXXXXX | FRCC201000352 | CIP-002-1 | R1 | The entity self-reported that its earliest risk-based assessment methodology, as required by CIP-002-1 R1, was not effective as of the date in which the entity was required to be in compliance and hence, the entity was in noncompliance with this Standard. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because the risk-based assessment was not documented for only a period and when it was applied did not result in any Critical Assets. In addition, the entity is relatively small. | The entity completed a risk-based assessment methodology and no Critical Asset were identified.
2011-09-30 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 1 (MRO_URE1) | NCRXXXXX | MRO201100309 | CIP-006-1 | R1 | The entity self-reported noncompliance with CIP-006-1 R1 because it discovered that its physical security plan was not approved by a senior manager or delegate. The violation was discovered during an internal audit performed by a third-party industry expert. | MRO determined that this issue posed a minimal risk to the reliability of the bulk power system (BPS) because the issue related to the failure to obtain the required signature and did not change the development or implementation of the physical security plan. | The entity performed the following actions to mitigate the issue: (1) revised its CIP leadership designation procedure and removed chief security officer involvement in designating the senior leader; (2) the senior security specialist was advised of the errors and the proper method of delegating authority from the senior manager to another individual, and the proper method of documenting review and approval of the NERC CIP physical security plan; (3) the physical security plan was modified to explicitly state who can approve the plan and that the approval has to be documented; (4) a formal delegation form for the chief security officer was completed evidencing the delegation of authority to review and approve the physical security plan; (5) the chief security officer reviewed and approved the NERC CIP physical security plan; (6) the physical security plan was modified to explicitly state that all changes require the review of the senior manager or his delegate; and (7) a review of all CIP requirements were performed to identify whether other areas require review or approval of the senior manager or delegate.
2011-09-30 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 13 (MRO_URE13) | NCRXXXXX | MRO201000216 | CIP-004-1 | R4.1 | During a CIP Spot Check, conducted jointly by MRO and another Regional Entity, it was determined that the entity was not able to demonstrate that it maintained and reviewed a list of personnel with authorized cyber access to Critical Cyber Assets. The entity did demonstrate that its unescorted physical access list for personnel including contractors and vendors was sufficient. | MRO determined that this issue posed a minimal risk to the reliability of the bulk power system (BPS) because although the entity did not review its list of authorized individuals on a quarterly basis, the individuals were properly authorized and had received cyber security training and personnel risk assessments were conducted prior to granting such access. | This partial period issue was corrected prior to the CIP Spot Check. Subsequently, the entity added granularity to its access tracking spreadsheet which further describes the five types of cyber access it grants. The entity's list is reviewed quarterly and updated within 7 calendar days of any change of personnel with access to Critical Cyber Assets or any change in the access rights of such personnel.
2011-09-30 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 2 (MRO_URE2) | NCRXXXXX | MRO201000238 | CIP-004-1 | R2 | The entity self-reported noncompliance with CIP-004-1 R2 because two contractors were not added to the authorized cyber or authorized unescorted physical access to Critical Cyber Assets (CCAs) access list. The entity failed to record the access approval on the list. As a result of not being added to the access list, two contractors did not have cyber security training within the required timeframe. | MRO_URE2determined that this issue posed a minimal risk to the reliability of the bulk power system (BPS) because the two CCAs that were accessed were later classified as non-critical Cyber Assets. They are not essential to the operation of the generating unit and have been moved from the Electronic Security Perimeter. | The entity reclassified the CCAs as non-critical Cyber Assets. Additionally, personnel involved in granting access have been reminded of the processes required for authorized cyber or authorized unescorted physical access.
2011-09-30 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 2 (MRO_URE2) | NCRXXXXX | MRO201000239 | CIP-004-1 | R3 | The entity self-reported noncompliance with CIP-004-1 R3 because one contractor was provided access to Critical Cyber Assets (CCAs) before the compliance date. However, this contractor was not added to the access list during the substantial compliant period for the Cyber Assets. As a consequence of not being added to the access list, this contractor did not have a personnel risk assessment (PRA) conducted pursuant to the entity's PRA program prior to such personnel being granted such access. | MRO_URE2determined that this issue posed a minimal risk to the reliability of the bulk power system (BPS) because the CCA was later determined to be non-critical and was later removed from the Electronic Security Perimeter. | The entity revoked access to the CCAs for the individual.
2011-09-30 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 2 (MRO_URE2) | NCRXXXXX | MRO201000240 | CIP-004-1 | R4 | The entity self-reported noncompliance with CIP-004-1 R4 because three contractors were not added to the authorized cyber or authorized unescorted physical access to Critical Cyber Assets (CCAs) access list and two contractors were not removed from the access list as required by CIP-004-1 R4. Three contractors accessed three personal computers at 2 of the entity's generating stations. The contractors were from three different companies. Additionally, two janitors from one janitorial contractor were not removed from the list of personnel with authorized unescorted physical access within seven calendar days of their not-for-cause termination. Both janitors were terminated during the substantially compliant period but were not deleted from the list. | MRO_URE2determined that this issue posed a minimal risk to the reliability of the bulk power system (BPS) because two of the CCAs that were accessed were later classified as non-critical Cyber Assets. They are not essential to the operation of the generating unit and have been moved from the Electronic Security Perimeter. Additionally, one CCA was accessed with view only privileges. The two janitors did not have access to the CCAs. They were just not removed from the list. | The entity reclassified the CCAs as non-critical Cyber Assets. The entity removed the janitors from the access list.
2011-09-30 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 3 (MRO_URE3) | NCRXXXXX | MRO201000241 | CIP-004-1 | R4.1 | The entity self-reported noncompliance with CIP-004-1 R4 because its authorized cyber or authorized unescorted physical access to Critical Cyber Assets (CCAs) access lists were not updated within 7 calendar days of the granting of access for 3 of 546 (less than 1%) individuals. Specifically, two access requests were processed out of order, and therefore, were not routed through the appropriate workflow. The other access was due to an oversight in documentation. The administrator that configured the access was configuring appropriate access per verbal approval for access, but failed to document the approval. As a result, the list of authorized personnel was not updated within 7 calendar days of a change in access rights of the personnel. One individual retained access for 18 days, another individual retained access for 52 days, another individual retained access for 5 days following the change in business need. | MRO determined that this issue posed a minimal risk to the reliability of the bulk power system (BPS) because all of the individuals had personnel risk assessments and cyber security training. Additionally, logs from the card reader system and user access logs demonstrate that access was not used for each individual. | At the point of discovery, the appropriate requests were submitted and completed correctly by personnel, removing access the same day.
2011-09-30 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 4 (MRO_URE4) | NCRXXXXX | MRO201000243 | CIP-004-1 | R4.1 | The entity self-reported noncompliance with CIP-004-1 R4 because its authorized cyber or authorized unescorted physical access to Critical Cyber Assets (CCAs) access lists were not updated within 7 calendar days of the granting of access for 3 of 546 (less than 1%) individuals. The removal tasks were routed appropriately but were processed incorrectly. Specifically, removal tickets were submitted in the access management tool, the work tickets were routed appropriately, but, at the last step, the guard staff failed to go into the badging server and remove the access from the badge. Therefore, the access list was updated, but the access remained on the actual badges. As a result, personnel were removed from the list of authorized personnel without actual revocation of access within the card access system, causing retention of access in excess of 7 calendar days. One individual retained access for 88 days following the change in business need, another individual retained access for 189 days following the change in business need, and another individual retained access for 63 days following the change in business need. | MRO determined that this issue posed a minimal risk to the reliability of the bulk power system (BPS) because the access removals were related to job changes, rather than for cause terminations. Additionally, logs from the card reader system and user access logs demonstrate that access was not used for each individual. | At the point of discovery, the appropriate requests were submitted and completed correctly by personnel, removing access the same day.
2011-09-30 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 5 (MRO_URE5) | NCRXXXXX | MRO201100257 | CIP-005-1 | R1.4, R1.6 | During a Spot Check, MRO determined that the entity failed to identify, protect, and document all noncritical Cyber Assets located within the Electronic Security Perimeter (ESP). MRO identified one noncritical Cyber Asset device (intermediate anti-virus server) that was moved "in and out" of the ESP every time the entity needed to update anti-virus signatures. Additionally, the entity failed to document another noncritical Cyber Asset device (network switch) which served as an access point to the ESP. | MRO determined that this issue posed a minimal risk to the reliability of the bulk power system (BPS) because the intermediate anti-virus server was configured as a hardened single purpose device. Additionally, although it was not identified, the network switch was being protected by the entity's IT policy consistent with CIP-005. | The intermediate anti-virus server was relocated outside of the ESP. Additionally, the entity revised its anti-virus signature update process to eliminate the need to re-introduce the intermediate anti-virus server into the ESP each time the anti-virus signatures on the CCAs needed to be updated. The network switch was added to the entity’s Cyber Asset inventory as a non-critical Cyber Asset residing within an ESP. IT then reviewed the protection being afforded to the network switch and confirmed it was being protected pursuant to the requirements of CIP-005. To confirm all Cyber Assets associated with Critical Assets were inventoried and properly classified, the entity decided to re-inventory its Cyber Assets. The inventory included a physical identification of the Cyber Assets followed by an electronic ping sweep of the Cyber Assets residing within the ESP. As a result of this process, and with the clearer understanding of the classification requirements gained through the evaluation of this finding, a similar network switch used to connect non-critical Cyber Assets within the ESP was identified and added to the entity’s inventory of non-critical Cyber Assets. Unlike the first network switch, this switch was located within a Physical Security Perimeter.
2011-09-30 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 5 (MRO_URE5) | NCRXXXXX | MRO201100259 | CIP-006-1 | R1.1 | During a Spot Check, MRO determined that the entity failed to locate all Cyber Assets in a defined Electronic Security Perimeter (ESP) within an identified Physical Security Perimeter (PSP) and failed to incorporate a completely enclosed six-wall border for a PSP in its Physical Security Plan. MRO discovered an opening above the ceiling tiles in the breezeway connecting the control center and administration buildings. The opening allowed passage from the breezeway into the control center's designated PSP, bypassing access controls. Although the unprotected opening in the PSP boundary provided the ability to bypass access control mechanisms, access to any Critical Cyber Assets within the PSP requires clearance of additional access controls. | MRO determined that this issue posed a minimal risk to the reliability of the bulk power system (BPS) because the entity's facility is protected against unauthorized access by three levels of physical security, and also includes video surveillance, and two levels of credential check-points. Additionally, although the unprotected opening in the PSP boundary provided the ability to bypass access control mechanisms, access to any Critical Cyber Assets within the PSP requires clearance of additional access controls. | During the spot check, MRO verified that the entity secured the opening with wire mesh, therefore restoring the six-wall border. MRO took photographs of the opening both before and after mitigation.
2011-09-30 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 5 (MRO_URE5) | NCRXXXXX | MRO201100331 | CIP-006-3c | R7 | The entity’s corporate security on-call personnel were notified by the entity’s security system contractor of a trouble alarm on the access control system. The support team was called in to review the system and locate the source of the alarm. The team first confirmed that the access control and logging system was operating properly at all the Physical Security Perimeter (PSP) access points. They then checked the system logs for any evidence of an attack or cyber intrusion following the appropriate procedure. No such evidence was found, and the incident response evaluation was documented. The team determined that the problem was associated with the nightly file backup process. The system logs indicated the nightly backup did not run completely. The team proceeded to restore following the change control, restoration, and testing procedures. The problem resurfaced on two more occasions. While the physical access system continued to provide the required access control and logging functionality, it was clear the system had a persistent technical problem. After the third incident, the team conducted a thorough analysis of all the services and discovered that the problem was a conflict between a replication application and the entity's automatic backup recovery system. Moreover, the in-depth analysis of the failures indicated that the data restoration process was actually corrupting the data while it was being restored. The entity self-reported noncompliance with CIP-006-3c R7 because an issue with its system led to corruption of physical access logs for its designated PSPs. Through recovery of corrupted log files and review of video surveillance recordings, all but five (5) hours of a 75-hour gap could be reconstructed. Therefore, the entity failed to retain physical access logs for at least ninety calendar days as required by CIP-006-3c R7. | MRO determined that this issue posed a minimal risk to the reliability of the bulk power system (BPS) because during the time logging did not function properly, the access controls were fully functional, and the five-hour gap was limited to two access points. Additionally, the gap in available logs spanned the time period of 12:03 pm to 5:27 pm CST. | The entity recovered all but five hours of the 75 hours of corrupted log files. Additionally, the entity reconfigured the system to preclude any subsequent data loss.
2011-09-30 | Midwest Reliability Organization (MRO) | Unidentified Registered Entity 5 (MRO_URE5) | NCRXXXXX | MRO201100254 | CIP-009-2 | R1 | The entity self-reported noncompliance with CIP-009-2 R1 because it did not have recovery plans for assets declared as Critical Cyber Assets. The assets were misclassified as Critical Cyber Assets in early versions of the entity's risk-based assessment methodology (RBAM). The entity's early methodology was overly broad and declared all Cyber Assets within the entity's Electronic Security Perimeters (ESPs) as Critical Cyber Assets. | MRO determined that this issue posed a minimal risk to the reliability of the bulk power system (BPS) because the misclassified Cyber Assets in question reside within the entity's Physical Security Perimeters and ESPs and were protected by the existing security controls implemented by the entity. The entity has continued to refine its RBAM and assessment of assets that are critical to the operation of its Critical Assets. Additionally, mock audits and assessments brought this issue to light and thus, exemplify a strong culture of compliance at the entity. | The entity has mitigated the issue by correctly identifying these assets as Cyber Assets and in some cases has moved the devices outside ESPs where appropriate.
2011-09-30 | Northeast Power Coordinating Council (NPCC) | Unidentified Registered Entity 2 (NPCC_URE2) | NCRXXXXX | NPCC2011007273 | CIP-007-1 | R4 | The entity self-reported noncompliance with the CIP Standards arising from the entity’s failure to timely submit Technical Feasibility Exception (TFE) requests in accordance with NERC procedures. There were 15 late TFE requests that were filed. The TFE- Part A approval for all was granted by NPCC and NPCC determined that these issues resulted from failures to comply with administrative processes related to the submission of formal TFE requests. | NPCC determined that there was a minimal risk to the reliability of the bulk power system. The entity's system is structured with intrusion prevention sensors at the network and host level, hardened operating systems, strong account management, logging for system configuration changes, and periodic vulnerability scans are run on the devices in question. The compensating measures were in place prior to the due date on which all such TFE requests were to originally have been submitted to NPCC. | The TFE- Part A approval was granted by NPCC. The approved TFE requests are open-ended because the hardened operating system in question does not support third party software.
2011-09-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 1 (RFC_URE1) | NCRXXXXX | RFC201100863 | CIP-003-3 | R2 | The entity submitted a Self-Report to ReliabilityFirst identifying a possible issue concerning CIP-003-3 R2 because the entity has one senior manager who was approving the implementation of and adherence to the CIP Standards, but failed to identify this individual by name, title, and date of designation as the CIP senior manager. | ReliabilityFirst determined that the issue posed a minimal risk to the reliability of the bulk power system (BPS) because the entity has one senior manager, who was performing the function of a CIP senior manager throughout the duration of the issue by approving the implementation of and adherence to the CIP Standards. In addition, the entity has no Critical Cyber Assets. | The entity designated its senior manager as the CIP senior manager.
2011-09-30 | ReliabilityFirst Corporation (ReliabilityFirst) | Unidentified Registered Entity 3 (RFC_URE3) | NCRXXXXX | RFC201000397 | CIP-004-1 | R4 | During a Spot Check, ReliabilityFirst determined that the entity failed to include the specific electronic access rights of personnel with authorized cyber access to Critical Cyber Assets on its lists of authorized personnel. The entity maintained two lists of personnel with authorized cyber access to Critical Cyber Assets: a general list of personnel and a list of support personnel. Both of these lists failed to include the specific electronic access rights of personnel with access to Critical Cyber Assets. ReliabilityFirst determined noncompliance with CIP-004-1 R4 by failing to include the specific electronic access rights of personnel with authorized cyber access to Critical Cyber Assets on its lists of authorized personnel. | ReliabilityFirst determined that the issue posed a minimal risk to the reliability of the bulk power system (BPS). This issue did not result from unauthorized access to Critical Cyber Assets; in fact the personnel on each access list had satisfied all of the requirements for access to Critical Cyber Assets, including the completion of annual cyber security training and personnel risk assessments, in accordance with CIP-004-1. Instead, this issue resulted from the entity's failure to specify the electronic access rights to Critical Cyber Assets within its lists of authorized personnel. Therefore, this was a documentation issue, rather than an instance of unauthorized access. | The entity memorialized the actions it took to address the issue related to CIP-004-1 R4. The entity updated its lists of authorized personnel to include the specific electronic access rights of personnel with authorized access to its Critical Cyber Assets.
2011-09-30 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 10 (SERC_URE10) | NCRXXXXX | SERC201100745 | CIP-005-1 | R1 | SERC_URE10 submitted a Self-Report to SERC reporting that it had failed to appropriately classify an asset as a non critical Cyber Asset within a defined Electronic Security Perimeter (ESP). Specifically, when applying the methodology, personnel did not realize the asset was located on a network with Critical Cyber Assets (CCA) that utilize a routable protocol. | SERC determined that the issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because: (1) The device was a hardened appliance that was utilized to monitor the network performance and system logging. (2) The appliance resided within the Physical Security Perimeter, which requires CIP 4 credentials or escorted access in order to gain physical access. | SERC_URE10 completed the following actions: (1) Removed the asset from the ESP. (2) Updated its CCA Identification Training to further clarify how to identify non-critical cyber assets within the ESP. (3) Trained its staff on the new CCA Identification process. (4) Created and reviewed with impacted business units the instructional procedure for the required annual CCA review.
2011-09-30 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 11 (SERC_URE11) | NCRXXXXX | SERC200900342 | CIP-004-1 | R2 | SERC_URE11 submitted a Self-Report to SERC reporting that it had retained an employee on the list that would have allowed access to a Control Center when the employee did not possess the required Cyber Security training. | SERC determined that the issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because the employee had been working for the entity for more than six years at the time of the incident. | SERC_URE11 completed the following actions: (1) Revoked card access allowing physical entry to the Control Center for the five identified employees was revoked. (2) Completed a personnel risk assessment and associated training for one of the five employees was completed to enable job required access to the Control Center. (3) Created a written procedure establishing a quarterly review of personnel having physical access to Critical Cyber Assets, including the Control Center that takes place within 5 calendar days of the end of a calendar year quarter.
2011-09-30 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 11 (SERC_URE11) | NCRXXXXX | SERC200900343 | CIP-004-1 | R3 | SERC_URE11 submitted a Self-Report to SERC reporting that it had allowed an employee, who did not possess the required Personnel Risk Assessment, to retain physical access to a Control Center. | SERC determined that the issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because the employee had been working for the entity for more than six years month at the time of the incident. | SERC_URE11 completed the following actions: (1) Revoked card access allowing physical entry to the Control Center for the five identified employees was revoked. (2) Completed a personnel risk assessment and associated training for one of the five employees was completed to enable job required access to the Control Center. (3) Created a written procedure establishing a quarterly review of personnel having physical access to Critical Cyber Assets, including the Control Center that takes place within 5 calendar days of the end of a calendar year quarter.
2011-09-30 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 11 (SERC_URE11) | NCRXXXXX | SERC200900344 | CIP-004-1 | R4 | SERC_URE11 submitted a Self-Report to SERC reporting that it had allowed four employees who were not included on the authorized cyber or authorized unescorted physical access lists to have access to Critical Cyber Assets. | SERC determined that the issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because the persons involved at the time of the of the incident were long term employees. | SERC_URE11 completed the following actions: (1) Revoked card access allowing physical entry to a Control Center for the five identified employees was revoked. (2) Completed a personnel risk assessment and associated training for one of the five employees was completed to enable job required access to a Control Center. (3) Created a written procedure establishing a quarterly review of personnel having physical access to Critical Cyber Assets, including a Control Center, that takes place within 5 calendar days of the end of a calendar year quarter.
2011-09-30 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 12 (SERC_URE12) | NCRXXXXX | SERC2011007153 | CIP-003-3 | R2 | This issue was discovered during a SERC on-site audit. SERC_URE12 was not able to establish the date of the delegate’s designation as required by the Standard. | SERC determined that the issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because: (1) SERC_URE12 has no Critical Assets. (2) SERC_URE12 does not own or operate any facilities that would meet any of the Critical Asset Criteria set forth in the proposed CIP-002-4. | SERC_URE12 completed the following action: Modified its procedure to include the date of designation of the delegate.
2011-09-30 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 2 (SERC_URE2) | NCRXXXXX | SERC2011007529 | CIP-002-1 | R2 | This issue was discovered during a SERC off-site audit. SERC_URE2 failed to consider all of its assets in the performance of the risk-based assessment methodology (RBAM) as required. Specifically, the evidence showed that 21 of 28 assets were not evaluated using the documented criteria. | SERC determined that the issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because: (1) SERC_URE2 has no Critical Assets (CA) and does not own or operate any facilities that would meet any of the Critical Asset Criteria (CCA) set forth in the proposed CIP-002-4. (2) SERC_URE2 has a documented RBAM. | SERC_URE2 completed the following action: Modified its procedure to clearly reflect the use of the RBAM to evaluate and identify CAs and CCAs.
2011-09-30 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 2 (SERC_URE2) | NCRXXXXX | SERC2011007527 | CIP-002-2 | R4 | This issue was discovered during a SERC off-site audit. SERC_URE2 was unable to provide a signed and dated record of the senior manager’s or delegate’s annual approval of the risk-based assessment methodology (RBAM) as required. | SERC determined that the issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because: (1) SERC_URE2 has no Critical Assets (CA) and does not own or operate any facilities that would meet any of the Critical Asset Criteria (CCA) set forth in the proposed CIP-002-4. (2) SERC_URE2 has a documented RBAM. | SERC_URE2 completed the following action: Modified its RBAM procedure to reflect an annual review and approval by the designated and documented senior manager.
2011-09-30 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 2 (SERC_URE2) | NCRXXXXX | SERC2011007528 | CIP-003-1 | R2 | This issue was discovered during a SERC off-site audit. SERC_URE2 failed to provide evidence that a single senior manager had been assigned with overall responsibility and authority for CIP-002 through CIP-009 as required. | SERC determined that the issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because SERC_URE2 has no Critical Assets and does not own or operate any facilities that would meet any of the Critical Asset Criteria set forth in the proposed CIP-002-4. | SERC_URE2 completed the following action: Assigned a senior manager with the overall responsibility and authority for leading and managing the implementation of and adherence to the CIP-002 through CIP-009.
2011-09-30 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 3 (SERC_URE3) | NCRXXXXX | SERC2011007282 | CIP-002-2 | R4 | This issue was discovered during a SERC off-site audit. SERC_URE3 was unable to provide a signed and dated record of the senior manager’s or delegate’s annual approval of the risk-based assessment methodology (RBAM) as required by the Standard for 2010. Specifically, SERC_URE3 established that its RBAM was reviewed and approved as required for 2009 and 2011. | SERC determined that the issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because: (1) SERC_URE3 has no Critical Assets and does not own or operate any facilities that would meet any of the Critical Asset Criteria set forth in the proposed CIP-002-4. (2) SERC_URE3 has a documented RBAM. | SERC_URE3 completed the following action: Revised its Memorandum to reflect that on an annual basis, the RBAM will be reviewed, approved by the designated and documented Senior manager for compliance, and will be used to identify critical and cyber assets.
2011-09-30 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 3 (SERC_URE3) | NCRXXXXX | SERC2011007290 | CIP-003-1 | R2 | This issue was discovered during a SERC off-site audit. SERC_URE3 failed to provide evidence that a designated senior manager was assigned responsibility for CIP-002 through CIP-009 as required. | SERC determined that the issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because: (1) SERC_URE3 has no critical assets and does not own or operate any facilities that would meet any of the Critical Asset Criteria set forth in the proposed CIP-002-4. (2) SERC_URE3 is a minimal size utility. | SERC_URE3 completed the following action: Revised its documentation to reflect that a single senior manager, identified by name, title, date of designation and contact information, is responsible for implementation and adherence to CIP-002 through CIP-009.
2011-09-30 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 5 (SERC_URE5) | NCRXXXXX | SERC2011007283 | CIP-003-1 | R2 | This issue was discovered during a SERC off-site audit. SERC_URE5 failed to provide evidence that a single senior manager had been assigned with overall responsibility and authority for CIP-002 through CIP-009 as required. SERC_URE5 created a procedure designating the responsibility and authority to a senior manager, who was identified by name, title, business phone and business address. This is a gap issue. | SERC determined that the issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because: (1) SERC_URE5 has no Critical Assets. (2) H69SERC_URE5 does not own or operate any facilities that would meet any of the Critical Asset Criteria set forth in the proposed CIP-002-4. | SERC_URE5 completed the following action: assigned a single senior manager with overall responsibility for compliance with CIP-002 through CIP-009.
2011-09-30 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 6 (SERC_URE6) | NCRXXXXX | SERC2011006593 | CIP-004-1 | R4 | SERC_URE6 submitted a Self-Report to SERC reporting that it had 12 out of 191 individuals who were omitted or incorrectly documented in its Critical Cyber Asset access lists. Also, one contracted custodian was authorized for one Physical Security Perimeter (PSP) list, but was inadvertently given access to two PSP lists and used this access for a total of 41 days. One of the employees accessed the PSP but had a current PRA and cyber security training. | SERC determined that the issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system because: (1) All of the omitted individuals possessed current training Personal Risk Assessments. (2) All of the omitted individuals possessed current CIP training credentials. (3) All individuals had a valid business need for their access. | SERC_URE6 completed the following actions: (1) Remedied all of the identified discrepancies in the existing CCA access lists (2) Created a new electronic access request form and request for change approval tool regarding access privileges to CCAs. (3) Sent an awareness communication to personnel involved in granting and approving access to CCAs and maintaining CCA access lists. (4) Implemented a quality assurance review process for all grants of unescorted physical access to CCAs.
2011-09-30 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 9 (SERC_URE9) | NCRXXXXX | SERC2011006763 | CIP-002-1 | R4 | This issue was discovered during a SERC off-site audit. SERC_URE9 failed to sign and date its annual approval of the list of Critical Assets (CA) and the list of Critical Cyber Assets (CCA) as required. | SERC determined that the issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because: (1) SERC_URE9 has no Critical Assets. (2) SERC_URE9 does not own or operate any facilities that would meet any of the Critical Asset Criteria set forth in the proposed CIP-002-4. (3) SERC_URE9 does not own or operate any BPS equipment. | SERC_URE9 completed the following action: Created a procedure requiring the designated senior manager to review and approve the risk-based assessment methodology, CA and CCA lists on an annual basis and establishing a retention policy for the signed and dated CA and CCA approval lists.
2011-09-30 | SERC Reliability Corporation (SERC) | Unidentified Registered Entity 9 (SERC_URE9) | NCRXXXXX | SERC2011006764 | CIP-003-1 | R2 | This issue was discovered during a SERC off-site audit. SERC_URE9 failed to provide evidence that a single senior manager had been assigned overall responsibility and authority for CIP-002 through CIP-009 as required. SERC_URE9 put a procedure in place in June 2010; however; it did not contain the title, business phone and business address of the senior manager as required. | SERC determined that the issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS) because: (1) SERC_URE9 has no Critical Assets. (2) SERC_URE9 does not own or operate any facilities that would meet any of the Critical Asset Criteria set forth in the proposed CIP-002-4. (3) SERC_URE9 does not own or operate any BPS equipment. | SERC_URE9 completed the following action: Developed a written document assigning responsibility for CIP-002 through CIP-009 to a senior manager identified.
2011-09-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 2 (SPPRE_URE2) | NCRXXXXX | SPP201000213 | CIP-007-1 | R5.3 | In a self-report, SPP_URE2 indicated that a password on its legacy SCADA system (a Critical Cyber Asset) was non-compliant with CIP-007-1 R5.3 because (1) it did not incorporate six characters per R5.3.1; (2) did not include a combination of alpha, numeric, and "special characters" per R5.3.2; and (3) was not changed annually per R5.3.3. | SPP RE determined that the issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). Although the root administrator password on SPP_URE2's legacy SCADA system (a Critical Cyber Asset) was non-compliant, the user access passwords that were used to access the legacy SCADA application addressed the requirements of CIP-007-1 R5.3. Further, SPP_URE2 utilized an outside security service that would detect and alarm any attempts at unauthorized access to the SCADA system. This combination of user access password requirements and unauthorized access monitoring established a redundant shield against unauthorized intrusions. | SPP_URE2 submitted a TFE, which was subsequently accepted and approved. An upgrade of the legacy SCADA system was installed and the new system addresses the requirements of CIP-007-1 R5.3.
2011-09-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 4 (SPPRE_URE4) | NCRXXXXX | SPP201000300 | CIP-002-1 | R3 | In a Spot Check, it was found that SPP_URE4's Critical Cyber Asset (CCA) list included four switches that were located logically outside the Electronic Security Perimeter. The switches were not essential to the function of the Critical Asset and should not have been included on the CCA list. | SPP RE determined that the issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). The four Cisco switches that had been included on the list of CCAs for SPP_URE4 did not, in fact, qualify as CCAs and, therefore, should not have been included on the list of CCAs. Because the four switches were the only “CCAs” located outside the ESP, and because the switches are not, in fact, CCAs, no CCAs were left unprotected or were subject to compromise. | SPP_URE4 updated its CCA list and the four switches were removed.
2011-09-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 5 (SPPRE_URE5) | NCRXXXXX | SPP201000351 | CIP-007-1 | R3 | SPPRE_URE5 self reported that it does not currently have a patch management procedure in place for third party applications installed on Critical Cyber Assets. The processes for network patch management and updates were performed informally and were not documented. SPPRE_URE5 was using an application to identify vulnerabilities in third party applications. | SPP RE determined that the issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). Although SPPRE_URE5 had not documented when it performed its process for network patch management and updates, the patch management and updates were, nonetheless, being performed. The performance of the management and updating is what minimized the risk to the BES. The lack of documentation did not impact the BES enough to raise the risk beyond minimal. | SPPRE_URE5 incorporated checks for security concerns into a tracking system to generate automated tickets, and these tickets are updated and closed once completed. Patches not applicable are not be installed and are documented within the ticket. The network operating system was updated on applicable devices. Any devices which do not support the latest network operating system were documented and known vulnerabilities have been documented and mitigated. Scans are to be used as a identification and verification component of this procedure.
2011-09-30 | Southwest Power Pool Regional Entity (SPP RE) | Unidentified Registered Entity 5 (SPPRE_URE5) | NCRXXXXX | SPP201000350 | CIP-007-1 | R2 | SPPRE_URE5 self reported that as a result of a Vulnerability Assessment, the configuration review of its electronic ports and services showed that one of the systems is not appropriately ‘hardened’, i.e., not all unnecessary services were disabled, ensuring that authentication to the system, or enumeration protection of information related to the system, were adequate. The configurations for the network devices responsible for CCA communications did not have some of their services disabled, in violation of this Standard. The identified services did not appear to be necessary and should have been disabled to reduce the footprint of the devices on the network. Should a vulnerability be discovered in one of these services, the risk could be mitigated by disabling the service. | SPP RE determined that the issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). The unnecessary ports and services were open on routers only and not on Critical Cyber Assets within the ESP. Furthermore, event logs sampled did not list these services as activated prior to them being disabled. | SPPRE_URE5 disabled the ports and services in question on its network devices responsible for CCA communications. By disabling these devices, SPPRE_URE5 prevented the possibility of any of these devices causing a cyber vulnerability.
2011-09-30 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 1 (TRE_URE1) | NCRXXXXX | TRE201100262 | CIP-003-2 | R1 | TRE_URE1’s self-reported that its Cyber Security policy document did not address all requirements of CIP-002When examining TRE_URE1’s Cyber Security policy in place at the beginning of the audit period, Texas RE concluded that the following deficiencies existed: • Did not address identifying or documenting a risk-based assessment in accordance with CIP-002-3, R1. • Did not directly address the identification of “Critical Asset”, in reference to the NERC definition of “Critical Asset”. This is deficient in accordance with CIP-002-3, R2. • Did not directly address the identification of “Critical Cyber Asset”, in reference to the NERC definition of “Critical Cyber Asset”. This is deficient in accordance with CIP-002-3, R3. • Did not address the requirement for annual approval of the risk-based methodology in accordance with CIP-002-3 R4. | This issue did not pose a serious or substantial risk and posed a minimal actual and potential risk to the bulk power system because TRE_URE1 had identified and documented a risk-based assessment methodology (RBAM), performed its RBAM, identified the Critical Asset and Critical Cyber Asset (CCA) lists and all were approved by a senior manager. In addition, the Cyber Security policy was made readily available to all personnel who had access to or who were responsible for CCAs. | This issue had already been mitigated by the time of the audit; the issue represents a deficiency with TRE_URE1’s Cyber Security policy at the date of registration. New Cyber Security policy was in place at the time of the audit, and it included the items missing in the original document. In addition, to the modifications to policy statements within the Cyber Security policy document, a supplement was added to explicitly cross reference each CIP requirement with the corresponding policy statement(s), thus demonstrating that the policy addresses each of the CIP requirements. The addition of this cross reference feature within the document provides documentation that the policy not only addresses all the requirements within CIP-002 through CIP-009 but also provides a mechanism to ensure the policy will continue to align with the CIP standards throughout each review and/or update.
2011-09-30 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 3 (TRE_URE3) | NCRXXXXX | TRE201000100 | CIP-004-1 | R4 | During a quarterly review, TRE_URE3 discovered that a manually kept aggregated list of personnel with authorized cyber or authorized unescorted physical access to Critical Assets (CA) and Critical Cyber Assets (CCA) was not timely updated when access was granted/revoked for 30 individuals. TRE_URE3 self-reported this issue, stating that nine (9) individuals were given physical access but not added to list within seven days, twelve (12) individuals whose physical access had been revoked were not removed from the list within seven days, and nine (9) individuals were given electronic access but not added to the list within seven days. | This issue did not pose a serious or substantial risk and posed a minimal potential and actual risk to the bulk power system (BPS) because only personnel who had personal risk assessment (PRA) and Cyber Security Training had access at all times. The list subject to the non-compliance does not determine access to CCA’s; Access is granted or denied from separate lists that were updated with the correct personnel names and access within the required timeframe. | Computer program written for verifying the access list is current. TRE_URE3 made the following changes in office procedures: (1) data center access request form modified to include a review by a Cyber Security staff member at the control center, (2) Security will now notify the Cyber Security staff member at the control center when any change is made to physical access list, (3) to prevent recurrence, automated alerts are to issued Cyber Security staff member at the control center are generated whenever changes to access are made.
2011-09-30 | Texas Reliability Entity (Texas RE) | Unidentified Registered Entity 8 (TRE_URE8) | NCRXXXXX | TRE201100241 | CIP-004-2 | R2.2.4 | During a Spot-Check, Texas RE reviewed a training presentation and determined that TRE_URE8's training program for personnel did not include actions plans and procedures to recover or re-establish Critical Cyber Assets and access thereto following a Cyber Security Incident. TRE_URE8 revised its training to include these actions plans and procedures to address the requirements of R2.2.4. This training was implemented once the last employee with CCA access received the training, which records indicate was early in 2011. | This issue did not pose a serious or substantial risk and posed a minimal actual risk and a moderate potential risk to the bulk power system because the entity had procedures in place that included action plans and procedures to recover or re-establish CCAs and access to CCAs but lacked personnel training on these procedures. The actual risk was minimal because an event triggering the use of procedures to recover or re-establish Critical Cyber Assets never occurred during the non-compliance period. | TRE_URE8 fixed its training program almost immediately following the discovery of the deficiency which was during their Certification. Employees were trained on the action plans and procedures to recover CCAs following a cyber-security incident.
2011-09-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 1 (WECC_URE1) | NCRXXXXX | WECC201002405 | CIP-004-2 | R4 | WECC_URE1 self-reported to WECC that it did not revoke access within 7 days for an employee working for a different entity at a co-owned facility who was terminated in good standing. The employee worked for a different entity in a co-owned facility, and the employer took possession of the employee's ID badge and substation card key. The employer did not notify WECC_URE1 until two months after the last day of employment, at which time WECC_URE1 revoked access and updated its access list. The co-owner did not notify WECC_URE1 until September 2010, during a quarterly update, that it revoked access for this employee. WECC_URE1 immediately updated its access list at that point, however, the employee’s last day at the co-owned facility was July 9, 2010. | This issue posed a minimal and not serious or substantial risk to the bulk power system. Although WECC_URE1 did not revoke access, the employee involved with this issue worked for a separate employer. The employee’s company promptly revoked access the same day the employee left the company. Specifically, the employer physically took possession of the employee's access card and substation card key. Therefore the employee had no means to access the substation, and the employee did not otherwise have electronic or physical access rights to Critical Cyber Assets. The entity has demonstrated a strong compliance culture demonstrated through prompt self-reporting, cooperation and collaboration in compliance matters, extensive mitigating measures when involved in compliance matters and steps to prevent recurrence. | The co-owner notified WECC_URE1 which updated its access list, disabled the employee’s ID card (which, as described above, was in the possession of the company, not the employee), and verified that that ID card had not been used since the employee’s last day at the co-owned facility.
2011-09-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 2 (WECC_URE2) | NCRXXXXX | WECC201102740 | CIP-004-1 | R3 | WECC_URE2 self-reported to WECC that a contractor was listed as completing a criminal background check on December 9, 2008 instead of the correct date December 9, 2002. WECC_URE2 reported that it failed to revoke access on December 9, 2009, the date on which the contractors Criminal background check performed on December 9, 2002 expired. WECC_URE2 detected this issue on January 17, 2011 during a review of personnel records, which indicated that the contractor's last background check was performed on December 9, 2002 and not December 9, 2008. | This issue posed a minimal and not serious or substantial risk to the bulk power system because the violation is limited to a single individual with access rights to one physical security perimeter (PSP) containing two Critical Cyber Assets which the contractor did not access at any time during the issue period of December 9, 2009 through January 17, 2011. Further, as represented by the individual’s background check expiring, the individual was a long-time contractor in good standing at WECC_URE2. | Access was revoked for the contractor. To avoid similar instances of noncompliance in the future, WECC_URE2 created a database that links to Human Resources records and does not require manual entry or review of personnel records. The database includes a reporting functionality and appropriate WECC_URE2 staff have completed CIP-004 retraining. Further, Personnel Risk Assessment reviews are now reviewed by Security personnel as well as Information Technology.
2011-09-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 3 (WECC_URE3) | NCRXXXXX | WECC201002322 | CIP-007-1 | R5 | A CIP Spot Check of WECC_URE3's parent company's facilities including WECC_URE3. During the course of Subject Matter Expert interviews at the WECC_URE3 control center, it was discovered that WECC_URE3 had not changed the shared Energy Management System (EMS) operator account when personnel changes had occurred. At the Audit, WECC_URE3 did not demonstrate how the EMS shared account at the operating system level on operator consoles has been changed following personnel changes. In 2009 the job status changed for two WECC_URE3 employees with EMS administrative account access such that they no longer needed access to the EMS administrative account. One employee with EMS administrative account access transferred to a different role within the company on August 31, 2009. The other employee with EMS administrative account access retired on December 31, 2009. Neither of these employees had RSA capability. However, the shared passwords for the WECC_URE3 EMS administrative account were not changed within 7 days of these changes in job status as required by the Company’s policy; rather, the shared password was changed on July 1, 2010. The issue arose because of a gap between the requirements of the company policy and the specific procedure to implement the policy. The detailed implementing procedure in effect at the time did not contain express instructions to manage the modifications for shared account access. In this instance, although WECC_URE3 had a policy for managing shared accounts, a shared EMS account password was not changed within 7 days of 2 personnel no longer requiring access to the account. | This issue posed a minimal and not serious or substantial risk to the bulk power system. While failure to establish technical and procedural controls to authenticate and account for user activity for system access could allow unauthorized access to the Cyber Assets to go unnoticed and unchecked, potentially allowing malicious access to these assets and such access may then be used to cause harm to Critical Cyber Assets essential to the operation of the BPS, in this instance, physical access to the facilities containing the EMS was removed within 1 day of the access change for these personnel and those personnel did not have remote cyber access into the EMS. WECC_URE3 had 24x7 monitoring of logs and alerts, physical controls per CIP-006 in place at the facilities in scope, and the personnel in scope had current Personnel Risk Assessments and current CIP training. | WECC_URE3 revised/replaced the subject procedure to address modifications of shared EMS account access passwords in the event of a change of assignment; changed the two shared account passwords identified as part of the Spot Check; corrected all shared accounts discovered to be non-compliant, where doing so does not pose unacceptable adverse impacts; completed the investigation and verification for shared password accounts in the CIP environment; completed the review and updating of policies, processes, and procedures to reflect accurate and up to date controls that comply with CIP-007 R5; communicated and trained administrators on any changes to the processes and procedures and comply with CIP-007 R5; and considered and evaluated longer-term solutions to improve the management of shared password accounts within the CIP environment.
2011-09-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 4 (WECC_URE4) | NCRXXXXX | WECC201102759 | CIP-003-3 | R2 | WECC_URE4 self-certified that it had failed to document a successor to the senior manager with CIP responsibilities within 30 days of the senior manager's retirement. The previous WECC_URE4 CIP senior manager retired on December 23, 2010, WECC_URE4 assigned the successor the same day the previous CIP senior manager retired. | This issue posed a minimal and not serious or substantial risk to the reliability of the bulk power system because WECC_URE4 did install a new senior manager; the failure was only in the lack of documentation. The WECC_URE4 CIP senior manager role was continually filled with no gaps, however WECC_URE4 did not document when the previous CIP senior manager retired and the new CIP senior manager assumed the role. There was no lag or gap in CIP oversight. Further, WECC_URE4 does not have Critical Cyber Assets. | WECC_URE4 implemented the process by effectively replacing the previous CIP senior manager in a timely manner without any lapse in CIP senior manager Responsibilities and documenting the new CIP senior manager.
2011-09-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 5 (WECC_URE5) | NCRXXXXX | WECC201002668 | CIP-006-1 | R1 | WECC_URE5 self-certified that it failed to provide continuous escorted access to an individual inside a Physical Security Perimeter (PSP). While in the PSP, the escort left the individual being escorted for 30 seconds to receive a package. | This issue posed minimal and not serious or substantial risk to the bulk power system because the person being escorted was not an extended distance for the escort. Further, the escort is a long-term employee in good standing and the visitor was a family member visiting the employee. The entity has demonstrated a strong compliance culture demonstrated through prompt self-reporting, cooperation and collaboration in compliance matters, extensive mitigating measures when involved in compliance matters and steps to prevent recurrence. | The entity conducted site evaluations to determine whether Cyber Assets were compromised and took disciplinary action against the employee that failed to follow the entity's CIP-006-1 R1 procedures.
2011-09-30 | Western Electricity Coordinating Council (WECC) | Unidentified Registered Entity 6 (WECC_URE6) | NCRXXXXX | WECC201102611 | CIP-009-1 | R4 | WECC_URE6 self-reported to WECC that while it included processes and procedures for backing up and storing information required to successfully restore Critical Cyber Assets in its recovery plan, it failed to document how it backed up certain devices. Specifically, WECC_URE6 did appropriately back-up the devices related to the issue, but WECC_URE6 did not document the back-up in accordance with WECC_URE6’s documented procedure. | This issue posed a minimal and not serious or substantial risk to the bulk power system because WECC_URE6 had a process and procedure in place. WECC_URE6 implemented the process, WECC_URE6 appropriately backed up the devices such that WECC_URE6 could successfully restore or recover the devices if necessary. WECC_URE6’s issue relates to how WECC_URE6 documented the back-up. WECC_URE6's internal procedures require documentation relating to backing up its devices. The referenced back up process is a sound security and cyber asset practice to ensure stability and recovery, if necessary, following a back-up. The entity has demonstrated a strong compliance culture demonstrated through prompt self-reporting, cooperation and collaboration in compliance matters, extensive mitigating measures when involved in compliance matters and steps to prevent recurrence. | WECC_URE6 documented the back-up process.