## EI (hidden)
Event ID | Time | Day | Time Zone | CERTS Est. MW | NERC SA Actual MW Loss | A Value Hz | B Value Hz | Point C Hz | B-A Delta Hz | C-A Delta Hz | B to A IFRM | C to A IFRM | FWG Sel. M-4 Events | Rev. BAL-003 Events (FWG) | (from 60) | M-4 | Operating Year | IFRO | Below IFRO
EI_2011-12-15_193216 | 2011-12-15 14:32 | 2011-12-15 14:32 | EST |  | 1105 | 60.0074 | 59.9558 | 59.957 | -0.05161 | -0.050375 | -2141.0457 | -2193.5486 | Yes | Yes | 0.007375 | 2141.0457 | 2012 | 1002 | 0
EI_2012-01-30_160157 | 2012-01-30 11:02 | 2012-01-30 11:02 | EST | 1227.1111 | 1152 | 59.9826 | 59.9292 | 59.944 | -0.05332 | -0.038562 | -2160.5371 | -2987.3582 | Yes | Yes | -0.017437 | 2160.5371 | 2012 | 1002 | 0
EI_2012-03-23_182826 | 2012-03-23 14:28 | 2012-03-23 14:28 | EDT | 1209.6273 | 1228 | 60.0038 | 59.9473 | 59.945 | -0.056479 | -0.058813 | -2174.253 | -2087.9915 | Yes | Yes | 0.0038125 | 2174.253 | 2012 | 1002 | 0
EI_2012-04-14_174650 | 2012-04-14 13:47 | 2012-04-14 13:47 | EDT | 1087.0493 | 1800 | 60.0111 | 59.9404 | 59.937 | -0.070669 | -0.074063 | -2547.1015 | -2430.3797 | Yes | Yes | 0.011063 | 2547.1015 | 2012 | 1002 | 0
EI_2012-04-30_140241 | 2012-04-30 10:03 | 2012-04-30 10:03 | EDT | 1866.3146 | 1237 | 59.9973 | 59.9392 | 59.939 | -0.058038 | -0.05825 | -2131.3667 | -2123.6052 | Yes | Yes | -0.00275 | 2131.3667 | 2012 | 1002 | 0
EI_2012-06-26_175002 | 2012-06-26 13:50 | 2012-06-26 13:50 | EDT | 1854.209 | 1320 | 60.0018 | 59.9383 | 59.942 | -0.063417 | -0.05975 | -2081.4717 | -2209.205 | Yes | Yes | 0.00175 | 2081.4717 | 2012 | 1002 | 0
EI_2012-07-02_025225 | 2012-07-01 22:52 | 2012-07-01 22:52 | EDT | 512.6206 | 1200 | 60.0104 | 59.9559 | 59.958 | -0.054528 | -0.052438 | -2200.6877 | -2288.4386 | Yes | Yes | 0.010438 | 2200.6877 | 2012 | 1002 | 0
EI_2012-08-28_073034 | 2012-08-28 03:31 | 2012-08-28 03:31 | EDT | 655.9036 | 1150 | 59.9983 | 59.95 | 59.954 | -0.048343 | -0.044312 | -2378.8443 | -2595.2045 | Yes | Yes | -0.0016875 | 2378.8443 | 2012 | 1002 | 0
EI_2012-10-23_222807 | 2012-10-23 18:28 | 2012-10-23 18:28 | EDT | 180.312 | 1234 | 60 | 59.9557 | 59.946 | -0.044333 | -0.054 | -2783.4586 | -2285.1852 | Yes | Yes | 0 | 2783.4586 | 2012 | 1002 | 0
EI_2012-11-09_061752 | 2012-11-09 01:18 | 2012-11-09 01:18 | EST | 1303.864 | 1165 | 60.0002 | 59.9492 | 59.958 | -0.051006 | -0.042188 | -2284.0593 | -2761.4815 | Yes | Yes | 0.0001875 | 2284.0593 | 2012 | 1002 | 0
EI_2012-12-29_061816 | 2012-12-29 01:18 | 2012-12-29 01:18 | EST | 1190.6551 | 1300 | 60.0003 | 59.9337 | 59.942 | -0.066585 | -0.058312 | -1952.385 | -2229.3676 | Yes | Yes | 0.0003125 | 1952.385 | 2013 | 1002 | 0
EI_2013-01-05_053700 | 2013-01-05 00:37 | 2013-01-05 00:37 | EST | 1149.0367 | 1360 | 60.001 | 59.9407 | 59.946 | -0.060312 | -0.054994 | -2254.9484 | -2472.9816 | Yes | Yes | 0.00099349 | 2254.9484 | 2013 | 1002 | 0
EI_2013-01-22_083259 | 2013-01-22 03:33 | 2013-01-22 03:33 | EST | 1730.8473 | 1276 | 60 | 59.9418 | 59.949 | -0.058182 | -0.051 | -2193.125 | -2501.9608 | Yes | Yes | 0 | 2193.125 | 2013 | 1002 | 0
EI_2013-02-24_020410 | 2013-02-23 21:04 | 2013-02-23 21:04 | EST | 1387.4675 | 1350 | 60.0064 | 59.9498 | 59.946 | -0.056527 | -0.060375 | -2388.2597 | -2236.0248 | Yes | Yes | 0.006375 | 2388.2597 | 2013 | 1002 | 0
EI_2013-02-25_191231 | 2013-02-25 14:13 | 2013-02-25 14:13 | EST | 1043.3197 | 1170 | 59.9976 | 59.9462 | 59.95 | -0.051443 | -0.047625 | -2274.3539 | -2456.6929 | Yes | Yes | -0.002375 | 2274.3539 | 2013 | 1002 | 0
EI_2013-03-12_185153 | 2013-03-12 14:52 | 2013-03-12 14:52 | EDT | 987.5387 | 1040 | 59.996 | 59.9542 | 59.955 | -0.041818 | -0.041 | -2486.9565 | -2536.5854 | Yes | Yes | -0.004 | 2486.9565 | 2013 | 1002 | 0
EI_2013-04-01_170733 | 2013-04-01 13:08 | 2013-04-01 13:08 | EDT | 932.2094 | 865 | 60.0039 | 59.969 | 59.966 | -0.034907 | -0.037937 | -2477.999 | -2280.0659 | Yes | No | 0.0039375 | 2477.999 | 2013 | 1002 | 0
EI_2013-04-04_195900 | 2013-04-04 15:59 | 2013-04-04 15:59 | EDT | 805.7167 | 1706 | 59.9886 | 59.9364 | 59.932 | -0.052261 | -0.056625 | -3264.3618 | -3012.8035 | Yes | Yes | -0.011375 | 3264.3618 | 2013 | 1002 | 0
EI_2013-04-17_195940 | 2013-04-17 16:00 | 2013-04-17 16:00 | EDT | 840.9993 | 2344 | 59.9904 | 59.9169 | 59.909 | -0.073496 | -0.081375 | -3189.28 | -2880.4916 | Yes | Yes | -0.009625 | 3189.28 | 2013 | 1002 | 0
EI_2013-04-18_132706 | 2013-04-18 09:27 | 2013-04-18 09:27 | EDT | 570.8947 | 852 | 59.9933 | 59.9478 | 59.952 | -0.045492 | -0.04125 | -1872.8393 | -2065.4545 | Yes | Yes | -0.00675 | 1872.8393 | 2013 | 1002 | 0
EI_2013-04-20_044506 | 2013-04-20 00:45 | 2013-04-20 00:45 | EDT | 349.6577 | 852 | 60.0059 | 59.9642 | 59.962 | -0.041723 | -0.043875 | -2042.0154 | -1941.8803 | Yes | No | 0.005875 | 2042.0154 | 2013 | 1002 | 0
EI_2013-05-01_161303 | 2013-05-01 12:13 | 2013-05-01 12:13 | EDT | 84.3809 | 852 | 60.0033 | 59.9561 | 59.964 | -0.047191 | -0.039313 | -1805.418 | -2167.2496 | Yes | No | 0.0033125 | 1805.418 | 2013 | 1002 | 0
EI_2013-05-04_130734 | 2013-05-04 09:08 | 2013-05-04 09:08 | EDT | 631.358 | 900 | 60.0103 | 59.9592 | 59.957 | -0.051131 | -0.053312 | -1760.1956 | -1688.1594 | Yes | No | 0.010312 | 1760.1956 | 2013 | 1002 | 0
EI_2013-05-07_173106 | 2013-05-07 13:31 | 2013-05-07 13:31 | EDT | 1923.8405 | 1275 | 59.985 | 59.9191 | 59.926 | -0.065879 | -0.059 | -1935.3726 | -2161.0169 | Yes | No | -0.015 | 1935.3726 | 2013 | 1002 | 0
EI_2013-05-09_014744 | 2013-05-08 21:48 | 2013-05-08 21:48 | EDT | 1103.5096 | 875 | 60.0223 | 59.9764 | 59.983 | -0.045949 | -0.039313 | -1904.2908 | -2225.7552 | Yes | No | 0.022312 | 1904.2908 | 2013 | 1002 | 0
EI_2013-05-10_145753 | 2013-05-10 10:58 | 2013-05-10 10:58 | EDT | 1574.6523 | 1298 | 60.0202 | 59.956 | 59.959 | -0.064218 | -0.061187 | -2021.2464 | -2121.3483 | Yes | No | 0.020187 | 2021.2464 | 2013 | 1002 | 0
EI_2013-05-28_190756 | 2013-05-28 15:08 | 2013-05-28 15:08 | EDT | 1384.3354 | 1006 | 60.0083 | 59.9564 | 59.961 | -0.051888 | -0.047313 | -1938.7816 | -2126.288 | Yes | No | 0.0083125 | 1938.7816 | 2013 | 1002 | 0
EI_2013-06-05_145414 | 2013-06-05 10:54 | 2013-06-05 10:54 | EDT | 1894.0788 | 1600 | 60.0079 | 59.9355 | 59.944 | -0.072453 | -0.063937 | -2208.3388 | -2502.4438 | Yes | Yes | 0.0079375 | 2208.3388 | 2013 | 1002 | 0
EI_2013-06-05_152324 | 2013-06-05 11:23 | 2013-06-05 11:23 | EDT | 923.313 | 858 | 59.9961 | 59.9586 | 59.96 | -0.037426 | -0.036062 | -2292.5156 | -2379.2028 | Yes | No | -0.0039375 | 2292.5156 | 2013 | 1002 | 0
EI_2013-06-05_185244 | 2013-06-05 14:53 | 2013-06-05 14:53 | EDT | 1366.393 | 1340 | 59.995 | 59.94 | 59.936 | -0.055 | -0.059 | -2436.3636 | -2271.1864 | Yes | Yes | -0.005 | 2436.3636 | 2013 | 1002 | 0
EI_2013-06-08_151817 | 2013-06-08 11:18 | 2013-06-08 11:18 | EDT | 1207.8554 | 1096 | 59.9803 | 59.9395 | 59.937 | -0.040797 | -0.043312 | -2686.4491 | -2530.4473 | Yes | No | -0.019688 | 2686.4491 | 2013 | 1002 | 0
EI_2013-06-27_222331 | 2013-06-27 18:24 | 2013-06-27 18:24 | EDT | 945.4778 | 850 | 60.0061 | 59.962 | 59.968 | -0.044032 | -0.038062 | -1930.4056 | -2233.1691 | Yes | No | 0.0060625 | 1930.4056 | 2013 | 1002 | 0
EI_2013-06-28_172946 | 2013-06-28 13:30 | 2013-06-28 13:30 | EDT | 1270.5316 | 1180 | 59.9982 | 59.942 | 59.946 | -0.056218 | -0.052188 | -2098.9792 | -2261.0778 | Yes | Yes | -0.0018125 | 2098.9792 | 2013 | 1002 | 0
EI_2013-06-30_012022 | 2013-06-29 21:20 | 2013-06-29 21:20 | EDT | 1401.8121 | 906 | 59.9897 | 59.9463 | 59.95 | -0.043354 | -0.039687 | -2089.7645 | -2282.8346 | Yes | No | -0.010312 | 2089.7645 | 2013 | 1002 | 0
EI_2013-07-27_043432 | 2013-07-27 00:35 | 2013-07-27 00:35 | EDT | 1452.7589 | 1298 | 60.0094 | 59.954 | 59.9565 | -0.055338 | -0.052886 | -2345.5832 | -2454.3353 | Yes | Yes | 0.009387 | 2345.5832 | 2013 | 1002 | 0
EI_2013-08-08_180156 | 2013-08-08 14:02 | 2013-08-08 14:02 | EDT | 1317.4826 | 1262 | 60 | 59.9495 | 59.9453 | -0.050475 | -0.054686 | -2500.2363 | -2307.7074 | Yes | Yes | -1.2636e-05 | 2500.2363 | 2013 | 1002 | 0
EI_2013-09-03_140957 | 2013-09-03 10:10 | 2013-09-03 10:10 | EDT | 411.5616 | 1200 | 60.0007 | 59.9564 | 59.955 | -0.044294 | -0.045687 | -2709.1974 | -2626.539 | Yes | Yes | 0.0006875 | 2709.1974 | 2013 | 1002 | 0
EI_2013-10-19_104205 | 2013-10-19 06:42 | 2013-10-19 06:42 | EDT | 941.3061 | 1204 | 59.9847 | 59.9415 | 59.9357 | -0.043166 | -0.049006 | -2789.2224 | -2456.8308 | Yes | Yes | -0.015294 | 2789.2224 | 2013 | 1002 | 0
EI_2013-11-09_201410 | 2013-11-09 15:14 | 2013-11-09 15:14 | EST | 673.2479 | 869 | 59.9929 | 59.942 | 59.946 | -0.050907 | -0.046937 | -1707.0278 | -1851.3981 | Yes | Yes | -0.0070625 | 1707.0278 | 2013 | 1002 | 0
EI_2013-11-14_171809 | 2013-11-14 12:18 | 2013-11-14 12:18 | EST | 1109.541 | 1042 | 60.0035 | 59.9513 | 59.953 | -0.052197 | -0.0505 | -1996.2845 | -2063.3663 | Yes | No | 0.0035 | 1996.2845 | 2013 | 1002 | 0
EI_2013-11-14_181327 | 2013-11-14 13:13 | 2013-11-14 13:13 | EST | 946.8787 | 1200 | 59.9941 | 59.9402 | 59.941 | -0.053881 | -0.053062 | -2227.1433 | -2261.4841 | Yes | No | -0.0059375 | 2227.1433 | 2013 | 1002 | 0
EI_2013-11-29_213126 | 2013-11-29 16:31 | 2013-11-29 16:31 | EST | 719.4568 | 800 | 60.0036 | 59.9608 | 59.959 | -0.042775 | -0.044562 | -1870.2679 | -1795.2314 | Yes | No | 0.0035625 | 1870.2679 | 2013 | 1002 | 0
EI_2013-12-01_111318 | 2013-12-01 06:13 | 2013-12-01 06:13 | EST | 1424.6082 | 1282 | 60.0101 | 59.9629 | 59.954 | -0.047186 | -0.056125 | -2716.9302 | -2284.1871 | Yes | Yes | 0.010125 | 2716.9302 | 2014 | 1014 | 0
EI_2013-12-09_134654 | 2013-12-09 08:47 | 2013-12-09 08:47 | EST | 996.9549 | 1004 | 59.9946 | 59.9472 | 59.948 | -0.047381 | -0.046563 | -2119.0071 | -2156.2416 | Yes | Yes | -0.0054375 | 2119.0071 | 2014 | 1014 | 0
EI_2014-01-02_182136 | 2014-01-02 13:22 | 2014-01-02 13:22 | EST | 970.1081 | 1043 | 59.9977 | 59.9508 | 59.956 | -0.04693 | -0.041687 | -2222.4626 | -2501.949 | Yes | No | -0.0023125 | 2222.4626 | 2014 | 1014 | 0
EI_2014-01-06_215909 | 2014-01-06 16:59 | 2014-01-06 16:59 | EST | 382.9596 | 950 | 59.9946 | 59.9495 | 59.958 | -0.04514 | -0.036625 | -2104.5565 | -2593.8567 | Yes | No | -0.005375 | 2104.5565 | 2014 | 1014 | 0
EI_2014-01-21_185002 | 2014-01-21 13:50 | 2014-01-21 13:50 | EST | 837.7321 | 1320 | 60.0115 | 59.9541 | 59.9566 | -0.057361 | -0.0549 | -2301.215 | -2404.3537 | Yes | Yes | 0.011501 | 2301.215 | 2014 | 1014 | 0
EI_2014-01-22_022529 | 2014-01-21 21:25 | 2014-01-21 21:25 | EST | 1654.6292 | 1863 | 59.9794 | 59.9361 | 59.939 | -0.043284 | -0.040375 | -4304.1218 | -4614.2415 | Yes | No | -0.020625 | 4304.1218 | 2014 | 1014 | 0
EI_2014-01-26_170924 | 2014-01-26 12:09 | 2014-01-26 12:09 | EST | 1705.2698 | 1241 | 59.9993 | 59.9555 | 59.95 | -0.043705 | -0.04925 | -2839.5216 | -2519.797 | Yes | Yes | -0.00075 | 2839.5216 | 2014 | 1014 | 0
EI_2014-02-02_135846 | 2014-02-02 08:59 | 2014-02-02 08:59 | EST | 151.2299 | 1032 | 59.9894 | 59.9554 | 59.9454 | -0.034017 | -0.043981 | -3033.7605 | -2346.4892 | Yes | Yes | -0.010619 | 3033.7605 | 2014 | 1014 | 0
EI_2014-02-16_035350 | 2014-02-15 22:54 | 2014-02-15 22:54 | EST | 1196.0121 | 1236 | 60.0044 | 59.9568 | 59.9526 | -0.047534 | -0.05177 | -2600.217 | -2387.4954 | Yes | Yes | 0.0043683 | 2600.217 | 2014 | 1014 | 0
EI_2014-02-19_053233 | 2014-02-19 00:33 | 2014-02-19 00:33 | EST | 733.8603 | 846 | 60.0015 | 59.9588 | 59.96 | -0.042764 | -0.041526 | -1978.2889 | -2037.2857 | Yes | Yes | 0.0015249 | 1978.2889 | 2014 | 1014 | 0
EI_2014-02-23_173202 | 2014-02-23 12:32 | 2014-02-23 12:32 | EST | 821.5823 | 1070 | 59.985 | 59.936 | 59.9436 | -0.049083 | -0.04145 | -2179.9968 | -2581.4516 | Yes | Yes | -0.014951 | 2179.9968 | 2014 | 1014 | 0
EI_2014-03-05_212417 | 2014-03-05 16:24 | 2014-03-05 16:24 | EST | 614.0996 | 1170 | 59.9852 | 59.9449 | 59.9461 | -0.040334 | -0.039126 | -2900.8008 | -2990.3086 | Yes | Yes | -0.014775 | 2900.8008 | 2014 | 1014 | 0
EI_2014-03-29_150742 | 2014-03-29 11:08 | 2014-03-29 11:08 | EDT | 1586.1222 | 1228 | 60.0066 | 59.9513 | 59.9525 | -0.055278 | -0.054088 | -2221.4819 | -2270.3693 | Yes | No | 0.0065875 | 2221.4819 | 2014 | 1014 | 0
EI_2014-04-03_123635 | 2014-04-03 08:37 | 2014-04-03 08:37 | EDT | 729.5435 | 1268 | 59.9866 | 59.9462 | 59.9433 | -0.040414 | -0.043288 | -3137.5506 | -2929.1865 | Yes | Yes | -0.013413 | 3137.5506 | 2014 | 1014 | 0
EI_2014-04-03_180037 | 2014-04-03 14:01 | 2014-04-03 14:01 | EDT | 605.4298 | 1004 | 59.9762 | 59.9435 | 59.9325 | -0.03266 | -0.043689 | -3074.1063 | -2298.0857 | Yes | Yes | -0.023813 | 3074.1063 | 2014 | 1014 | 0
EI_2014-04-04_163058 | 2014-04-04 12:31 | 2014-04-04 12:31 | EDT | 176.7669 | 800 | 59.9921 | 59.9458 | 59.9478 | -0.046373 | -0.044331 | -1725.1295 | -1804.5935 | Yes | No | -0.007869 | 1725.1295 | 2014 | 1014 | 0
EI_2014-04-08_082756 | 2014-04-08 04:28 | 2014-04-08 04:28 | EDT | 939.7699 | 1225 | 60.0038 | 59.9476 | 59.9432 | -0.056236 | -0.060589 | -2178.3233 | -2021.8325 | Yes | Yes | 0.0037878 | 2178.3233 | 2014 | 1014 | 0
EI_2014-04-25_173023 | 2014-04-25 13:30 | 2014-04-25 13:30 | EDT | 1970.0362 | 1692 | 60.0004 | 59.9395 | 59.9378 | -0.060872 | -0.062562 | -2779.6052 | -2704.5279 | Yes | Yes | 0.00036311 | 2779.6052 | 2014 | 1014 | 0
EI_2014-04-30_084301 | 2014-04-30 04:43 | 2014-04-30 04:43 | EDT | 665.5662 | 930 | 59.9816 | 59.9463 | 59.9433 | -0.035238 | -0.038257 | -2639.2246 | -2430.9048 | Yes | No | -0.018444 | 2639.2246 | 2014 | 1014 | 0
EI_2014-05-01_141700 | 2014-05-01 10:17 | 2014-05-01 10:17 | EDT | 1221.4611 | 942 | 59.996 | 59.9447 | 59.9462 | -0.051302 | -0.049851 | -1836.185 | -1889.6424 | Yes | Yes | -0.0039899 | 1836.185 | 2014 | 1014 | 0
EI_2014-05-06_133123 | 2014-05-06 09:31 | 2014-05-06 09:31 | EDT | 725.205 | 1067 | 59.9981 | 59.9435 | 59.9566 | -0.054613 | -0.041482 | -1953.7321 | -2572.2165 | Yes | No | -0.0019028 | 1953.7321 | 2014 | 1014 | 0
EI_2014-05-11_233755 | 2014-05-11 19:38 | 2014-05-11 19:38 | EDT | 0 | 887 | 60.017 | 59.9487 | 59.9507 | -0.068217 | -0.066206 | -1300.2641 | -1339.7533 | Yes | No | 0.016955 | 1300.2641 | 2014 | 1014 | 0
EI_2014-05-22_161017 | 2014-05-22 12:10 | 2014-05-22 12:10 | EDT | 891.008 | 1500 | 60.0096 | 59.9429 | 59.9448 | -0.06677 | -0.064857 | -2246.5333 | -2312.7972 | Yes | Yes | 0.0096273 | 2246.5333 | 2014 | 1014 | 0
EI_2014-05-25_110146 | 2014-05-25 07:02 | 2014-05-25 07:02 | EDT | 2261.1591 | 2103 | 59.9734 | 59.9147 | 59.9103 | -0.058705 | -0.063116 | -3582.3322 | -3331.9689 | Yes | Yes | -0.026572 | 3582.3322 | 2014 | 1014 | 0
EI_2014-07-24_161401 | 2014-07-24 12:14 | 2014-07-24 12:14 | EDT | 1695.0096 | 1812 | 59.9961 | 59.9357 | 59.9375 | -0.060372 | -0.058594 | -3001.3814 | -3092.4926 | Yes | Yes | -0.0039065 | 3001.3814 | 2014 | 1014 | 0
EI_2014-07-25_191632 | 2014-07-25 15:17 | 2014-07-25 15:17 | EDT | 709.6856 | 1678 | 59.999 | 59.9533 | 59.9529 | -0.045687 | -0.046076 | -3672.7844 | -3641.8422 | Yes | Yes | -0.0010245 | 3672.7844 | 2014 | 1014 | 0
EI_2014-07-27_180932 | 2014-07-27 14:10 | 2014-07-27 14:10 | EDT | 775.0586 | 1195 | 60.0043 | 59.9549 | 59.9579 | -0.049387 | -0.046386 | -2419.6701 | -2576.2081 | Yes | Yes | 0.004287 | 2419.6701 | 2014 | 1014 | 0
EI_2014-08-13_155744 | 2014-08-13 11:58 | 2014-08-13 11:58 | EDT | 800.9316 | 1025 | 60.0018 | 59.9603 | 59.9592 | -0.041509 | -0.042598 | -2469.3315 | -2406.2023 | Yes | Yes | 0.0018001 | 2469.3315 | 2014 | 1014 | 0
EI_2014-10-09_133005 | 2014-10-09 09:30 | 2014-10-09 09:30 | EDT | 1108.9167 | 848 | 59.9925 | 59.9557 | 59.9543 | -0.036751 | -0.038169 | -2307.4273 | -2221.6898 | Yes | No | -0.0075309 | 2307.4273 | 2014 | 1014 | 0
EI_2014-10-20_061839 | 2014-10-20 02:19 | 2014-10-20 02:19 | EDT | 1440.4642 | 1320 | 59.9899 | 59.9447 | 59.9408 | -0.04516 | -0.049063 | -2922.9502 | -2690.3941 | Yes | Yes | -0.010137 | 2922.9502 | 2014 | 1014 | 0
EI_2014-10-24_224323 | 2014-10-24 18:43 | 2014-10-24 18:43 | EDT | 892.0595 | 861 | 59.991 | 59.9549 | 59.9515 | -0.036113 | -0.039519 | -2384.1981 | -2178.7081 | Yes | Yes | -0.0089812 | 2384.1981 | 2014 | 1014 | 0
EI_2014-11-01_064938 | 2014-11-01 02:50 | 2014-11-01 02:50 | EDT | 624.8068 | 1554 | 59.988 | 59.9398 | 59.9421 | -0.048225 | -0.045937 | -3222.3749 | -3382.8894 | Yes | Yes | -0.011962 | 3222.3749 | 2014 | 1014 | 0
EI_2014-11-03_192114 | 2014-11-03 14:21 | 2014-11-03 14:21 | EST | 580.2598 | 1532 | 59.9943 | 59.9439 | 59.9349 | -0.050325 | -0.059358 | -3044.1975 | -2580.965 | Yes | Yes | -0.005744 | 3044.1975 | 2014 | 1014 | 0
EI_2014-11-07_134803 | 2014-11-07 08:48 | 2014-11-07 08:48 | EST | 473.4687 | 1270 | 59.9956 | 59.9592 | 59.9459 | -0.036409 | -0.049706 | -3488.1386 | -2555.0245 | Yes | Yes | -0.0043941 | 3488.1386 | 2014 | 1014 | 0
EI_2014-11-22_081815 | 2014-11-22 03:18 | 2014-11-22 03:18 | EST | 0 | 911 | 59.9942 | 59.9647 | 59.9491 | -0.0295 | -0.045105 | -3088.1855 | -2019.7219 | Yes | Yes | -0.0057943 | 3088.1855 | 2014 | 1014 | 0
EI_2014-12-03_062255 | 2014-12-03 01:23 | 2014-12-03 01:23 | EST | 479.9776 | 1234 | 59.983 | 59.9293 | 59.9283 | -0.053678 | -0.054658 | -2298.8875 | -2257.6776 | Yes | Yes | -0.017043 | 2298.8875 | 2015 | 1014 | 0
EI_2014-12-10_185741 | 2014-12-10 13:58 | 2014-12-10 13:58 | EST | 1491.3726 | 1280 | 60.0036 | 59.9456 | 59.9486 | -0.057945 | -0.054975 | -2208.9756 | -2328.3297 | Yes | Yes | 0.0035758 | 2208.9756 | 2015 | 1014 | 0
EI_2015-01-31_193145 | 2015-01-31 14:32 | 2015-01-31 14:32 | EST | 344.429 | 846 | 60.0008 | 59.9597 | 59.9569 | -0.041118 | -0.043917 | -2057.4757 | -1926.3532 | Yes | Yes | 0.00081873 | 2057.4757 | 2015 | 1014 | 0
EI_2015-02-08_005517 | 2015-02-07 19:55 | 2015-02-07 19:55 | EST | 569.1294 | 1478 | 60.0094 | 59.9491 | 59.9453 | -0.06024 | -0.064055 | -2453.4989 | -2307.3933 | Yes | Yes | 0.009356 | 2453.4989 | 2015 | 1014 | 0
EI_2015-02-21_153119 | 2015-02-21 10:31 | 2015-02-21 10:31 | EST | 1023.4966 | 1251 | 59.9821 | 59.9508 | 59.9439 | -0.031299 | -0.038204 | -3996.9155 | -3274.4892 | Yes | No | -0.017895 | 3996.9155 | 2015 | 1014 | 0
EI_2015-02-28_123140 | 2015-02-28 07:32 | 2015-02-28 07:32 | EST | 1989.9887 | 1330 | 60.0047 | 59.9488 | 59.9512 | -0.055944 | -0.053551 | -2377.385 | -2483.6046 | Yes | Yes | 0.0047498 | 2377.385 | 2015 | 1014 | 0
EI_2015-03-02_114539 | 2015-03-02 06:46 | 2015-03-02 06:46 | EST | 1190.4623 | 1160 | 60.0031 | 59.953 | 59.9585 | -0.050101 | -0.044619 | -2315.3432 | -2599.7984 | Yes | No | 0.0031188 | 2315.3432 | 2015 | 1014 | 0
EI_2015-03-03_170120 | 2015-03-03 12:01 | 2015-03-03 12:01 | EST | 1550.7146 | 1190 | 60.0027 | 59.9437 | 59.9476 | -0.059025 | -0.055093 | -2016.0999 | -2159.9727 | Yes | Yes | 0.0026946 | 2016.0999 | 2015 | 1014 | 0
EI_2015-03-11_102155 | 2015-03-11 06:22 | 2015-03-11 06:22 | EDT | 1220.604 | 1154 | 59.9899 | 59.9519 | 59.9511 | -0.038023 | -0.038832 | -3035.0223 | -2971.7432 | Yes | No | -0.010068 | 3035.0223 | 2015 | 1014 | 0
EI_2015-03-14_082945 | 2015-03-14 04:30 | 2015-03-14 04:30 | EDT | 964.6437 | 1235 | 59.9927 | 59.9416 | 59.9395 | -0.051067 | -0.053201 | -2418.4056 | -2321.3763 | Yes | Yes | -0.0072999 | 2418.4056 | 2015 | 1014 | 0
EI_2015-03-16_175351 | 2015-03-16 13:54 | 2015-03-16 13:54 | EDT | 454.8861 | 862 | 59.9882 | 59.9458 | 59.944 | -0.042437 | -0.044206 | -2031.2665 | -1949.9658 | Yes | Yes | -0.011794 | 2031.2665 | 2015 | 1014 | 0
EI_2015-04-02_082510 | 2015-04-02 04:25 | 2015-04-02 04:25 | EDT | 1266.8876 | 973 | 60.0034 | 59.9519 | 59.9504 | -0.051531 | -0.053024 | -1888.1752 | -1835.0163 | Yes | Yes | 0.0034254 | 1888.1752 | 2015 | 1014 | 0
EI_2015-04-03_014709 | 2015-04-02 21:47 | 2015-04-02 21:47 | EDT | 848.0304 | 1168 | 59.9919 | 59.9446 | 59.9439 | -0.047374 | -0.048049 | -2465.4816 | -2430.8653 | Yes | Yes | -0.0080502 | 2465.4816 | 2015 | 1014 | 0
EI_2015-04-06_141326 | 2015-04-06 10:13 | 2015-04-06 10:13 | EDT | 1414.7147 | 850 | 59.9829 | 59.9502 | 59.9419 | -0.032723 | -0.040982 | -2597.5728 | -2074.0568 | Yes | Yes | -0.017119 | 2597.5728 | 2015 | 1014 | 0
EI_2015-04-06_145116 | 2015-04-06 10:51 | 2015-04-06 10:51 | EDT | 814.1465 | 831 | 59.9916 | 59.9534 | 59.9514 | -0.038289 | -0.040243 | -2170.3375 | -2064.96 | Yes | No | -0.0083563 | 2170.3375 | 2015 | 1014 | 0
EI_2015-04-15_081148 | 2015-04-15 04:12 | 2015-04-15 04:12 | EDT | 1000.7208 | 916 | 59.9975 | 59.9694 | 59.9597 | -0.028056 | -0.037755 | -3264.8634 | -2426.1986 | Yes | No | -0.0025439 | 3264.8634 | 2015 | 1014 | 0
EI_2015-04-25_031918 | 2015-04-24 23:19 | 2015-04-24 23:19 | EDT | 1505.4829 | 1172 | 60.0044 | 59.9496 | 59.953 | -0.054841 | -0.051439 | -2137.1028 | -2278.4248 | Yes | Yes | 0.0044382 | 2137.1028 | 2015 | 1014 | 0
EI_2015-05-09_215100 | 2015-05-09 17:51 | 2015-05-09 17:51 | EDT | 647.5474 | 1020 | 60.002 | 59.9428 | 59.9499 | -0.059123 | -0.052061 | -1725.2063 | -1959.2281 | Yes | Yes | 0.0019629 | 1725.2063 | 2015 | 1014 | 0
EI_2015-05-23_062000 | 2015-05-23 02:20 | 2015-05-23 02:20 | EDT | 576.3445 | 856 | 59.9934 | 59.9537 | 59.9499 | -0.039705 | -0.043479 | -2155.9142 | -1968.7573 | Yes | Yes | -0.0066192 | 2155.9142 | 2015 | 1014 | 0
EI_2015-05-25_212634 | 2015-05-25 17:27 | 2015-05-25 17:27 | EDT | 1130.423 | 975 | 59.9865 | 59.9483 | 59.9471 | -0.03821 | -0.039417 | -2551.7212 | -2473.5502 | Yes | No | -0.013481 | 2551.7212 | 2015 | 1014 | 0
EI_2015-05-31_195523 | 2015-05-31 15:55 | 2015-05-31 15:55 | EDT | 1448.8802 | 960 | 59.9954 | 59.9542 | 59.9518 | -0.041205 | -0.043611 | -2329.7877 | -2201.289 | Yes | Yes | -0.0045879 | 2329.7877 | 2015 | 1014 | 0
EI_2015-06-09_224948 | 2015-06-09 18:50 | 2015-06-09 18:50 | EDT | 1324.1286 | 1260 | 60.0065 | 59.9511 | 59.951 | -0.055412 | -0.055545 | -2273.8936 | -2268.4467 | Yes | Yes | 0.0065448 | 2273.8936 | 2015 | 1014 | 0
EI_2015-06-15_231942 | 2015-06-15 19:20 | 2015-06-15 19:20 | EDT | 647.8814 | 1045 | 59.9856 | 59.9535 | 59.9473 | -0.032088 | -0.038288 | -3256.6972 | -2729.3234 | Yes | No | -0.014412 | 3256.6972 | 2015 | 1014 | 0
EI_2015-07-24_175329 | 2015-07-24 13:53 | 2015-07-24 13:53 | EDT | 291.5663 | 1130 | 60.0028 | 59.9551 | 59.952 | -0.047748 | -0.050812 | -2366.5797 | -2223.8734 | Yes | Yes | 0.0028119 | 2366.5797 | 2015 | 1014 | 0
EI_2015-08-05_193855 | 2015-08-05 15:39 | 2015-08-05 15:39 | EDT | 1022.9109 | 1198 | 59.9853 | 59.9515 | 59.9421 | -0.033822 | -0.043186 | -3542.0231 | -2774.0657 | Yes | Yes | -0.014714 | 3542.0231 | 2015 | 1014 | 0
EI_2015-08-11_063950 | 2015-08-11 02:40 | 2015-08-11 02:40 | EDT | 1744.1121 | 1240 | 60.0085 | 59.96 | 59.9568 | -0.048508 | -0.051695 | -2556.2561 | -2398.6906 | Yes | Yes | 0.0084934 | 2556.2561 | 2015 | 1014 | 0
EI_2015-08-21_182854 | 2015-08-21 14:29 | 2015-08-21 14:29 | EDT | 1538.8756 | 860 | 59.9992 | 59.9638 | 59.961 | -0.035369 | -0.038195 | -2431.4746 | -2251.5958 | Yes | No | -0.00080633 | 2431.4746 | 2015 | 1014 | 0
EI_2015-09-05_010657 | 2015-09-04 21:07 | 2015-09-04 21:07 | EDT | 2172.167 | 1310 | 59.9897 | 59.9387 | 59.9374 | -0.05103 | -0.052293 | -2567.1148 | -2505.1124 | Yes | Yes | -0.010306 | 2567.1148 | 2015 | 1014 | 0
EI_2015-09-14_030605 | 2015-09-13 23:06 | 2015-09-13 23:06 | EDT | 810.1409 | 1198 | 59.9847 | 59.9538 | 59.9441 | -0.030869 | -0.040606 | -3880.8635 | -2950.284 | Yes | Yes | -0.015294 | 3880.8635 | 2015 | 1014 | 0
EI_2015-09-14_082630 | 2015-09-14 04:26 | 2015-09-14 04:26 | EDT | 703.2522 | 1225 | 60.0018 | 59.9527 | 59.9478 | -0.049149 | -0.054001 | -2492.4203 | -2268.4926 | Yes | Yes | 0.0018003 | 2492.4203 | 2015 | 1014 | 0
EI_2015-10-04_041049 | 2015-10-04 00:11 | 2015-10-04 00:11 | EDT | 853.4792 | 1185 | 60.0081 | 59.9374 | 59.9407 | -0.070694 | -0.067418 | -1676.2302 | -1757.6883 | Yes | Yes | 0.0081186 | 1676.2302 | 2015 | 1014 | 0
EI_2015-10-13_221536 | 2015-10-13 18:16 | 2015-10-13 18:16 | EDT | 711.2089 | 860 | 59.9875 | 59.9457 | 59.9433 | -0.041738 | -0.04417 | -2060.474 | -1947.0377 | Yes | Yes | -0.012532 | 2060.474 | 2015 | 1014 | 0
EI_2015-10-20_205502 | 2015-10-20 16:55 | 2015-10-20 16:55 | EDT | 1163.6562 | 810 | 60.0047 | 59.9552 | 59.9603 | -0.049518 | -0.044399 | -1635.7645 | -1824.3449 | Yes | No | 0.0046999 | 1635.7645 | 2015 | 1014 | 0
EI_2015-11-12_163232 | 2015-11-12 11:33 | 2015-11-12 11:33 | EST | 732.1223 | 1280 | 60.0134 | 59.952 | 59.9574 | -0.061354 | -0.055999 | -2086.2395 | -2285.7534 | Yes | Yes | 0.0134 | 2086.2395 | 2015 | 1014 | 0
EI_2015-11-21_170808 | 2015-11-21 12:08 | 2015-11-21 12:08 | EST | 170.1629 | 1200 | 59.9864 | 59.9517 | 59.9387 | -0.034727 | -0.047723 | -3455.4955 | -2514.5331 | Yes | Yes | -0.013576 | 3455.4955 | 2015 | 1014 | 0
EI_2015-11-23_134423 | 2015-11-23 08:44 | 2015-11-23 08:44 | EST | 355.9368 | 1161 | 59.994 | 59.9476 | 59.9481 | -0.046452 | -0.045912 | -2499.337 | -2528.7623 | Yes | Yes | -0.0059872 | 2499.337 | 2015 | 1014 | 0
EI_2015-12-05_223137 | 2015-12-05 17:32 | 2015-12-05 17:32 | EST | 881.8021 | 1031 | 59.988 | 59.945 | 59.948 | -0.043 | -0.04 | -2397.6744 | -2577.5 | Yes | Yes | -0.012 | 2397.6744 | 2016 | 1015 | 0
EI_2015-12-09_083803 | 2015-12-09 03:38 | 2015-12-09 03:38 | EST | 662.4544 | 809 | 60.006 | 59.957 | 59.959 | -0.049 | -0.047 | -1651.0204 | -1721.2766 | Yes | Yes | 0.006 | 1651.0204 | 2016 | 1015 | 0
EI_2015-12-09_160455 | 2015-12-09 11:05 | 2015-12-09 11:05 | EST | 1333.1298 | 654.5 | 59.999 | 59.952 | 59.961 | -0.047 | -0.038 | -1392.5532 | -1722.3684 | Yes | Yes | -0.001 | 1392.5532 | 2016 | 1015 | 0
EI_2015-12-15_000429 | 2015-12-14 19:04 | 2015-12-14 19:04 | EST | 292.4606 | 1040 | 60.0113 | 59.9761 | 59.969 | -0.035144 | -0.04222 | -2959.2907 | -2463.2947 | Yes | No | 0.011269 | 2959.2907 | 2016 | 1015 | 0
EI_2015-12-16_012703 | 2015-12-15 20:27 | 2015-12-15 20:27 | EST | 212.6509 | 840 | 60.016 | 59.965 | 59.964 | -0.051 | -0.052 | -1647.0588 | -1615.3846 | Yes | No | 0.016 | 1647.0588 | 2016 | 1015 | 0
EI_2015-12-27_164750 | 2015-12-27 11:48 | 2015-12-27 11:48 | EST | 448.0958 | 816 | 59.995 | 59.96 | 59.96 | -0.035 | -0.035 | -2331.4286 | -2331.4286 | Yes | No | -0.005 | 2331.4286 | 2016 | 1015 | 0
EI_2016-01-09_083701 | 2016-01-09 03:37 | 2016-01-09 03:37 | EST | 487.3441 | 977 | 59.996 | 59.957 | 59.961 | -0.039 | -0.035 | -2505.1282 | -2791.4286 | Yes | No | -0.004 | 2505.1282 | 2016 | 1015 | 0
EI_2016-01-25_064704 | 2016-01-25 01:47 | 2016-01-25 01:47 | EST | 360.7517 | 1231 | 60.018 | 59.971 | 59.968 | -0.047 | -0.05 | -2619.1489 | -2462 | Yes | No | 0.018 | 2619.1489 | 2016 | 1015 | 0
EI_2016-01-29_182125 | 2016-01-29 13:21 | 2016-01-29 13:21 | EST | 238.6653 | 915 | 59.995 | 59.97 | 59.954 | -0.025 | -0.041 | -3660 | -2231.7073 | Yes | Yes | -0.005 | 3660 | 2016 | 1015 | 0
EI_2016-02-01_150229 | 2016-02-01 10:02 | 2016-02-01 10:02 | EST | 582.5907 | 970 | 59.991 | 59.947 | 59.947 | -0.044 | -0.044 | -2204.5455 | -2204.5455 | Yes | Yes | -0.009 | 2204.5455 | 2016 | 1015 | 0
EI_2016-02-04_162153 | 2016-02-04 11:22 | 2016-02-04 11:22 | EST | 656.1571 | 880 | 60.02 | 59.962 | 59.96 | -0.058 | -0.06 | -1517.2414 | -1466.6667 | Yes | No | 0.02 | 1517.2414 | 2016 | 1015 | 0
EI_2016-02-16_133306 | 2016-02-16 08:33 | 2016-02-16 08:33 | EST | 389.7433 | 829 | 60.007 | 59.972 | 59.967 | -0.035 | -0.04 | -2368.5714 | -2072.5 | Yes | No | 0.007 | 2368.5714 | 2016 | 1015 | 0
EI_2016-02-21_030538 | 2016-02-20 22:06 | 2016-02-20 22:06 | EST | 465.1383 | 915 | 59.99 | 59.96 | 59.959 | -0.03 | -0.031 | -3050 | -2951.6129 | Yes | No | -0.01 | 3050 | 2016 | 1015 | 0
EI_2016-03-02_075329 | 2016-03-02 02:53 | 2016-03-02 02:53 | EST | 649.077 | 1194 | 60.005 | 59.947 | 59.947 | -0.058 | -0.058 | -2058.6207 | -2058.6207 | Yes | Yes | 0.005 | 2058.6207 | 2016 | 1015 | 0
EI_2016-03-06_201159 | 2016-03-06 15:12 | 2016-03-06 15:12 | EST | 296.6345 | 895 | 59.99 | 59.958 | 59.949 | -0.032 | -0.041 | -2796.875 | -2182.9268 | Yes | Yes | -0.01 | 2796.875 | 2016 | 1015 | 0
EI_2016-03-12_135535 | 2016-03-12 08:56 | 2016-03-12 08:56 | EST | 567.4907 | 623 | 59.996 | 59.954 | 59.946 | -0.042 | -0.05 | -1483.3333 | -1246 | Yes | Yes | -0.004 | 1483.3333 | 2016 | 1015 | 0
EI_2016-03-16_174757 | 2016-03-16 13:48 | 2016-03-16 13:48 | EDT | 718.8093 | 889 | 60.009 | 59.96 | 59.963 | -0.049 | -0.046 | -1814.2857 | -1932.6087 | Yes | No | 0.009 | 1814.2857 | 2016 | 1015 | 0
EI_2016-03-22_153105 | 2016-03-22 11:31 | 2016-03-22 11:31 | EDT | 339.3055 | 1111 | 59.978 | 59.934 | 59.934 | -0.044 | -0.044 | -2525 | -2525 | Yes | Yes | -0.022 | 2525 | 2016 | 1015 | 0
EI_2016-04-04_112644 | 2016-04-04 07:27 | 2016-04-04 07:27 | EDT | 375 | 589 | 60.008 | 59.961 | 59.96 | -0.047 | -0.048 | -1253.1915 | -1227.0833 | Yes | Yes | 0.008 | 1253.1915 | 2016 | 1015 | 0
EI_2016-04-15_000523 | 2016-04-14 20:05 | 2016-04-14 20:05 | EDT | 299 | 1092 | 59.991 | 59.944 | 59.941 | -0.047 | -0.05 | -2323.4043 | -2184 | Yes | Yes | -0.009 | 2323.4043 | 2016 | 1015 | 0
EI_2016-04-18_013115 | 2016-04-17 21:31 | 2016-04-17 21:31 | EDT | 502 | 856 | 60.005 | 59.97 | 59.96 | -0.035 | -0.045 | -2445.7143 | -1902.2222 | Yes | Yes | 0.005 | 2445.7143 | 2016 | 1015 | 0
EI_2016-05-11_195318 | 2016-05-11 15:53 | 2016-05-11 15:53 | EDT | 610 | 1155 | 60.011 | 59.945 | 59.944 | -0.066 | -0.067 | -1750 | -1723.8806 | Yes | Yes | 0.011 | 1750 | 2016 | 1015 | 0
EI_2016-05-16_020311 | 2016-05-15 22:03 | 2016-05-15 22:03 | EDT | 255 | 541 | 59.99 | 59.966 | 59.948 | -0.024 | -0.042 | -2254.1667 | -1288.0952 | Yes | Yes | -0.01 | 2254.1667 | 2016 | 1015 | 0
EI_2016-05-25_060603 | 2016-05-25 02:06 | 2016-05-25 02:06 | EDT | 210 | 1221 | 60.014 | 59.958 | 59.952 | -0.056 | -0.062 | -2180.3571 | -1969.3548 | Yes | Yes | 0.014 | 2180.3571 | 2016 | 1015 | 0
EI_2016-05-30_182633 | 2016-05-30 14:27 | 2016-05-30 14:27 | EDT | 298 | 945 | 59.987 | 59.95 | 59.948 | -0.037 | -0.039 | -2554.0541 | -2423.0769 | Yes | No | -0.013 | 2554.0541 | 2016 | 1015 | 0
EI_2016-05-31_202648 | 2016-05-31 16:27 | 2016-05-31 16:27 | EDT | 558 | 934 | 59.997 | 59.953 | 59.954 | -0.044 | -0.043 | -2122.7273 | -2172.093 | Yes | Yes | -0.003 | 2122.7273 | 2016 | 1015 | 0
EI_2016-06-05_211333 | 2016-06-05 17:14 | 2016-06-05 17:14 | EDT |  | 918 | 60.014 | 59.983 | 59.98 | -0.031 | -0.034 | -2961.2903 | -2700 | Yes | Yes | 0.014 | 2961.2903 | 2016 | 1015 | 0
EI_2016-06-25_190725 | 2016-06-25 15:07 | 2016-06-25 15:07 | EDT |  | 1266 | 60.024 | 59.96 | 59.975 | -0.064 | -0.049 | -1978.125 | -2583.6735 | Yes | No | 0.024 | 1978.125 | 2016 | 1015 | 0
EI_2016-06-28_082258 | 2016-06-28 04:23 | 2016-06-28 04:23 | EDT |  | 1213 | 59.994 | 59.964 | 59.955 | -0.03 | -0.039 | -4043.3333 | -3110.2564 | Yes | Yes | -0.006 | 4043.3333 | 2016 | 1015 | 0
EI_2016-07-05_222533 | 2016-07-05 18:26 | 2016-07-05 18:26 | EDT |  | 1299 | 59.97 | 59.935 | 59.933 | -0.035 | -0.037 | -3711.4286 | -3510.8108 | Yes | No | -0.03 | 3711.4286 | 2016 | 1015 | 0
EI_2016-07-06_133806 | 2016-07-06 09:38 | 2016-07-06 09:38 | EDT |  | 994 | 59.978 | 59.941 | 59.942 | -0.037 | -0.036 | -2686.4865 | -2761.1111 | Yes | No | -0.022 | 2686.4865 | 2016 | 1015 | 0
EI_2016-07-12_181312 | 2016-07-12 14:13 | 2016-07-12 14:13 | EDT |  | 800 | 59.986 | 59.956 | 59.956 | -0.03 | -0.03 | -2666.6667 | -2666.6667 | Yes | No | -0.014 | 2666.6667 | 2016 | 1015 | 0
EI_2016-07-13_110101 | 2016-07-13 07:01 | 2016-07-13 07:01 | EDT |  | 938 | 59.988 | 59.963 | 59.955 | -0.025 | -0.033 | -3752 | -2842.4242 | Yes | No | -0.012 | 3752 | 2016 | 1015 | 0
EI_2016-07-24_202210 | 2016-07-24 16:22 | 2016-07-24 16:22 | EDT |  | 1300 | 60 | 59.961 | 59.96 | -0.039 | -0.04 | -3333.3333 | -3250 | Yes | Yes | 0 | 3333.3333 | 2016 | 1015 | 0
EI_2016-07-28_172741 | 2016-07-28 13:28 | 2016-07-28 13:28 | EDT |  | 801 | 59.979 | 59.944 | 59.95 | -0.035 | -0.029 | -2288.5714 | -2762.069 | Yes | No | -0.021 | 2288.5714 | 2016 | 1015 | 0
EI_2016-08-08_150943 | 2016-08-08 11:10 | 2016-08-08 11:10 | EDT |  | 680 | 60.006 | 59.971 | 59.967 | -0.035 | -0.039 | -1942.8571 | -1743.5897 | Yes | No | 0.006 | 1942.8571 | 2016 | 1015 | 0
EI_2016-08-09_064348 | 2016-08-09 02:44 | 2016-08-09 02:44 | EDT |  | 893 | 59.983 | 59.947 | 59.944 | -0.036 | -0.039 | -2480.5556 | -2289.7436 | Yes | No | -0.017 | 2480.5556 | 2016 | 1015 | 0
EI_2016-08-13_001034 | 2016-08-12 20:11 | 2016-08-12 20:11 | EDT |  | 800 | 59.992 | 59.968 | 59.96 | -0.024 | -0.032 | -3333.3333 | -2500 | Yes | No | -0.008 | 3333.3333 | 2016 | 1015 | 0
EI_2016-08-17_171816 | 2016-08-17 13:18 | 2016-08-17 13:18 | EDT |  | 830 | 59.988 | 59.962 | 59.957 | -0.026 | -0.031 | -3192.3077 | -2677.4194 | Yes | No | -0.012 | 3192.3077 | 2016 | 1015 | 0
EI_2016-08-31_010912 | 2016-08-30 21:09 | 2016-08-30 21:09 | EDT |  | 1137 | 60.009 | 59.954 | 59.959 | -0.055 | -0.05 | -2067.2727 | -2274 | Yes | Yes | 0.009 | 2067.2727 | 2016 | 1015 | 0
EI_2016-08-31_191307 | 2016-08-31 15:13 |  | EDT |  | 1202 | 59.994 | 59.958 | 59.958 | -0.036 | -0.036 | -3338.8889 | -3338.8889 | Yes | Yes | -0.006 | 3338.8889 | 2016 | 1015 | 0
EI_2016-09-03_120248 | 2016-09-03 08:03 | 2016-09-03 08:03 | EDT |  | 855 | 59.994 | 59.954 | 59.957 | -0.04 | -0.037 | -2137.5 | -2310.8108 | Yes | No | -0.006 | 2137.5 | 2016 | 1015 | 0
EI_2016-09-09_211758 | 2016-09-09 17:18 | 2016-09-09 17:18 | EDT |  | 1395 | 59.983 | 59.939 | 59.934 | -0.044 | -0.049 | -3170.4545 | -2846.9388 | Yes | Yes | -0.017 | 3170.4545 | 2016 | 1015 | 0
EI_2016-09-10_074331 | 2016-09-10 03:44 | 2016-09-10 03:44 | EDT |  | 931 | 59.988 | 59.958 | 59.952 | -0.03 | -0.036 | -3103.3333 | -2586.1111 | Yes | No | -0.012 | 3103.3333 | 2016 | 1015 | 0
EI_2016-09-11_232803 | 2016-09-11 19:28 | 2016-09-11 19:28 | EDT |  | 1270 | 59.984 | 59.947 | 59.941 | -0.037 | -0.043 | -3432.4324 | -2953.4884 | Yes | No | -0.016 | 3432.4324 | 2016 | 1015 | 0
EI_2016-09-26_202712 | 2016-09-26 16:27 | 2016-09-26 16:27 | EDT |  | 978 | 60.004 | 59.96 | 59.958 | -0.044 | -0.046 | -2222.7273 | -2126.087 | Yes | Yes | 0.004 | 2222.7273 | 2016 | 1015 | 0
EI_2016-09-27_114615 | 2016-09-27 07:46 | 2016-09-27 07:46 | EDT |  | 795 | 60.023 | 59.971 | 59.978 | -0.052 | -0.045 | -1528.8462 | -1766.6667 | Yes | No | 0.023 | 1528.8462 | 2016 | 1015 | 0
EI_2016-10-01_101453 | 2016-10-01 06:15 | 2016-10-01 06:15 | EDT |  | 930 | 60.005 | 59.97 | 59.955 | -0.035 | -0.05 | -2657.1429 | -1860 | Yes | Yes | 0.005 | 2657.1429 | 2016 | 1015 | 0
EI_2016-10-09_065405 | 2016-10-09 02:54 | 2016-10-09 02:54 | EDT |  | 865 | 60.011 | 59.96 | 59.956 | -0.051 | -0.055 | -1696.0784 | -1572.7273 | Yes | No | 0.011 | 1696.0784 | 2016 | 1015 | 0
EI_2016-10-09_082725 | 2016-10-09 04:27 | 2016-10-09 04:27 | EDT |  | 850 | 59.994 | 59.969 | 59.954 | -0.025 | -0.04 | -3400 | -2125 | Yes | Yes | -0.006 | 3400 | 2016 | 1015 | 0
EI_2016-10-12_183852 | 2016-10-12 14:39 | 2016-10-12 14:39 | EDT |  | 1163 | 59.969 | 59.942 | 59.93 | -0.027 | -0.039 | -4307.4074 | -2982.0513 | Yes | No | -0.031 | 4307.4074 | 2016 | 1015 | 0
EI_2016-10-15_024554 | 2016-10-14 22:46 | 2016-10-14 22:46 | EDT |  | 595 | 60.022 | 59.98 | 59.983 | -0.042 | -0.039 | -1416.6667 | -1525.641 | Yes | No | 0.022 | 1416.6667 | 2016 | 1015 | 0
EI_2016-10-24_212806 | 2016-10-24 17:28 | 2016-10-24 17:28 | EDT |  | 1133 | 59.973 | 59.945 | 59.933 | -0.028 | -0.04 | -4046.4286 | -2832.5 | Yes | Yes | -0.027 | 4046.4286 | 2016 | 1015 | 0
EI_2016-10-27_155859 | 2016-10-27 11:59 | 2016-10-27 11:59 | EDT |  | 853 | 60.027 | 60.002 | 59.986 | -0.025 | -0.041 | -3412 | -2080.4878 | Yes | No | 0.027 | 3412 | 2016 | 1015 | 0
EI_2016-11-11_140713 | 2016-11-11 09:07 | 2016-11-11 09:07 | EST |  | 987 | 59.993 | 59.96 | 59.954 | -0.033 | -0.039 | -2990.9091 | -2530.7692 | Yes | No | -0.007 | 2990.9091 | 2016 | 1015 | 0
EI_2016-11-14_095434 | 2016-11-14 04:55 | 2016-11-14 04:55 | EST |  | 851 | 60.002 | 59.96 | 59.957 | -0.042 | -0.045 | -2026.1905 | -1891.1111 | Yes | Yes | 0.002 | 2026.1905 | 2016 | 1015 | 0
EI_2016-11-16_134835 | 2016-11-16 08:49 | 2016-11-16 08:49 | EST |  | 750 | 60.012 | 59.976 | 59.976 | -0.036 | -0.036 | -2083.3333 | -2083.3333 | Yes | No | 0.012 | 2083.3333 | 2016 | 1015 | 0
EI_2016-11-17_132105 | 2016-11-17 08:21 | 2016-11-17 08:21 | EST |  | 754 | 60.014 | 59.959 | 59.965 | -0.055 | -0.049 | -1370.9091 | -1538.7755 | Yes | No | 0.014 | 1370.9091 | 2016 | 1015 | 0
EI_2016-11-20_094845 | 2016-11-20 04:49 | 2016-11-20 04:49 | EST |  | 700 | 60.018 | 59.976 | 59.977 | -0.042 | -0.041 | -1666.6667 | -1707.3171 | Yes | No | 0.018 | 1666.6667 | 2016 | 1015 | 0
EI_2016-11-27_062631 | 2016-11-27 01:27 | 2016-11-27 01:27 | EST |  | 980 | 60.006 | 59.95 | 59.95 | -0.056 | -0.056 | -1750 | -1750 | Yes | Yes | 0.006 | 1750 | 2016 | 1015 | 0
EI_2016-11-29_163110 | 2016-11-29 11:31 | 2016-11-29 11:31 | EST |  | 559 | 60.005 | 59.965 | 59.962 | -0.04 | -0.043 | -1397.5 | -1300 | Yes | No | 0.005 | 1397.5 | 2016 | 1015 | 0

## WI M4
Event ID | Local Time | Time Zone | MW Loss | A Value Hz | B Value Hz | Point C Hz | B-A Delta Hz | C-A Delta Hz | B to A IFRM | C to A IFRM | IFRO | 1st Step UFLS | Margin =C-UFLS (Hz)
WI_2017-05-03_124756 | 2017-05-03 04:48 | PDT | 500 | 60.014 | 59.963 | 59.931 | -0.051 | -0.083 | -980.3922 | -602.4096 | 858 | 59.5 | 0.431
WI_2017-05-17_062846 | 2017-05-16 22:29 | PDT | 491 | 60.014 | 59.981 | 59.936 | -0.033 | -0.078 | -1487.8788 | -629.4872 | 858 | 59.5 | 0.436
WI_2017-05-27_124655 | 2017-05-27 04:47 | PDT | 578 | 60.009 | 59.966 | 59.926 | -0.043 | -0.083 | -1344.186 | -696.3855 | 858 | 59.5 | 0.426
WI_2017-06-08_144717 | 2017-06-08 06:47 | PDT | 766 | 59.974 | 59.949 | 59.893 | -0.025 | -0.081 | -3064 | -945.679 | 858 | 59.5 | 0.393
WI_2017-06-15_200018 | 2017-06-15 12:00 | PDT | 875 | 60.013 | 59.941 | 59.902 | -0.072 | -0.111 | -1215.2778 | -788.2883 | 858 | 59.5 | 0.402
WI_2017-06-16_121400 | 2017-06-16 04:14 | PDT | 2685 | 59.974 | 59.85 | 59.697 | -0.124 | -0.277 | -2165.3226 | -969.3141 | 858 | 59.5 | 0.197
WI_2017-06-19_214320 | 2017-06-19 13:43 | PDT | 1313 | 59.991 | 59.915 | 59.855 | -0.076 | -0.136 | -1727.6316 | -965.4412 | 858 | 59.5 | 0.355
WI_2017-06-23_174501 | 2017-06-23 09:45 | PDT | 2619 | 59.98 | 59.862 | 59.764 | -0.118 | -0.216 | -2219.4915 | -1212.5 | 858 | 59.5 | 0.264
WI_2017-07-04_182353 | 2017-07-04 10:24 | PDT | 706 | 60.002 | 59.95 | 59.924 | -0.052 | -0.078 | -1357.6923 | -905.1282 | 858 | 59.5 | 0.424
WI_2017-07-05_075543 | 2017-07-04 23:56 | PDT | 633 | 60.032 | 59.985 | 59.947 | -0.047 | -0.085 | -1346.8085 | -744.7059 | 858 | 59.5 | 0.447
WI_2017-07-15_183907 | 2017-07-15 10:39 | PDT | 708 | 60.008 | 59.962 | 59.935 | -0.046 | -0.073 | -1539.1304 | -969.863 | 858 | 59.5 | 0.435
WI_2017-07-29_164834 | 2017-07-29 08:49 | PDT | 928 | 59.991 | 59.948 | 59.907 | -0.043 | -0.084 | -2158.1395 | -1104.7619 | 858 | 59.5 | 0.407
WI_2017-07-30_185540 | 2017-07-30 10:56 | PDT | 1494 | 59.989 | 59.909 | 59.862 | -0.08 | -0.127 | -1867.5 | -1176.378 | 858 | 59.5 | 0.362
WI_2017-08-08_100816 | 2017-08-08 02:08 | PDT | 1634 | 60.005 | 59.898 | 59.827 | -0.107 | -0.178 | -1527.1028 | -917.9775 | 858 | 59.5 | 0.327
WI_2017-08-10_235052 | 2017-08-10 15:51 | PDT | 547 | 60.001 | 59.959 | 59.93 | -0.042 | -0.071 | -1302.381 | -770.4225 | 858 | 59.5 | 0.43
WI_2017-08-20_230542 | 2017-08-20 15:06 | PDT | 833 | 60.025 | 59.961 | 59.931 | -0.064 | -0.094 | -1301.5625 | -886.1702 | 858 | 59.5 | 0.431
WI_2017-09-10_034555 | 2017-09-09 19:46 | PDT | 1370 | 59.993 | 59.93 | 59.878 | -0.063 | -0.115 | -2174.6032 | -1191.3043 | 858 | 59.5 | 0.378
WI_2017-09-12_002352 | 2017-09-11 16:24 | PDT | 779 | 59.978 | 59.953 | 59.914 | -0.025 | -0.064 | -3116 | -1217.1875 | 858 | 59.5 | 0.414
WI_2017-09-15_040444 | 2017-09-14 20:05 | PDT | 1623 | 59.979 | 59.908 | 59.817 | -0.071 | -0.162 | -2285.9155 | -1001.8519 | 858 | 59.5 | 0.317
WI_2017-09-20_151429 | 2017-09-20 07:14 | PDT | 731 | 59.976 | 59.965 | 59.901 | -0.011 | -0.075 | -6645.4545 | -974.6667 | 858 | 59.5 | 0.401
WI_2017-10-06_083718 | 2017-10-06 00:37 | PDT | 363 | 60.021 | 59.997 | 59.948 | -0.024 | -0.073 | -1512.5 | -497.2603 | 858 | 59.5 | 0.448
WI_2017-11-24_151731 | 2017-11-24 07:18 | PST | -547 | 60.014 | 60.046 | 60.086 | 0.032 | 0.072 | -1709.375 | -759.7222 | 858 | 59.5 | N/A LoL
WI_2017-12-02_195659 | 2017-12-02 11:57 | PST | 731 | 60.015 | 59.975 | 59.914 | -0.04 | -0.101 | -1827.5 | -723.7624 | 858 | 59.5 | 0.414
WI_2017-12-28_045209 | 2017-12-27 20:52 | PST | 755 | 60.008 | 59.96 | 59.924 | -0.048 | -0.084 | -1572.9167 | -898.8095 | 858 | 59.5 | 0.424
WI_2017-12-28_100542 | 2017-12-28 02:06 | PST | 628 | 60.004 | 59.961 | 59.929 | -0.043 | -0.075 | -1460.4651 | -837.3333 | 858 | 59.5 | 0.429
WI_2018-02-16_045335 | 2018-02-15 20:54 | PST | 1336 | 60.011 | 59.941 | 59.876 | -0.07 | -0.135 | -1908.5714 | -989.6296 | 858 | 59.5 | 0.376
WI_2018-02-18_013647 | 2018-02-17 17:37 | PST | 1059 | 59.993 | 59.942 | 59.868 | -0.051 | -0.125 | -2076.4706 | -847.2 | 858 | 59.5 | 0.368
WI_2018-02-22_123137 | 2018-02-22 04:32 | PST | 567 | 60.008 | 59.96 | 59.934 | -0.048 | -0.074 | -1181.25 | -766.2162 | 858 | 59.5 | 0.434
WI_2018-02-23_144538 | 2018-02-23 06:46 | PST | 750 | 59.987 | 59.939 | 59.908 | -0.048 | -0.079 | -1562.5 | -949.3671 | 858 | 59.5 | 0.408
WI_2018-03-04_174357 | 2018-03-04 09:44 | PST | 542 | 60.011 | 59.972 | 59.932 | -0.039 | -0.079 | -1389.7436 | -686.0759 | 858 | 59.5 | 0.432
WI_2018-03-07_003211 | 2018-03-06 16:32 | PST | 752 | 59.96 | 59.934 | 59.888 | -0.026 | -0.072 | -2892.3077 | -1044.4444 | 858 | 59.5 | 0.388
WI_2018-03-13_113015 | 2018-03-13 04:30 | PDT | -320 | 59.972 | 60.003 | 60.045 | 0.031 | 0.073 | -1032.2581 | -438.3562 | 858 | 59.5 | N/A LoL
WI_2018-03-14_162442 | 2018-03-14 09:25 | PDT | 1575 | 60.036 | 59.945 | 59.864 | -0.091 | -0.172 | -1730.7692 | -915.6977 | 858 | 59.5 | 0.364
WI_2018-03-15_115420 | 2018-03-15 04:54 | PDT | 968 | 59.989 | 59.945 | 59.894 | -0.044 | -0.095 | -2200 | -1018.9474 | 858 | 59.5 | 0.394
WI_2018-03-16_104109 | 2018-03-16 03:41 | PDT | 596 | 59.986 | 59.949 | 59.897 | -0.037 | -0.089 | -1610.8108 | -669.6629 | 858 | 59.5 | 0.397
WI_2018-03-26_203152 | 2018-03-26 13:32 | PDT | 707 | 60.004 | 59.971 | 59.921 | -0.033 | -0.083 | -2142.4242 | -851.8072 | 858 | 59.5 | 0.421
WI_2018-04-30_160100 | 2018-04-30 09:01 | PDT | 497 | 60.01 | 59.983 | 59.928 | -0.027 | -0.082 | -1840.7407 | -606.0976 | 858 | 59.5 | 0.428
WI_2018-05-01_015514 | 2018-04-30 18:55 | PDT | 482 | 60.015 | 59.974 | 59.933 | -0.041 | -0.082 | -1175.6098 | -587.8049 | 858 | 59.5 | 0.433
WI_2018-05-02_200532 | 2018-05-02 13:06 | PDT | 693 | 59.983 | 59.941 | 59.902 | -0.042 | -0.081 | -1650 | -855.5556 | 858 | 59.5 | 0.402
WI_2018-05-05_021054 | 2018-05-04 19:11 | PDT | 1126 | 60.013 | 59.971 | 59.898 | -0.042 | -0.115 | -2680.9524 | -979.1304 | 858 | 59.5 | 0.398
WI_2018-05-10_020048 | 2018-05-09 19:01 | PDT | 642 | 60.008 | 59.972 | 59.915 | -0.036 | -0.093 | -1783.3333 | -690.3226 | 858 | 59.5 | 0.415
WI_2018-05-10_165903 | 2018-05-10 09:59 | PDT | 745 | 60.011 | 59.95 | 59.906 | -0.061 | -0.105 | -1221.3115 | -709.5238 | 858 | 59.5 | 0.406
WI_2018-05-12_230222 | 2018-05-12 16:02 | PDT | 602 | 60.009 | 59.967 | 59.93 | -0.042 | -0.079 | -1433.3333 | -762.0253 | 858 | 59.5 | 0.43
WI_2018-05-17_111515 | 2018-05-17 04:15 | PDT | -310 | 59.983 | 60.017 | 60.057 | 0.034 | 0.074 | -911.7647 | -418.9189 | 858 | 59.5 | N/A LoL
WI_2018-05-18_135111 | 2018-05-18 06:51 | PDT | 1156 | 60.013 | 59.939 | 59.858 | -0.074 | -0.155 | -1562.1622 | -745.8065 | 858 | 59.5 | 0.358
WI_2018-05-22_045301 | 2018-05-21 21:53 | PDT | 580 | 60.018 | 59.992 | 59.943 | -0.026 | -0.075 | -2230.7692 | -773.3333 | 858 | 59.5 | 0.443
WI_2018-06-06_202351 | 2018-06-06 13:24 | PDT | 716 | 59.991 | 59.963 | 59.912 | -0.028 | -0.079 | -2557.1429 | -906.3291 | 858 | 59.5 | 0.412
WI_2018-06-11_130959 | 2018-06-11 06:10 | PDT | 534 | 60.026 | 59.966 | 59.934 | -0.06 | -0.092 | -890 | -580.4348 | 858 | 59.5 | 0.434
WI_2018-06-21_032028 | 2018-06-20 20:20 | PDT | 1236 | 60.011 | 59.943 | 59.893 | -0.068 | -0.118 | -1817.6471 | -1047.4576 | 858 | 59.5 | 0.393
WI_2018-06-22_001620 | 2018-06-21 17:16 | PDT | 778 | 59.988 | 59.957 | 59.922 | -0.031 | -0.066 | -2509.6774 | -1178.7879 | 858 | 59.5 | 0.422
WI_2018-06-27_224744 | 2018-06-27 15:48 | PDT | 721 | 60.007 | 59.963 | 59.916 | -0.044 | -0.091 | -1638.6364 | -792.3077 | 858 | 59.5 | 0.416
WI_2018-06-28_061217 | 2018-06-27 23:12 | PDT | 881 | 59.973 | 59.935 | 59.885 | -0.038 | -0.088 | -2318.4211 | -1001.1364 | 858 | 59.5 | 0.385
WI_2018-07-18_230927 | 2018-07-18 16:09 | PDT | 1007 | 59.976 | 59.93 | 59.887 | -0.046 | -0.089 | -2189.1304 | -1131.4607 | 858 | 59.5 | 0.387
WI_2018-07-19_003022 | 2018-07-18 17:30 | PDT | 2741 | 59.985 | 59.863 | 59.746 | -0.122 | -0.239 | -2246.7213 | -1146.8619 | 858 | 59.5 | 0.246
WI_2018-08-12_101109 | 2018-08-12 03:11 | PDT | 850 | 59.994 | 59.947 | 59.898 | -0.047 | -0.096 | -1808.5106 | -885.4167 | 858 | 59.5 | 0.398
WI_2018-09-02_115548 | 2018-09-02 04:56 | PDT | 710 | 59.991 | 59.942 | 59.906 | -0.049 | -0.085 | -1448.9796 | -835.2941 | 858 | 59.5 | 0.406
WI_2018-09-07_143008 | 2018-09-07 07:30 | PDT | 450 | 60.022 | 59.983 | 59.947 | -0.039 | -0.075 | -1153.8462 | -600 | 858 | 59.5 | 0.447
WI_2018-09-22_174655 | 2018-09-22 10:47 | PDT | 593 | 59.998 | 59.954 | 59.928 | -0.044 | -0.07 | -1347.7273 | -847.1429 | 858 | 59.5 | 0.428
WI_2018-10-12_143748 | 2018-10-12 07:38 | PDT | 743 | 59.983 | 59.956 | 59.916 | -0.027 | -0.067 | -2751.8519 | -1108.9552 | 858 | 59.5 | 0.416
WI_2018-10-29_165404 | 2018-10-29 09:54 | PDT | 765 | 60.009 | 59.966 | 59.924 | -0.043 | -0.085 | -1779.0698 | -900 | 858 | 59.5 | 0.424
WI_2018-10-30_015611 | 2018-10-29 18:56 | PDT | 660 | 60.005 | 59.969 | 59.922 | -0.036 | -0.083 | -1833.3333 | -795.1807 | 858 | 59.5 | 0.422
WI_2018-10-30_050119 | 2018-10-29 22:01 | PDT | 734 | 59.997 | 59.945 | 59.906 | -0.052 | -0.091 | -1411.5385 | -806.5934 | 858 | 59.5 | 0.406
WI_2018-11-09_152815 | 2018-11-09 07:28 | PST | 784 | 60.029 | 59.982 | 59.931 | -0.047 | -0.098 | -1668.0851 | -800 | 858 | 59.5 | 0.431
WI_2018-11-20_143939 | 2018-11-20 06:40 | PST | 757 | 59.978 | 59.95 | 59.908 | -0.028 | -0.07 | -2703.5714 | -1081.4286 | 858 | 59.5 | 0.408
WI_2018-11-29_144451 | 2018-11-29 06:45 | PST | 1208 | 59.991 | 59.923 | 59.86 | -0.068 | -0.131 | -1776.4706 | -922.1374 | 858 | 59.5 | 0.36
WI_2018-12-01_180644 | 2018-12-01 10:07 | PST | 1114 | 60.018 | 59.944 | 59.888 | -0.074 | -0.13 | -1505.4054 | -856.9231 | 858 | 59.5 | 0.388
WI_2018-12-19_033647 | 2018-12-18 19:37 | PST | 726 | 60.004 | 59.956 | 59.909 | -0.048 | -0.095 | -1512.5 | -764.2105 | 858 | 59.5 | 0.409
WI_2019-01-02_082143 | 2019-01-02 00:22 | PST | 807 | 59.977 | 59.94 | 59.891 | -0.037 | -0.086 | -2181.0811 | -938.3721 | 858 | 59.5 | 0.391
WI_2019-01-06_020750 | 2019-01-05 18:08 | PST | 743 | 60.015 | 59.975 | 59.937 | -0.04 | -0.078 | -1857.5 | -952.5641 | 858 | 59.5 | 0.437
WI_2019-01-07_073123 | 2019-01-06 23:31 | PST | 675 | 60.011 | 59.956 | 59.923 | -0.055 | -0.088 | -1227.2727 | -767.0455 | 858 | 59.5 | 0.423
WI_2019-01-16_031539 | 2019-01-15 19:16 | PST | 1122 | 59.986 | 59.934 | 59.882 | -0.052 | -0.104 | -2157.6923 | -1078.8462 | 858 | 59.5 | 0.382
WI_2019-02-28_150348 | 2019-02-28 07:04 | PST | 512 | 60.018 | 59.979 | 59.946 | -0.039 | -0.072 | -1312.8205 | -711.1111 | 858 | 59.5 | 0.446
WI_2019-03-11_020655 | 2019-03-10 19:07 | PDT | 698 | 59.972 | 59.941 | 59.892 | -0.031 | -0.08 | -2251.6129 | -872.5 | 858 | 59.5 | 0.392
WI_2019-03-11_204811 | 2019-03-11 13:48 | PDT | 541 | 60.004 | 59.987 | 59.934 | -0.017 | -0.07 | -3182.3529 | -772.8571 | 858 | 59.5 | 0.434
WI_2019-03-12_205453 | 2019-03-12 13:55 | PDT | 380 | 60.013 | 59.999 | 59.943 | -0.014 | -0.07 | -2714.2857 | -542.8571 | 858 | 59.5 | 0.443
WI_2019-03-13_184756 | 2019-03-13 11:48 | PDT | 290 | 60.032 | 60.019 | 59.961 | -0.013 | -0.071 | -2230.7692 | -408.4507 | 858 | 59.5 | 0.461
WI_2019-03-18_192945 | 2019-03-18 12:30 | PDT | 558 | 60.005 | 59.965 | 59.93 | -0.04 | -0.075 | -1395 | -744 | 858 | 59.5 | 0.43
WI_2019-03-25_011045 | 2019-03-24 18:11 | PDT | 1533 | 59.991 | 59.927 | 59.875 | -0.064 | -0.116 | -2395.3125 | -1321.5517 | 858 | 59.5 | 0.375
WI_2019-04-29_111456 | 2019-04-29 04:15 | PDT | 438 | 60.01 | 59.962 | 59.936 | -0.048 | -0.074 | -912.5 | -591.8919 | 858 | 59.5 | 0.436
WI_2019-05-10_035828 | 2019-05-09 20:58 | PDT | 396 | 60.025 | 59.994 | 59.951 | -0.031 | -0.074 | -1277.4194 | -535.1351 | 858 | 59.5 | 0.451
WI_2019-05-21_010019 | 2019-05-20 18:00 | PDT | -289 | 59.958 | 59.981 | 60.028 | 0.023 | 0.07 | -1256.5217 | -412.8571 | 858 | 59.5 | N/A LoL
WI_2019-05-31_202145 | 2019-05-31 13:22 | PDT | 496 | 60.016 | 59.967 | 59.935 | -0.049 | -0.081 | -1012.2449 | -612.3457 | 858 | 59.5 | 0.435
WI_2019-06-02_190537 | 2019-06-02 12:06 | PDT | 573 | 60.027 | 59.982 | 59.931 | -0.045 | -0.096 | -1273.3333 | -596.875 | 858 | 59.5 | 0.431
WI_2019-07-24_072645 | 2019-07-24 00:27 | PDT | 550 | 60.031 | 59.979 | 59.955 | -0.052 | -0.076 | -1057.6923 | -723.6842 | 858 | 59.5 | 0.455
WI_2019-07-26_071213 | 2019-07-26 00:12 | PDT | 738 | 59.999 | 59.955 | 59.906 | -0.044 | -0.093 | -1677.2727 | -793.5484 | 858 | 59.5 | 0.406
WI_2019-07-28_181517 | 2019-07-28 11:15 | PDT | -301 | 59.97 | 59.997 | 60.031 | 0.027 | 0.061 | -1114.8148 | -493.4426 | 858 | 59.5 | N/A LoL
WI_2019-08-01_195136 | 2019-08-01 12:52 | PDT | 750 | 59.976 | 59.949 | 59.907 | -0.027 | -0.069 | -2777.7778 | -1086.9565 | 858 | 59.5 | 0.407
WI_2019-08-02_223351 | 2019-08-02 15:34 | PDT | -888 | 60.008 | 60.052 | 60.081 | 0.044 | 0.073 | -2018.1818 | -1216.4384 | 858 | 59.5 | N/A LoL
WI_2019-08-03_204104 | 2019-08-03 13:41 | PDT | 757 | 59.981 | 59.945 | 59.906 | -0.036 | -0.075 | -2102.7778 | -1009.3333 | 858 | 59.5 | 0.406
WI_2019-08-06_002322 | 2019-08-05 17:23 | PDT | 712 | 59.987 | 59.963 | 59.946 | -0.024 | -0.041 | -2966.6667 | -1736.5854 | 858 | 59.5 | 0.446
WI_2019-08-16_152106 | 2019-08-16 08:21 | PDT | 1311 | 60.009 | 59.938 | 59.887 | -0.071 | -0.122 | -1846.4789 | -1074.5902 | 858 | 59.5 | 0.387
WI_2019-08-23_174301 | 2019-08-23 10:43 | PDT | 1442 | 59.989 | 59.926 | 59.857 | -0.063 | -0.132 | -2288.8889 | -1092.4242 | 858 | 59.5 | 0.357
WI_2019-08-25_150818 | 2019-08-25 08:08 | PDT | 749 | 60.022 | 59.967 | 59.932 | -0.055 | -0.09 | -1361.8182 | -832.2222 | 858 | 59.5 | 0.432
WI_2019-08-31_144432 | 2019-08-31 07:45 | PDT | 702 | 59.962 | 59.945 | 59.901 | -0.017 | -0.061 | -4129.4118 | -1150.8197 | 858 | 59.5 | 0.401
WI_2019-09-03_191505 | 2019-09-03 12:15 | PDT | 744 | 59.977 | 59.952 | 59.905 | -0.025 | -0.072 | -2976 | -1033.3333 | 858 | 59.5 | 0.405
WI_2019-09-11_042240 | 2019-09-10 21:23 | PDT | 855 | 59.981 | 59.936 | 59.9 | -0.045 | -0.081 | -1900 | -1055.5556 | 858 | 59.5 | 0.4

## QI (hidden)
Event ID | Time | Day | Time Zone | CERTS Est. MW | NERC SA Actual MW Loss | A Value Hz | B Value Hz | Point C Hz | B-A Delta Hz | C-A Delta Hz | B to A IFRM | C to A IFRM | FWG Sel. M-4 Events | Rev. BAL-003 Events (FWG) | (from 60) | M-4 | Operating Year | IFRO | Below IFRO
QI_2012-01-13_133351 | 2012-01-13 08:34 | 2012-01-13 08:34 | EST | 1226.8019 | 615 | 60.0174 | 59.9215 | 59.6998 | -0.095909 | -0.31756 | -641.2314 | -193.6631 | Yes | Yes | 0.01736 | 641.2314 | 2012 | 179 | 0
QI_2012-02-09_141750 | 2012-02-09 09:18 | 2012-02-09 09:18 | EST | -689.3907 | -785.2 | 59.9925 | 60.0693 | 60.4409 | 0.076866 | 0.44842 | -1021.5141 | -175.105 | Yes | Yes | -0.0075179 | 1021.5141 | 2012 | 179 | 0
QI_2012-03-03_185654 | 2012-03-03 13:57 | 2012-03-03 13:57 | EST | 1758.2719 | 2060 | 60.0175 | 59.5153 | 58.7919 | -0.50224 | -1.2256 | -410.1661 | -168.077 | Yes | Yes | 0.017529 | 410.1661 | 2012 | 179 | 0
QI_2012-03-15_191435 | 2012-03-15 15:15 | 2012-03-15 15:15 | EDT | -454.9977 | -575 | 60.0173 | 60.0625 | 60.3846 | 0.045174 | 0.36726 | -1272.8437 | -156.5646 | Yes | Yes | 0.017341 | 1272.8437 | 2012 | 179 | 0
QI_2012-04-12_171252 | 2012-04-12 13:13 | 2012-04-12 13:13 | EDT | -491.4049 | -453 | 59.9829 | 60.1051 | 60.4552 | 0.12217 | 0.47225 | -370.7824 | -95.9231 | Yes | Yes | -0.017053 | 370.7824 | 2012 | 179 | 0
QI_2012-04-23_122724 | 2012-04-23 08:27 | 2012-04-23 08:27 | EDT | 367.2103 | 477 | 60.0042 | 59.9397 | 59.69 | -0.064473 | -0.31416 | -739.8393 | -151.8335 | Yes | Yes | 0.0041585 | 739.8393 | 2012 | 179 | 0
QI_2012-05-05_043347 | 2012-05-05 00:34 | 2012-05-05 00:34 | EDT | 363.9347 | 1293 | 59.9414 | 59.8641 | 59.5579 | -0.077259 | -0.38347 | -1673.583 | -337.1881 | Yes | Yes | -0.058635 | 1673.583 | 2012 | 179 | 0
QI_2012-06-11_213051 | 2012-06-11 17:31 | 2012-06-11 17:31 | EDT | 1383.8489 | 1479 | 59.9848 | 59.7565 | 59.087 | -0.22829 | -0.89776 | -647.8716 | -164.7439 | Yes | Yes | -0.015241 | 647.8716 | 2012 | 179 | 0
QI_2012-06-18_021056 | 2012-06-17 22:11 | 2012-06-17 22:11 | EDT | 230.1009 | 459 | 60.0103 | 59.9449 | 59.6595 | -0.06531 | -0.35076 | -702.797 | -130.8591 | Yes | Yes | 0.010259 | 702.797 | 2012 | 179 | 0
QI_2012-06-21_140715 | 2012-06-21 10:07 | 2012-06-21 10:07 | EDT | -992.8517 | -605 | 60.0128 | 60.0755 | 60.4307 | 0.062679 | 0.4179 | -965.2392 | -144.7721 | Yes | Yes | 0.0128 | 965.2392 | 2012 | 179 | 0
QI_2012-06-29_141922 | 2012-06-29 10:19 | 2012-06-29 10:19 | EDT | 377.3927 | 560 | 60.0063 | 59.9413 | 59.6508 | -0.064962 | -0.35547 | -862.0485 | -157.5371 | Yes | Yes | 0.0062707 | 862.0485 | 2012 | 179 | 0
QI_2012-07-02_025214 | 2012-07-01 22:52 | 2012-07-01 22:52 | EDT | -1193.3076 | -876 | 60.0419 | 60.1578 | 60.6215 | 0.1159 | 0.57959 | -755.8245 | -151.1409 | Yes | Yes | 0.041906 | 755.8245 | 2012 | 179 | 0
QI_2012-07-24_060640 | 2012-07-24 02:07 | 2012-07-24 02:07 | EDT | 2032.771 | 872 | 59.9911 | 59.8041 | 59.3205 | -0.18698 | -0.67059 | -466.3717 | -130.0339 | Yes | Yes | -0.0089064 | 466.3717 | 2012 | 179 | 0
QI_2012-08-13_003222 | 2012-08-12 20:32 | 2012-08-12 20:32 | EDT | 1806.9386 | 618 | 60.0068 | 59.8864 | 59.5715 | -0.1204 | -0.43528 | -513.3053 | -141.9769 | Yes | Yes | 0.0067811 | 513.3053 | 2012 | 179 | 0
QI_2012-08-26_021548 | 2012-08-25 22:16 | 2012-08-25 22:16 | EDT | 145.5757 | 465 | 60.0105 | 59.9373 | 59.6303 | -0.073223 | -0.38024 | -635.0479 | -122.2913 | Yes | Yes | 0.010538 | 635.0479 | 2012 | 179 | 0
QI_2012-08-26_040641 | 2012-08-26 00:07 | 2012-08-26 00:07 | EDT | 114.1714 | 944 | 60.0246 | 59.812 | 59.3041 | -0.21256 | -0.7205 | -444.102 | -131.0201 | Yes | Yes | 0.0246 | 444.102 | 2012 | 179 | 0
QI_2012-08-26_182500 | 2012-08-26 14:25 | 2012-08-26 14:25 | EDT | 202.2338 | 608 | 59.992 | 59.9081 | 59.5522 | -0.08394 | -0.43981 | -724.3264 | -138.2426 | Yes | Yes | -0.0079932 | 724.3264 | 2012 | 179 | 0
QI_2012-08-30_231423 | 2012-08-30 19:14 | 2012-08-30 19:14 | EDT | 562.8051 | 1414 | 60.0276 | 59.8018 | 59.1421 | -0.2258 | -0.8855 | -626.2088 | -159.684 | Yes | Yes | 0.0276 | 626.2088 | 2012 | 179 | 0
QI_2012-08-31_014245 | 2012-08-30 21:43 | 2012-08-30 21:43 | EDT |  | 1302 | 60.003 | 59.741 | 59.1178 | -0.26196 | -0.88517 | -497.0174 | -147.0909 | Yes | Yes | 0.0029685 | 497.0174 | 2012 | 179 | 0
QI_2012-09-07_215617 | 2012-09-07 17:56 | 2012-09-07 17:56 | EDT | 189.0068 | 452 | 60.0455 | 59.9317 | 59.6633 | -0.11381 | -0.38223 | -397.1632 | -118.2548 | Yes | Yes | 0.045525 | 397.1632 | 2012 | 179 | 0
QI_2012-09-08_080803 | 2012-09-08 04:08 | 2012-09-08 04:08 | EDT | -362.1064 | -682 | 60.0154 | 60.1649 | 60.6267 | 0.14945 | 0.61128 | -456.3469 | -111.5687 | Yes | Yes | 0.015419 | 456.3469 | 2012 | 179 | 0
QI_2012-09-15_225749 | 2012-09-15 18:58 | 2012-09-15 18:58 | EDT | 87.2122 | 452 | 60.0088 | 59.9553 | 59.6827 | -0.053519 | -0.32614 | -844.5541 | -138.5922 | Yes | Yes | 0.0088377 | 844.5541 | 2012 | 179 | 0
QI_2012-09-29_031755 | 2012-09-28 23:18 | 2012-09-28 23:18 | EDT | 285.2227 | 733 | 59.9483 | 59.8077 | 59.4469 | -0.14064 | -0.50141 | -521.1979 | -146.1866 | Yes | Yes | -0.051687 | 521.1979 | 2012 | 179 | 0
QI_2012-10-26_185846 | 2012-10-26 14:59 | 2012-10-26 14:59 | EDT | 220.5817 | 807 | 60.0023 | 59.8514 | 59.4343 | -0.15091 | -0.56799 | -534.7606 | -142.0789 | Yes | Yes | 0.0022938 | 534.7606 | 2012 | 179 | 0
QI_2012-10-28_144144 | 2012-10-28 10:42 | 2012-10-28 10:42 | EDT | 88.1122 | 571 | 60.0175 | 59.9078 | 59.5852 | -0.10973 | -0.43231 | -520.3774 | -132.0826 | Yes | Yes | 0.017507 | 520.3774 | 2012 | 179 | 0
QI_2012-12-12_154455 | 2012-12-12 10:45 | 2012-12-12 10:45 | EST | 377.1218 | 670 | 60.021 | 59.9234 | 59.6673 | -0.097561 | -0.3537 | -686.7522 | -189.4266 | Yes | Yes | 0.021 | 686.7522 | 2013 | 179 | 0
QI_2012-12-18_193143 | 2012-12-18 14:32 | 2012-12-18 14:32 | EST | 1628.6199 | 1405 | 59.9843 | 59.781 | 59.3258 | -0.20335 | -0.6585 | -690.9311 | -213.3623 | Yes | Yes | -0.015694 | 690.9311 | 2013 | 179 | 0
QI_2013-01-10_204412 | 2013-01-10 15:44 | 2013-01-10 15:44 | EST | 3987.3337 | 1461 | 59.9938 | 59.8296 | 59.5296 | -0.16422 | -0.4642 | -889.6695 | -314.7339 | Yes | Yes | -0.0062001 | 889.6695 | 2013 | 179 | 0
QI_2013-01-20_135612 | 2013-01-20 08:56 | 2013-01-20 08:56 | EST | 499.7039 | 650 | 59.9828 | 59.9242 | 59.646 | -0.058627 | -0.33679 | -1108.7127 | -193.0002 | Yes | Yes | -0.017213 | 1108.7127 | 2013 | 179 | 0
QI_2013-02-22_180006 | 2013-02-22 13:00 | 2013-02-22 13:00 | EST | 1781.3878 | 1249 | 60.0218 | 59.7597 | 59.2935 | -0.26215 | -0.72831 | -476.436 | -171.4935 | Yes | Yes | 0.021806 | 476.436 | 2013 | 179 | 0
QI_2013-03-21_142458 | 2013-03-21 10:25 | 2013-03-21 10:25 | EDT | -485.1222 | -820 | 59.9903 | 60.0724 | 60.4193 | 0.082161 | 0.42901 | -998.0439 | -191.1367 | Yes | Yes | -0.0097122 | 998.0439 | 2013 | 179 | 0
QI_2013-04-03_124407 | 2013-04-03 08:44 | 2013-04-03 08:44 | EDT | 986.5011 | 996 | 60.0037 | 59.8333 | 59.4298 | -0.1704 | -0.57391 | -584.5169 | -173.5451 | Yes | Yes | 0.0037124 | 584.5169 | 2013 | 179 | 0
QI_2013-04-30_144658 | 2013-04-30 10:47 | 2013-04-30 10:47 | EDT | 220.0018 | 993 | 59.9901 | 59.7349 | 59.317 | -0.2552 | -0.67315 | -389.1045 | -147.5158 | Yes | Yes | -0.0098503 | 389.1045 | 2013 | 179 | 0
QI_2013-05-04_073917 | 2013-05-04 03:39 | 2013-05-04 03:39 | EDT | -1044.448 | -889 | 60.0049 | 60.2133 | 60.7828 | 0.20844 | 0.77793 | -426.4955 | -114.2776 | Yes | Yes | 0.0048687 | 426.4955 | 2013 | 179 | 0
QI_2013-05-04_161245 | 2013-05-04 12:13 | 2013-05-04 12:13 | EDT | 826.0649 | 518 | 60.0038 | 59.908 | 59.5808 | -0.095792 | -0.42303 | -540.757 | -122.4511 | Yes | Yes | 0.0038252 | 540.757 | 2013 | 179 | 0
QI_2013-05-06_182445 | 2013-05-06 14:25 | 2013-05-06 14:25 | EDT | 540.3025 | 551 | 60.0005 | 59.9205 | 59.6019 | -0.079954 | -0.39858 | -689.1469 | -138.2417 | Yes | Yes | 0.00047541 | 689.1469 | 2013 | 179 | 0
QI_2013-05-07_162256 | 2013-05-07 12:23 | 2013-05-07 12:23 | EDT | 1220.3229 | 553 | 59.9829 | 59.9379 | 59.6272 | -0.04504 | -0.35571 | -1227.7983 | -155.4631 | Yes | Yes | -0.017087 | 1227.7983 | 2013 | 179 | 0
QI_2013-05-12_122317 | 2013-05-12 08:23 | 2013-05-12 08:23 | EDT | 676.9761 | 488 | 60.0055 | 59.9029 | 59.5638 | -0.10258 | -0.44171 | -475.7167 | -110.4793 | Yes | Yes | 0.0055125 | 475.7167 | 2013 | 179 | 0
QI_2013-06-11_212813 | 2013-06-11 17:28 | 2013-06-11 17:28 | EDT | 3026.6046 | 1276 | 60.0327 | 59.7832 | 59.2101 | -0.24954 | -0.82261 | -511.3415 | -155.1164 | Yes | Yes | 0.032706 | 511.3415 | 2013 | 179 | 0
QI_2013-06-12_202904 | 2013-06-12 16:29 | 2013-06-12 16:29 | EDT | 2682.2242 | 1466 | 59.9991 | 59.7675 | 59.1568 | -0.23161 | -0.84234 | -632.9686 | -174.0382 | Yes | Yes | -0.00085664 | 632.9686 | 2013 | 179 | 0
QI_2013-06-14_190016 | 2013-06-14 15:00 | 2013-06-14 15:00 | EDT | 786.0232 | 1004 | 59.9882 | 59.8342 | 59.3217 | -0.15402 | -0.66649 | -651.8756 | -150.6394 | Yes | Yes | -0.011807 | 651.8756 | 2013 | 179 | 0
QI_2013-06-14_190337 | 2013-06-14 15:04 | 2013-06-14 15:04 | EDT | 2692.0385 | 848 | 59.9934 | 59.829 | 59.3862 | -0.16436 | -0.60717 | -515.9317 | -139.6632 | Yes | Yes | -0.0066252 | 515.9317 | 2013 | 179 | 0
QI_2013-06-22_201848 | 2013-06-22 16:19 | 2013-06-22 16:19 | EDT | 1064.6043 | 1123 | 59.9946 | 59.7609 | 59.2537 | -0.23368 | -0.74092 | -480.5728 | -151.5686 | Yes | Yes | -0.0053813 | 480.5728 | 2013 | 179 | 0
QI_2013-06-22_212115 | 2013-06-22 17:21 | 2013-06-22 17:21 | EDT | 633.4943 | 1122 | 59.9856 | 59.7276 | 59.2281 | -0.25801 | -0.75753 | -434.8719 | -148.1138 | Yes | Yes | -0.014375 | 434.8719 | 2013 | 179 | 0
QI_2013-06-30_184651 | 2013-06-30 14:47 | 2013-06-30 14:47 | EDT | 2356.6478 | 1203 | 60.0226 | 59.8022 | 59.2538 | -0.22037 | -0.76879 | -545.8927 | -156.4788 | Yes | Yes | 0.022594 | 545.8927 | 2013 | 179 | 0
QI_2013-07-03_150503 | 2013-07-03 11:05 | 2013-07-03 11:05 | EDT | 513.4885 | 1176 | 59.9786 | 59.8055 | 59.2641 | -0.1731 | -0.71454 | -679.3587 | -164.5804 | Yes | Yes | -0.021356 | 679.3587 | 2013 | 179 | 0
QI_2013-07-04_203349 | 2013-07-04 16:34 | 2013-07-04 16:34 | EDT | 1240.8344 | 837 | 59.9963 | 59.8559 | 59.4733 | -0.14037 | -0.52296 | -596.2895 | -160.0501 | Yes | Yes | -0.0037377 | 596.2895 | 2013 | 179 | 0
QI_2013-07-04_215255 | 2013-07-04 17:53 | 2013-07-04 17:53 | EDT | 1131.3073 | 1900 | 60.01 | 59.6072 | 58.868 | -0.4028 | -1.142 | -471.7037 | -166.3684 | Yes | Yes | 0.010044 | 471.7037 | 2013 | 179 | 0
QI_2013-07-05_174630 | 2013-07-05 13:46 | 2013-07-05 13:46 | EDT |  | 902 | 59.9959 | 59.8231 | 59.3626 | -0.17281 | -0.63333 | -521.9504 | -142.4211 | Yes | Yes | -0.0040684 | 521.9504 | 2013 | 179 | 0
QI_2013-07-05_200645 | 2013-07-05 16:07 | 2013-07-05 16:07 | EDT | 441.5445 | 877 | 59.9954 | 59.8378 | 59.3614 | -0.15759 | -0.63402 | -556.5004 | -138.3241 | Yes | Yes | -0.004581 | 556.5004 | 2013 | 179 | 0
QI_2013-07-19_170623 | 2013-07-19 13:06 | 2013-07-19 13:06 | EDT | 553.1358 | 854 | 59.9904 | 59.8739 | 59.5111 | -0.11647 | -0.47927 | -733.2476 | -178.1886 | Yes | Yes | -0.0096316 | 733.2476 | 2013 | 179 | 0
QI_2013-07-23_204710 | 2013-07-23 16:47 | 2013-07-23 16:47 | EDT | -515.925 | -912 | 59.9775 | 60.1181 | 60.6423 | 0.14057 | 0.66481 | -648.7848 | -137.1816 | Yes | Yes | -0.022513 | 648.7848 | 2013 | 179 | 0
QI_2013-07-30_172156 | 2013-07-30 13:22 | 2013-07-30 13:22 | EDT | -420.9366 | -906 | 60.0145 | 60.1573 | 60.6513 | 0.14283 | 0.63679 | -634.3186 | -142.2769 | Yes | Yes | 0.014512 | 634.3186 | 2013 | 179 | 0
QI_2013-07-30_202350 | 2013-07-30 16:24 | 2013-07-30 16:24 | EDT |  | 1227 | 60.0029 | 59.7572 | 59.1531 | -0.24572 | -0.84982 | -499.3514 | -144.3836 | Yes | Yes | 0.0029187 | 499.3514 | 2013 | 179 | 0
QI_2013-08-23_211545 | 2013-08-23 17:16 | 2013-08-23 17:16 | EDT | 117.5008 | 769 | 59.9965 | 59.8856 | 59.5119 | -0.11089 | -0.48459 | -693.4957 | -158.6922 | Yes | Yes | -0.0035124 | 693.4957 | 2013 | 179 | 0
QI_2013-09-03_140935 | 2013-09-03 10:10 | 2013-09-03 10:10 | EDT | -1380.4302 | -741 | 59.9837 | 60.1066 | 60.4616 | 0.12292 | 0.47789 | -602.8278 | -155.0551 | Yes | Yes | -0.016293 | 602.8278 | 2013 | 179 | 0
QI_2013-09-06_123552 | 2013-09-06 08:36 | 2013-09-06 08:36 | EDT | 209.7576 | 836 | 59.9822 | 59.8479 | 59.4526 | -0.13431 | -0.52961 | -622.4548 | -157.8508 | Yes | Yes | -0.017787 | 622.4548 | 2013 | 179 | 0
QI_2013-09-18_184057 | 2013-09-18 14:41 | 2013-09-18 14:41 | EDT | 2316.0775 | 792 | 60.0073 | 59.8463 | 59.4202 | -0.16093 | -0.58706 | -492.1431 | -134.9105 | Yes | Yes | 0.007256 | 492.1431 | 2013 | 179 | 0
QI_2013-11-05_213642 | 2013-11-05 16:37 | 2013-11-05 16:37 | EST | 490.1499 | 777 | 59.961 | 59.8512 | 59.5598 | -0.1098 | -0.40124 | -707.6648 | -193.6508 | Yes | Yes | -0.038963 | 707.6648 | 2013 | 179 | 0
QI_2013-11-26_010255 | 2013-11-25 20:03 | 2013-11-25 20:03 | EST | 1450.2559 | 680 | 59.964 | 59.8047 | 59.5309 | -0.1593 | -0.43313 | -426.873 | -156.9959 | Yes | Yes | -0.035969 | 426.873 | 2013 | 179 | 0
QI_2013-12-03_115118 | 2013-12-03 06:51 | 2013-12-03 06:51 | EST | -700.1812 | -889 | 60.0529 | 60.1387 | 60.5142 | 0.085788 | 0.46129 | -1036.2736 | -192.7194 | Yes | Yes | 0.052906 | 1036.2736 | 2014 | 180 | 0
QI_2013-12-05_213647 | 2013-12-05 16:37 | 2013-12-05 16:37 | EST | 2325.1562 | 752 | 60.0237 | 59.8499 | 59.4979 | -0.17387 | -0.52585 | -432.5027 | -143.0076 | Yes | Yes | 0.023744 | 432.5027 | 2014 | 180 | 0
QI_2014-01-16_115455 | 2014-01-16 06:55 | 2014-01-16 06:55 | EST | 1661.0091 | 501 | 59.9959 | 59.9269 | 59.7094 | -0.069053 | -0.28654 | -725.53 | -174.8461 | Yes | Yes | -0.0040622 | 725.53 | 2014 | 180 | 0
QI_2014-01-26_105336 | 2014-01-26 05:54 | 2014-01-26 05:54 | EST | -1659.702 | -469 | 60.0069 | 60.045 | 60.2853 | 0.038112 | 0.27842 | -1230.5969 | -168.4511 | Yes | Yes | 0.0068822 | 1230.5969 | 2014 | 180 | 0
QI_2014-03-09_173952 | 2014-03-09 13:40 | 2014-03-09 13:40 | EDT | 1674.2252 | 997 | 59.992 | 59.9097 | 59.5595 | -0.082235 | -0.43245 | -1212.3762 | -230.5446 | Yes | Yes | -0.008044 | 1212.3762 | 2014 | 180 | 0
QI_2014-03-13_200534 | 2014-03-13 16:06 | 2014-03-13 16:06 | EDT | 1715.1369 | 995 | 59.9778 | 59.8002 | 59.4106 | -0.17766 | -0.56724 | -560.0445 | -175.4113 | Yes | Yes | -0.022163 | 560.0445 | 2014 | 180 | 0
QI_2014-05-17_214140 | 2014-05-17 17:42 | 2014-05-17 17:42 | EDT | 907.3038 | 450 | 60.0004 | 59.8792 | 59.5342 | -0.12121 | -0.46623 | -371.2672 | -96.5197 | Yes | Yes | 0.00042486 | 371.2672 | 2014 | 180 | 0
QI_2014-05-20_183650 | 2014-05-20 14:37 | 2014-05-20 14:37 | EDT | 1312.9403 | 484 | 60.0097 | 59.8946 | 59.632 | -0.11513 | -0.37774 | -420.3972 | -128.1291 | Yes | Yes | 0.0097439 | 420.3972 | 2014 | 180 | 0
QI_2014-05-22_074420 | 2014-05-22 03:44 | 2014-05-22 03:44 | EDT | -1357.1766 | -457 | 59.9964 | 60.1171 | 60.5174 | 0.12078 | 0.52104 | -378.3849 | -87.7099 | Yes | Yes | -0.0036371 | 378.3849 | 2014 | 180 | 0
QI_2014-05-22_160954 | 2014-05-22 12:10 | 2014-05-22 12:10 | EDT | -1841.7711 | -670 | 60.014 | 60.1299 | 60.5465 | 0.1159 | 0.53248 | -578.087 | -125.8258 | Yes | Yes | 0.014019 | 578.087 | 2014 | 180 | 0
QI_2014-05-27_225531 | 2014-05-27 18:56 | 2014-05-27 18:56 | EDT | 350.8409 | 490 | 60.0081 | 59.9338 | 59.6378 | -0.07429 | -0.37031 | -659.5737 | -132.3225 | Yes | Yes | 0.0081058 | 659.5737 | 2014 | 180 | 0
QI_2014-06-08_142852 | 2014-06-08 10:29 | 2014-06-08 10:29 | EDT | 116.809 | 933 | 59.9897 | 59.7727 | 59.2682 | -0.217 | -0.72149 | -429.9479 | -129.315 | Yes | Yes | -0.010306 | 429.9479 | 2014 | 180 | 0
QI_2014-06-15_233705 | 2014-06-15 19:37 | 2014-06-15 19:37 | EDT | -707.922 | -465 | 60.0367 | 60.1125 | 60.4312 | 0.0758 | 0.3945 | -613.4537 | -117.8694 | Yes | Yes | 0.036694 | 613.4537 | 2014 | 180 | 0
QI_2014-06-18_174748 | 2014-06-18 13:48 | 2014-06-18 13:48 | EDT | 116.7261 | 898 | 60.0176 | 59.7955 | 59.3732 | -0.22205 | -0.6444 | -404.4194 | -139.3555 | Yes | Yes | 0.017595 | 404.4194 | 2014 | 180 | 0
QI_2014-06-18_180639 | 2014-06-18 14:07 | 2014-06-18 14:07 | EDT | 94.6331 | 698 | 60.0451 | 59.8692 | 59.4909 | -0.17585 | -0.5542 | -396.9189 | -125.9482 | Yes | Yes | 0.045094 | 396.9189 | 2014 | 180 | 0
QI_2014-06-30_143145 | 2014-06-30 10:32 | 2014-06-30 10:32 | EDT | 107.8185 | 519 | 60.0027 | 59.9016 | 59.6041 | -0.1011 | -0.39863 | -513.3353 | -130.1974 | Yes | Yes | 0.0027249 | 513.3353 | 2014 | 180 | 0
QI_2014-07-28_054930 | 2014-07-28 01:50 | 2014-07-28 01:50 | EDT | 603.3176 | 460 | 60.0171 | 59.8576 | 59.5119 | -0.15954 | -0.50522 | -288.3238 | -91.05 | Yes | Yes | 0.017119 | 288.3238 | 2014 | 180 | 0
QI_2014-07-29_093815 | 2014-07-29 05:38 | 2014-07-29 05:38 | EDT | 842.3868 | 492 | 59.9954 | 59.8474 | 59.5418 | -0.148 | -0.45357 | -332.4223 | -108.4721 | Yes | Yes | -0.0046258 | 332.4223 | 2014 | 180 | 0
QI_2014-07-30_191255 | 2014-07-30 15:13 | 2014-07-30 15:13 | EDT | 1918.035 | 1477 | 60.0014 | 59.6863 | 58.9861 | -0.31506 | -1.0153 | -468.7944 | -145.4724 | Yes | Yes | 0.0014122 | 468.7944 | 2014 | 180 | 0
QI_2014-08-05_062658 | 2014-08-05 02:27 | 2014-08-05 02:27 | EDT | 446.8176 | 520 | 60.0149 | 59.884 | 59.5291 | -0.13086 | -0.4858 | -397.3598 | -107.0395 | Yes | Yes | 0.0149 | 397.3598 | 2014 | 180 | 0
QI_2014-08-05_165252 | 2014-08-05 12:53 | 2014-08-05 12:53 | EDT | 1937.2009 | 698 | 60.0323 | 59.8399 | 59.3396 | -0.19243 | -0.69272 | -362.7219 | -100.7624 | Yes | Yes | 0.032319 | 362.7219 | 2014 | 180 | 0
QI_2014-08-06_152239 | 2014-08-06 11:23 | 2014-08-06 11:23 | EDT | 791.7992 | 665 | 59.9776 | 59.8796 | 59.5067 | -0.098001 | -0.47093 | -678.5611 | -141.2109 | Yes | Yes | -0.022375 | 678.5611 | 2014 | 180 | 0
QI_2014-08-10_184217 | 2014-08-10 14:42 | 2014-08-10 14:42 | EDT | 637.0918 | 627 | 59.979 | 59.8939 | 59.512 | -0.085095 | -0.46702 | -736.8268 | -134.2544 | Yes | Yes | -0.020975 | 736.8268 | 2014 | 180 | 0
QI_2014-08-14_175434 | 2014-08-14 13:55 | 2014-08-14 13:55 | EDT | 1291.5593 | 1351 | 60.0427 | 59.7488 | 59.0492 | -0.2939 | -0.99346 | -459.6875 | -135.9888 | Yes | Yes | 0.042662 | 459.6875 | 2014 | 180 | 0
QI_2014-08-19_161706 | 2014-08-19 12:17 | 2014-08-19 12:17 | EDT | 559.0528 | 1242 | 60.0049 | 59.7434 | 59.1349 | -0.26149 | -0.86999 | -474.9729 | -142.7595 | Yes | Yes | 0.004894 | 474.9729 | 2014 | 180 | 0
QI_2014-08-22_050609 | 2014-08-22 01:06 | 2014-08-22 01:06 | EDT | 379.5188 | 889 | 59.9708 | 59.7663 | 59.2797 | -0.20445 | -0.69106 | -434.8309 | -128.6438 | Yes | Yes | -0.029243 | 434.8309 | 2014 | 180 | 0
QI_2014-09-04_102433 | 2014-09-04 06:25 | 2014-09-04 06:25 | EDT | -453.2697 | -467 | 60.0015 | 60.116 | 60.4215 | 0.11453 | 0.42001 | -407.7416 | -111.1885 | Yes | Yes | 0.0014937 | 407.7416 | 2014 | 180 | 0
QI_2014-09-05_153715 | 2014-09-05 11:37 | 2014-09-05 11:37 | EDT | 1004.6762 | 1458 | 59.9831 | 59.7314 | 59.0397 | -0.25171 | -0.9434 | -579.2343 | -154.5474 | Yes | Yes | -0.0169 | 579.2343 | 2014 | 180 | 0
QI_2014-09-05_162612 | 2014-09-05 12:26 | 2014-09-05 12:26 | EDT | 1014.9681 | 1293 | 60.0156 | 59.7476 | 59.1753 | -0.268 | -0.84034 | -482.4603 | -153.8657 | Yes | Yes | 0.015644 | 482.4603 | 2014 | 180 | 0
QI_2014-09-18_214254 | 2014-09-18 17:43 | 2014-09-18 17:43 | EDT | -386.4036 | -483 | 60.0255 | 60.1113 | 60.5114 | 0.085791 | 0.48593 | -562.9948 | -99.3972 | Yes | Yes | 0.025469 | 562.9948 | 2014 | 180 | 0
QI_2014-09-27_201730 | 2014-09-27 16:18 | 2014-09-27 16:18 | EDT | 954.7553 | 451 | 59.9943 | 59.8966 | 59.5857 | -0.097747 | -0.40863 | -461.3968 | -110.3686 | Yes | Yes | -0.0056682 | 461.3968 | 2014 | 180 | 0
QI_2014-10-16_114400 | 2014-10-16 07:44 | 2014-10-16 07:44 | EDT | -464.5252 | -477 | 59.9904 | 60.1256 | 60.4159 | 0.13521 | 0.42551 | -352.7856 | -112.0998 | Yes | Yes | -0.0096126 | 352.7856 | 2014 | 180 | 0
QI_2014-11-04_162340 | 2014-11-04 11:24 | 2014-11-04 11:24 | EST | -137.9184 | -500 | 59.9974 | 60.0537 | 60.3871 | 0.056364 | 0.38974 | -887.0849 | -128.2914 | Yes | Yes | -0.0026374 | 887.0849 | 2014 | 180 | 0
QI_2014-12-04_200550 | 2014-12-04 15:06 | 2014-12-04 15:06 | EST | 2696.4094 | 1019 | 60.0221 | 59.8894 | 59.6416 | -0.13272 | -0.38047 | -767.8 | -267.8248 | Yes | Yes | 0.022074 | 767.8 | 2015 | 183 | 0
QI_2014-12-05_112543 | 2014-12-05 06:26 | 2014-12-05 06:26 | EST | -207.2486 | -640 | 60.0033 | 60.0776 | 60.3653 | 0.074275 | 0.362 | -861.6598 | -176.7962 | Yes | Yes | 0.0033004 | 861.6598 | 2015 | 183 | 0
QI_2014-12-06_123731 | 2014-12-06 07:38 | 2014-12-06 07:38 | EST | 216.2633 | 1033 | 60.0011 | 59.8068 | 59.4996 | -0.19425 | -0.50148 | -531.8022 | -205.9894 | Yes | Yes | 0.0010815 | 531.8022 | 2015 | 183 | 0
QI_2015-01-13_124236 | 2015-01-13 07:43 | 2015-01-13 07:43 | EST | -214.8565 | -1787 | 60.0247 | 60.2714 | 60.5618 | 0.24675 | 0.53712 | -724.2154 | -332.7019 | Yes | Yes | 0.024681 | 724.2154 | 2015 | 183 | 0
QI_2015-01-22_090140 | 2015-01-22 04:02 | 2015-01-22 04:02 | EST | 60.7987 | 489 | 59.988 | 59.9162 | 59.722 | -0.07178 | -0.26602 | -681.2468 | -183.8214 | Yes | Yes | -0.011981 | 681.2468 | 2015 | 183 | 0
QI_2015-03-10_091107 | 2015-03-10 05:11 | 2015-03-10 05:11 | EDT | 1054.966 | 600 | 60.0355 | 59.9841 | 59.6953 | -0.051397 | -0.34018 | -1167.3897 | -176.377 | Yes | Yes | 0.035481 | 1167.3897 | 2015 | 183 | 0
QI_2015-04-06_120555 | 2015-04-06 08:06 | 2015-04-06 08:06 | EDT | 2581.1628 | 781 | 60.0122 | 59.8567 | 59.5392 | -0.15552 | -0.47303 | -502.1982 | -165.1074 | Yes | Yes | 0.012225 | 502.1982 | 2015 | 183 | 0
QI_2015-05-28_083003 | 2015-05-28 04:30 | 2015-05-28 04:30 | EDT | -50.1076 | -455 | 59.9796 | 60.0915 | 60.4446 | 0.11194 | 0.46501 | -406.4777 | -97.8482 | Yes | Yes | -0.020407 | 406.4777 | 2015 | 183 | 0
QI_2015-06-24_080841 | 2015-06-24 04:09 | 2015-06-24 04:09 | EDT | -306.9723 | -455 | 59.9902 | 60.0585 | 60.3549 | 0.068339 | 0.3647 | -665.7948 | -124.76 | Yes | Yes | -0.0098 | 665.7948 | 2015 | 183 | 0
QI_2015-06-27_201247 | 2015-06-27 16:13 | 2015-06-27 16:13 | EDT | 471.3729 | 456 | 60.003 | 59.9331 | 59.6268 | -0.069908 | -0.37624 | -652.2857 | -121.1982 | Yes | Yes | 0.0030439 | 652.2857 | 2015 | 183 | 0
QI_2015-06-27_224636 | 2015-06-27 18:47 | 2015-06-27 18:47 | EDT | 431.4781 | 580 | 59.9947 | 59.9036 | 59.5694 | -0.091014 | -0.42526 | -637.2641 | -136.3886 | Yes | Yes | -0.0053437 | 637.2641 | 2015 | 183 | 0
QI_2015-06-28_094004 | 2015-06-28 05:40 | 2015-06-28 05:40 | EDT | 819.0154 | 848 | 60.0057 | 59.7408 | 59.2733 | -0.26489 | -0.7324 | -320.136 | -115.7838 | Yes | Yes | 0.0056999 | 320.136 | 2015 | 183 | 0
QI_2015-06-29_150359 | 2015-06-29 11:04 | 2015-06-29 11:04 | EDT | 1364.8289 | 513 | 60.0215 | 59.9217 | 59.6707 | -0.099792 | -0.3508 | -514.0709 | -146.2372 | Yes | Yes | 0.0215 | 514.0709 | 2015 | 183 | 0
QI_2015-06-29_184207 | 2015-06-29 14:42 | 2015-06-29 14:42 | EDT | 580.5019 | 630 | 59.9987 | 59.8756 | 59.567 | -0.12314 | -0.4317 | -511.6279 | -145.9352 | Yes | Yes | -0.0013001 | 511.6279 | 2015 | 183 | 0
QI_2015-06-30_065339 | 2015-06-30 02:54 | 2015-06-30 02:54 | EDT | -630.616 | -790 | 60.022 | 60.2132 | 60.5111 | 0.19127 | 0.48913 | -413.0343 | -161.5107 | Yes | Yes | 0.021969 | 413.0343 | 2015 | 183 | 0
QI_2015-07-02_144741 | 2015-07-02 10:48 | 2015-07-02 10:48 | EDT | 482.1789 | 467 | 60.0052 | 59.9427 | 59.6496 | -0.06253 | -0.3556 | -746.8364 | -131.3276 | Yes | Yes | 0.0052004 | 746.8364 | 2015 | 183 | 0
QI_2015-07-03_012428 | 2015-07-02 21:24 | 2015-07-02 21:24 | EDT | 661.3992 | 461 | 60.0041 | 59.9228 | 59.6592 | -0.081314 | -0.34495 | -566.9408 | -133.6421 | Yes | Yes | 0.0041499 | 566.9408 | 2015 | 183 | 0
QI_2015-07-18_134335 | 2015-07-18 09:44 | 2015-07-18 09:44 | EDT | 22.3678 | 496 | 60.0025 | 59.9526 | 59.6511 | -0.049968 | -0.35144 | -992.6296 | -141.1346 | Yes | Yes | 0.0025377 | 992.6296 | 2015 | 183 | 0
QI_2015-07-30_232103 | 2015-07-30 19:21 | 2015-07-30 19:21 | EDT | 564.1264 | 880 | 59.9915 | 59.8482 | 59.5546 | -0.14325 | -0.43689 | -614.2921 | -201.4246 | Yes | Yes | -0.0085123 | 614.2921 | 2015 | 183 | 0
QI_2015-07-31_002550 | 2015-07-30 20:26 | 2015-07-30 20:26 | EDT | 1155.6781 | 958 | 60.0121 | 59.7872 | 59.3897 | -0.22491 | -0.62238 | -425.9509 | -153.9254 | Yes | Yes | 0.012081 | 425.9509 | 2015 | 183 | 0
QI_2015-08-04_182756 | 2015-08-04 14:28 | 2015-08-04 14:28 | EDT | 918.9996 | 635 | 60.0062 | 59.8833 | 59.549 | -0.12287 | -0.45716 | -516.8249 | -138.9021 | Yes | Yes | 0.0061564 | 516.8249 | 2015 | 183 | 0
QI_2015-08-10_145935 | 2015-08-10 11:00 | 2015-08-10 11:00 | EDT | 141.5902 | 521 | 60.0218 | 59.8892 | 59.6178 | -0.13262 | -0.40404 | -392.844 | -128.9469 | Yes | Yes | 0.021844 | 392.844 | 2015 | 183 | 0
QI_2015-09-22_091701 | 2015-09-22 05:17 | 2015-09-22 05:17 | EDT | 257.1251 | 564 | 59.983 | 59.8586 | 59.5178 | -0.12438 | -0.46518 | -453.4449 | -121.243 | Yes | Yes | -0.017019 | 453.4449 | 2015 | 183 | 0
QI_2015-10-03_134913 | 2015-10-03 09:49 | 2015-10-03 09:49 | EDT | 308.055 | 672 | 60.0094 | 59.8514 | 59.5114 | -0.15799 | -0.49801 | -425.3383 | -134.9358 | Yes | Yes | 0.0094128 | 425.3383 | 2015 | 183 | 0
QI_2015-10-06_204422 | 2015-10-06 16:44 | 2015-10-06 16:44 | EDT | 165.1272 | 515 | 59.9948 | 59.8915 | 59.6216 | -0.10327 | -0.37316 | -498.6694 | -138.0101 | Yes | Yes | -0.0052378 | 498.6694 | 2015 | 183 | 0
QI_2015-10-21_151621 | 2015-10-21 11:16 | 2015-10-21 11:16 | EDT | 246.4071 | 939 | 60.0144 | 59.8578 | 59.3786 | -0.1566 | -0.63583 | -599.6265 | -147.6811 | Yes | Yes | 0.014431 | 599.6265 | 2015 | 183 | 0
QI_2015-11-05_213005 | 2015-11-05 16:30 | 2015-11-05 16:30 | EST | 329.2198 | 960 | 59.9829 | 59.7647 | 59.4087 | -0.2182 | -0.57417 | -439.9594 | -167.198 | Yes | Yes | -0.017132 | 439.9594 | 2015 | 183 | 0
QI_2015-11-06_184302 | 2015-11-06 13:43 | 2015-11-06 13:43 | EST | 261.7918 | 682 | 59.9926 | 59.8738 | 59.5314 | -0.1188 | -0.46123 | -574.0551 | -147.8647 | Yes | Yes | -0.0073688 | 574.0551 | 2015 | 183 | 0
QI_2015-11-20_112920 | 2015-11-20 06:29 | 2015-11-20 06:29 | EST | 229.4308 | 810 | 59.97 | 59.8109 | 59.4859 | -0.15908 | -0.4841 | -509.1731 | -167.3191 | Yes | No | -0.029994 | 509.1731 | 2015 | 183 | 0
QI_2015-11-22_150559 | 2015-11-22 10:06 | 2015-11-22 10:06 | EST | 211.4745 | 793 | 59.976 | 59.7751 | 59.4793 | -0.20088 | -0.4967 | -394.7721 | -159.6544 | Yes | Yes | -0.024001 | 394.7721 | 2015 | 183 | 0
QI_2015-12-03_102712 | 2015-12-03 05:27 | 2015-12-03 05:27 | EST | 660.5602 | 808 | 59.99 | 59.832 | 59.485 | -0.158 | -0.505 | -511.3924 | -160 | Yes | Yes | -0.01 | 511.3924 | 2016 | 179 | 0
QI_2015-12-28_130418 | 2015-12-28 08:04 | 2015-12-28 08:04 | EST | 222.9315 | 1709 | 59.983 | 59.657 | 59.072 | -0.326 | -0.911 | -524.2331 | -187.596 | Yes | Yes | -0.017 | 524.2331 | 2016 | 179 | 0
QI_2016-01-18_212451 | 2016-01-18 16:25 | 2016-01-18 16:25 | EST | 679.0169 | 620 | 60.002 | 59.912 | 59.69 | -0.09 | -0.312 | -688.8889 | -198.7179 | Yes | Yes | 0.002 | 688.8889 | 2016 | 179 | 0
QI_2016-02-08_015136 | 2016-02-07 20:52 | 2016-02-07 20:52 | EST | -378.6208 | -474 | 60.003 | 60.059 | 59.989 | 0.056 | -0.014 | -846.4286 | 3385.7143 | Yes | Yes | 0.003 | 846.4286 | 2016 | 179 | 0
QI_2016-02-14_160519 | 2016-02-14 11:05 | 2016-02-14 11:05 | EST | 214.9231 | 498 | 60.013 | 59.9 | 59.717 | -0.113 | -0.296 | -440.708 | -168.2432 | Yes | Yes | 0.013 | 440.708 | 2016 | 179 | 0
QI_2016-03-08_164833 | 2016-03-08 11:49 | 2016-03-08 11:49 | EST | -307.939 | -962 | 60.003 | 60.107 | 59.989 | 0.104 | -0.014 | -925 | 6871.4286 | Yes | Yes | 0.003 | 925 | 2016 | 179 | 0
QI_2016-03-10_071011 | 2016-03-10 03:10 | 2016-03-10 03:10 | EST | 105.6572 | 760 | 59.979 | 59.939 | 59.665 | -0.04 | -0.314 | -1900 | -242.0382 | Yes | Yes | -0.021 | 1900 | 2016 | 179 | 0
QI_2016-04-02_004830 | 2016-04-01 20:49 | 2016-04-01 20:49 | EDT | 132.3181 | 603 | 59.9907 | 59.878 | 59.5912 | -0.11263 | -0.39947 | -535.3985 | -150.9511 | Yes | Yes | -0.009331 | 535.3985 | 2016 | 179 | 0
QI_2016-04-13_185231 | 2016-04-13 14:53 | 2016-04-13 14:53 | EDT | -246.8151 | -960 | 60.0156 | 60.1533 | 60.5872 | 0.1377 | 0.57164 | -697.1919 | -167.9386 | Yes | Yes | 0.015563 | 697.1919 | 2016 | 179 | 0
QI_2016-04-28_022739 | 2016-04-27 22:28 | 2016-04-27 22:28 | EDT | 141.0484 | 482 | 60.0043 | 59.9239 | 59.6376 | -0.080335 | -0.36665 | -599.9893 | -131.4604 | Yes | Yes | 0.0042503 | 599.9893 | 2016 | 179 | 0
QI_2016-05-03_130350 | 2016-05-03 09:04 | 2016-05-03 09:04 | EDT | 173.7544 | 455 | 60.0306 | 59.9561 | 59.6547 | -0.074502 | -0.37594 | -610.719 | -121.0288 | Yes | Yes | 0.030645 | 610.719 | 2016 | 179 | 0
QI_2016-05-03_174436 | 2016-05-03 13:45 | 2016-05-03 13:45 | EDT | 206.6327 | 884 | 60.0021 | 59.8349 | 59.2953 | -0.16717 | -0.70678 | -528.7969 | -125.0751 | Yes | Yes | 0.0020747 | 528.7969 | 2016 | 179 | 0
QI_2016-05-10_065006 | 2016-05-10 02:50 | 2016-05-10 02:50 | EDT | -147.1093 | -471 | 59.9876 | 60.0807 | 60.4677 | 0.093104 | 0.48011 | -505.8876 | -98.1018 | Yes | Yes | -0.012413 | 505.8876 | 2016 | 179 | 0
QI_2016-05-16_203421 | 2016-05-16 16:34 | 2016-05-16 16:34 | EDT | -146.8422 | -468 | 59.984 | 60.0409 | 60.3918 | 0.0569 | 0.40779 | -822.4957 | -114.7638 | Yes | Yes | -0.015994 | 822.4957 | 2016 | 179 | 0
QI_2016-05-19_053410 | 2016-05-19 01:34 | 2016-05-19 01:34 | EDT | -181.721 | -476 | 60.0184 | 60.1158 | 60.5004 | 0.09739 | 0.48197 | -488.7574 | -98.7616 | Yes | Yes | 0.018432 | 488.7574 | 2016 | 179 | 0
QI_2016-05-24_223702 | 2016-05-24 18:37 | 2016-05-24 18:37 | EDT | 248.4499 | 765 | 59.9883 | 59.842 | 59.4979 | -0.14631 | -0.49043 | -522.8624 | -155.9865 | Yes | Yes | -0.011675 | 522.8624 | 2016 | 179 | 0
QI_2016-05-26_055400 | 2016-05-26 01:54 | 2016-05-26 01:54 | EDT | -158.682 | -453 | 60.0013 | 60.1156 | 60.5577 | 0.11421 | 0.55635 | -396.6455 | -81.4234 | Yes | Yes | 0.0013499 | 396.6455 | 2016 | 179 | 0
QI_2016-06-02_235132 | 2016-06-02 19:52 | 2016-06-02 19:52 | EDT | 172.2207 | 1022 | 60.0059 | 59.788 | 59.3257 | -0.21794 | -0.6802 | -468.938 | -150.2497 | Yes | Yes | 0.0058997 | 468.938 | 2016 | 179 | 0
QI_2016-06-03_044600 | 2016-06-03 00:46 | 2016-06-03 00:46 | EDT | -311.4672 | -473 | 60.0054 | 60.0683 | 60.445 | 0.062838 | 0.43957 | -752.7253 | -107.6041 | Yes | Yes | 0.0054252 | 752.7253 | 2016 | 179 | 0
QI_2016-06-19_194616 | 2016-06-19 15:46 | 2016-06-19 15:46 | EDT | -183.0685 | -510 | 59.975 | 60.1275 | 60.5102 | 0.15249 | 0.53516 | -334.455 | -95.2991 | Yes | Yes | -0.024956 | 334.455 | 2016 | 179 | 0
QI_2016-06-20_024836 | 2016-06-19 22:49 | 2016-06-19 22:49 | EDT | -132.4364 | -517.64 | 59.9926 | 60.1188 | 60.4288 | 0.12623 | 0.43619 | -410.0865 | -118.6739 | Yes | Yes | -0.0073881 | 410.0865 | 2016 | 179 | 0
QI_2016-06-27_172627 | 2016-06-27 13:26 | 2016-06-27 13:26 | EDT | 170.613 | 592 | 59.9736 | 59.901 | 59.5328 | -0.07261 | -0.44082 | -815.3156 | -134.295 | Yes | Yes | -0.026381 | 815.3156 | 2016 | 179 | 0
QI_2016-07-27_163959 | 2016-07-27 12:40 | 2016-07-27 12:40 | EDT |  | 439 | 59.986 | 59.907 | 59.603 | -0.079 | -0.383 | -555.6962 | -114.6214 | Yes | Yes | -0.014 | 555.6962 | 2016 | 179 | 0
QI_2016-08-04_060740 | 2016-08-04 02:08 | 2016-08-04 02:08 | EDT |  | 881 | 60.059 | 59.869 | 59.274 | -0.19 | -0.785 | -463.6842 | -112.2293 | Yes | Yes | 0.059 | 463.6842 | 2016 | 179 | 0
QI_2016-08-04_185629 | 2016-08-04 14:56 | 2016-08-04 14:56 | EDT |  | 928 | 60.014 | 59.832 | 59.244 | -0.182 | -0.77 | -509.8901 | -120.5195 | Yes | Yes | 0.014 | 509.8901 | 2016 | 179 | 0
QI_2016-08-10_165438 | 2016-08-10 12:55 | 2016-08-10 12:55 | EDT |  | 492 | 59.993 | 59.943 | 59.629 | -0.05 | -0.364 | -984 | -135.1648 | Yes | Yes | -0.007 | 984 | 2016 | 179 | 0
QI_2016-08-11_131246 | 2016-08-11 09:13 | 2016-08-11 09:13 | EDT |  | 706 | 60.01 | 59.859 | 59.504 | -0.151 | -0.506 | -467.5497 | -139.5257 | Yes | Yes | 0.01 | 467.5497 | 2016 | 179 | 0
QI_2016-08-16_002202 | 2016-08-15 20:22 | 2016-08-15 20:22 | EDT |  | 529 | 60.001 | 59.912 | 59.628 | -0.089 | -0.373 | -594.382 | -141.8231 | Yes | Yes | 0.001 | 594.382 | 2016 | 179 | 0
QI_2016-08-29_132057 | 2016-08-29 09:21 | 2016-08-29 09:21 | EDT |  | 514 | 59.989 | 59.918 | 59.649 | -0.071 | -0.34 | -723.9437 | -151.1765 | Yes | Yes | -0.011 | 723.9437 | 2016 | 179 | 0
QI_2016-09-02_215041 | 2016-09-02 17:51 | 2016-09-02 17:51 | EDT |  | 1177 | 60.012 | 59.764 | 59.213 | -0.248 | -0.799 | -474.5968 | -147.3091 | Yes | Yes | 0.012 | 474.5968 | 2016 | 179 | 0
QI_2016-09-15_133518 | 2016-09-15 09:35 | 2016-09-15 09:35 | EDT |  | 932 | 60 | 59.792 | 59.239 | -0.208 | -0.761 | -448.0769 | -122.4704 | Yes | Yes | 0 | 448.0769 | 2016 | 179 | 0
QI_2016-09-16_235036 | 2016-09-16 19:51 | 2016-09-16 19:51 | EDT |  | 846 | 59.969 | 59.803 | 59.366 | -0.166 | -0.603 | -509.6386 | -140.2985 | Yes | Yes | -0.031 | 509.6386 | 2016 | 179 | 0
QI_2016-10-05_155732 | 2016-10-05 11:58 | 2016-10-05 11:58 | EDT |  | 495 | 60.009 | 59.919 | 59.586 | -0.09 | -0.423 | -550 | -117.0213 | Yes | Yes | 0.009 | 550 | 2016 | 179 | 0
QI_2016-10-12_215205 | 2016-10-12 17:52 | 2016-10-12 17:52 | EDT |  | -451 | 60.011 | 60.117 | 60.042 | 0.106 | 0.031 | -425.4717 | -1454.8387 | Yes | Yes | 0.011 | 425.4717 | 2016 | 179 | 0
QI_2016-10-26_112451 | 2016-10-26 07:25 | 2016-10-26 07:25 | EDT |  | -484 | 59.981 | 60.07 | 59.999 | 0.089 | 0.018 | -543.8202 | -2688.8889 | Yes | Yes | -0.019 | 543.8202 | 2016 | 179 | 0
QI_2016-10-26_180825 | 2016-10-26 14:08 | 2016-10-26 14:08 | EDT |  | 1141 | 59.948 | 59.727 | 59.2294 | -0.221 | -0.7186 | -516.2896 | -158.781 | Yes | Yes | -0.052 | 516.2896 | 2016 | 179 | 0
QI_2016-10-26_214901 | 2016-10-26 17:49 | 2016-10-26 17:49 | EDT |  | 859 | 59.995 | 59.816 | 59.4398 | -0.179 | -0.5552 | -479.8883 | -154.719 | Yes | Yes | -0.005 | 479.8883 | 2016 | 179 | 0
QI_2016-10-27_160538 | 2016-10-27 12:06 | 2016-10-27 12:06 | EDT |  | 485 | 59.99 | 59.908 | 59.683 | -0.082 | -0.307 | -591.4634 | -157.9805 | Yes | Yes | -0.01 | 591.4634 | 2016 | 179 | 0
QI_2016-11-04_063042 | 2016-11-04 02:31 | 2016-11-04 02:31 | EDT |  | 785 | 59.9931 | 59.8099 | 59.4234 | -0.1832 | -0.5697 | -428.4915 | -137.7922 | Yes | Yes | -0.0069008 | 428.4915 | 2016 | 179 | 0
QI_2016-11-11_140715 | 2016-11-11 09:07 | 2016-11-11 09:07 | EST |  | -730 | 60.012 | 60.131 | 59.966 | 0.119 | -0.046 | -613.4454 | 1586.9565 | Yes | Yes | 0.012 | 613.4454 | 2016 | 179 | 0
QI_2016-11-12_084721 | 2016-11-12 03:47 | 2016-11-12 03:47 | EST |  | 457 | 60.003 | 59.918 | 59.66 | -0.085 | -0.343 | -537.6471 | -133.2362 | Yes | Yes | 0.003 | 537.6471 | 2016 | 179 | 0
QI_2016-11-22_112442 | 2016-11-22 06:25 | 2016-11-22 06:25 | EST |  | -483 | 59.995 | 60.062 | 59.961 | 0.067 | -0.034 | -720.8955 | 1420.5882 | Yes | No | -0.005 | 720.8955 | 2016 | 179 | 0
QI_2016-11-22_112442 | 2016-11-22 06:25 | 2016-11-12 03:47 | EST |  | -483 | 59.9769 | 60.0477 | 60.3279 | 0.070801 | 0.351 | -682.1959 | -137.6062 | Yes | No |  | 682.1959 | 2016 | 179 | 0
QI_2016-11-23_144809 | 2016-11-23 09:48 | 2016-11-23 09:48 | EST |  | 1637 | 60.009 | 59.625 | 59.0189 | -0.384 | -0.9901 | -426.3021 | -165.3368 | Yes | Yes | 0.009 | 426.3021 | 2016 | 179 | 0
QI_2016-11-23_175453 | 2016-11-23 12:55 | 2016-11-23 12:55 | EST |  | 478 | 60.003 | 59.946 | 59.69 | -0.057 | -0.313 | -838.5965 | -152.7157 | Yes | Yes | 0.003 | 838.5965 | 2016 | 179 | 0
QI_2016-11-25_024832 | 2016-11-24 21:49 | 2016-11-24 21:49 | EST |  | -483 | 59.995 | 60.071 | 59.985 | 0.076 | -0.01 | -635.5263 | 4830 | Yes | No | -0.005 | 635.5263 | 2016 | 179 | 0
QI_2016-11-25_031749 | 2016-11-24 22:18 | 2016-11-24 22:18 | EST |  | -487 | 59.998 | 60.049 | 59.982 | 0.051 | -0.016 | -954.902 | 3043.75 | Yes | No | -0.002 | 954.902 | 2016 | 179 | 0
QI_2016-11-25_031749 | 2016-11-24 22:18 | 2016-11-24 22:18 | EST |  | -487 | 59.9915 | 60.0503 | 60.3719 | 0.0588 | 0.3804 | -828.2349 | -128.0239 | Yes | No |  | 828.2349 | 2016 | 179 | 0
QI_2016-11-30_184730 | 2016-11-30 13:47 | 2016-11-30 13:47 | EST |  | 706 | 60 | 59.871 | 59.5388 | -0.129 | -0.4612 | -547.2868 | -153.0789 | Yes | Yes | 0 | 547.2868 | 2016 | 179 | 0

## Event_Color_Description (hidden)
EPG has implemented a secondary methodology for the EI and the ERCOT interconnection in order to capture additional events with Point C below/above certain thresholds.
Highlighted in Yellow | For the EI, the Point C threshold is at or below 59.96 Hz AND delta frequency of at least 30 mHz within a 15 second time window.
For the ERCOT interconnection, the Point C threshold is at or below 59.90 Hz and at or above 60.10 Hz
The events reported by NERC S/A that did not meet the significant event threshold criteria, as defined by the RS, are highlighted in pink.
Highlighted in Pink | The event frequency data (A Value, B Value, etc.) are shown in the summary report, spreadsheet, and frequency plots are provided for the events identified by CERTS/EPG. The event frequency data columns are marked as NA in the summary report and spreadsheet, and the frequency plots are not shown for the events not identifiable by CERTS/EPG.
If less than 2 events for Quebec or no event for the other interconnections detected with agreed thresholds, EPG will reduce thresholds to capture more events to expand event candidates list. These events are highlighted in grey.
Highlighted in Grey | If less than 2 events detected with threshold 350mHz, EPG will reduce threshold to 250mHz to capture more events to expand event candidates list.
If no events detected with agreed thresholds for the other interconnections, EPG will reduce threshold until several events can be captured. The adjusted threshold will be noted in the report.
The scheduled frequency will be shown with a red-dotted line on the frequency plots in instances where scheduled frequency during the event is other than 60 Hz.

## Update_History (hidden)
Date | Updates
2015-04-22 | Frequency Working Group made the selection and confirmed MW loss. Column E, F, W and X for all interconnects are updated.
2015-04-27 | HQ updated the column E and F Selections
2015-05-15 | EPG added april 2015 events for all four interconnections.
2015-06-19 | EPG added May 2015 events for all four interconnections.
2015-07-16 | Verified HQ events for BAL-003-1 from Form 1s. Updated selections.
2015-07-17 | EPG added June 2015 events for all four interconnections.
2015-07-22 | Frequency Working Group made event selections and confirmed MW loss. Column E, F, W and X for all interconnections Mar Apr and May.
2015-07-22 | Changed to a formula in column Z to calculate the Estimated Frequency Response using the NERC SA MW data column. This column will be updated by the Region if more accurate MW loss data is found.
2015-07-23 | Updated Region information and MW loss for the Western Interconnection.
2015-08-18 | EPG added July 2015 events for all four interconnections.
2015-09-11 | Added C' Frequency columns for the Eastern Interconnection. Updated MW loss data from Form 1s.
2015-09-16 | EPG added August 2015 events for all four interconnections.
2015-10-07 | EPG added September 2015 events for all four interconnections.
2015-10-27 | Frequency Working Group made event selections and confirmed MW loss. Column E, F, W and X for all interconnections Jun, Jul and Aug (Sept for EI and ERCOT)
2016-01-27 | FWG updated with approval of December 2015 events.
2016-04-06 | Corrected the MW Loss for the WI event on 5/26/2014 at 17:31:32 PDT from 2,636 MW to 2,826 MW, as verified by Jim Burns from BPA.
2016-04-27 | Added 2016 1st quarter events, corrected M4 formula, and revised format for quicker data entry in FWG meetings.
2016-08-08 | Added 2016 2nd quarter events, added CPT calculation to EI and WI.
2016-11-15 | Added 2016 3rd quarter events.