## 1- Operation Summary
Data Reporting Year | Data Reporting Quarter | Regional Entity Name (or Lead Regional Entity, if MRRE) | NERC Compliance Registry Number (NCR) (ex:NCR00123) | Jurisdiction | Voltage Class | Total PSOPs Occurred in MRO | Total PSOPs Occurred in NPCC | Total PSOPs Occurred in RF | Total PSOPs Occurred in SERC | Total PSOPs Occurred in TRE | Total PSOPs Occurred in WECC
[5 empty] | <100 kV | 0 | 0 | 0 | 0 | 0 | 0
CPSOP - Composite Protection System Operation |  |  |  |  | 100 kV | 0 | 0 | 0 | 0 | 0 | 0
Version | 012 |  |  |  | 115 kV | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 120 kV | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 138 kV | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 161 kV | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 230 kV | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 345 kV | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 500 kV | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 735 kV | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 765 kV | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | HVdc | 0 | 0 | 0 | 0 | 0 | 0
|  | Total Composite Protection System Operations (for each region) |  |  |  | 0 | 0 | 0 | 0 | 0 | 0

## 2 - Misoperation Entry Form
Misoperation ID (CONCATENATED FIELD OF COLUMNS (B,C,E,F,H,I) DO NOT ENTER DATA) | Region Where Misoperation Occurred (select from dropdown) | NERC Compliance Registry Number (NCR) (ex:NCR00123) | Jurisdiction (select from dropdown) | Misoperation Date (MM/DD/YYYY) | Misoperation Time (HH:MM:SS) | Time zone (select from dropdown) | Facility Name (Location of Misoperation) | Equipment Name (protected by Protection System that Misoperated) | Equipment Type (select from drop down) | Facility Voltage (select from drop down) | Equipment Removed from Service (Permanently or Temporarily) as the result of the Misoperation | Fault Type (Optional, select from drop down) | Event Description | Restoration Method (Optional, select from drop down) | Misoperation Category (select from drop down) | Cause(s) of Misoperation (select from drop down) | Incorrect Setting/Logic Errors/Design Errors and Relay Failure/Malfunctions Sub Cause Code (Optional, select from drop down) | Communication Sub Cause of Misoperation (Optional, select from drop down) | Communication System Type (Optional, select from drop down) | Protection System Schemes (Optional, select from drop down) | Protection Systems/Components that Misoperated | Relay Technology (select from drop down) | Microprocessor Relay Manufacturer (Optional, select from drop down) | Count of Transmission AC & DC Circuits Removed From Service | Count of Transmission Transformers Removed From Service | Count of Conventional Generation Units and Inverter-Based Plants Removed From Service | Analysis and Corrective Action Status (select from drop down) | Corrective Action Plan | Corrective Action Plan Target Completion Date (MM/DD/YYYY) | Corrective Action Plan Actual Completion Date (MM/DD/YYYY) | Reported By | Reporter's Phone Number (999)999-9999 | Reporter's Email Address (name@domain.com) | Date Reported (MM/DD/YYYY) | Additional Contact Name (Optional) | Additional Contact's Phone Number (Optional, (999)999-9999) | Additional Contact's Email Address (Optional, name@domain.com) | Comments (Optional)
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__
__ _00:00:00__

## 3 - Opt-Out Waiver Form
Note: This form should only be filled out if you have no Composite Protection System Operations and/or Misoperations to report. If you had Composite Protection System Operations or Misoperations occur on your system for the listed quarter you are expected to report them.
*-If the entity being reported for exists in multiple regions opt-out waivers should be created for each region that did not have any Composite Protection System Operations and/or Misoperations.
NERC Compliance Registry Number (NCR) (ex:NCR00123) | Data Reporting Year | Data Reporting Quarter | Regional Entity Name* | The entity listed has no CPS Operations to report for the listed quarter (Mark "Yes" if there are no operations to report, Opt-Out) | The entity listed has no Misoperations to report for the listed quarter (Mark "Yes" if there are no misoperations to report, Opt-Out)

## 4 - Definitions
Misoperation Category
Failure to Trip - During Fault | A failure of a Composite Protection System to operate for a Fault condition for which it is designed. The failure of a Protection System component is not a Misoperation as long as the overall performance of the Composite Protection System is correct.
Failure to Trip - Other than Fault | A failure of a Composite Protection System to operate for a non-Fault condition for which it is designed, such as a power swing, undervoltage, overexcitation, or loss of excitation. The failure of a Protection System component is not a Misoperation as long as the performance of the Composite Protection System is correct.
Slow Trip - During Fault | A Composite Protection System operation that is slower than intended for a Fault condition if the duration of its operating time resulted in the operation of at least one other Element’s Composite Protection System.
Slow Trip - Other than Fault | A Composite Protection System operation that is slower than required for a non-Fault condition, such as a power swing, undervoltage, overexcitation, or loss of excitation, if the duration of its operating time resulted in the operation of at least one other Element’s Composite Protection System.
Unnecessary Trip - During Fault | An unnecessary Composite Protection System operation for a Fault condition on another Element.
Unnecessary Trip - Other than Fault | An unnecessary Composite Protection System operation for a non-Fault condition. A Composite Protection System operation that is caused by personnel during on-site maintenance, testing, inspection, construction or commissioning activities is not a Misoperation.
Note that;
(1) Failure to automatically reclose after a fault is not a Misoperation.
(2) Transformer operations are reported by the high-side voltage. Generator operations are reported by the generator step-up transformer high-side voltage.
(3) All Misoperations due to the same equipment and cause within a 24-hour period are to be recorded as one Misoperation and one Composite Protection System Operation. The 24-hour period guideline does not apply to Composite Protection System Operations that are not associated with Misoperations.
(4) Operations which are initiated by control systems (not by Protection Systems), such as those associated with generator controls, turbine/boiler controls, SVCs, FACTS, HVdc transmission systems, circuit breaker mechanisms, or other facility control systems, are not Misoperations.
Cause(s) of Misoperation
AC system | This cause includes Misoperations due to problems in the ac inputs to the Composite Protection System. Examples would include Misoperations associated with CT saturation, loss of potential, or damaged wiring in a voltage or current circuit.
As-left personnel error | This cause includes Misoperations due to the as-left condition of the Composite Protection System following maintenance or construction procedures. These include test switches left open, wiring errors not associated with incorrect drawings, carrier grounds left in place, settings placed in the wrong relay, or settings left in the relay that do not match engineering intended and approved settings. This includes personnel activation of an incorrect settings group.
Communication failures | This cause includes Misoperations due to failures in the communication systems associated with protection schemes inclusive of transmitters and receivers. Examples would include Misoperations caused by loss of carrier, spurious transfer trips associated with noise, Telco errors resulting in malperformance of communications over leased lines, loss of fiber optic communication equipment, or microwave problems associated with signal loss or degradation.
DC system | This cause includes Misoperations due to problems in the dc control circuits. These include problems in the battery or charging systems, trip wiring to breakers, or loss of dc power to a relay or communication device.
Incorrect settings | This cause includes Misoperations due to issued setting errors, including those associated with electromechanical or solid state relays and the protection element settings in microprocessor-based relays (excluding logic errors discussed in the Logic Error cause code). This includes setting errors caused by inaccurate modeling.
Logic errors | This cause includes Misoperations due to issued logic setting errors associated with programming microprocessor relay inputs, outputs, custom user logic, or protection function mapping to communication or physical I/O points.
Design errors | This cause includes Misoperations due to incorrect physical design. Examples would include incorrect configuration on ac or dc schematic or wiring drawings, or incorrectly applied protective equipment (hardware or firmware).
Relay failures/malfunctions | This cause includes Misoperations due to improper operation of the relays themselves. These may be due to component failures, physical damage to a device, firmware problems, or manufacturer errors. Examples would include Misoperations caused by loss of calibration, component degradation, misfiring thyristors, relay power supply failure, or internal wiring/logic error. Failures of auxiliary tripping relays fall under this category.
Unknown/unexplainable | This cause includes Misoperations where no clear cause can be determined. Use this cause code if the analysis is still in progress. Ensure that cause code is updated, if necessary, once analysis is complete. If this cause code is selected following final analysis, extensive documentation of investigative actions may be required.
Other/Explainable | This cause includes Misoperations that were determined to have an identified cause but they do not fit into any of the above categories. For example, temporary changes in network topology that because of their low probability of occurrence are not accounted for in the design of the Protection System, or environmental issues such as damage due to water from a leaking roof or animal intrusion.
Time Zones
ADT | Atlantic Daylight Time
APT | Atlantic Prevailing Time
AST | Atlantic Standard Time
CDT | Central Daylight Time
CPT | Central Prevailing Time
CST | Central Standard Time
EDT | Eastern Daylight Saving Time
EPT | Eastern Prevailing Time
EST | Eastern Standard Time
MDT | Mountain Daylight Time
MPT | Mountain Prevailing Time
MST | Mountain Standard Time
PDT | Pacific Daylight Time
PPT | Pacific Prevailing Time
PST | Pacific Standard Time
GMT | Greenwich Mean Time
Quarters
Qtr 1 (Jan 1 - Mar 31)
Qtr 2 (Apr 1 - Jun 30)
Qtr 3 (Jul 1 - Sep 30)
Qtr 4 (Oct 1 - Dec 31)
Analysis
Analysis - In Progress
Analysis - Completed
Corrective Action - In Progress
Corrective Action - Completed
Declaration made - No corrective actions
Equipment Type
Line
Transformer
Generator
Shunt Capacitor
Series Capacitor
Bus
Series Reactor/Inductor
Shunt Reactor/Inductor
Dynamic Var Systems
Breaker
HVdc
BES UFLS
BES UVLS
Other
Voltage
<100 (Bulk Electric System Elements Only)
<100 (Non-BES)
100
115
120
138
161
230
345
500
735
765
HVdc
Quarter Name
Qtr 1 (Jan 1 - Mar 31)
Qtr 2 (Apr 1 - Jun 30)
Qtr 3 (Jul 1 - Sep 30)
Qtr 4 (Oct 1 - Dec 31)
Jurisdiction
United States
Canada
Mexico
Fault Type
3 Phase (3PH)
3 Phase to Ground (3PH-GND)
Phase to Phase (PH-PH)
Phase to Phase to Ground (PH-PH-GND)
Phase to Ground (PH-GND)
Unknown (UNK)
Other (OTH)
None
Restoration
Automatic
Manual
NA
sub category
Incorrect setting/logic/design - Incorrect Numeric Value Specified
Incorrect setting/logic/design - Incorrect User-Programmed Logic Specified
Incorrect setting/logic/design - Incorrect System Coordination
Incorrect setting/logic/design - Incorrect Physical Design
Incorrect setting/logic/design - Failure to Update Firmware Version by User
Incorrect setting/logic/design - (Communication) Programming/Logic Error
Incorrect setting/logic/design - Other
Relay - Power Supply Failure/Malfunction
Relay - AC I/O Module Failure/Malfunction
Relay - Digital I/O Module Failure/Malfunction
Relay - Communication Module Failure/Malfunction
Relay - (Communication) Loss of Synchronism
Relay - Self-Diagnostic Failure/Malfunction
Relay - CPU Processor Failure/Malfunction
Relay - Continuous Reboot
Relay - Incorrect Manufacturer Programming ('Bug')
Relay - Incorrect Manufacturer Design
Relay - Incorrect Manufacturer Documentation
Relay - Unknown
Relay - Other
Bulk Power
Yes
No
Microprocessors
ABB
AREVA
Basler
GE
RFL
SEL/ Schweitzer
Siemens
Alstom
Schneider
Iniven
ERL Phase
Beckwith
Unknown
System Schemes
Step Distance
DCB
POR/POTT/PUTT
DCUB
DUTT
Phase Comparison
Line Current Differential
Differential
DTT
Overcurrent
Breaker Failure
Other
Mitigation_Status
Complete
In Progress
Comm Causes
Communication Interface Failure
Communication Medium
Station Signal Path Failure
Incorrect Logic Settings Issued
Other
Communication System Types
Fiber Optic
Microwave
Phone line
Power Line Carrier
Pilot Wire
Unknown/Other
Reporting Years
2013
2014
2015
2016
2017
2018
2019
2020
2021
2022
2023
2024
2025
2026
2027
2028
2029
2030
Regional Entity Name
MRO
NPCC
RF
SERC
Texas RE
WECC
Tech
Electromechanical
Solid State
Microprocessor
Other
N/A
Yes / No
Yes
No
Definition of Composite Protection System Operation
1. The correct operation of a Composite Protection System associated with isolating a faulted system Element.
2. The correct operation of a Composite Protection System associated with isolating equipment for non-Fault conditions such as power swings, over excitation, or loss of field (excluding control functions performed by a protective relay; e.g., when a reverse power relay is used to trip a breaker during generator shutdown).
3. The unintended operation of a Composite Protection System for a Fault outside the zone it is designed to protect.
4. The unintended operation of a Composite Protection System for a non-Fault condition.
5. Any failure of a Composite Protection System to operate for its intended function such as clearing a Fault within the zone it is designed to protect.
Notes:
1. Multiple operations of a Composite Protection System due to a sequence of automatic or manual reclosing and tripping should be counted as a single operation.
2. Transformer operations are reported by the high-side voltage. Generator operations are reported by the generator step-up transformer high-side voltage.
3. Operations which are initiated by control systems (not by Protection Systems), such as those associated with generator controls, turbine/boiler controls, static var compensators (SVCs), flexible ac transmission systems (FACTS), high-voltage dc (HVdc) transmission systems, circuit breaker mechanisms, or other facility control systems, are not reported as operations of a Protection System.
4. The Composite Protection System operations count reported is inclusive of all Composite Protective System operations, not just correct Composite Protection System operations. This means that every reported Misoperation will have at least one associated Composite Protection System operation.
Composite Protection System Operation Examples
1. A permanent Fault occurs on Line A and all line breakers operate and go through a complete reclose sequence (trip, close, trip, close, and trip). This event is considered one Composite Protection System operation. Analysis would indicate that this was a correct Composite Protection System operation.
2. A permanent Fault occurs on Line B and all line breakers operate correctly but, at the same time, a breaker on Line C operates. This event is considered two Composite Protection System operation, since two transmission Elements were involved. Analysis would identify that the Line B Composite Protection System operation was correct, and the Line C Composite Protection System operation was a Misoperation. This means that two Composite Protection System operations and one Misoperation would be reported.
3. A breaker(s) on Line D opens under a non-fault condition due to a failed relay. This event is considered one Composite Protection System operation. Analysis would identify the Line D Composite Protection System operation as a Misoperation. This means that one Composite Protection System operation and one Misoperation would be reported.
4. Line faults with one breaker failure.
  a. No breaker failure relaying: There would be one Composite Protection System operation associated with the line fault, and one additional Composite Protection System operation for each required remote backup clearing operation.
  b. Breaker failure relaying with local tripping and no transfer tripping of remote ends: There would be one Composite Protection System operation for the Fault with the breaker failure, one Composite Protection System operation for the breaker failure local clearing, and an additional Composite Protection System operation for each required remote back up clearing. For example, if the line fault occurred and the breaker between two lines on a breaker-and-a-half bus failed, there would be three Composite Protection System operation . One Composite Protection System operation associated with the fault, one Composite Protection System operation for the breaker failure local clearing, and one Composite Protection System operation for the remote end trip of the second line connected to the failed breaker.
  c. Breaker failure with transfer tripping of remote ends: For the example scenario in 4b, there would be two Composite Protection System operation . One for the fault, and a second for the breaker failure protection clearing.

## 5 - Data Description
Tab 1 - Operation Summary
Field Name | Required Field (Y/N) | Field Description
Data Submission Year | Y | The calendar year for which the operation data is reported.
Data Submission Quarter | Y | The calendar quarter for which the operation data is reported.
Regional Entity Name | Y | The entity’s Regional Entity. If the entity is registered in multiple Regional Entities, the primary Regional Entity should be selected.
NERC ID | Y | The entity’s NERC compliance registry number. This should include the three letters NCR and any preceding or following 0's.
Voltage Class | Y | Lists the 12 Voltage Classes
Total CPSOPs [Composite Protection System Operations] Occurred in (FRCC) | Y | The total number of Composite Protection System operations that occurred during the selected Quarter/Year for the registered entity within FRCC for each voltage class
Total CPSOPs [Composite Protection System Operations] Occurred in (MRO) | Y | The total number of Composite Protection System operations that occurred during the selected Quarter/Year for the registered entity within MRO for each voltage class
Total CPSOPs [Composite Protection System Operations] Occurred in (NPCC) | Y | The total number of Composite Protection System operations that occurred during the selected Quarter/Year for the registered entity within NPCC for each voltage class
Total CPSOPs [Composite Protection System Operations] Occurred in (RF) | Y | The total number of Composite Protection System operations that occurred during the selected Quarter/Year for the registered entity within RF for each voltage class
Total CPSOPs [Composite Protection System Operations] Occurred in (SERC) | Y | The total number of Composite Protection System operations that occurred during the selected Quarter/Year for the registered entity within SERC for each voltage class
Total CPSOPs [Composite Protection System Operations] Occurred in (TRE) | Y | The total number of Composite Protection System operations that occurred during the selected Quarter/Year for the registered entity within TRE for each voltage class
Total CPSOPs [Composite Protection System Operations] Occurred in (WECC) | Y | The total number of Composite Protection System operations that occurred during the selected Quarter/Year for the registered entity within WECC for each voltage class
Tab 2 - Misoperation Entry Form
Field Name | Required Field (Y/N) | Field Description
Misoperation ID | Y | An automatically concatenated entity-specific Misoperation identifier.
Region Where Misoperation Occurred | Y | The Regional location where the Misoperation occurred.
NERC Compliance Registry Number | Y | The entity’s NERC compliance registry number. Ex:NCR99999 Use this URL you need to lookup your NERC Compliance Registry Number: http://www.nerc.com/pa/comp/Pages/Registration.aspx
Jurisdiction | Y | The country the Misoperation occurred in.
Misoperation Date | Y | The date of the Misoperation in MM/DD/YYYY format.
Misoperation Time | Y | The time of the Misoperation in 24hr HH:MM:SS format.
Time Zone | Y | The time zone in which the Misoperation occurred, see Definitions tab for detailed definitions.
Facility Name (Location of Misoperation) | Y | The name of the facility (i.e., substation or generating station) where the Misoperation occurred.
Equipment Name (protected by Composite Protection System that Misoperated) | Y | The name of the generator, transmission line, transformer, bus, or equipment protected by the Composite Protection System that Misoperated.
Equipment Type | Y | The type of equipment being protected (i.e., line, transformer, etc.).
Facility Voltage | Y | The system voltage of the protected Element. If the Element is a transformer, the high-side voltage. If the Element is a generator, the GSU transformer high-side voltage.
Equipment Removed from Service (Permanently or Temporarily) as the result of the Misoperation | Y | The names of the equipment becoming unavailable due to the Misoperation (Equipment refers only to circuits, transformers, buses, but not breakers UNLESS the breaker is the only Element). Breaker should be used only if a single breaker tripped and did not disconnect any Element at one of its terminals (one breaker in a multiple breaker protected line, bus tie breaker, etc.).
Fault Type | N | Identify the type of fault that occurred from the following choices: -3 Phase -3 Phase to Ground -Phase to Phase -Phase to Phase to Ground -Phase to Ground -Unknown -Other
Event Description | Y | A brief description of the event including: 1. Initiating event: include a description of any internal or external fault causes, any abnormal system conditions which may have contributed to the Misoperation, or state that the Misoperation occurred under normal operating conditions. 2. Facilities involved on which Protection Systems operated correctly and/or incorrectly concurrent with the Misoperation. 3. Component(s) of the Composite Protection System(s) that failed and/or did not function correctly. 4. Detailed description of root causes determined by completed Corrective Action Plans.
Restoration Method | N | The Restoration Method choices are: -Automatic, the system went back to normal without human intervention -Manual, operation of manual control switches -Operator, operator action and/or supervisory operation through EMS -Combination, restoration involved a combination of 2 or 3 of the above items
Misoperation Category | Y | The category of the Misoperation: • Failure to Trip – During Fault • Failure to Trip – Other Than Fault • Slow Trip – During Fault • Slow Trip – Other Than Fault • Unnecessary Trip – During Fault • Unnecessary Trip – Other Than Fault
Cause(s) of Misoperation | Y | The primary cause of the Misoperation: • AC system • As-left personnel error • Communication failures • DC system • Incorrect settings • Logic errors • Design errors • Relay failures/malfunctions • Unknown/unexplainable • Other/Explainable
Incorrect Setting/Logic Errors/Design Errors and Relay Failure/Malfunctions Sub Cause Code | N | Select a sub-cause only if: - Misoperation involved a microprocessor relay AND 'incorrect settings', 'logic errors', 'design errors' or 'relay failures/malfunctions' was selected for Cause(s) of Misoperation valid choices include: -Incorrect Setting/logic/design - Incorrect Numeric Value Specified (This category includes misoperations due to Incorrect Numerical Value Specified of a Microprocessor Relay Setting. This sub cause code does not include field personnel incorrectly inputting the relay settings. Example would include misoperation caused by incorrect specification of pickup magnitude, or protection operation time delay, or angle, or positive/negative/zero sequence parameters, etc. Example 2: incorrectly specifying 5 ohms instead of 0.5 ohms. Example 3: incorrectly substituting parameter unit such as msec instead of cycle.) -Incorrect Setting/logic/design - Incorrect User-Programmed Logic Specified (This category includes misoperations due to Incorrect Logic as specified by the user. Example would include misoperation caused by wrong function selection such as selection of positive/negative/zero sequence voltage for polarization, supervision element, loss of potential, trip logic , breaker failure logic, 2nd harmonic blocking, etc. Example 2: incorrectly select zero sequence voltage for polarization of directional control for transmission lines sharing common right of way.) -Incorrect Setting/logic/design - Incorrect System Coordination (This category includes misoperations due to lack of Protection System coordination. Lack of coordination may occur for example when studies are not up-to-date with actual fault values, or fail to consider mutual coupling, or does not take into account specific system configuration. It also includes wrong determination of Timed Overcurrent curves and time delays used for coordination purposes. Example 2: Failure to recognize the effect of changes due to transformer impedances and winding configurations.) -Incorrect Setting/logic/design - Incorrect Physical Design (This category includes misoperations due to Incorrect Physical Design. Example would include drawings errors such as incorrect CT polarity, multiple groundings, wrong wiring diagram, etc. This sub cause code does not include construction personnel incorrectly wiring or failing to follow the construction drawing.) -Incorrect Setting/logic/design - Failure to Update Firmware Version by User (This category includes misoperations due wrong application of relay firmware version. This category includes misoperations due to latest firmware version not being installed by the user.) -Incorrect Setting/logic/design - (Communication) Programming/Logic Error (This category includes misoperations due to incorrect programming or application of microporcessor-based communication equipment . These include multiplexer relay teleprotection devices.) -Incorrect Setting - Other (This category includes misoperations that are determined to be associated with Incorrect Setting/Logic/Design of a microprocessor relay, but they do not fit into any of the above categories.) -Relay - Power Supply Failure/Malfunction (Failure or malfunction of power supply ) -Relay - AC I/O Module Failure/Malfunction (Failure or malfunction of AC I/O module) -Relay - Digital I/O Module Failure/Malfunction (Failure or malfunction of digital I/O module) -Relay - Communication Module Failure/Malfunction (Failure or malfunction of communication module) -Relay - (Communication) Loss of Synchronism (This sub-cause code would capture those Composite Protection System failures resulting from systems which depend upon the integrity of the communications network. An example would be a misoperation of a current differential scheme due to loss of synchronism, or loss of time stamping.) -Relay - Self-Diagnostic Failure/Malfunction (This sub-cause code would capture those Composite Protection System failures resulting from an inappropriate action or inaction of the device self-diagnostics.) -Relay - CPU Processor Failure/Malfunction (This sub-cause code captures those Composite Protection System failures resulting from a failure of the main processor. Examples could be temperature related failures, memory corruption, etc.) -Relay - Incorrect Manufacturer Programming ('Bug') (Failures as a result of a programming error in the devices firmware, internal programming, or user interface software. These are usually addressed by the manufacturer issuing a new firmware Example: CPU erratic operation caused by interaction with communication software.) -Relay - Incorrect Manufacturer Design (Failures resulting from wrong conceptual design in physical hardware, or components, or software. An example of these designs are the various distance schemes that come prepackaged in a line protection. Example 2: sensitive input prone to incorrectly operate for spurious voltage.) -Relay - Incorrect Manufacturer Documentation (Failures as a result of an action taken which was attributed to incorrect documentation from the manufacturer. Example: incorrect description of relay logic in user manual.) -Relay - Unknown (Captures that relay failure/malfunctions whose underlying sub-cause could not be determined) -Relay - Other (All other failures/malfunctions whose cause has been determined but which has no other "more appropriate" sub-cause code.)
Communication Sub Cause of Misoperation | N | Communication Interface Failure (Modulator): Power-line carrier radios, fiber optic interfaces, microwave radios, audio-tone/telecommunications, and pilot wire components Communication Medium: The external signal path, leased phone circuits, cables, transmission lines, etc Station Signal Path Failure: All signal carrying components within the substation fence including cables, frequency filters, connectors, etc Incorrect Logic Settings Issued: This subcause code includes logic settings associated with communication function that have been incorrectly issued such as; channel addressing, channel timing, dip switches etc. Human Error (Misapplication in field): Incorrect settings both logic and relay reach, as left conditions, etc Other: Any Communication Failures which do not fit in the above Sub Causes
Communication System Type | N | If Cause of Misoperation is 'Communication Failure' then this field is used to further describe the type of communication failure.
Protection System Schemes | N | Focuses on keeping the power system stable by isolating only the components that are under fault, thus leaving as much of the network as possible still in operation Step Distance DCB = Directional Comparison Blocking Scheme (a scheme which allows over reaching elements to trip if a blocking scheme is not received within a predetermined time) POR/POTT = Permissive Over Reaching Schemes (A scheme which uses over reaching elements at all terminals to send permissive signals to all remote terminals. The overreaching elements will trip without delay upon receipt of permissive signals from all remote terminals. This also intends to include Permissive Under Reaching Transfer Trip (PUTT) schemes) DCUB = Directional Comparison Unblocking Scheme (a type of POR scheme modified for use with power line carrier communications) DUTT = Direct Under Reaching Transfer Trip Schemes (a scheme which uses local under reaching elements to trip locally, and to send direct transfer trip commands to the remote terminal) Phase Comparison = compare the phase of the current entering each line terminal to identify internal/external faults Line Current Differential = measure the phase and magnitude of local fault currents Differential = used for schemes using local current sources connected to differential relays DTT = Direct Transfer Tripping Scheme Breaker Failure = identify a breakers inability to interrup current within a set time after it has been commanded to trip Other
Protection Systems/Components that Misoperated | Conditionally | Information on the Protection Systems/Components that Misoperated. If the “Cause of Misoperation” is “Relay failures/malfunctions”, “Incorrect settings”, “Logic errors”, or “Design errors”, and the cause is associated with a relay, list relay models (types). For non-relay component Misoperation causes, include specific information on non-relay Protection System components that Misoperated, such as "damaged CT secondary cable".
Relay Technology | Conditionally | If the Cause of Misoperation is “Relay failures/malfunctions,” “Incorrect settings,” “Logic errors,” or “Design errors”, this field is used to identify the relay technology installed. • Electromechanical • Solid State • Microprocessor
Microprocessor Relay Manufacturer | N | If the Relay Technology is 'Microprocessor' then select the name of the manufacturer
Count of Transmission AC & DC Circuits Removed From Service | Y | The number of transmission AC and/or DC circuits removed from service as a result of the Misoperation. A single transmission AC circuit is considered to be three-phase conductors over 100kV+, overhead or underground, that are bound by AC substations. Radial circuits above 100kV should be included. A single transmission DC circuit is considered to be one pole of the 100kV+ overhead or underground DC line that is bound by an AC/DC terminal on each end. Circuit breakers, transformers, and associated disconnect switches are not considered to be part of the circuit. A transmission circuit is considered to be out of service if it is de-energized and/or disconnected at one or more terminals. This definition is for MIDAS Section 1600 reporting only, it should align with TADS Section 1600 reporting, but may or may not align with other NERC reporting or compliance definitions.
Count of Transmission Transformers Removed From Service | Y | The number of transmission transformers removed from service as a result of the Misoperation. A singe transmission transformer is considered a bank comprised of three single-phase transformers or a single three-phase transformer with a 100kV+ low-side voltage. A transformer is bounded by its associated switching or interrupting devices. This definition is for MIDAS Section 1600 reporting only, it should align with TADS Section 1600 reporting, but may or may not align with other NERC reporting or compliance definitions.
Count of Conventional Generation Units and Inverter-Based Plants Removed From Service | Y | The number of conventional generation units >=20MW and inverter-based (i.e. wind, solar) plants >=20MW removed from service as a result of the Misoperation. An inverter-based plant consists of one or more generators, inverters, or turbines with a shared point of interconnection. The plant's capacity should be based on the total MW capacity at the point of interconnection. Plants with multiple points of interconnection that are still able to provide energy to the BES should not be included in this count. This definition is for MIDAS Section 1600 reporting only, it may or may not align with other NERC reporting or compliance definitions.
Analysis and Corrective Action Status | Y | The status, selected from a drop-down list.
Corrective Action Plan | Conditionally | Identification of the corrective actions. “None” if, in place of a CAP, a declaration was made stating no further corrective actions will be taken.
Corrective Action Plan Target Completion Date | Conditionally | If corrective actions are not complete, an estimate of when they will be complete.
Actual Completion Date | Conditionally | If corrective actions are complete, the actual completion date.
Reported By | Y | The person who filled out the report.
Reporter’s Telephone Number | Y | The reporting person's phone number. Format: (999)999-9999
Reporter’s Email Address | Y | The e-mail address of the reporter. Format: name@domain.com
Date Reported | Y | The report date. Format: MM/DD/YYYY
Additional Contact Name | N | An additional contact with knowledge of the data.
Additional Contact’s Phone Number | N | If entering an additional contact, the person's phone number. Format: (999)999-9999
Additional Contact’s Email Address | N | If entering an additional contact, the person's e-mail address. Format: name@domain.com
Comments | N | Free form text entered by the Registered Entity to provide clarification or additional information (use if needed).

## 6 - Version History
Version Number | Date | Description
012-2 | 07/09/2024 | Version control corrections, listed changes initially implemented 12/15/2020. Version number remains 012.
Columns E & F coumn headers on Opt-Out Waiver Form tab have been modified for further clarification
"Operator Action" and "Combination" removed from "Restoration Method" dropdown from Misoperation Entry Form tab
"POR/POTT" changed to "POR/POTT/PUTT" under "System Schemes" dropdown from Misoperation Entry Form tab
"Overcurrent" added to "System Schemes" dropdown from Misoperation Entry Form tab
"Communication SubCauses", "Human Error" and "Not Enough Information" removed from "Comm SubCauses" dropdown from Misoperation Entry Form tab
012-1 | 01/01/2024
Removed the following fields from Misoperation Entry Form: -Is this a TADS reportable event? -Enter one or more TADS "Element IDs" for any TADS reportable Elements outaged in the Misoperation. -Is this a GADS reportable event? -If the Misoperation caused a generator forced outage, enter one or more Generation Availability Data System (GADS) "Unit IDs" for any GADS reportable Elements outaged in the Misoperation.
Added the following integer fields to Misoperation Entry Form: -Count of Transmission AC & DC Circuits Removed From Service -Count of Transmission Transformers Removed From Service (see data description for single-phase transformers) -Count of Generation Plants Removed From Service
Removed old fields from Data Description tab.
Added new fields to Data Description tab.
011 | 05/17/2023
Clarified the phrasing in cells E3 & F3 on tab 3.
Clarified note 1 on tab 4.
Added a note to tab 3 stating the user should deactivate opt-out waivers for the selected quarter if they want to create them through the Bulk Submission form.
Added Excel validation for several columns in Misoperation Entry Form.
010 | 08/05/2019
Version number added to 1-Operation Summary tab
6 - Version History tab was added
009 | 04/26/2019
Opt-Out Waiver Form changed from tab 5 to tab 3
“FRCC” removed from Definitions tab, and consequentially all dropdowns
“Total PSOPs Occurred in FRCC” (column G) removed from Operation Summary tab
008 | 12/11/2018
Added Opt-Out Waiver Form sheet
Not released, incorporated into version 009
007 | 05/16/2018
SPP removed from Definitions tab, and consequentially all dropdowns
“Total PSOPs Occurred in SPP" removed from Operation Summary tab
006 | 03/19/2018
Definitions tab was scrolled to the top by default.
005 | 06/01/2017
TRE changed to Texas RE
004 | 05/11/2017
Default printing options for each sheet adjusted
Cells A2-E2 have been highlighted yellow for increased visibility to users.
Cells A3-E13 & A14-C14 have been X'ed out instead of previous black out method. This is to prevent some confusion that was arising and make cells A2-E2 more prominent.
Various cell sizes were changed for increased useability.
Text boxes on sheet 3-Definitions were re-sized for better visibility on smaller screens.
Contents of rows 32-75 on sheet 3-Definitions were shifted left to be flush with column A.
Excess blank cells on bottom/right of sheets removed to reduce file size.
003 | 05/01/2017
Operation Summary headers for columns G:N changed from "Total Number of Operations Occurred in *Region*" to "Total Number of Protection System Operations Occurred in *Region*".
Definitions & Data Description sheets fully unlocked.
Method for locking cells on Operation Summary & Misoperation Entry Form sheets changed to allow submitters to reformat locked cells allowing them to fully view contents or resize as needed.
Formula for column A (Misoperation ID) in Misoperation Entry Form revised to display "Required fields incomplete, please complete or delete row contents" in an attempt to more clearly indicate to submitters rows that will likely cause submission errors.
002 | 02/23/2017
Operation Summary headers for columns G:N changed from "Total Number of Operations Occurred in (*Region*)" to "Total Number of Operations Occurred in *Region*".
Columns in "Operation Summary" resized to attempt to better accomodate for submitters with smaller screens.
All cells which do not require submitter entry have been locked. Unlocked cells include;
Operation Summary; A2:E2, G2:N13
Misoperation Entry Form: B2:AN499
Definitions; All locked
Data Description; All locked
001 | 01/18/2017
Initial Document Release