## Instructions
Cause Code Report
The Cause Code report is an export from NERC's GADS data
Cause Codes are identified for each Event
Each Event has an attributed capacity in Megawatts, as well as duration where generation loss in Megawatt hours can be calculated.
The Report includes different types of Forced Outages and Deratings: Forced Immediate (U1, D1), Forced Delay (U2, D2), Force Postponed (U3, D3) and Startup Failure (SF).
Excluded are Planned Outages and Deratings, Maintenance Outages and Deratings, Reserve Shutowns, and any other non-forced outages.
The Data page is the aggregated export file.
This export masks the identity of each unit by aggregating data instead of including each confidential data item.
Each Cause Code with similar units are listed on the same row
The Report Page allows different analysis
| Cause Code | The identified cause of an event. For events with multiple cause codes, only the primary cause code is tallied.
| Sum of Distinct Untis | The number of units that were tallied to create the row
| Sum of Event Count | the number of events that were tallied to create the row
| Sum of MW Lost | The sum of MegaWatts lost during the Events in each row
| Sum of MWHrsLost | The sum of MegaWatt Hours lost during the Events in the row
Pre-populated Filters allow ease of use to go from broad analysis to more granular analysis
|  | Season |  | Summer months are from June - september.Winter Months December -February.
|  |  | Off-Peak |  | Neither Wintor Nor summer months
|  |  | Summer |  | Peak Summer months
|  |  | Winter |  | Peak Winter months
|  | Region code |  | NERC defined regions can give some territorial information.
|  |  | MRO |  | Midwest Reliability Organization
|  |  | NPCC |  | Northeast Power Coordinating Council
|  |  | RF |  | ReliabilityFirst
|  |  | SERC |  | SERC Reliabilty Council
|  |  | TRE |  | Texas Reliability Entity
|  |  | WECC |  | West Electric Coordinating Council
|  | Fuel Category |  | some fuels are used among different unit types
|  |  | Coal | solid coal fuel
|  |  | Gas | air-burned fuel
|  |  | Hydro | Water turbine
|  |  | Nuclear | Nuclear radioactive fuel
|  |  | Oil | Liquid fuel
|  |  | Other | fuel not categorized in other categories
|  |  | Waste Heat | Vented heat from primary fuel source
|  | Unit Type |  | some unit types burn different types of fuel
100- Fossil-Steam
200 - Nuclear
300 - Gas Turbine / Jet Engine
400 - Internal Combustion / Reciprocating Engine
500 - Pumped Storage / Hydro
650 - Fluidized Ben
800 - Miscellaneous
810 - Multi-Boiler / Multi-turbine
850 - Combined Cycle Block
851 - Combined Cycle Gas Turbine
852 - Combined Cycle Steam unit
860 - Cogeneration Block
861 - Cogeneration Gas Turbine
862 - Cogeneration Steam unit
|  | Event Type |  | there are several types of Forced Event Types, Outages remove the full capacity of the unit, Deratings remove partial capacity from the unit.
D1 - Forced immediate Derating
D2 - Forced Delayed Derating
D3 - Forced Postponed Derating
U1 - Forced Immediate Outage
U2 - Forced Delayed Outage
U3 - Forced Postponed Outage
SF - Startup Failure
|  | System Name |  | Cause Codes fall under different Systems of a plant. Some systems apply to all Unit Types, others aply to certain unit types.
Balance of Plant
Boiler
Diesel Engine
External
Gas Turbine
Generator
HRSG Boiler
Hydro Turbine / Pump
Nuclear Reactor
Performance
Personnel Errors
Pollution control Equipment
Regulatory, Safety, Environmental
Steam Turbine
|  | Component Name |  | Components are subsets under the System Name. Each System has a different set of Components
Each cause Code has an associated Component that falls under one of the listed Systems

## Report
Season | - all -
RegionCode | - all -
FuelCategory | - all -
UnitType | - all -
EventType | - all -
SystemName | - all -
ComponentName | - all -
Data
Cause | Sum of DISTINCT_UNITS | Sum of EVENT_COUNT | Sum of MWLost | Sum of MWHrsLost
0010-Thaw shed failure or fire | 1 | 1 | 0.1 | 0.001667
0020-Coal car dumpers; shakers; and unloaders | 17 | 17 | 2665.29 | 14549.8331
0022-Unloading/receiving hopper (train/truck) | 3 | 3 | 34 | 350.1833
0024-Rotary plow | 6 | 6 | 1073.2 | 3700.7626
0026-Dust suppression system | 2 | 2 | 193 | 480.3999
0028-Dust collection system | 4 | 4 | 882 | 3516.033
0030-Coal conveyors and feeders | 485 | 486 | 62230.28 | 1809549.6717
0035-Metal detector/collector (including magnetic separator) | 1 | 1 | 134 | 348.4
0040-Coal elevators | 5 | 5 | 1719 | 9522.1824
0050-Coal storage fires | 3 | 3 | 464 | 1082.583
0060-Coal crushers including motors | 46 | 46 | 4961 | 64477.5819
0070-Coal samplers | 1 | 1 | 4 | 32
0075-Storage silos/hoppers | 27 | 27 | 3553.75 | 333075.0411
0080-Stackers/reclaimers | 13 | 13 | 1582.2 | 15544.9662
0084-Coal conveyor scales-storage coal pile | 15 | 15 | 642 | 8846.5497
0085-Bunker feeder coal scales | 3 | 3 | 60 | 520.2166
0090-Bunker fires | 22 | 22 | 1500 | 21223.6162
0095-Bunker flow problems | 149 | 149 | 10320.04 | 58934.0997
0100-Bunker gates | 10 | 10 | 1092 | 9253.133
0105-Bunker structures | 9 | 9 | 272 | 6537.4332
0106-Coal drying system (see additional codes 0125-0127) | 9 | 9 | 352 | 1785.2499
0110-Other coal fuel supply problems up through bunkers | 171 | 173 | 26141.24 | 343378.2756
0111-Solid fuel feeder conveyors | 9 | 9 | 198.05 | 8508.7706
0114-Solid fuel volumetric feeder | 1 | 1 | 14 | 14
0115-Solid fuel gravimetric feeder | 12 | 12 | 158 | 451.4333
0119-Solid fuel crushers | 1 | 1 | 10.5 | 11.9
0121-Other solid fuel feed problems | 17 | 17 | 453 | 3836.0833
0125-Coal crusher dryer hammers | 1 | 1 | 170 | 3697.5
0126-Coal crusher lube oil system | 6 | 6 | 496 | 1873.4332
0127-Other coal crusher dryer problems (see code 0106) | 15 | 15 | 1198.25 | 9513.9203
0129-Other coal processing system problems | 80 | 87 | 7206.02 | 55696.2949
0131-Sorbent handling conveyors | 4 | 4 | 1212.94 | 21873.0046
0132-Sorbent handling feeders | 1 | 1 | 53 | 61.8333
0160-Bed material tanks/hoppers | 1 | 1 | 34.58 | 1348.62
0168-Bed material blowers/fans | 1 | 1 | 129 | 784.75
0173-Bed material pneumatic transport system including piping and valves | 1 | 1 | 35 | 561.1667
0174-Other bed material handling equipment | 9 | 9 | 1198.48 | 29397.0736
0200-Pulverizer exhauster fan (for indirect firing) | 35 | 35 | 2102 | 22601.9163
0205-Pulverizer exhauster fan drive | 30 | 31 | 1363.46 | 54263.2578
0220-Pulverizer system cyclone separator | 3 | 3 | 152 | 724.6667
0240-Pulverized coal bin | 42 | 42 | 3131 | 18760.4824
0250-Pulverizer feeders | 2344 | 2377 | 187630.52 | 809802.2105
0253-Pulverizer feeder motor | 131 | 132 | 8955.55 | 61982.1397
0255-Pulverizer feeder coal scales | 27 | 27 | 3052 | 19825.5156
0256-Seal air system (air to pulverizers) | 23 | 23 | 2374.32 | 19185.3015
0260-Primary air fan | 353 | 354 | 33169.84 | 1289884.664
0262-Primary air fan lube oil system | 22 | 22 | 2518.61 | 13248.9544
0263-Primary air fan drives | 97 | 97 | 12456.51 | 273113.625
0264-Other primary air fan problems | 100 | 100 | 11888.9 | 338226.5392
0265-Primary air heater | 11 | 11 | 1587 | 312633.4994
0266-Primary air heater fouling | 33 | 33 | 3347 | 233608.5154
0267-Primary air flow instrumentation | 50 | 50 | 5094.78 | 19573.449
0270-Primary air duct and dampers | 178 | 178 | 20594.08 | 301226.147
0280-Pulverizer fires | 126 | 126 | 11653.5 | 164523.1479
0290-Pulverizer reduced capacity due to wear | 29 | 29 | 1195 | 38876.3996
0300-Pulverizer motors and drives | 232 | 236 | 16389.93 | 592244.2875
0310-Pulverizer mills | 1471 | 1475 | 120105.14 | 1324013.7143
0312-Pulverizer mill classifiers | 53 | 53 | 5367.51 | 38774.5398
0313-Pulverizer mill trunnion seals | 16 | 16 | 1782.41 | 20580.604
0315-Pulverizer mill coal level controls | 32 | 32 | 2163 | 10473.9494
0320-Foreign object in Pulverizers mill | 330 | 333 | 36610.11 | 170929.8137
0325-Pulverizer skidding | 44 | 44 | 3518.66 | 22940.359
0330-Pulverizer coal leak (pulverizers only) | 189 | 189 | 15449.45 | 92082.7596
0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | 162 | 162 | 12011.95 | 111673.7321
0335-Pulverizer lube oil system | 233 | 234 | 21317.29 | 119913.4819
0338-Pulverizer control systems (temperature and pressure) | 87 | 87 | 6830.76 | 34063.6884
0339-Pulverizer System Puff | 21 | 21 | 2424.66 | 95469.2833
0340-Other pulverizer problems | 776 | 777 | 72305.95 | 1063696.6771
0341-Pulverizer deluge system | 6 | 6 | 530 | 3676.9666
0342-Pulverizer inert system | 14 | 14 | 1997.46 | 16583.7809
0344-Pulverizer inspection | 137 | 137 | 9983.7 | 184387.2925
0345-Pulverizer overhaul | 63 | 63 | 2280.2 | 367891.3896
0346-Pulverizer pyrite removal system | 171 | 172 | 13474.31 | 51494.9848
0350-Pulverized fuel and air piping (from pulverizer to wind box) | 195 | 195 | 16135.43 | 228084.9071
0358-Oil burner piping and valves | 13 | 13 | 3801 | 31794.8822
0359-Gas burner piping and valves | 78 | 78 | 11732.03 | 151125.4233
0360-Burners | 182 | 185 | 15920.25 | 401148.346
0361-Burner orfices | 8 | 8 | 456 | 7061.6499
0366-Duct burners (FBC only) | 1 | 1 | 102 | 289
0370-Burner instruments and controls (except light-off) | 125 | 126 | 15399.2 | 53394.2695
0380-Light-off (igniter) systems (including fuel supply) | 117 | 117 | 19878.97 | 101318.1907
0385-Igniters | 91 | 91 | 11170.1 | 58955.1233
0390-Burner wind boxes and dampers | 24 | 24 | 2173.5 | 111780.8328
0400-Burner wind box fires | 10 | 10 | 2570.67 | 387818.9502
0410-Other burner problems | 119 | 119 | 9740.12 | 172647.7308
0415-Cyclone feeders | 340 | 351 | 17684.02 | 173556.5175
0420-Cyclone crusher | 23 | 23 | 1159 | 8530.2164
0425-Cyclone dampers | 48 | 49 | 2468.4 | 72520.8325
0426-Cyclone air ducts | 8 | 8 | 381 | 2008.8832
0430-Cyclone furnace | 24 | 26 | 1657 | 41123.8164
0435-Other cyclone problems | 505 | 947 | 26956.52 | 105367.8694
0440-Fuel oil pumps (general) | 3 | 3 | 857 | 970.5
0441-Fuel oil pumps (burner supply) | 5 | 5 | 1390.02 | 10368.7585
0442-Fuel oil pumps (forwarding/transfer) | 1 | 1 | 60 | 1740
0450-Fuel oil heaters | 2 | 2 | 715.21 | 11705.095
0460-Fuel oil atomizers | 11 | 11 | 1261.33 | 2471.0771
0470-Oil and gas fires | 2 | 2 | 424.5 | 23081.8498
0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | 61 | 61 | 9189.9 | 233712.8616
0500-Main steam piping up to turbine stop valves | 375 | 383 | 19855.13 | 2519086.6863
0510-Main steam relief/safety valves off superheater | 62 | 62 | 4990.8 | 204808.4469
0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | 49 | 49 | 11854.82 | 351683.7131
0530-Other main steam system problems | 604 | 626 | 15790.57 | 212144.0863
0540-Hot reheat steam piping up to turbine stop valves | 20 | 20 | 6314.19 | 605388.0713
0541-Cold reheat steam piping up to boiler | 15 | 15 | 5984.9 | 910194.827
0550-Reheat steam relief/safety valves | 27 | 27 | 3908 | 252476.7327
0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | 28 | 28 | 4934.6 | 162348.287
0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | 14 | 16 | 2609 | 43548.6159
0570-Other reheat steam problems | 218 | 290 | 10766.22 | 160245.8754
0580-Desuperheater/attemperator piping | 8 | 8 | 2433 | 64166.6656
0590-Desuperheater/attemperator valves | 57 | 57 | 8824.36 | 242487.9239
0600-Desuperheater/attemperator spray nozzles | 2 | 2 | 123 | 2588.9166
0610-Desuperheater/attemperator drums | 2 | 2 | 360 | 928.7999
0620-Other desuperheater/attemperator problems | 24 | 25 | 2753.75 | 54623.178
0630-Startup bypass system piping (including drain lines up to heaters or condenser) | 6 | 6 | 3190 | 65664.7816
0640-Startup bypass system valves | 46 | 47 | 27934.4 | 652359.3359
0650-Startup bypass tanks or flash tanks | 3 | 3 | 1268.1 | 10645.1927
0655-Steam by-pass system instrumentation and controls | 1 | 1 | 453 | 2793.4997
0660-Other startup bypass system problems | 8 | 8 | 4411.4 | 31181.6347
0670-Feedwater piping downstream of feedwater regulating valve | 17 | 17 | 2405.3 | 28012.9924
0680-Feedwater valves (not feedwater regulating valve) | 33 | 33 | 7699.6 | 344113.1919
0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | 6 | 6 | 1058.15 | 5999.2138
0700-Blowdown system valves A | 11 | 11 | 2520.12 | 30161.6656
0710-Blowdown system piping B | 13 | 13 | 3904 | 68009.5661
0720-Blowdown system controls / instrumentation | 1 | 1 | 66 | 247.5
0730-Other blowdown system problems | 9 | 9 | 1293 | 11986.2998
0740-Boiler recirculation pumps | 82 | 82 | 14895 | 1126487.7281
0741-Boiler recirculation pumps - motors | 24 | 24 | 5530 | 1823154.5823
0742-Boiler recirculation pumps - motors - cooling system | 33 | 33 | 2569 | 76757.7996
0750-Boiler recirculation piping including downcomers | 7 | 7 | 1239.85 | 32632.3827
0760-Boiler recirculation valves | 10 | 10 | 3941.67 | 70161.1164
0770-Other boiler recirculation problems | 28 | 28 | 2051.1 | 27273.1329
0775-Economizer piping | 37 | 37 | 3077.74 | 96654.3861
0780-Headers between tube bundles | 8 | 8 | 1383 | 13234.0327
0782-Headers and caps | 9 | 9 | 1586 | 2245136.8492
0790-Pipe hangers; brackets; supports (general) | 2 | 2 | 1600 | 186718.3331
0799-Other miscellaneous piping system problems | 23 | 23 | 4378.9 | 69013.8473
0800-Drums and drum internals (single drum only) | 60 | 60 | 15262.47 | 101479.9032
0801-HP Drum (including drum level trips not attributable to other causes) | 70 | 71 | 11576.9 | 144754.3584
0802-IP Drum (including drum level trips not attributable to other causes) | 34 | 34 | 6216.41 | 29814.6237
0803-LP Drum (including drum level trips not attributable to other causes) | 20 | 20 | 2682.55 | 12421.6837
0810-Boiler supports and structures (use code 1320 for tube supports) | 6 | 6 | 1771 | 248205.1997
0820-Casing | 50 | 50 | 10813.95 | 519387.346
0830-Doors | 19 | 19 | 2853.53 | 62268.0835
0840-Refractory and insulation | 59 | 59 | 3588.9 | 175225.2822
0845-Windbox expansion joints | 8 | 8 | 587 | 20399.2999
0847-Other expansion joints | 10 | 10 | 1449.1 | 60612.5812
0850-Other internal or structural problems | 10 | 10 | 1686.4 | 1126707.5096
0855-Drum relief/safety valves (Single drum only) | 35 | 35 | 5878.44 | 136292.4627
0856-HP Drum relief/safety valves | 1 | 1 | 22 | 183.3333
0859-Tube external fins/membranes A | 2 | 2 | 360 | 78947.9998
0860-Soot blowers - air (see code 3844 for air delivery system) | 48 | 48 | 5114.54 | 60763.5896
0870-Soot blowers - steam | 68 | 68 | 7000.98 | 71372.5871
0871-Soot blowers - sonic | 1 | 1 | 0.2 | 0.15
0872-Soot blowers - water | 11 | 11 | 458.4 | 16763.5015
0873-Soot blower drives | 1 | 1 | 61 | 1411.1333
0876-Soot blower controls | 20 | 20 | 2370.75 | 8058.2327
0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | 94 | 94 | 8410.11 | 111909.2235
0885-Fly ash Removal System - wet transport | 15 | 15 | 3572.51 | 29237.1694
0890-Bottom ash systems (wet or dry) | 111 | 111 | 13913.52 | 711034.7548
0891-Bottom ash hoppers (including gates) | 25 | 25 | 6607.7 | 148692.4961
0892-Bottom ash clinker grinders | 74 | 74 | 5345.75 | 48189.915
0893-Bottom ash water pumps and motors | 6 | 6 | 574 | 10905.5831
0894-Bottom ash piping and valves | 16 | 16 | 2126.97 | 17122.3697
0895-Ashpit trouble | 4 | 4 | 362.9 | 951.1548
0896-Bottom ash dewatering bin system; instruments and controls | 1 | 1 | 159 | 3007.7499
0897-Bottom ash rotary (drag chain type) conveyor and motor | 110 | 110 | 22285.9 | 509373.5201
0898-Bottom ash pyrite hopper (pulverizer reject) system | 2 | 2 | 150 | 1294.9999
0900-Slag-tap (cyclone furnace) | 24 | 24 | 4458.38 | 187456.7708
0910-Slag-tap (other than cyclone furnace) | 3 | 3 | 338 | 4493.5999
0920-Other slag and ash removal problems A | 276 | 284 | 35966.45 | 671611.0709
0930-Bed material coolers | 2 | 2 | 649 | 36568.85
0931-Bed material transport piping/valves | 2 | 2 | 651.6 | 14427.5099
0932-Bed material transport tanks/hoppers | 2 | 2 | 354.58 | 16121.7437
0933-Bed material fans/blowers | 4 | 4 | 754.8 | 2733.1266
0936-Bed material conveyors B | 1 | 1 | 16 | 230.1333
0950-Other bed material system problems | 23 | 23 | 2031.68 | 54043.186
0972-Flue gas-solids separator controls | 1 | 1 | 8.42 | 58.94
0981-High pressure loop seal recirculation fan/blower motors | 2 | 2 | 886.52 | 35165.65
0989-Other bed solids recirculation problems | 5 | 5 | 467.1 | 9547.5497
0990-Refractory | 2 | 2 | 217.23 | 18986.9701
0991-Tube leaks | 8 | 8 | 623.71 | 331725.9692
1000-Waterwall (Furnace wall) | 907 | 907 | 262306.94 | 20428818.4297
1003-Steam generating tubes between steam drum and mud drum | 24 | 24 | 3683.9 | 567758.5046
1005-Generating tubes | 30 | 30 | 2178.59 | 232035.676
1010-Cyclone furnace (in cyclone area only) | 59 | 59 | 9381.24 | 1022876.9219
1020-Convection pass wall (water tubes only) | 40 | 40 | 16664 | 1052884.4623
1030-Boiler screen; wing wall; or slag screen (water tubes only) | 13 | 13 | 6069 | 478883.8804
1035-Platen superheater | 57 | 57 | 25852.95 | 2272033.7764
1040-First superheater | 222 | 222 | 59243.19 | 5057352.5828
1050-Second superheater | 338 | 338 | 112842.44 | 9549656.2905
1055-External superheater link tubing | 3 | 3 | 396.5 | 24661.6914
1060-First reheater | 209 | 209 | 67844.15 | 5933072.2103
1070-Second reheater | 73 | 73 | 31062.3 | 2087266.2316
1075-External reheater link tubing | 4 | 4 | 1029 | 58035.6831
1080-Economizer | 198 | 200 | 48840.19 | 3229898.3639
1090-Other boiler tube leaks | 157 | 157 | 39393.18 | 2521275.7099
1100-Waterwall (Furnace wall) | 108 | 114 | 11773.66 | 281479.8
1103-Steam generating tubes between steam drum and mud drum | 1 | 1 | 59.36 | 1142.68
1105-Generating tubes | 20 | 20 | 271.5 | 34189.1033
1120-Convection pass wall | 5 | 5 | 230.8 | 784.9166
1130-Boiler screen; wing wall; or slag screen (water tubes only) | 71 | 71 | 5889.73 | 112264.3173
1140-First superheater | 156 | 156 | 11637.49 | 475180.779
1150-Second superheater | 152 | 152 | 24432.17 | 346741.0712
1160-First reheater | 138 | 161 | 11038.3 | 461923.3737
1170-Second reheater | 16 | 16 | 2770.92 | 31943.802
1180-Economizer | 150 | 167 | 7708.15 | 123621.5662
1190-Other tube slagging or fouling | 235 | 243 | 15657.25 | 521208.6524
1191-Bed agglomeration (FBC only) | 5 | 5 | 1136.6 | 65512.3263
1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | 164 | 189 | 8166 | 134373.481
1210-Operation at reduced power to avoid slagging or fouling on waterwalls (Furnace walls) (use codes 1100-1190 to report power reductions for slag accumulation or slag removal) | 6 | 6 | 780.8 | 44267.5807
1300-Water side fouling | 5 | 5 | 657.9 | 56001.4565
1305-Fireside cleaning (which requires a full outage) Use code 1200 for cleanings that cause deratings. | 2 | 2 | 433 | 44910.25
1320-Tube supports/attachments | 2 | 2 | 408 | 20758
1330-Slag fall damage | 5 | 5 | 2950 | 520801.1151
1340-Tube modifications (including addition and removal of tubes) | 3 | 3 | 58 | 2884.4
1350-Other miscellaneous boiler tube problems | 115 | 126 | 8647.61 | 344607.3962
1360-Boiler drains system | 9 | 9 | 2148.8 | 63093.1085
1400-Forced draft fans | 269 | 276 | 27978.56 | 1512039.8678
1407-Forced draft fan lubrication system | 35 | 35 | 8666.4 | 88063.8403
1410-Forced draft fan motors | 102 | 102 | 19689.06 | 1372199.3456
1411-Forced draft fan motors - variable speed | 15 | 15 | 1972 | 14689.0492
1412-Forced draft fan drives (other than motor) | 61 | 61 | 7774.46 | 174312.4677
1413-Forced draft fan couplings | 8 | 8 | 1121.87 | 32830.4304
1415-Forced draft fan controls | 110 | 111 | 21134.14 | 146110.9376
1420-Other forced draft fan problems | 163 | 167 | 17413.9 | 1061778.9516
1421-Secondary air fans/blowers | 19 | 20 | 2058.67 | 25552.5592
1422-Secondary air fan/blower motors - single speed | 6 | 6 | 489.6 | 4191.7114
1423-Secondary air fan/blower motors - variable speed | 4 | 4 | 1665.58 | 6120.9261
1424-Secondary air fan/blower controls | 8 | 8 | 1221 | 5679.1997
1430-Air supply ducts from FD fan | 32 | 32 | 1649 | 202297.8995
1431-Air supply dampers from FD fan | 17 | 17 | 2441.99 | 23278.4048
1432-Air supply duct expansion joints | 5 | 5 | 874.47 | 40898.9962
1440-Air supply dampers | 22 | 22 | 1188.82 | 20362.5321
1450-Other air supply problems | 122 | 123 | 12799.46 | 335306.7621
1455-Induced draft fans | 1051 | 1068 | 62602.76 | 3073971.6027
1457-Induced draft fan lubrication systems | 71 | 71 | 19251.35 | 374074.4132
1460-Induced draft fan fouling | 130 | 130 | 9438.4 | 150187.997
1470-Induced draft fan motors and drives | 486 | 491 | 35334.98 | 1422513.5221
1471-Induced draft fan motors - variable speed | 71 | 71 | 11783.44 | 295179.0777
1472-Inducted draft fan coupling | 4 | 4 | 140 | 89280.95
1475-Induced draft fan controls | 142 | 142 | 27735.06 | 378558.5391
1476-Induced draft fan speed changer | 22 | 22 | 4513 | 45820.582
1480-Other induced draft fan problems | 386 | 386 | 37158.93 | 1069558.7847
1487-Air heater (tubular) | 8 | 8 | 1867.7 | 70377.1743
1488-Air heater (regenerative) | 215 | 215 | 54967.06 | 2115574.439
1489-Air heater (heat pipe; plate-type) | 6 | 6 | 603 | 17544.6664
1492-Air heater fouling (tubular) | 19 | 19 | 2111 | 214543.4164
1493-Air heater fouling (regenerative) | 373 | 375 | 17989.13 | 907285.8195
1495-Other air heater fouling (heat pipe; plate-type) | 46 | 46 | 4265 | 114957.2817
1500-Air heater soot blowers | 30 | 31 | 1955.16 | 49957.9488
1510-Flue gas ducts (except recirculation) | 68 | 76 | 3954 | 272897.6989
1512-Flue gas expansion joints | 58 | 58 | 3820 | 160698.299
1520-Flue gas dampers (except recirculation) | 19 | 19 | 2859.5 | 99777.6518
1530-Other flue gas problems | 265 | 265 | 7808.07 | 476042.1251
1535-Flue gas recirculating fan | 3 | 3 | 1025 | 206208.8998
1537-Flue gas recirculating fan lubrication systems | 1 | 1 | 427 | 505.2832
1550-Flue gas recirculation fan motors | 5 | 5 | 902 | 21774.9995
1555-Flue gas recirculation fan controls | 1 | 1 | 427 | 2277.3332
1560-Other flue gas recirculation fan problems | 7 | 7 | 1577 | 24327.799
1570-Flue gas recirculation ducts | 2 | 2 | 236 | 8783
1590-Stacks (use code 8430 for stack problems due to pollution control equipment) | 2 | 2 | 816 | 140618
1591-Stack damper and linkage | 8 | 8 | 1920.5 | 108848.3409
1592-Stack damper linkage motors | 2 | 3 | 260 | 190.9332
1599-Other miscellaneous boiler air and gas system problems | 147 | 147 | 10178.9 | 291127.1117
1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | 242 | 242 | 57496.29 | 390288.4146
1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | 366 | 367 | 42469.13 | 387444.509
1720-Desuperheater/attemperator controls | 39 | 39 | 7455.5 | 51207.0626
1740-Boiler drum gage glasses/level indicator | 61 | 63 | 15535.32 | 72959.0932
1741-Furnace and water gauge television auxiliary system | 2 | 2 | 406 | 4735.2831
1750-Burner management system | 191 | 193 | 35622.4 | 179910.3378
1760-Feedwater instrumentation (not local controls) | 30 | 30 | 5789.61 | 38302.3922
1761-Combustion /Steam condition instrumentation (not local controls) | 39 | 39 | 5578.13 | 163171.1303
1762-Desuperheater/attemperator instrumentation (not local controls) | 8 | 8 | 445 | 3421.15
1799-Other boiler instrumentation and control problems | 310 | 311 | 58872.74 | 3659115.1898
1800-Major boiler overhaul (720 hours or longer) (use for non-specific overhaul only; see page B-1) | 7 | 7 | 985 | 385255.5828
1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | 22 | 22 | 696.51 | 26504.0165
1810-Other boiler inspections | 5 | 5 | 116 | 88410.6499
1811-Boiler Inspections - problem identification/investigative | 4 | 4 | 561 | 56643.7166
1812-Boiler Inspections - scheduled or routine | 6 | 6 | 1615.6 | 118869.4333
1850-Boiler water condition (not feedwater water quality) | 947 | 948 | 126296.92 | 1073422.2995
1900-Improper balance between tube sections not due to fouling or plugging | 12 | 12 | 2178.3 | 39206.3654
1910-Inadequate air not due to equipment problems | 37 | 37 | 1962.8 | 471882.2662
1980-Boiler safety valve test | 16 | 16 | 1172.5 | 5487.1247
1990-Boiler performance testing (use code 9999 for total unit performance testing) | 19 | 19 | 2672 | 10061.2988
1999-Boiler; miscellaneous | 899 | 927 | 45037.73 | 5883666.5816
2020-Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | 15 | 15 | 941.03 | 11818.3511
2021-Power limited by rod pattern. (If rod pattern is limited by fuel limits; use appropriate code below.) | 1 | 1 | 443 | 36067.583
2031-Fuel preconditioning | 1 | 1 | 513 | 33216.75
2035-Core xenon restrictions | 1 | 1 | 8 | 65.3333
2062-Other fuel/core related instrumentation problems | 1 | 1 | 15 | 127.5
2070-Normal refueling | 2 | 2 | 1501.7 | 38305.4946
2071-Refueling equipment problems | 53 | 53 | 12516 | 1009897.7965
2090-Other core/fuel problems | 2 | 2 | 1378 | 13165.4
2120-Control rod scram mechanisms | 3 | 3 | 1841.02 | 213652.2432
2150-Control rod instrumentation | 1 | 1 | 1364.2 | 112205.45
2151-Control rod drive controls | 8 | 8 | 3474 | 98436.2
2152-Control rod drive power supplies | 7 | 7 | 3896.87 | 87349.3377
2160-Other control rod drive problems | 3 | 3 | 492.39 | 8057.6796
2176-Control rod guides (not in fuel) | 3 | 3 | 1425.49 | 515118.6457
2199-Other reactor vessel problems | 2 | 2 | 2347 | 314877.7826
2200-Reactor coolant/recirculating pumps | 13 | 13 | 5999.97 | 693922.6674
2210-Reactor coolant/recirculating pump motors | 6 | 6 | 3847.23 | 706181.5783
2220-Reactor coolant/recirculating pump MG sets | 7 | 7 | 1080 | 38109.2333
2230-Reactor coolant system piping | 2 | 2 | 2251 | 186108.1652
2270-Power operated relief and safety/relief valves | 9 | 9 | 2389 | 157258.1328
2290-Pressurizer spray valves | 2 | 2 | 2123 | 79636.25
2300-Recirculation loop flow control valves | 2 | 2 | 1442 | 132200.3662
2350-BWR feedwater controls | 9 | 9 | 445.88 | 26199.7755
2370-Reactor trip system including sensors; logic; and actuators (includes spurious trips but not valid trips) | 6 | 6 | 343 | 415.0665
2380-Reactor control system/integrated control system problems | 4 | 4 | 108 | 4427.6333
2390-Other reactor coolant system instruments and controls | 4 | 4 | 884.3 | 8321.1333
2400-Steam generator tube leaks | 1 | 1 | 1080 | 4074840
2411-Steam generator tube inspections | 1 | 1 | 1070 | 4037110
2421-Steam generator feedwater nozzles | 2 | 2 | 24.93 | 1448.9445
2440-Steam generator chemistry (excluding feedwater chemistry) | 1 | 1 | 688 | 5309.0662
2470-Blowdown system instruments and controls | 2 | 2 | 1395.95 | 65574.9481
2480-Other blowdown | 1 | 1 | 17.54 | 1029.598
2500-Steam piping (up to turbine stop valves and bypass valves) | 1 | 1 | 680 | 34000
2510-Main steam isolation valves (BWR and PWR) | 7 | 7 | 5298.13 | 957013.4402
2521-Main steam safety/relief valve testing | 1 | 1 | 1129 | 20830.05
2540-Other steam valves | 2 | 2 | 1023 | 31629.633
2550-Steam generator instruments (including piping and valves) (no RPS or SAS inputs) | 2 | 2 | 2347 | 152396.8992
2599-Other steam generator problems | 15 | 15 | 1868.7 | 127414.4348
2600-High pressure safety injection; core injection; or core spray pumps (including RCIC) | 2 | 2 | 2264.2 | 48638.7196
2603-High pressure piping | 12 | 12 | 5515 | 430479.7323
2609-Other high pressure injection problems | 1 | 1 | 883 | 19867.5
2625-Accumulators (up to and including check valves) | 1 | 1 | 1210 | 24200
2630-Safeguard actuation system (including sensors; logic; activators; and sequencers) | 5 | 5 | 3724.03 | 169353.679
2649-Other emergency core cooling/residual heat removal system problems | 1 | 1 | 806 | 421538
2650-Emergency diesel generators (including actuating systems) | 2 | 2 | 2420 | 95590
2660-Safeguard buses and associated equipment (transformers; breakers; etc.) | 2 | 2 | 273.25 | 478.1872
2699-Other electrical safety system power supplies (use codes 3600 to 3659 for nonsafety electrical systems) | 1 | 1 | 12 | 35.4
2700-Containment structure | 1 | 1 | 877 | 1073448
2720-Containment isolation valves and dampers | 3 | 3 | 2789 | 48368.8823
2799-Other containment system problems | 5 | 5 | 2088 | 44863.2496
2810-Makeup pumps | 1 | 1 | 195 | 4095
2813-Demineralizers | 1 | 1 | 27 | 8845.65
2816-Valves and piping | 2 | 2 | 19.07 | 33.2973
2819-Other CVCS and RWC problems | 7 | 7 | 2356.43 | 61751.3511
2829-Other closed cooling water system problems B | 4 | 4 | 170.57 | 2359.94
2833-Nuclear service water heat exchangers | 1 | 1 | 818 | 124336
2849-Other auxiliary feedwater problems | 1 | 1 | 15 | 60.5
2890-Condenser off-gas system problems | 3 | 3 | 814 | 15108.9997
2999-Other miscellaneous nuclear reactor problems | 2 | 2 | 2023.91 | 124785.0875
3110-Condenser tube leaks | 375 | 377 | 86099.46 | 3309927.0636
3111-Condenser tube fouling shell side | 19 | 19 | 852.8 | 15441.4712
3112-Condenser tube fouling tube side | 414 | 416 | 27881.91 | 446860.405
3113-Condenser tube and water box cleaning (including circulating water flow reversal) | 240 | 242 | 25439.49 | 224502.9183
3114-Air-cooled condenser tubes | 7 | 7 | 745 | 14185.9
3115-Air-cooled condenser pumps | 3 | 3 | 858 | 15922.7829
3116-Air-cooled condenser fans | 8 | 8 | 796.52 | 14379.2721
3117-Air-cooled condenser fan motors | 7 | 7 | 99.46 | 715.8933
3118-Other Air-cooled condenser problems | 61 | 65 | 2333.94 | 8475.4311
3119-Other condenser tube casing or shell and internal problems | 23 | 23 | 3006.5 | 133530.3324
3120-Tube sheets | 1 | 1 | 132 | 1595
3121-Expansion joint | 12 | 12 | 1373 | 135797.4499
3122-Gaskets and seals | 2 | 2 | 878 | 114002.2332
3123-Hot well | 9 | 9 | 1266.8 | 17775.163
3124-Tube sheet fouling | 64 | 65 | 3373.7 | 44294.2525
3129-Other condenser casing or shell and internal problems | 219 | 221 | 5301.36 | 254052.6669
3130-Air ejectors | 59 | 59 | 4085.05 | 21356.2554
3131-Air ejector piping and valves | 7 | 7 | 972.4 | 9803.6833
3132-Inter and after condensers | 3 | 3 | 474.1 | 6364.8514
3133-Vacuum pumps | 71 | 71 | 12573.98 | 308077.4072
3134-Vacuum pump piping and valves | 21 | 21 | 6701.03 | 61714.5184
3135-Vacuum pump motor and auxiliaries | 8 | 8 | 837 | 19002.7833
3139-Other air extraction system problems - general | 17 | 17 | 1731.55 | 23533.4752
3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | 444 | 463 | 29373.47 | 448720.9233
3150-Hot well level controls | 40 | 40 | 8202.41 | 196431.296
3151-Vacuum pump and air ejector controls | 5 | 5 | 1136.43 | 6923.6292
3152-Air-cooled condenser controls | 3 | 3 | 270 | 1047.4999
3159-Other condensing system controls and instruments | 22 | 22 | 3533 | 16078.1871
3170-Condenser inspection (use code 3110 to report looking for tube leaks) | 3 | 3 | 1190 | 14484.5663
3171-Air-cooled condenser inspections | 1 | 1 | 56 | 690.6666
3186-Auxiliary Condenser and Associated Equipment | 41 | 41 | 4687 | 33807.1199
3190-Air leakage (for losses not attributable to previously noted equipment related codes) | 39 | 39 | 5395.22 | 215744.8702
3199-Other miscellaneous condensing system problems | 126 | 128 | 10824 | 187574.109
3210-Circulating water pumps | 278 | 278 | 22249.47 | 1018146.0623
3211-Circulating water pump motors | 263 | 271 | 26936.35 | 1139339.3618
3220-Circulating water piping | 50 | 50 | 13838.62 | 1905558.9856
3221-Circulating water piping fouling | 12 | 12 | 1590.32 | 8557.2387
3230-Circulating water valves | 98 | 98 | 10400.04 | 147356.9037
3233-Circulating water priming system | 2 | 2 | 366.53 | 795.7618
3235-Cooling tower booster pump | 8 | 8 | 2380.98 | 29592.5758
3236-Cooling tower booster motor | 47 | 47 | 3488.08 | 36236.5522
3238-Cooling tower fan motors | 44 | 44 | 1955.61 | 36255.9457
3239-Cooling tower fan motors - variable speed | 2 | 2 | 105 | 435.8333
3240-Cooling tower fans | 71 | 71 | 3193.06 | 245764.6339
3241-Cooling tower efficiency below design | 33 | 33 | 416.5 | 48307.8833
3242-Cooling tower fill damage | 5 | 5 | 202.84 | 1736.1833
3243-Cooling tower icing | 21 | 21 | 2163 | 147136.0491
3245-Other cooling tower problems | 32 | 32 | 3994.17 | 332565.423
3246-Cooling tower fouling | 3 | 3 | 179.46 | 1271.9545
3247-Cooling tower instrumentation | 22 | 22 | 2204.78 | 10819.5628
3250-Circulating water system instruments and controls | 25 | 26 | 3459.04 | 10341.5378
3260-Traveling screens | 70 | 70 | 6982.04 | 237059.7344
3261-Traveling screen fouling | 26 | 26 | 4632.97 | 48026.1992
3269-Circulating water biological conditions (ie; zebra mussels) | 19 | 19 | 1493 | 28052.8328
3270-Intake system problems other than traveling screens | 136 | 137 | 13012.75 | 308415.3015
3271-Intake grating fouling | 9 | 9 | 1256.4 | 26832.683
3272-Circulating water screenwash system | 2 | 2 | 393 | 9298.5
3273-Debris in circulating water from outside sources (leaves; mud; etc.) | 107 | 110 | 12944.75 | 36578.7856
3274-Ice blockages at intake structures including frazil ice; sheets; blocks of ice; etc B | 6 | 6 | 397 | 2785.3499
3280-High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | 199 | 199 | 7083.2 | 79497.9082
3281-Circulating water tempering system | 2 | 2 | 38 | 248.75
3285-Circulating water chemistry | 10 | 10 | 1134.3 | 22352.1962
3299-Other circulating water system problems | 71 | 71 | 8245.53 | 172728.5915
3300-Condensate water pre-treatment | 9 | 9 | 1388 | 31921.3911
3310-Condensate/hotwell pumps | 182 | 182 | 22239.12 | 507827.1821
3311-Condensate/hotwell pump motor | 49 | 49 | 5049 | 356500.9655
3312-Condensate booster pump | 19 | 19 | 3459.88 | 63436.3425
3313-Condensate booster pump motor | 7 | 7 | 1275 | 31492.2329
3314-Condensate booster pump motor - variable speed | 2 | 2 | 450.18 | 4847.9063
3315-Condensate booster pump drive (other than 3313 and 3314) | 1 | 1 | 115 | 404.4166
3320-Condensate piping | 22 | 22 | 4365.97 | 35650.424
3330-Condensate valves | 45 | 45 | 8134.74 | 118101.1375
3339-LP heater head leaks | 1 | 1 | 72 | 138
3340-LP heater tube leaks | 34 | 34 | 3803.76 | 305864.8337
3341-Other LP heater - general | 23 | 23 | 2734.71 | 74688.9993
3342-IP heater tube leaks | 6 | 6 | 783.65 | 26880.0472
3343-Other IP heater - general | 13 | 13 | 2691 | 49276.1487
3344-Deaerator (including level control) | 135 | 151 | 16707.35 | 343255.2209
3350-Condensate polishing and filtering systems | 33 | 33 | 7218.27 | 131246.9713
3351-Chemical addition systems | 11 | 11 | 1074 | 14824.2161
3352-Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | 195 | 198 | 23939.13 | 445436.1114
3360-Condensate makeup and return (including storage tanks) | 23 | 23 | 2665.5 | 22053.2155
3370-Condensate system controls and instrumentation (not hotwell level; heater level; or deaerator level controls: see codes 3150-3159; 3344; 3502. | 28 | 29 | 3808.68 | 15102.9569
3380-Condensate coolers | 1 | 1 | 30 | 57
3399-Other miscellaneous condensate system problems | 66 | 66 | 8810.29 | 237978.2239
3401-Startup feedwater pump | 22 | 22 | 6999.95 | 179560.5555
3402-Startup feedwater pump drives - all types | 6 | 6 | 2322.19 | 292869.3644
3407-Feedwater pump suction screens | 15 | 15 | 2547 | 16940.4495
3408-Feedwater pump drive - local controls | 91 | 91 | 27000.73 | 257372.4582
3409-Feedwater pump drive motor - variable speed | 43 | 43 | 3066.5 | 127216.4157
3410-Feedwater pump | 608 | 609 | 114723.84 | 4387554.5322
3411-Feedwater pump drive - motor | 138 | 138 | 14869.03 | 1498363.3898
3412-Feedwater pump drive - steam turbine | 212 | 214 | 52547.22 | 5597107.6244
3413-Feedwater pump coupling and drive shaft | 44 | 44 | 9834.35 | 458832.8072
3414-Feedwater pump local controls | 81 | 81 | 21459.09 | 229017.0609
3415-Feedwater pump/drive lube oil system | 163 | 164 | 34529.43 | 647940.1636
3416-Other feedwater pump problems | 174 | 175 | 36679.62 | 981050.1603
3417-Feedwater pump drive - main shaft | 6 | 6 | 1981.6 | 243126.8157
3418-Feedwater pump drive - other | 11 | 11 | 1242.87 | 33989.2764
3419-Feedwater pump drive - gear | 1 | 1 | 37 | 3811
3420-Feedwater piping and supports | 42 | 42 | 10389.01 | 245656.7547
3430-Feedwater regulating (boiler level control) valve | 168 | 168 | 33049.26 | 690428.2229
3431-Other feedwater valves | 208 | 208 | 50665.69 | 1215316.2553
3439-HP heater head leaks | 42 | 42 | 3291.87 | 76891.9467
3440-High pressure heater tube leaks | 287 | 295 | 21837.15 | 1567848.6695
3441-Other high pressure heater problems (see condensate system for LP and IP heater codes) | 137 | 137 | 18283.86 | 1083148.8391
3451-Feedwater Booster Pump Suction Screens | 1 | 1 | 127.3 | 1665.5083
3452-Feedwater Booster Pump Drive - Local Controls | 1 | 1 | 633 | 8334.4996
3454-Feedwater Booster Pump | 9 | 9 | 2436 | 35464.2333
3455-Feedwater Booster Pump Drive - Motor | 8 | 8 | 2587.8 | 26586.4226
3456-Feedwater Booster Pump Drive - Steam Turbine | 2 | 2 | 698 | 5918.9664
3457-Feedwater Booster Pump Coupling and Drive Shaft | 5 | 5 | 1037 | 151787.1996
3458-Feedwater Booster Pump Local Controls | 2 | 2 | 497.9 | 966.9715
3459-Feedwater Booster Pump/Drive Lube Oil System | 3 | 3 | 923 | 3000.1663
3460-Other Feedwater Booster Pump Problems | 2 | 2 | 885 | 73705.5163
3499-Other feedwater system problems | 179 | 180 | 29374.55 | 871319.4994
3501-Heater drain pumps | 27 | 27 | 3439 | 232097.6384
3502-Heater level control | 59 | 59 | 8508.6 | 104910.3661
3503-Heater drain piping | 16 | 16 | 1679 | 60000.9329
3504-Heater drain valves | 24 | 26 | 2623.21 | 52641.5982
3505-Heater drain pump drive | 7 | 7 | 1918 | 18518.3662
3509-Other heater drain system problems | 10 | 10 | 756.41 | 21118.3347
3520-HP Extraction steam piping | 14 | 14 | 4495.5 | 412745.0629
3521-HP Extraction steam valves | 26 | 26 | 3121.35 | 53138.4941
3522-HP Extraction steam instruments and controls | 4 | 4 | 859 | 4791.2499
3529-Other HP extraction steam system problems | 4 | 4 | 150 | 74747.2333
3530-IP Extraction steam piping | 3 | 3 | 1568 | 54075.0661
3531-IP Extraction steam valves | 15 | 15 | 3691.5 | 54808.5485
3532-IP Extraction steam instruments and controls | 4 | 4 | 1237 | 4242.7664
3539-Other IP extraction steam system problems | 4 | 4 | 381.8 | 1509.9216
3540-LP Extraction steam piping | 9 | 9 | 2003 | 103980.8496
3541-LP Extraction steam valves | 9 | 9 | 1907.57 | 33256.878
3542-LP Extraction steam instruments and controls | 2 | 2 | 31 | 38.3333
3549-Other LP extraction steam system problems | 6 | 6 | 1051.65 | 67404.1506
3600-Switchyard transformers and associated cooling systems - external | 24 | 24 | 3257.06 | 56735.0477
3601-Switchyard transformers and associated cooling systems ? (not outside management control) | 6 | 6 | 396.58 | 3301.3289
3610-Switchyard circuit breakers - (not outside management control) | 54 | 54 | 6971.2 | 272742.4886
3611-Switchyard circuit breakers - external | 133 | 133 | 22736.84 | 516710.1809
3612-Switchyard system protection devices - external | 85 | 85 | 7360.92 | 385896.6131
3613-Switchyard system protection devices - (not outside management control) | 37 | 37 | 5189.58 | 127316.5528
3618-Other switchyard equipment ? (not outside management control) | 25 | 25 | 4611.15 | 120142.1554
3619-Other switchyard equipment - external | 318 | 321 | 18791.66 | 1029614.8375
3620-Main transformer | 406 | 409 | 56389.33 | 14747120.2935
3621-Unit auxiliaries transformer | 109 | 110 | 17393.84 | 945834.7812
3622-Station service startup transformer | 24 | 24 | 7258.09 | 423580.3164
3623-Auxiliary generators | 4 | 4 | 639.9 | 6031.7796
3624-Generator Voltage Supply System | 13 | 13 | 2497.28 | 22083.9824
3629-Other switchyard or high voltage system problems - external | 407 | 412 | 17166.39 | 440842.7654
3630-480-volt transformers | 206 | 249 | 8557.08 | 45679.9565
3631-480-volt circuit breakers | 172 | 175 | 27982.44 | 296925.1605
3632-480-volt conductors and buses | 49 | 49 | 7511.55 | 136072.6931
3634-480-volt protection devices | 21 | 21 | 2802.72 | 42371.7818
3639-Other 480-volt problems | 28 | 28 | 2915.56 | 63543.2065
3640-AC instrument power transformers | 34 | 34 | 4298.4 | 59857.8083
3641-AC Circuit breakers | 90 | 90 | 16752.24 | 221546.7161
3642-AC Conductors and buses | 28 | 28 | 3916.4 | 769399.0265
3643-AC Inverters | 18 | 18 | 3708.9 | 86861.2603
3644-AC Protection devices | 167 | 167 | 19235.65 | 436538.5132
3649-Other AC instrument power problems | 38 | 38 | 7518.01 | 28752.9515
3650-DC instrument power battery chargers | 26 | 26 | 3200.69 | 35013.4048
3651-DC circuit breakers | 14 | 14 | 1513.44 | 13774.5339
3652-DC conductors and buses | 14 | 14 | 2715.59 | 94450.5307
3653-DC protection devices | 27 | 27 | 1984.31 | 48463.0306
3659-Other DC power problems | 69 | 69 | 7861.73 | 208174.6872
3660-4160-volt transformers | 31 | 31 | 6187.4 | 81187.6055
3661-4160-volt circuit breakers | 150 | 150 | 31144.48 | 817099.7757
3662-4160-volt conductors and buses | 47 | 47 | 15126 | 565626.9286
3663-4160-volt insulators | 2 | 2 | 102.7 | 875.595
3664-4160-volt protection devices | 25 | 25 | 4191.75 | 85202.0834
3669-Other 4160-volt problems | 11 | 11 | 3596.79 | 248791.3902
3670-12kV transformers | 11 | 11 | 1039.28 | 19428.5702
3671-12kV circuit breakers | 103 | 103 | 9456.07 | 888578.6939
3672-12kV conductors and buses | 41 | 41 | 6901.71 | 945791.9053
3673-12kV insulators | 17 | 17 | 1573 | 9165.2495
3674-12kV protection devices | 27 | 27 | 3094.24 | 57301.5117
3679-Other 12kV problems | 15 | 15 | 1007.21 | 8449.1683
3680-Other voltage system transformers | 33 | 33 | 5969.26 | 69408.1175
3681-Other voltage system breakers | 27 | 27 | 5045.7 | 70946.4391
3682-Other voltage system conductors and buses | 28 | 29 | 6712.93 | 280019.116
3683-Other voltage system insulators | 15 | 15 | 890.8 | 102749.1582
3684-Other voltage system protection devices | 40 | 40 | 3752.89 | 544874.9146
3689-Other Other voltage system problems | 51 | 51 | 7455.22 | 40689.5022
3690-Station Service Power Distribution System; General | 48 | 48 | 5352.32 | 127508.9583
3700-Power Station switchyard (non generating unit equipment) | 42 | 42 | 4984.04 | 83378.002
3710-Transmission line (connected to powerhouse switchyard to 1st Substation) | 126 | 127 | 10467.44 | 113410.3643
3720-Transmission equipment at the 1st substation) | 61 | 62 | 6988.52 | 119257.0202
3730-Transmission equipment beyond the 1st substation | 99 | 99 | 6957.52 | 68991.2296
3800-Open cooling water pumps and motors | 3 | 3 | 572 | 3315.6832
3801-Open cooling water piping | 3 | 3 | 652.04 | 15078.4533
3802-Open cooling water valves | 2 | 2 | 492 | 1122.5998
3804-Open cooling water system fouling | 1 | 1 | 85 | 140.25
3805-Open cooling water system instrumentation | 2 | 2 | 878 | 8990.4827
3806-Open cooling water strainer | 3 | 3 | 61.01 | 209.313
3809-Other open cooling water problems | 1 | 1 | 780 | 3783
3810-Service water pumps and motors | 16 | 16 | 3157 | 221102.6987
3811-Service water piping | 29 | 29 | 4607.75 | 134934.5584
3812-Service water valves | 17 | 17 | 1642.4 | 24002.1597
3813-Service water heat exchangers | 9 | 9 | 695.92 | 16638.2684
3814-Service water system fouling | 16 | 16 | 1393.75 | 4182.0988
3815-Service water strainer | 1 | 1 | 202 | 168.3333
3819-Other service water problems A | 37 | 37 | 1402.31 | 32489.309
3820-Closed cooling water pumps | 22 | 22 | 2005.75 | 7773.9191
3821-Closed cooling water piping | 24 | 24 | 2782.88 | 87827.5792
3822-Closed cooling water valves | 7 | 7 | 772.42 | 12428.2857
3823-Closed cooling water heat exchangers | 20 | 20 | 2671.92 | 38948.0693
3824-Closed cooling water system fouling | 9 | 9 | 1652.91 | 17885.2795
3825-Closed cooling water instrumentation | 3 | 3 | 132.13 | 162.9603
3829-Other closed cooling water system problems A | 33 | 33 | 3103.45 | 145896.6529
3830-Auxiliary boiler | 30 | 30 | 8258.54 | 134380.3307
3831-Auxiliary steam piping | 12 | 12 | 3118.2 | 57665.2845
3832-Auxiliary steam valves | 7 | 7 | 2357.6 | 15186.0334
3833-Auxiliary steam controls and instruments | 26 | 26 | 5746.57 | 40534.9748
3834-Auxiliary boiler tube leaks | 13 | 13 | 1255 | 83960.3612
3835-Auxiliary boiler burner management system | 2 | 2 | 674 | 8302.1831
3836-Steam Transfer to Other Unit | 213 | 213 | 9959.46 | 204722.0264
3839-Other auxiliary steam problems (also see extraction steam codes 3520 to 3529; startup bypass codes 0630 to 0660; and soot blower steam code 0870) | 33 | 33 | 4196.11 | 404498.6352
3840-Service air compressors | 21 | 21 | 2178.42 | 15105.0427
3841-Service air piping | 7 | 7 | 1019 | 1463.0831
3842-Service air valves | 2 | 2 | 57 | 110.6833
3843-Service air dryers | 5 | 5 | 165 | 244.3833
3844-Soot blowing air compressor and system | 30 | 30 | 2795.45 | 38804.8214
3849-Other service air problems | 12 | 12 | 1059.44 | 4184.5886
3850-Instrument air compressors | 50 | 50 | 11892.95 | 128181.8239
3851-Instrument air piping | 22 | 22 | 4040.61 | 103876.5987
3852-Instrument air valves | 15 | 15 | 1992.7 | 20331.9343
3853-Instrument air dryers | 16 | 16 | 2109.51 | 24592.6953
3859-Other instrument air problems | 19 | 19 | 3033.51 | 23752.3778
3861-Fire protection system piping | 23 | 23 | 628.51 | 8572.6359
3862-Fire protection system valves | 10 | 10 | 631.68 | 11855.8475
3863-Fire protection system fouling | 1 | 1 | 103.45 | 81.0358
3864-Fire protection system instrumentation and controls | 74 | 74 | 6041.17 | 107017.4603
3869-Other fire protection system problems | 49 | 49 | 4087.86 | 86156.4675
3870-Fuel Gas Compressor and Motors | 54 | 54 | 4360.42 | 32365.4686
3871-Fuel Gas Compressor Piping | 5 | 5 | 531.18 | 18318.7986
3872-Fuel Gas Compressor Valves | 91 | 91 | 3304.75 | 12175.9754
3873-Fuel Gas Compressor Heat Exchangers | 14 | 14 | 610 | 7765.4332
3874-Fuel Gas Compressor Controls and Instrumentation | 52 | 52 | 3851.67 | 67596.3741
3875-Fuel Gas Compressor Filters | 3 | 3 | 244.76 | 504.5613
3876-Fuel Gas Compressor Fire System | 3 | 3 | 141 | 257.7167
3879-Fuel Gas Compressor - other | 63 | 63 | 3083.59 | 4788.9859
3880-Seal air fan | 2 | 2 | 71 | 135
3882-Seal air control dampers and drives | 2 | 2 | 93 | 19.5
3889-Other seal air fan system problems | 1 | 1 | 190.7 | 162.095
3898-Miscellaneous plant auxiliary process and services instrumentation and controls | 59 | 61 | 6265.28 | 41891.3131
3899-Other miscellaneous auxiliary system problems | 155 | 158 | 18753.8 | 290049.4553
3950-Process computer | 60 | 60 | 6907.93 | 215838.6409
3960-Thermal derating (thermal efficiency losses in balance of plant when specific cause(s) unknown) | 164 | 169 | 2357.22 | 91953.2983
3970-Distributive Control System (DCS) - process computer | 67 | 68 | 8787.16 | 96068.8948
3971-DCS - data highway | 73 | 73 | 9297.1 | 120222.518
3972-DCS - hardware problems (including card failure) | 172 | 173 | 24391.19 | 345148.7632
3973-DCS - internal and termination wiring | 18 | 18 | 1198.06 | 7237.5747
3974-DCS - logic problems | 104 | 105 | 16973.84 | 173863.6826
3975-DCS - upgrades | 64 | 64 | 5378.81 | 128760.2313
3979-Other DCS problems | 68 | 68 | 10794.4 | 130092.759
3980-Programmable Logic Controller (PLC) | 7 | 7 | 988.85 | 5415.3055
3981-PLC - data highway | 18 | 18 | 2701.5 | 57282.399
3982-PLC - hardware problems (including card failure) | 61 | 61 | 4801.46 | 41889.7543
3983-PLC - internal and termination wiring | 6 | 6 | 2192.06 | 11648.7346
3984-PLC - logic problems | 14 | 14 | 635.51 | 15115.268
3985-PLC - upgrades | 4 | 4 | 44 | 541.2
3989-Other PLC problems | 18 | 18 | 1389.38 | 21580.3765
3995-Powerhouse heating and ventilating systems | 7 | 7 | 1200.5 | 19311.0746
3996-Air conditioning systems - rooms and areas | 10 | 10 | 4635.16 | 815234.5691
3999-Other miscellaneous balance of plant problems | 540 | 541 | 66258.11 | 2117880.0577
4000-Outer casing A | 5 | 5 | 2267 | 99064.2825
4001-Inner casing C | 3 | 3 | 364.3 | 255.9183
4009-Nozzle bolting A | 1 | 1 | 5 | 47.9167
4010-Nozzles and nozzle blocks C | 10 | 10 | 304 | 819537.5666
4012-Buckets or blades A | 5 | 5 | 1007.1 | 504751.9799
4013-Diaphragms unit and shroud type | 1 | 1 | 72 | 33339.6
4014-Bucket or blade fouling C | 143 | 143 | 1426.23 | 328766.1979
4020-Shaft seals B | 69 | 127 | 2920.4 | 1037045.1925
4030-Rotor shaft C | 39 | 40 | 11427.68 | 3269189.4916
4040-Bearings C | 104 | 104 | 19039.6 | 1125963.5503
4041-HP steam turbine thrust bearings | 13 | 13 | 2358.62 | 632107.3201
4099-Other high pressure turbine problems | 1490 | 1728 | 52058.88 | 2305599.4133
4110-Nozzles and nozzle blocks B | 2 | 2 | 121.55 | 307.9266
4120-Shaft seals C | 3 | 3 | 877 | 4898.6497
4130-Rotor shaft B | 2 | 2 | 640 | 15149.3331
4140-Bearings D | 33 | 33 | 5759.57 | 385627.7966
4141-IP steam turbine thrust bearings | 3 | 3 | 958 | 26876.4497
4199-Other intermediate pressure turbine problems | 19 | 19 | 7866.65 | 180250.7734
4201-Inner casing A | 4 | 4 | 726 | 2250.6
4211-Diaphragms C | 7 | 7 | 2609 | 198516.1666
4212-Buckets or blades C | 67 | 78 | 4426 | 1896448.3153
4213-Bucket or blade fouling A | 1 | 1 | 266 | 17618.0666
4215-Wheels or spindles B | 4 | 4 | 1060 | 572947.6662
4220-Shaft seals D | 10 | 10 | 2614.52 | 62270.7425
4230-Rotor shaft A | 10 | 10 | 2025.82 | 260736.9195
4240-Bearings E | 30 | 30 | 8735.4 | 772494.5495
4250-Other low pressure turbine problems | 201 | 201 | 14788.3 | 1683700.9408
4260-Main stop valves | 120 | 121 | 17917.24 | 510130.9774
4261-Control valves | 753 | 762 | 73099.8 | 4513895.4466
4262-Intercept valves | 43 | 45 | 10513.2 | 166111.3127
4263-Reheat stop valves | 37 | 37 | 11282.96 | 262339.2203
4264-Combined intercept valves | 7 | 7 | 971 | 8177.0163
4265-Miscellaneous drain and vent valves | 21 | 21 | 6037.04 | 203730.6323
4266-Main stop valve testing | 23 | 23 | 2940.38 | 16724.1883
4267-Control valve testing | 127 | 128 | 16823.18 | 42779.2636
4268-Reheat/intercept valve testing | 12 | 12 | 3103 | 8874.9156
4269-Other turbine valves (including LP steam admission valves) | 78 | 78 | 17004.71 | 303842.442
4270-Crossover or under piping | 26 | 26 | 9764.37 | 781070.3651
4279-Miscellaneous turbine piping | 49 | 49 | 14018.98 | 1078102.0617
4280-Lube oil pumps A | 37 | 37 | 8895.18 | 508119.9682
4281-Lube oil coolers A | 9 | 9 | 906.8 | 25260.0332
4282-Lube oil conditioners | 1 | 1 | 155 | 41.3332
4283-Lube oil system valves and piping | 34 | 34 | 8776.04 | 384548.0232
4284-Lube oil pump drive | 7 | 7 | 1433.6 | 78919.7398
4289-Other lube oil system problems | 57 | 57 | 8561.62 | 621957.753
4290-Hydraulic system pumps | 18 | 18 | 5816.25 | 48974.7439
4291-Hydraulic system coolers | 2 | 2 | 601.7 | 11987.15
4292-Hydraulic system filters | 10 | 10 | 1965.72 | 12497.8244
4293-Hydraulic system pipes and valves | 119 | 120 | 31623.86 | 794309.9379
4299-Other hydraulic system problems | 98 | 100 | 21017 | 415076.5068
4300-Turbine supervisory system (use codes 4290 to 4299 for hydraulic oil) | 74 | 74 | 17940.53 | 221429.9038
4301-Turbine governing system | 92 | 92 | 12979.41 | 456066.1266
4302-Turbine trip devices (including instruments) | 229 | 229 | 55273.94 | 784805.0444
4303-Exhaust hood and spray controls | 9 | 9 | 2615.71 | 9441.3892
4304-Automatic turbine control systems - mechanical | 13 | 13 | 2447.14 | 55975.797
4305-Automatic turbine control systems - mechanical - hydraulic | 24 | 24 | 5372.3 | 379100.5546
4306-Automatic turbine control systems - electro-hydraulic - analog | 13 | 13 | 2911.05 | 12386.8081
4307-Automatic turbine control systems - electro-hydraulic - digital | 33 | 33 | 8346.17 | 584497.4446
4308-Automatic turbine control systems - digital control and monitoring | 51 | 51 | 12849.1 | 132351.8324
4309-Other turbine instrument and control problems | 172 | 175 | 34013.44 | 459726.494
4310-Steam Turbine Control System - data highway | 11 | 11 | 1929.14 | 6671.8136
4311-Steam Turbine Control System - hardware problems (including card failure) | 47 | 47 | 10437.93 | 124491.5086
4312-Steam Turbine Control System - internal and termination wiring | 17 | 17 | 3257.7 | 34826.1652
4313-Steam Turbine Control System - logic problems | 46 | 46 | 10014.36 | 78006.8869
4400-Major turbine overhaul (720 hrs or longer) (use for non-specific overhaul only; see page B-1) | 5 | 5 | 1749.8 | 11329.0026
4401-Inspection F | 3 | 3 | 822 | 102677.7666
4402-Minor turbine overhaul (less than 720 hrs.) (use for non-specific overhaul only; see page B-1) | 3 | 3 | 1285 | 10317.2829
4410-Turning gear and motor A | 47 | 47 | 9538.94 | 770055.4469
4411-Steam turbine gear box (single shaft configuration) | 1 | 1 | 250 | 1512.5
4412-Steam turbine clutch (single shaft configuration) | 4 | 4 | 796.84 | 59967.2031
4420-Vibration of the turbine generator unit that cannot be attributed to a specific cause such as bearings or blades (use this code for balance moves) | 201 | 201 | 47749.8 | 1700915.4007
4430-Gland seal system | 64 | 64 | 14865.43 | 268488.4004
4440-Moisture separator/reheater (nuclear including MSR drains; controls; etc.) | 9 | 9 | 3867.56 | 265588.8226
4445-Steam reheater | 4 | 4 | 820.3 | 9617.4682
4450-Water induction | 6 | 6 | 1070.9 | 8358.8446
4460-Turbine overspeed trip test | 17 | 17 | 4501.25 | 21208.957
4470-Differential expansion | 56 | 56 | 18711.79 | 179602.8122
4490-Turbine performance testing (use code 9999 for total unit performance testing) | 25 | 25 | 2557.69 | 8934.12
4499-Other miscellaneous steam turbine problems | 478 | 504 | 50450.99 | 4188216.3413
4500-Rotor windings (including damper windings and fan blades on hydro units) | 34 | 34 | 4172.95 | 6696045.9126
4510-Rotor collector rings | 15 | 15 | 1634.36 | 48672.6389
4511-Rotor; General | 53 | 53 | 7686.9 | 10402107.708
4520-Stator windings; bushings; and terminals | 66 | 66 | 12479.03 | 7298527.1858
4530-Stator core iron | 9 | 9 | 593 | 2744.1999
4535-Stator; General | 49 | 50 | 10471.98 | 6426330.781
4536-Generator heaters | 2 | 2 | 133 | 2591.9499
4540-Brushes and brush rigging | 21 | 21 | 3662.39 | 230822.7767
4550-Generator bearings and lube oil system (including thrust bearings on hydro units) | 212 | 213 | 14732.84 | 2077293.1977
4551-Generator bearings | 65 | 65 | 7593.82 | 967247.2464
4552-Generator lube oil system | 52 | 52 | 3121.76 | 35704.3445
4555-Bearing cooling system A | 73 | 73 | 2864.15 | 112392.4607
4560-Generator vibration (excluding vibration due to failed bearing and other components) | 162 | 163 | 22161.62 | 1062007.0776
4570-Generator casing | 5 | 5 | 1441.57 | 148815.9622
4590-Generator brakes | 51 | 52 | 4882.58 | 126841.7474
4600-Exciter drive - motor | 28 | 28 | 5765.23 | 268731.473
4601-Exciter field rheostat | 22 | 22 | 2304.4 | 13884.9381
4602-Exciter commutator and brushes | 35 | 35 | 4404.32 | 249096.7321
4603-Solid state exciter element | 68 | 68 | 9907.51 | 371674.2098
4604-Exciter drive - shaft | 6 | 6 | 1319 | 9638.8833
4605-Exciter transformer | 289 | 306 | 3964.28 | 659897.5867
4609-Other exciter problems | 700 | 703 | 116737.32 | 4195343.3027
4610-Hydrogen cooling system piping and valves | 27 | 27 | 5221.5 | 251852.7812
4611-Hydrogen coolers | 72 | 72 | 9510.38 | 389235.1705
4612-Hydrogen storage system | 1 | 1 | 115 | 111780
4613-Hydrogen seals | 21 | 21 | 5802.78 | 891624.4127
4619-Other hydrogen system problems | 41 | 41 | 8130.72 | 284852.2906
4620-Air cooling system | 61 | 61 | 5669.37 | 115259.536
4630-Liquid cooling system | 82 | 82 | 16470.76 | 227542.285
4640-Seal oil system and seals A | 51 | 51 | 10925 | 434307.8802
4650-Other cooling system problems | 53 | 53 | 11461.21 | 182057.1119
4700-Generator voltage control | 243 | 244 | 33559.47 | 895105.9878
4710-Generator metering devices | 65 | 65 | 9649.71 | 132512.8575
4720-Generator synchronization equipment | 316 | 333 | 27813.31 | 306997.3773
4730-Generator current and potential transformers | 95 | 95 | 20329.82 | 398635.0156
4740-Emergency generator trip devices | 256 | 256 | 37171.06 | 1691360.8577
4750-Other generator controls and metering problems | 334 | 337 | 30622.14 | 546715.2369
4800-Generator main leads | 43 | 43 | 5933.59 | 495244.9311
4805-Generator Bus Duct Cooling System | 30 | 30 | 7119.08 | 994476.1091
4810-Generator output breaker | 276 | 280 | 30747.25 | 1569367.1149
4831-Minor overhaul (less than 720 hrs.) (use for non-specific overhaul only; see page B-1) | 1 | 1 | 139.16 | 15569.6846
4840-Inspection E | 3 | 3 | 234.2 | 511.5332
4842-Reactive and capability testing | 17 | 17 | 1512.37 | 54322.3774
4850-Core monitor alarm | 5 | 5 | 408.94 | 5259.3088
4860-Generator Neutral Grounding Equipment | 33 | 33 | 5997.34 | 418632.2822
4899-Other miscellaneous generator problems | 414 | 414 | 48592.04 | 2475336.6892
5000-Inlet air ducts A | 29 | 31 | 1932.9 | 48653.1106
5001-Inlet air vanes / nozzles | 145 | 146 | 17712.74 | 226140.0308
5002-Inlet air filters A | 76 | 76 | 6988.29 | 66515.4035
5003-Inlet cone | 1 | 2 | 0 | 0
5004-Inlet air chillers B | 37 | 37 | 1632.14 | 82451.8907
5005-Inlet air evaporative coolers B | 43 | 43 | 969.03 | 42252.1291
5006-Inlet air foggers B | 3 | 3 | 177 | 593.7333
5009-Other inlet air problems A | 135 | 156 | 6992.65 | 127971.8018
5010-High pressure shaft D | 1 | 1 | 158.3 | 153.0232
5012-High pressure blades/buckets B | 32 | 38 | 2584.71 | 1498930.7499
5013-Compressor casing and bolts | 8 | 8 | 742.72 | 604584.2145
5014-Compressor diaphragms | 5 | 5 | 491.63 | 4672.324
5016-High pressure compressor bleed valves | 155 | 156 | 18938.48 | 108805.3106
5017-Low pressure compressor bleed valves | 40 | 40 | 4634.3 | 34982.0691
5019-Other high pressure problems A | 6 | 6 | 425.49 | 5854.3261
5020-Low pressure shaft D | 1 | 1 | 147.26 | 8614.71
5022-Low pressure blades/buckets A | 83 | 99 | 2444.72 | 464266.3938
5029-Other low pressure problems E | 16 | 16 | 1517.06 | 58658.4793
5035-Compressor Washing | 2 | 2 | 406.69 | 1261.325
5039-Other compressor problems | 36 | 38 | 2975.29 | 403732.4924
5040-Fuel tanks B | 5 | 5 | 469.51 | 4925.4525
5041-Fuel piping and valves A | 674 | 682 | 85693.23 | 956936.3904
5042-Fuel nozzles/vanes B | 75 | 76 | 9748.59 | 1618132.3951
5043-Fuel filters A | 46 | 46 | 5638.31 | 62788.4803
5044-Liquid fuel oil pump A | 20 | 20 | 1309.81 | 7844.4893
5046-Liquid fuel oil transfer/forwarding pump B | 18 | 18 | 1329.5 | 3982.9978
5047-Liquid fuel purge system A | 42 | 42 | 5451.91 | 35123.4316
5048-Gas fuel system B | 685 | 695 | 77226.05 | 663383.2142
5049-Other fuel system problems B | 392 | 398 | 36120.15 | 383913.9455
5050-Ignition system A | 333 | 342 | 39090.53 | 226774.8992
5051-Pilot fuel piping and valves A | 70 | 72 | 8910.24 | 42891.8906
5052-Pilot fuel nozzles/vanes B | 18 | 18 | 2854.85 | 35175.4002
5053-Pilot fuel filters A | 1 | 1 | 365 | 5487.1665
5054-Water Injection System (Gas Turbine) | 122 | 122 | 9631.89 | 190117.6557
5060-Atomizing air system B | 28 | 28 | 3649.4 | 32098.6571
5070-Combustor casing A | 7 | 7 | 784 | 12053.7412
5071-Combustor liner B | 15 | 15 | 2798 | 135084.6324
5072-Combustor caps B | 3 | 3 | 645 | 1627.8498
5073-Flame scanners B | 100 | 103 | 11798.63 | 59948.8178
5074-Flashback including instruments | 79 | 103 | 9087.33 | 69831.0461
5075-Blade Path Temperature Spread A | 238 | 243 | 40791.84 | 1288729.892
5079-Other combustor problems B | 511 | 548 | 67564.93 | 1120980.4868
5080-High pressure shaft C | 3 | 3 | 303.5 | 15455.5916
5081-High pressure bearings D | 20 | 20 | 2149.51 | 208920.6285
5082-High pressure blades/buckets A | 30 | 30 | 3268.56 | 1832426.4986
5083-High pressure nozzles/vanes A | 8 | 8 | 561.75 | 292542.7999
5084-High pressure casing/expansion joints | 3 | 3 | 321.29 | 26620.1118
5085-Interstage gas passages - HP | 4 | 4 | 177.3 | 454220.7166
5089-Other high pressure problems B | 3 | 3 | 179.4 | 342.0467
5090-Low pressure shaft A | 6 | 6 | 237 | 8250.2666
5091-Low pressure bearings A | 6 | 6 | 586.94 | 23886.9444
5092-Low pressure blades/buckets D | 14 | 14 | 2299.63 | 1448842.3391
5097-Other low pressure problems B | 6 | 6 | 539.54 | 1943.5391
5098-Expansion joints A | 3 | 4 | 649 | 3377.4
5099-HP to LP coupling | 1 | 1 | 34.3 | 22354.4533
5100-Chamber A | 6 | 6 | 639 | 43785.9164
5102-Vanes/nozzles A | 1 | 1 | 95 | 1116.25
5103-Silencer B | 1 | 1 | 17.5 | 22596.5833
5104-Cones A | 4 | 4 | 570 | 53826.2499
5105-Diverter Dampers B | 11 | 11 | 1142.07 | 2359.9821
5108-High engine exhaust temperature A | 155 | 155 | 15639.74 | 148493.2078
5109-Other exhaust problems (including high exhaust system temperature not attributable to a specific problem) | 199 | 199 | 25065.92 | 447213.8258
5110-Lube oil system - general | 205 | 207 | 14587.03 | 248622.4822
5111-Lube oil pumps B | 82 | 82 | 7971.41 | 176947.2256
5112-Lube oil coolers B | 37 | 37 | 3061.35 | 75551.002
5113-Lube oil valves/piping | 22 | 22 | 2368.52 | 24325.1225
5114-Lube oil filters | 23 | 23 | 1273.61 | 43641.279
5115-Oil vapor extractor | 8 | 8 | 774.3 | 5577.3165
5116-Power Augmentation System Equipment B | 27 | 27 | 1416.87 | 19354.3894
5120-Hydraulic oil system A | 195 | 196 | 24417.77 | 324050.0237
5130-Starting system (including motor) A | 429 | 433 | 47612.1 | 996749.8829
5140-Battery and charger system B | 40 | 40 | 3459.89 | 70125.3513
5150-Turning gear and motor C | 53 | 53 | 4919.6 | 239312.9903
5151-Load gear compartment B | 6 | 6 | 438.8 | 30545.5949
5160-Cooling and seal air system B | 122 | 123 | 19206.88 | 144374.6429
5170-Cooling water system A | 34 | 34 | 2721.5 | 24903.7257
5180-Anti-icing system A | 42 | 43 | 1647.75 | 20267.8845
5190-Other auxiliary system problems A | 196 | 203 | 20579.32 | 197040.1179
5200-Reduction gear B | 9 | 9 | 671 | 3734.358
5201-Load shaft and bearings A | 14 | 14 | 1423.32 | 85491.8157
5205-Main coupling between the turbine and generator A | 14 | 14 | 1210 | 75784.2994
5206-Gas Turbine Clutch | 14 | 14 | 970.5 | 9744.7997
5210-Intercoolers A | 2 | 2 | 281 | 109.0166
5230-Heat shields C | 1 | 1 | 128 | 181102.9332
5240-Fire detection and extinguishing system B | 132 | 132 | 15071.58 | 291664.0402
5241-Fire in unit A | 13 | 13 | 1257.3 | 122281.5446
5245-Gas Turbine Control System - data highway | 61 | 61 | 6753.23 | 57598.7694
5246-Gas Turbine Control System - hardware problems (including card failure) | 179 | 179 | 17931.14 | 266637.5275
5247-Gas Turbine Control System - internal and termination wiring | 39 | 39 | 3543.93 | 37778.2314
5248-Gas Turbine Control System - logic problems | 120 | 121 | 15364.6 | 453197.3685
5249-Gas Turbine Control System - upgrades | 28 | 28 | 2828.14 | 20492.3434
5250-Other Controls and instrumentation Problems A | 764 | 792 | 75956.12 | 751595.0774
5255-Computer | 46 | 46 | 5930.28 | 70309.8433
5260-Major overhaul (use for non-specific overhaul only; see page B-1) A | 2 | 2 | 72 | 49438.5833
5261-Gas turbine/compressor washing | 12 | 12 | 1434.22 | 13836.9203
5262-Gas turbine exchange | 3 | 3 | 99 | 29097.35
5270-Hot end inspection B | 1 | 1 | 120 | 1051200
5272-Boroscope inspection A | 19 | 19 | 1970.33 | 67531.0352
5274-General unit inspection A | 8 | 8 | 1095.7 | 36625.623
5280-Vibration (not engine) in unit not attributable to bearings or other components B | 56 | 57 | 4893.95 | 220096.6844
5285-Gas turbine vibration | 262 | 270 | 20130.38 | 2094455.1946
5286-Gas Turbine lockout cause by OEM specifications | 8 | 8 | 872.53 | 1612.2203
5290-Gas turbine performance testing - individual engines (use code 9999 for total unit performance testing) | 6 | 6 | 556 | 1090.3665
5295-Synchronous condenser equipment A | 2 | 2 | 116.3 | 440.4066
5299-Other miscellaneous gas turbine problems | 504 | 511 | 47873.23 | 2157224.0534
5400-Inlet air ducts B | 8 | 8 | 346.1 | 537.5215
5401-Inlet air vanes/noozles | 6 | 6 | 361 | 2667.2932
5402-Inlet air filters B | 1 | 1 | 10 | 0.83333
5404-Inlet air chillers A | 36 | 36 | 289.07 | 30474.2496
5405-Inlet air evaporative coolers A | 3 | 3 | 11 | 67.1833
5406-Inlet air foggers A | 1 | 1 | 52 | 26
5409-Other inlet air problems B | 8 | 8 | 295.4 | 5813.54
5410-High pressure shaft B | 3 | 3 | 138.5 | 515.9283
5411-High pressure bearings B | 1 | 1 | 45 | 35457.75
5412-High pressure blades/buckets C | 5 | 5 | 234.2 | 279159.5233
5413-Other high pressure problems D | 15 | 15 | 722.2 | 3773.8865
5414-Compressor diaphragms/vanes | 10 | 10 | 535.5 | 186091.7099
5420-Low pressure shaft C | 1 | 1 | 48 | 680
5429-Other low pressure problems D | 15 | 15 | 846.6 | 3215.9597
5435-Jet Engine Compressor Washing | 2 | 2 | 120 | 254
5439-Jet engine other compressor problems | 16 | 16 | 661.92 | 6366.8498
5441-Fuel piping and valves B | 72 | 73 | 4030.32 | 33913.5902
5442-Fuel nozzles/vanes A | 29 | 29 | 871.15 | 3952.786
5443-Fuel filters B | 17 | 17 | 740.1 | 4663.793
5444-Liquid fuel oil pump B | 11 | 11 | 469.51 | 5385.5652
5445-Liquid fuel oil transfer/forwarding pump A | 14 | 14 | 516.8 | 4170.5498
5446-Liquid fuel purge system B | 6 | 7 | 378.74 | 491.6795
5447-Gas fuel system A | 135 | 135 | 6672.66 | 58992.0881
5449-Other fuel system problems A | 108 | 108 | 5739.35 | 151870.6261
5450-Ignition system B | 45 | 46 | 2370.29 | 11630.3124
5451-Pilot fuel piping and valves B | 2 | 2 | 54 | 360.1667
5452-Pilot fuel nozzles/vanes A | 1 | 1 | 42 | 889
5454-Water injection system (Jet Engine) | 63 | 64 | 2498.87 | 26756.5445
5455-Fuel nozzle/vane cooling air system | 1 | 1 | 90 | 67.5
5460-Atomizing air system A | 1 | 1 | 59 | 1060.0333
5471-Combustor liner A | 1 | 1 | 37 | 888
5473-Flame scanners A | 33 | 35 | 1618.14 | 7071.782
5474-Flashback (including instrumentation) | 4 | 4 | 316 | 258.0166
5475-Blade Path Temperature Spread B | 36 | 36 | 2829.06 | 10042.7865
5479-Other combustor problems A | 41 | 41 | 2070.76 | 46311.6924
5481-High pressure bearings A | 1 | 1 | 18.5 | 4403
5482-High pressure blades/buckets D | 11 | 15 | 389.8 | 310822.675
5483-High pressure nozzles/vanes B | 1 | 1 | 49 | 153649.3
5485-Interstage gas passages | 2 | 2 | 52 | 72.2
5489-Other high pressure problems C | 11 | 12 | 477.6 | 10577.0631
5490-Low pressure shaft B | 2 | 2 | 94 | 1090.3
5491-Low pressure bearings C | 5 | 5 | 171 | 143014.6166
5492-Low pressure blades/buckets B | 3 | 3 | 141 | 96910.5666
5497-Other low pressure problems C | 7 | 7 | 441.8 | 27128.5699
5500-Chamber B | 2 | 2 | 73 | 42208.9
5505-Diverter Dampers A | 1 | 1 | 158.4 | 22471.6799
5508-High engine exhaust temperature B | 35 | 36 | 2094.2 | 15648.2159
5509-Other exhaust problems (including high exhaust temperature not attributable to a specific problem) | 32 | 32 | 2453.6 | 29194.6396
5510-Lube oil system A | 137 | 137 | 5647.74 | 141311.333
5516-Power Augmentation System Equipment A | 12 | 12 | 261 | 4055.5999
5520-Hydraulic oil system B | 32 | 32 | 2276.88 | 24627.3241
5530-Starting system (including motor) B | 79 | 79 | 4192.64 | 59695.6731
5540-Battery and charger system A | 10 | 10 | 736.69 | 29399.6886
5550-Turning gear and motor B | 2 | 2 | 105.52 | 1362.5085
5551-Load gear compartment A | 2 | 2 | 80.58 | 34961.2309
5560-Cooling and seal air system A | 27 | 27 | 1759.8 | 14618.3409
5570-Cooling water system B | 6 | 6 | 436.02 | 3698.4443
5580-Anti-icing system B | 7 | 7 | 269.4 | 593.3199
5590-Other auxiliary system problems B | 72 | 72 | 2947.97 | 17919.9481
5601-Load shaft and bearings B | 3 | 3 | 86 | 3866.1666
5606-Jet Engine Clutch | 4 | 4 | 138.5 | 439.1833
5610-Intercoolers B | 1 | 1 | 48.51 | 4573.6845
5640-Fire detection and extinguishing system A | 23 | 23 | 1032.4 | 16132.1013
5645-Jet Engine Control System - data highway | 21 | 22 | 898.32 | 2968.489
5646-Jet Engine Control System - hardware problems (including card failure) | 73 | 73 | 3040.95 | 22402.5843
5647-Jet Engine Control System - internal and termination wiring | 8 | 8 | 304.14 | 5074.8382
5648-Jet Engine Control System - logic problems | 67 | 67 | 2735.7 | 14595.9358
5649-Jet Engine Control System - upgrades | 2 | 2 | 95 | 1134.7166
5650-Other Controls and instrumentation Problems B | 226 | 227 | 9701.22 | 120633.1599
5661-Engine/compressor washing | 2 | 2 | 165 | 675.9999
5662-Engine exchange | 12 | 12 | 437.82 | 64072.9721
5665-Engine shafts and bearings | 1 | 1 | 37.24 | 4.9653
5672-Boroscope inspection B | 4 | 4 | 184.9 | 1363.3033
5674-General unit inspection B | 13 | 13 | 486.55 | 34611.3874
5680-Vibration (not engine) in unit not attributable to bearings or other components A | 76 | 76 | 3703.12 | 22846.1186
5685-Engine vibration | 72 | 73 | 3106.72 | 239502.5324
5686-Jet Engine lockout cause by OEM specifications | 7 | 7 | 324.51 | 6368.6866
5690-Engine performance testing - individual engines (use code 9999 for total unit performance testing) A | 2 | 2 | 75 | 49.9999
5699-Other miscellaneous jet engine problems | 117 | 120 | 5078.73 | 599214.4239
5710-Cylinders | 2 | 2 | 14.2 | 398.7933
5720-Pistons | 1 | 1 | 1.8 | 4766.4
5731-Exhaust valves | 1 | 1 | 6.4 | 10.0267
5799-Other engine problems | 2 | 2 | 6 | 17648.3
5800-Lube oil system C | 2 | 2 | 7.31 | 130.8642
5805-Cooling system | 2 | 2 | 5.14 | 132.098
5815-Fuel system | 5 | 5 | 18.14 | 6377.8805
5820-Start system | 3 | 3 | 58.4 | 57.6133
5855-Engine control system | 1 | 1 | 7.2 | 4.92
5999-other miscellaneous Internal Combustion/Reciprocating Engines problems | 11 | 11 | 111.6 | 612.0008
6000-Heat recovery steam generator to gas turbine connecting equipment. For additional codes; use Fossil Steam Cause Codes 0010 to 1999. | 40 | 41 | 6043.54 | 89083.2737
6005-HP Evaporator tubes | 9 | 9 | 1195 | 91991.9163
6006-IP Evaporator tubes | 1 | 1 | 257 | 8695.1666
6007-LP Evaporator tubes | 6 | 6 | 618 | 37026.3331
6010-HP superheater | 29 | 29 | 4283.5 | 403105.4817
6011-HP reheater | 12 | 12 | 2225.07 | 137828.0083
6012-HP economizer | 19 | 19 | 1657.63 | 138825.7167
6020-IP superheater | 4 | 4 | 486.5 | 37502.1332
6021-IP reheater | 13 | 13 | 2729.1 | 98778.2306
6022-IP economizer | 2 | 2 | 298.5 | 4666.9166
6031-LP superheater | 2 | 2 | 151 | 10437.15
6032-LP economizer | 8 | 8 | 1546 | 69992.4327
6090-Other HRSG tube Problems | 9 | 9 | 1378 | 34233.1164
6100-Steam turbine to gas turbine coupling. For additional codes; use Fossil Steam Cause Codes 4000 to 4499. | 13 | 13 | 1714 | 7680.8663
6110-HP steam piping up to turbine stop valves - Greater than 600 PSIG; (see 0790 for piping supports) | 21 | 21 | 3041.5 | 229929.2654
6111-HP steam relief/safety valves | 4 | 4 | 384 | 4542.4
6112-Other HP steam valves (including vent and drain valves but not including the turbine stop valves) | 42 | 42 | 6895.33 | 69285.3148
6113-Other HP steam system problems | 34 | 34 | 5637.69 | 101646.5015
6120-IP steam piping up to turbine stop valves - Between 200 & 600 PSIG (see 0790 for piping supports) | 17 | 17 | 2339.5 | 31953.6411
6121-IP steam relief/safety valves | 1 | 1 | 64 | 914.1333
6122-Other IP steam valves (including vent and drain valves but not including the turbine stop valves) | 14 | 14 | 2093.6 | 38151.8775
6123-Other IP steam system problems | 11 | 11 | 2089 | 14072.5259
6130-LP steam piping up to turbine stop valves - Less than 200 PSIG (see 0790 for piping supports) | 2 | 2 | 299.33 | 4261.9275
6131-LP steam relief/safety valves | 3 | 3 | 630 | 8720.6832
6132-Other LP steam valves (including vent and drain valves but not including the turbine stop valves) | 5 | 5 | 602 | 12901.4665
6133-Other LP steam system problems | 12 | 12 | 1810.7 | 41493.3578
6134-Other main steam valves (including vent and drain valves but not including the turbine stop valves) B | 54 | 54 | 9028.15 | 989539.9675
6140-HP Desuperheater/attemperator piping - Greater than 600 PSIG. | 23 | 23 | 3485.8 | 122365.4963
6141-HP Desuperheater/attemperator valves | 34 | 34 | 4730.08 | 34568.037
6142-HP Desuperheater/attemperator spray nozzles | 1 | 1 | 376 | 432.4
6143-HP Desuperheater/attemperator drums | 1 | 1 | 169 | 9340.0666
6144-Other HP desuperheater/attemperator problems | 5 | 5 | 581 | 2428.1165
6145-IP Desuperheater/attemperator piping - Between 200-600 PSIG | 4 | 4 | 431.3 | 2797.1549
6146-IP Desuperheater/attemperator valves | 8 | 9 | 1127 | 16330.1996
6148-IP Desuperheater/attemperator drums | 1 | 1 | 115.5 | 102.025
6149-Other IP desuperheater/attemperator problems | 1 | 1 | 82 | 20.5
6160-HP Startup bypass system piping (including drain lines up to heaters or condenser)- Greater than 600 PSIG | 7 | 7 | 1099 | 31752.55
6161-HP Startup bypass system valves | 65 | 65 | 10262.05 | 123426.0899
6163-Other HP startup bypass system problems | 2 | 2 | 506 | 205.5665
6164-HP Startup bypass instrumentation and controls | 20 | 20 | 3418.63 | 148701.1711
6170-IP Startup bypass system piping (including drain lines up to heaters or condenser) - Between 200-600 PSIG | 4 | 4 | 600 | 67945.0166
6171-IP Startup bypass system valves | 21 | 21 | 3563.67 | 17275.7822
6174-IP Startup bypass instrumentation and controls | 18 | 18 | 3833.56 | 16804.9188
6181-LP Startup bypass system valves | 2 | 2 | 284 | 5483.5666
6200-Combined cycle instruments and controls. (Report instruments and controls specific to the gas turbine; steam turbine; boiler; generator; or balance of plant using the codes for the appropriate piece of equipment. | 67 | 67 | 11622.38 | 67989.7449
6299-Other combined cycle problems. (Use other gas turbine problem codes; other steam turbine codes; etc. whenever appropriate.) | 273 | 279 | 39418.76 | 1100486.2532
6399-Other coal gasification equipment problems | 1 | 1 | 260 | 104
6410-Steam wells/steam field piping problems | 25 | 26 | 186 | 2438.4166
6415-Low steam pressure | 81 | 88 | 1096.27 | 15499.1691
6420-Condensate reinjection system | 6 | 6 | 155 | 591.6332
6430-Unit H2S emission limitations ? regulatory | 9 | 9 | 384 | 1398.1999
6440-H2S abatement system problems ? general | 8 | 8 | 344 | 2360.85
6460-Condenser problems due to H2S abatement system | 1 | 1 | 48 | 175.2
6480-Steam strainer plugging ? mineral deposits | 8 | 8 | 28 | 2816.6333
6499-Geothermal | 527 | 562 | 6872.52 | 99263.61
7000-Shaft B | 3 | 3 | 655.16 | 14638.4999
7001-Shaft packing | 32 | 33 | 4131.3 | 653822.6129
7003-Lube oil system (use code 7007 to report bearing failures due to lube oil problems) | 46 | 46 | 2579.98 | 52770.1146
7007-Bearings A | 50 | 50 | 5905.07 | 1854248.9344
7008-Bearing cooling system B | 64 | 64 | 3720.6 | 115263.9486
7009-Bearing Oil System | 72 | 72 | 4691.13 | 220336.1036
7010-Runner cavitation damage | 2 | 2 | 148.39 | 44212.4147
7011-Other runner problems | 293 | 318 | 1853.26 | 971575.2145
7012-Casing; wear ring; or liner cavitation damage | 3 | 3 | 274.2 | 12127.9465
7014-Blade or bucket cracking | 2 | 2 | 98 | 815787.9333
7020-Nozzle assembly | 5 | 5 | 253.64 | 8739.2944
7030-Vibration (Only for unbalance; report bearing failure; etc. in appropriate category) | 29 | 30 | 1541.49 | 236967.3139
7050-Turbine governor | 303 | 314 | 18860.72 | 890205.0046
7052-Other turbine control problems (Report specific wicket gate controls; etc. using the code for the appropriate equipment item.) | 65 | 65 | 6138.4 | 209798.2855
7053-Governor Oil System | 118 | 130 | 6763.11 | 154971.8159
7099-Other turbine problems | 518 | 563 | 7636.53 | 1390873.6635
7100-Upper reservoir dams and dikes | 5 | 5 | 589.24 | 63003.9456
7101-Lower reservoir dams and dikes | 16 | 16 | 309 | 1286.0666
7110-Intake channel or flume (including trash racks) | 196 | 201 | 9506.17 | 765638.2159
7111-Intake tunnel | 46 | 46 | 5740.69 | 104899.0886
7112-Ice blockages at intake structures including frazil ice; sheets; blocks of ice; etc A | 29 | 29 | 552.32 | 15026.8518
7120-Headgates | 40 | 40 | 3685.94 | 367336.4774
7121-Shutoff valves | 16 | 16 | 3054.41 | 190875.3671
7123-Shutoff valve bypass line and valve | 13 | 13 | 2043.32 | 165397.9668
7124-Penstock | 16 | 17 | 996.47 | 10727.2369
7130-Spiral case | 3 | 3 | 371.05 | 551900.8148
7140-Wicket gate assembly | 26 | 27 | 4192.49 | 200550.466
7141-Wicket gate operating mechanism or positioner | 29 | 29 | 3432.78 | 326152.8139
7142-Wicket gate shear pin | 206 | 207 | 15294.71 | 453541.132
7162-Relief valve and vacuum breakers | 6 | 6 | 397.3 | 122654.3159
7170-Draft tube | 13 | 13 | 1581.56 | 864883.6164
7180-Tailrace | 16 | 16 | 922.78 | 38793.4174
7181-Tail water depressing equipment | 6 | 6 | 743.6 | 3035.1929
7190-Dewatering and rewatering equipment | 3 | 3 | 122.5 | 206.6166
7191-Equalizing line | 2 | 2 | 690 | 1604.25
7199-Other water supply/discharge problems (use for equipment related problems; use codes 9135 or 9320 for lack of water or discharge limit related problems) | 202 | 203 | 2430.27 | 78365.5319
7201-Inspection A | 9 | 9 | 377.26 | 6170.811
7210-Canals (including siphons; radial gates; and spills) | 7 | 7 | 180.69 | 3249.4628
7220-Unit out of service due to common penstock with unit under repair | 9 | 9 | 482.6 | 3189.0529
7230-Pony motor (pumped storage units only) | 7 | 7 | 2000 | 5779.3656
7299-Other miscellaneous hydro turbine/pump problems (use generator codes and balance of plant electrical and auxiliary codes as appropriate) | 43 | 43 | 4521.69 | 309248.4581
7820-Bearings B | 5 | 5 | 243.5 | 235391.05
7840-Discs | 2 | 2 | 414 | 18571.3499
7860-Nozzles/vanes | 1 | 1 | 53.57 | 1129.4341
7880-Exhaust diffusers | 1 | 1 | 254 | 7649.6332
7900-Inner casing D | 1 | 1 | 56.5 | 42132.9916
7910-Outer exhaust casing | 2 | 2 | 141.5 | 8045.4083
7920-Lube oil system B | 18 | 18 | 926.79 | 21128.5398
7930-Controls and instrumentation A | 12 | 12 | 478.64 | 25685.6292
7940-Evactor | 1 | 1 | 24 | 482
7960-Other expander turbine problems | 5 | 5 | 168.5 | 108641.95
8002-Screw conveyors | 6 | 6 | 462 | 625.6665
8006-Weigh feeders | 1 | 1 | 318 | 2194.2
8010-Crushers/mills | 12 | 12 | 2600 | 26632.9328
8020-Mill slurry tanks supply problems | 6 | 6 | 1740 | 8886.1824
8030-Classifiers | 6 | 6 | 953 | 7890.9
8040-Slurry transfer pumps and motors | 4 | 4 | 451 | 10421.6497
8050-Chemical unavailability | 2 | 2 | 279 | 22889.3998
8099-Other chemical supply problems | 8 | 8 | 940.21 | 4284.4119
8100-Scrubber/absorber tower or module | 107 | 107 | 9660.33 | 166844.7469
8110-Spray nozzles | 3 | 3 | 362 | 151405.6333
8115-Disc scrubber throats | 4 | 4 | 540 | 7102.3332
8120-Spray pumps and motors | 9 | 9 | 1770 | 13129.1663
8125-Scrubber recycle (liquid) pumps | 44 | 45 | 4982 | 52268.5819
8127-Scrubber recycle (liquid) pump motors | 9 | 9 | 905 | 7476.0997
8130-Recirculation tanks including agitators | 4 | 4 | 499 | 3664.2331
8140-Reaction tanks including agitators | 18 | 18 | 3294.67 | 49098.9476
8160-Mist eliminators/demisters and washdown | 24 | 24 | 1997 | 79640.7326
8199-Other scrubber problems | 66 | 66 | 8311.9 | 152851.4561
8200-Piping | 34 | 34 | 3421.2 | 60593.5192
8210-Valves | 12 | 12 | 1408 | 23041.9826
8220-Strainers or filters | 1 | 1 | 76 | 240.6666
8230-Ducting | 11 | 11 | 3382.1 | 205611.3688
8235-Demister | 20 | 20 | 456.02 | 883.8889
8240-Bypass dampers | 4 | 4 | 606 | 9265.6997
8250-Dampers other than bypass | 21 | 21 | 4533.27 | 47490.4171
8260-Scrubber booster I.D. fan (fan specific to the scrubber) | 136 | 136 | 11939.77 | 626696.0121
8261-Scrubber booster I.D. fan drive | 28 | 28 | 6259.25 | 374176.0066
8262-Scrubber booster I.D. fan vibration (fan specific to the scrubber) | 60 | 60 | 4441.5 | 114178.8903
8264-Scrubber booster I.D. fan blades (fan specific to the scrubber) | 3 | 3 | 345 | 2015.9167
8270-Scrubber booster F.D. fan (fan specific to the scrubber) | 26 | 26 | 7444.44 | 49975.6705
8271-Scrubber booster F.D. fan drive | 9 | 9 | 767 | 9624.733
8272-Scrubber booster F.D. fan vibration (fan specific to the scrubber) | 5 | 5 | 1621 | 53745.7662
8274-Scrubber booster F.D. fan blades (fan specific to the scrubber) | 1 | 1 | 160 | 2200
8280-Reagent feed piping | 8 | 8 | 822 | 2933.3663
8299-Other piping; ducting; damper; and fan problems | 14 | 14 | 3140 | 39535.9495
8310-Waste disposal/recovery pumps | 2 | 2 | 550 | 4014.9997
8325-Ash disposal problems | 6 | 6 | 1726 | 47937.083
8330-Dewatering equipment (thickener; centrifuge; etc.) | 8 | 8 | 3190 | 15932.3318
8349-Other waste disposal and recovery problems | 1 | 1 | 300 | 930
8399-Solids conveying and mixing system problems | 1 | 1 | 145 | 2808.1666
8400-Scrubber gas discharge reheaters - general | 1 | 1 | 31 | 558
8404-Scrubber gas discharge reheaters - tube leaks | 1 | 1 | 93 | 186
8410-Scrubber instruments and controls | 10 | 10 | 1996.23 | 5587.7126
8415-Liquid level controls | 10 | 10 | 1208.85 | 3568.6071
8425-Miscellaneous mechanical failures | 3 | 3 | 547.12 | 737.7399
8426-Miscellaneous electrical failures | 12 | 12 | 914.78 | 18914.7624
8430-Stack damage related to scrubber system | 2 | 2 | 394 | 35860.5666
8450-Inspection | 2 | 2 | 369 | 6534.3749
8470-SO2 monitor | 2 | 2 | 214 | 424.5665
8499-Other miscellaneous wet scrubber problems | 87 | 87 | 3555.29 | 200227.9001
8500-Slurry storage and feed tanks | 4 | 4 | 625.04 | 4019.8587
8501-Reagent storage; feed bins; and conveyors | 1 | 1 | 65.8 | 834.5633
8502-Weigh feeders | 4 | 4 | 1198.3 | 6868.4648
8503-Screw conveyors | 1 | 1 | 23 | 218.5
8504-Mills/slakers | 4 | 4 | 534.8 | 4640.9698
8505-Scalping screens | 2 | 2 | 143.59 | 843.475
8506-Slurry pipelines | 11 | 11 | 1117 | 8197.7329
8507-Reagent uploading and transfer systems | 2 | 2 | 245 | 1721.1499
8508-Reagent unavailability | 23 | 23 | 2089.14 | 15667.4989
8510-Slurry mixers and agitators | 4 | 4 | 1329.9 | 25527.718
8520-Slurry transfer pumps and motors | 8 | 8 | 1141.9 | 7194.4427
8521-Reagent/slurry problems | 14 | 14 | 1959 | 19217.3162
8522-Piping | 7 | 7 | 929 | 3786.8164
8524-Strainers or filters | 3 | 3 | 168 | 743.2166
8525-Ducting | 3 | 3 | 536.5 | 2638.0413
8526-Dampers | 2 | 2 | 357 | 3004.4332
8527-Other piping; ducting; and damper problems | 1 | 1 | 405 | 29369.2497
8528-Dry scrubber instruments and controls | 14 | 14 | 1864.19 | 29757.5123
8530-Spray towers | 14 | 14 | 591.7 | 19696.2124
8531-Spray machine/atomizer | 46 | 46 | 4801.7 | 19810.1387
8532-Spray machine/atomizer motors | 7 | 7 | 1085 | 1336.6664
8533-Spray machine/atomizer lubrication systems | 9 | 9 | 464 | 2003.1831
8534-Spray machine/atomizer vibration problems | 13 | 13 | 865.61 | 3931.9698
8535-Fly ash conveyors | 6 | 6 | 1774.5 | 101409.5659
8538-Recycle storage and feed tanks including agitators | 2 | 2 | 77 | 142.6666
8539-Recycle slurry transfer pumps | 9 | 9 | 1713.71 | 24099.3974
8541-Recycle feed bins | 1 | 1 | 45 | 133.5
8542-Recycle feed bins aeration systems | 2 | 2 | 128.25 | 2606.7375
8544-Mechanical failures | 12 | 12 | 976.83 | 9450.8337
8545-Electrical failures | 1 | 1 | 340 | 2023
8549-Other dry scrubber problems | 159 | 159 | 17205.85 | 213365.5215
8550-Electrostatic precipitator fouling | 312 | 315 | 14259.65 | 502105.6249
8551-Electrostatic precipitator field out of service | 392 | 395 | 21391.44 | 304756.6377
8560-Electrostatic precipitator problems | 326 | 328 | 22139.46 | 359507.9359
8580-Mechanical precipitator problems | 3 | 3 | 41 | 663.1233
8590-Other precipitator problems | 72 | 72 | 4581.61 | 56428.3863
8600-Flue gas additives (furnace injection) | 67 | 67 | 4555.4 | 111667.2021
8601-SO3 mitigation | 24 | 24 | 2906 | 10095.874
8650-Baghouse systems; general | 419 | 423 | 20403.92 | 266997.5523
8651-Bag failures and rebagging | 407 | 408 | 14125.84 | 233623.7702
8652-Shakers and rappers | 6 | 6 | 181.5 | 263.5833
8653-Inflation and deflation fans and motors | 6 | 6 | 214.11 | 1360.9246
8654-Baghouse booster fans and motors | 47 | 47 | 1863.05 | 20968.5419
8655-Structural duct work and dampers | 2 | 2 | 872 | 48822.7999
8656-Controls and instrumentation B | 89 | 97 | 8993.47 | 162458.6681
8657-Ash handling system and hoppers | 66 | 66 | 8668.44 | 229209.1384
8658-Slurry system from precipitators | 4 | 4 | 1047 | 5343.9662
8670-Emission monitors (other than CEMS) A | 21 | 21 | 1035 | 8199.8497
8699-Other miscellaneous pollution control equipment problems | 218 | 218 | 11017.76 | 90375.7568
8700-CEMS Certification and Recertification | 43 | 43 | 3726.91 | 14788.8394
8710-SO2 analyzer problems | 1 | 1 | 249 | 4527.6499
8720-NOx analyzer problems | 47 | 47 | 4124.56 | 59499.7867
8730-CO analyzer problems | 25 | 25 | 1901.1 | 51878.4558
8750-O2 analyzer problems | 5 | 5 | 182.8 | 3235.1716
8760-Opacity monitor problems | 52 | 52 | 3775.64 | 28671.803
8770-Flow monitor problems | 12 | 12 | 1015.57 | 31292.6612
8780-Data acquisition system problems | 13 | 13 | 1741.6 | 42539.7178
8790-Miscellaneous CEMS problems | 95 | 97 | 6522.94 | 41208.3792
8802-SNCR NOx Control system | 22 | 23 | 1427.69 | 6645.7388
8809-Other SNCR NOx problems | 12 | 12 | 1016.5 | 42080.9797
8810-SCR NOx Reactor | 11 | 11 | 1462.6 | 34353.3929
8811-SCR NOx Reagent | 2 | 2 | 544.5 | 2403.1497
8812-SCR NOxCatalyst | 38 | 39 | 1351.26 | 97226.9534
8813-SCR NOx Injection grid piping/valves | 6 | 6 | 543 | 4092.8663
8815-SCR NOx Soot blowers | 2 | 2 | 73 | 36.55
8816-SCR NOx Plugging | 26 | 28 | 1256.59 | 157013.1318
8817-SCR NOx Control system | 36 | 37 | 3722.77 | 37272.4697
8820-SCR NOx Ammonia injection grid piping/valves | 34 | 34 | 4743.87 | 49469.744
8821-SCR NOx Ammonia tanks; piping and valves (not injection) | 27 | 27 | 3101.43 | 35341.0948
8822-SCR NOx Ammonia air blowers | 14 | 14 | 1780.36 | 28228.405
8823-SCR NOx Other ammonia system problems | 80 | 83 | 8627.84 | 74486.1069
8825-Other SCR NOx problems | 83 | 83 | 5369.76 | 52616.2462
8832-CAH NOx Plugging | 1 | 1 | 10 | 230
8835-CAH NOx Other CAH problems | 4 | 4 | 194.22 | 2335.3776
8840-CO Active catalyst | 73 | 217 | 1434.77 | 18083.2718
8842-CO Plugging | 15 | 15 | 18 | 986.2333
8845-Other CO reduction problems | 42 | 43 | 2672.17 | 56259.0943
9000-Flood | 91 | 91 | 3642.18 | 2628194.5445
9010-Fire; not related to a specific component | 26 | 26 | 1021.13 | 1026680.6457
9020-Lightning | 280 | 280 | 37443.75 | 1198597.5301
9030-Earthquake | 5 | 5 | 221.8 | 1295.9032
9031-Tornado | 18 | 18 | 1421.54 | 205151.0622
9035-Hurricane | 124 | 139 | 30596.8 | 4877359.1345
9036-Storms (ice; snow; etc) | 100 | 100 | 13679.59 | 1030357.7729
9040-Other catastrophe | 32 | 32 | 3179.55 | 15072.873
9130-Lack of fuel: Physical failures of fuel supply or delivery/transportation of fuel | 294 | 502 | 42307.25 | 1088389.9315
9131-Lack of fuel: Contract or Tariff allows for interruption | 226 | 232 | 14510 | 479190.1713
9134-Fuel conservation | 185 | 186 | 4065.69 | 89006.6139
9135-Lack of water (hydro) | 2370 | 2562 | 32807.85 | 1909158.6173
9136-Problems with Primary Fuel for Units with Secondary Fuel Operation | 16 | 16 | 1873.69 | 7543.0038
9137-Ground water or other water supply problems | 12 | 12 | 1329.38 | 59131.8398
9160-Other economic problems | 30 | 30 | 4460.74 | 2501383.5614
9200-High ash content | 105 | 111 | 8128.69 | 46050.6423
9201-High ash content ? (not outside management control) | 87 | 87 | 3794.9 | 59284.1723
9205-Poor quality natural gas fuel; low heat content | 127 | 178 | 2419.25 | 14676.1464
9210-Low grindability | 3 | 3 | 75 | 5879.3333
9211-Low grindability (not outside management control) | 12 | 12 | 950 | 8243.5663
9220-High sulfur content | 13 | 13 | 347.8 | 6455.6049
9221-High sulfur content ? (not outside management control) | 24 | 24 | 2308 | 41842.7162
9230-High vanadium content | 3 | 3 | 276 | 22227.9998
9240-High sodium content | 1 | 1 | 6 | 67.4
9250-Low Btu coal due to low BTU vane of coal not expected (Outside Management Control) | 1089 | 1097 | 30726.17 | 732803.4953
9251-Low Btu Coal From Contract For Low Btu Coal | 173 | 181 | 4520.25 | 131570.5736
9260-Low Btu oil | 5 | 5 | 13.5 | 80.415
9261-Low Btu oil (not outside management control) | 2 | 2 | 15 | 95.4
9270-Wet coal | 1952 | 2001 | 151521.91 | 1772121.516
9271-Wet coal (not outside management control) | 733 | 733 | 64080.86 | 635765.8527
9280-Frozen coal | 24 | 24 | 1084 | 56674.1662
9281-Frozen coal (not outside management control) | 26 | 26 | 1734.3 | 25446.5143
9290-Other fuel quality problems | 844 | 854 | 76020.69 | 299086.156
9291-Other fuel quality problems (not outside management control) | 366 | 383 | 10829.88 | 266260.7005
9300-Transmission system problems other than catastrophes (do not include switchyard problems in this category; see codes 3600 to 3629) | 3001 | 3010 | 143127.6 | 4435532.6154
9305-Ash disposal problem | 4 | 4 | 452.6 | 4658.1765
9310-Operator training | 2 | 2 | 645.5 | 713.6665
9320-Other miscellaneous external problems | 1191 | 1380 | 67673.78 | 1727407.7728
9345-Pumping Operations | 4 | 4 | 172.89 | 472.1748
9350-Public Safety/River Rescue | 14 | 14 | 540 | 2436.9332
9500-Regulatory (nuclear) proceedings and hearings - regulatory agency initiated | 1 | 1 | 479 | 4079643
9504-Regulatory (environmental) proceedings and hearings - regulatory agency initiated | 1 | 1 | 47 | 7872.5
9510-Plant modifications strictly for compliance with new or changed regulatory requirements (scrubbers; cooling towers; etc.) | 6 | 6 | 252.09 | 3298.085
9590-Miscellaneous regulatory (this code is primarily intended for use with event contribution code 2 to indicate that a regulatory-related factor contributed to the primary cause of the event) | 195 | 202 | 15150.58 | 963335.4566
9600-SO2 stack emissions (fossil) | 94 | 94 | 5235.83 | 55829.1991
9604-SO2 stack emissions (jet engines) | 2 | 2 | 86.5 | 822.425
9610-NOx stack emissions (fossil) | 84 | 84 | 6116.82 | 149965.7989
9613-NOx stack emissions (gas turbine) | 97 | 97 | 9001.47 | 552953.3214
9614-NOx stack emissions (jet engines) | 30 | 30 | 1521.5 | 14389.161
9616-CO stack emissions | 85 | 90 | 4430.27 | 47132.6295
9620-Particulate stack emissions (fossil) | 83 | 85 | 7072.03 | 217656.2493
9623-Particulate stack emissions (gas turbine) | 7 | 7 | 150 | 101953.7999
9630-Opacity (fossil) | 1631 | 1646 | 95492.62 | 1756397.8869
9633-Opacity (gas turbine) | 4 | 4 | 64 | 510.9833
9650-Other stack or exhaust emissions (fossil) | 74 | 74 | 4757.54 | 57574.738
9653-Other stack or exhaust emissions (gas turbine) | 28 | 28 | 2073.48 | 52799.0695
9655-Other stack or exhaust emissions (Internal Combustion/Reciprocating Engines) | 4 | 4 | 312.5 | 52322.7666
9656-Other stack or exhaust emissions testing - fossil | 31 | 31 | 2655 | 16876.7493
9657-Other stack or exhaust emissions testing - gas turbine | 2 | 2 | 91 | 114.1666
9660-Thermal discharge limits (fossil and nuclear) | 131 | 133 | 3912.65 | 50527.8404
9663-Thermal discharge limits (gas turbine) | 24 | 24 | 172.7 | 4194.76
9680-Fish kill (fossil and nuclear) | 1 | 1 | 179 | 3245.8666
9690-Other miscellaneous operational environmental limits (fossil and nuclear) | 67 | 72 | 2490.14 | 212519.6946
9693-Other miscellaneous operational environmental limits (gas turbines) | 44 | 44 | 3311 | 66225.2824
9694-Other miscellaneous operational environmental limits (jet engines) | 6 | 6 | 144.75 | 494.5625
9695-Other miscellaneous operational environmental limits (Internal Combustion/Reciprocating Engines) | 5 | 5 | 27.5 | 17689.5095
9696-Other miscellaneous operational environmental limits (hydro and PS) | 9 | 9 | 392.51 | 11192.9638
9720-Other safety problems | 78 | 79 | 7805.83 | 327045.4884
9900-Operator error | 645 | 648 | 136946.59 | 9262236.3431
9910-Maintenance personnel error | 186 | 187 | 33295.45 | 1801706.5611
9920-Contractor error | 89 | 89 | 17735.71 | 381539.8846
9930-Operating procedure error | 55 | 55 | 12241.28 | 261141.6559
9940-Maintenance procdure error | 40 | 41 | 6825.3 | 108996.6256
9950-Contractor procedure error | 16 | 16 | 1391.9 | 23697.9962
9960-Staff shortage | 35 | 37 | 3167.25 | 801844.5826
9997-NERC Reliability Standards requirements | 27 | 27 | 3969.46 | 115952.8786
9998-Black Start testing | 13 | 16 | 610 | 5789.4998
9999-Total unit performance testing (use appropriate codes for individual component testing) | 156 | 157 | 5740.03 | 1316044.0343
Total Result | 87942 | 90696 | 9121789.25 | 405923308.7901

## Data
CauseCode | CauseCodeName | SystemName | ComponentName | EventTypeCode | EventTypeName | EventYearNbr | FuelCategory | FuelCode | UnitTypeCode | UnitTypeCodeDesc | RegionCode | Season | MWHrsLost | MWLost | DISTINCT_UNITS | EVENT_COUNT | Cause | EventType | UnitType
0010 | Thaw shed failure or fire | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | OS | 650 | Fluidized Bed | RFC | Winter | 0.001667 | 0.1 | 1 | 1 | 0010-Thaw shed failure or fire | D1-Forced - Immediate | 650-Fluidized Bed
0020 | Coal car dumpers; shakers; and unloaders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 397.5 | 50 | 1 | 1 | 0020-Coal car dumpers; shakers; and unloaders | D1-Forced - Immediate | 100-Fossil-Steam
0020 | Coal car dumpers; shakers; and unloaders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 603.1999 | 174 | 1 | 1 | 0020-Coal car dumpers; shakers; and unloaders | D1-Forced - Immediate | 100-Fossil-Steam
0020 | Coal car dumpers; shakers; and unloaders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2030.5 | 262 | 1 | 1 | 0020-Coal car dumpers; shakers; and unloaders | D1-Forced - Immediate | 100-Fossil-Steam
0020 | Coal car dumpers; shakers; and unloaders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 530.6666 | 40 | 1 | 1 | 0020-Coal car dumpers; shakers; and unloaders | D1-Forced - Immediate | 100-Fossil-Steam
0020 | Coal car dumpers; shakers; and unloaders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1175.5 | 30 | 1 | 1 | 0020-Coal car dumpers; shakers; and unloaders | D1-Forced - Immediate | 100-Fossil-Steam
0020 | Coal car dumpers; shakers; and unloaders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1507.8671 | 222.29 | 1 | 1 | 0020-Coal car dumpers; shakers; and unloaders | D1-Forced - Immediate | 100-Fossil-Steam
0020 | Coal car dumpers; shakers; and unloaders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 149.3333 | 40 | 1 | 1 | 0020-Coal car dumpers; shakers; and unloaders | D1-Forced - Immediate | 100-Fossil-Steam
0020 | Coal car dumpers; shakers; and unloaders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1711.6666 | 260 | 1 | 1 | 0020-Coal car dumpers; shakers; and unloaders | D1-Forced - Immediate | 100-Fossil-Steam
0020 | Coal car dumpers; shakers; and unloaders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 115.4999 | 198 | 1 | 1 | 0020-Coal car dumpers; shakers; and unloaders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0020 | Coal car dumpers; shakers; and unloaders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 1270.3333 | 148 | 1 | 1 | 0020-Coal car dumpers; shakers; and unloaders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0020 | Coal car dumpers; shakers; and unloaders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 410.6666 | 88 | 1 | 1 | 0020-Coal car dumpers; shakers; and unloaders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0020 | Coal car dumpers; shakers; and unloaders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 1356.5833 | 223 | 1 | 1 | 0020-Coal car dumpers; shakers; and unloaders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0020 | Coal car dumpers; shakers; and unloaders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 409.2 | 88 | 1 | 1 | 0020-Coal car dumpers; shakers; and unloaders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0020 | Coal car dumpers; shakers; and unloaders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 1533.3666 | 293 | 1 | 1 | 0020-Coal car dumpers; shakers; and unloaders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0020 | Coal car dumpers; shakers; and unloaders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 365.7 | 138 | 1 | 1 | 0020-Coal car dumpers; shakers; and unloaders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0020 | Coal car dumpers; shakers; and unloaders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 367.9999 | 138 | 1 | 1 | 0020-Coal car dumpers; shakers; and unloaders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0020 | Coal car dumpers; shakers; and unloaders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 614.25 | 273 | 1 | 1 | 0020-Coal car dumpers; shakers; and unloaders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0022 | Unloading/receiving hopper (train/truck) | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 2 | 8 | 1 | 1 | 0022-Unloading/receiving hopper (train/truck) | D2-Forced - Delayed | 100-Fossil-Steam
0022 | Unloading/receiving hopper (train/truck) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 240.9333 | 13 | 1 | 1 | 0022-Unloading/receiving hopper (train/truck) | D1-Forced - Immediate | 800-Miscellaneous
0022 | Unloading/receiving hopper (train/truck) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 107.25 | 13 | 1 | 1 | 0022-Unloading/receiving hopper (train/truck) | D1-Forced - Immediate | 800-Miscellaneous
0024 | Rotary plow | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1902.0133 | 23.2 | 1 | 1 | 0024-Rotary plow | D2-Forced - Delayed | 100-Fossil-Steam
0024 | Rotary plow | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 108.3333 | 50 | 1 | 1 | 0024-Rotary plow | D1-Forced - Immediate | 100-Fossil-Steam
0024 | Rotary plow | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 303.3332 | 140 | 1 | 1 | 0024-Rotary plow | D1-Forced - Immediate | 100-Fossil-Steam
0024 | Rotary plow | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 443.3665 | 283 | 1 | 1 | 0024-Rotary plow | D1-Forced - Immediate | 100-Fossil-Steam
0024 | Rotary plow | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 488.7998 | 312 | 1 | 1 | 0024-Rotary plow | D1-Forced - Immediate | 100-Fossil-Steam
0024 | Rotary plow | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 454.9165 | 265 | 1 | 1 | 0024-Rotary plow | D1-Forced - Immediate | 100-Fossil-Steam
0026 | Dust suppression system | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 315.7332 | 128 | 1 | 1 | 0026-Dust suppression system | D1-Forced - Immediate | 100-Fossil-Steam
0026 | Dust suppression system | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 164.6666 | 65 | 1 | 1 | 0026-Dust suppression system | D1-Forced - Immediate | 100-Fossil-Steam
0028 | Dust collection system | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 588.2 | 173 | 1 | 1 | 0028-Dust collection system | D1-Forced - Immediate | 100-Fossil-Steam
0028 | Dust collection system | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2682.1664 | 385 | 1 | 1 | 0028-Dust collection system | D3-Forced - Postponed | 100-Fossil-Steam
0028 | Dust collection system | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 48.5 | 194 | 1 | 1 | 0028-Dust collection system | D2-Forced - Delayed | 100-Fossil-Steam
0028 | Dust collection system | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 197.1666 | 130 | 1 | 1 | 0028-Dust collection system | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 0.4 | 2 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1.8 | 18 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4 | 4 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 19.5 | 65 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 20.25 | 45 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 31 | 31 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 42.4999 | 150 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 587.6666 | 172 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1026 | 120 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1080 | 270 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1269.9333 | 172 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1648 | 103 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1653.2998 | 297 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1749.3499 | 177 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1966.8 | 447 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 13 | 26 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 51.9333 | 82 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 53.3333 | 40 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 150.4 | 16 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 163.7999 | 108 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 200.5833 | 29 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 200.6 | 68 | 2 | 2 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 245.4166 | 155 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 305.1333 | 92 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 587.6 | 226 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1191.3 | 49.5 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2.9 | 6 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 23.3333 | 70 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 49 | 35 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 170.6666 | 160 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 192 | 240 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 283.5 | 27 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 421.9999 | 120 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 489.6666 | 65 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 576 | 64 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 673.9999 | 120 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1035 | 15 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1083.75 | 289 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2962.175 | 252.1 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4612.5 | 250 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 56 | 56 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 75 | 75 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 206 | 60 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1963.7565 | 306.04 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Other | BM | 100 | Fossil-Steam | SERC | Winter | 3.3 | 3.3 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 4614.9999 | 195 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 76 | 120 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1337.6 | 152 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 408.3833 | 107 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 990 | 220 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5 | 15 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 10.2666 | 56 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 17.0667 | 32 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 68 | 34 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 199.3333 | 130 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 281.75 | 115 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 363 | 242 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 399.55 | 131 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 434.6332 | 221 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 438.5333 | 104 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 562.6666 | 160 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 631.35 | 207 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 737.4999 | 150 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1456 | 91 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1725.8266 | 90.2 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 22 | 22 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 26.4517 | 26.9 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 37.5 | 10 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 114 | 19 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 266.7 | 127 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 349.3332 | 262 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 558.9332 | 256 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3575.3332 | 310 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4365.6 | 408 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 4721.4999 | 210 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2.9333 | 8 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3.5 | 10 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 111 | 37 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 174.0071 | 114.73 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 321.2665 | 244 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 377.0665 | 202 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 440 | 10 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 453.6 | 72 | 2 | 2 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 512.8332 | 170 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 615.6 | 342 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 669.1666 | 146 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 835.3333 | 28 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 852.8333 | 34 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1042.9999 | 210 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 5071.6666 | 170 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5920.6666 | 332 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 32.5 | 26 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 422.9333 | 208 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2164.1666 | 245 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 23497.9499 | 207 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 6257.35 | 341 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 112.1 | 57 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 775 | 100 | 1 | 1 | 0030-Coal conveyors and feeders | D3-Forced - Postponed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 20.3666 | 94 | 1 | 1 | 0030-Coal conveyors and feeders | D3-Forced - Postponed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 612 | 80 | 1 | 1 | 0030-Coal conveyors and feeders | D3-Forced - Postponed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7810.75 | 199 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 408.155 | 18.1 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2013 | Other | BM | 100 | Fossil-Steam | WECC | Off-Peak | 105.75 | 45 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 650483.6663 | 610 | 1 | 1 | 0030-Coal conveyors and feeders | U2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2.4 | 8 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 14.3333 | 4 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 29 | 29 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 117 | 195 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 352.6 | 164 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 410.9333 | 184 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 538.3333 | 85 | 2 | 2 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 724.2 | 71 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1304.3333 | 130 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1344.15 | 103 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1454.1333 | 76 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1530.8331 | 275 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 6988.1666 | 230 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 19864.4998 | 306 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 19.5 | 45 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 36 | 36 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 40.1333 | 56 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 71 | 60 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 306.6666 | 200 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 428.1333 | 169 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 480 | 120 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 564 | 94 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 641.2499 | 81 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1491.6 | 66 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1534.9998 | 300 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1609.9999 | 120 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2737.4499 | 159 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5557.5 | 30 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1.75 | 7 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2.3333 | 7 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2.5667 | 7 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3.4667 | 8 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3.8667 | 8 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4.6667 | 14 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 10.2 | 17 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 15.4999 | 93 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 183 | 61 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 187 | 11 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 265.1666 | 215 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 340 | 170 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 652 | 120 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1511.875 | 61.5 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2126.25 | 243 | 2 | 2 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2429.6664 | 370 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 4445 | 127 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 210 | 70 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 49.1666 | 50 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 4825.0666 | 332 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Other | BM | 100 | Fossil-Steam | SERC | Winter | 9.51 | 3.17 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 9.1 | 26 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 47.7 | 53 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 99.7333 | 34 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 115.15 | 47 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1262.05 | 129 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1620 | 180 | 1 | 1 | 0030-Coal conveyors and feeders | D3-Forced - Postponed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 436 | 80 | 1 | 1 | 0030-Coal conveyors and feeders | D3-Forced - Postponed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 13729.4166 | 335 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 513 | 540 | 2 | 2 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2013 | Oil | DI | 100 | Fossil-Steam | SERC | Summer | 688.2666 | 58 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2.25 | 5 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 12 | 12 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 16 | 16 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 23.9167 | 35 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 32.1 | 18 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 40 | 40 | 1 | 2 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 63.6876 | 112.39 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 149.1 | 71 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 170.8667 | 44 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 407.0999 | 207 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 789.75 | 195 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1611.6 | 408 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2590.6666 | 290 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 13448.7 | 293 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5 | 5 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 160.8333 | 10 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 218.1666 | 170 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 288.025 | 140.5 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 505.7499 | 255 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 949.1666 | 134 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1672.4 | 74 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 8.75 | 15 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 14 | 28 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 16.9993 | 23.72 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 134.1 | 44.7 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 378.6 | 18 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 668.5333 | 109 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 722.5 | 170 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 736.6666 | 170 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 736.6666 | 170 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 1052.3 | 34 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1260.4166 | 275 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1499.5833 | 61 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 374.3999 | 216 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 967.02 | 161.17 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 448 | 12 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 206.7 | 53 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 82.15 | 53 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1050 | 105 | 1 | 1 | 0030-Coal conveyors and feeders | D3-Forced - Postponed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1700 | 170 | 1 | 1 | 0030-Coal conveyors and feeders | D3-Forced - Postponed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 5799.2665 | 289 | 1 | 1 | 0030-Coal conveyors and feeders | D3-Forced - Postponed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 2530.8 | 54 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1.5833 | 5 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1.6333 | 7 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2.2167 | 7 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 12.6667 | 8 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 23.85 | 53 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 26.9166 | 85 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 28.75 | 115 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 51 | 51 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 101 | 101 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 166.5 | 74 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 205.8333 | 50 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 211.5 | 141 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 215 | 215 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 273 | 273 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 414.4 | 148 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1035.6666 | 239 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1525.5 | 270 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2815.2999 | 282 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 6596.1665 | 190 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 10426.6664 | 340 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 29 | 58 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 65.9925 | 29.33 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 193.75 | 125 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 249.9999 | 150 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 271.95 | 111 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 278.6665 | 220 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 502.5 | 30 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 542.05 | 111 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1144.5831 | 335 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1597.9999 | 120 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1649.4666 | 278 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3162.5 | 275 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9956.9165 | 455 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3.2667 | 7 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4.5 | 9 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 16.8 | 63 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 72.0666 | 92 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 177.8667 | 23 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 196.9997 | 129.89 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 224 | 105 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 256 | 120 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 335.7999 | 219 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 625.6 | 102 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 824.5 | 170 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1475.8332 | 230 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2904.1665 | 250 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 912 | 152 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 19.5 | 6 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Oil | DI | 100 | Fossil-Steam | SERC | Winter | 38.6333 | 38 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Other | BM | 100 | Fossil-Steam | SERC | Winter | 3.25 | 3.25 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 9 | 12 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 2554.3332 | 158 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 19482.2833 | 187 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 306.9166 | 145 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 420 | 20 | 1 | 1 | 0030-Coal conveyors and feeders | D3-Forced - Postponed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2013 | Oil | DI | 100 | Fossil-Steam | SERC | Winter | 255.2 | 58 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1932.3333 | 124 | 1 | 1 | 0030-Coal conveyors and feeders | U2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 0.55 | 3 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 22.6667 | 8 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 45 | 20 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 98.0833 | 107 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 154 | 120 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 195.4167 | 35 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 593.5999 | 159 | 2 | 2 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 616 | 123.2 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 988 | 130 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2445.45 | 357 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2485.8666 | 236 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 50.75 | 35 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 149.3333 | 10 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 562.5 | 30 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 612 | 306 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 940.8 | 224 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1004.4998 | 294 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1155 | 105 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1606 | 120 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1690.2166 | 269 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2502.4998 | 273 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 6357 | 18 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2.6667 | 8 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3 | 20 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4.8 | 16 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 6.5333 | 14 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 32.9166 | 25 | 2 | 2 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 218.3333 | 100 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 329.55 | 169 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 406.5 | 18 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 473.3332 | 200 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 559.9999 | 120 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 813 | 271 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1246.8999 | 222 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1982.3833 | 121 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 649.2833 | 163 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 93 | 31 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 4294.0832 | 227 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Oil | DI | 100 | Fossil-Steam | SERC | Off-Peak | 6.9667 | 38 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Oil | DI | 100 | Fossil-Steam | SERC | Winter | 292.2 | 18 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 3.9 | 18 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 400 | 200 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 197.6333 | 77 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 440.2333 | 94 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 22.75 | 39 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 44.95 | 29 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1900 | 190 | 1 | 1 | 0030-Coal conveyors and feeders | D3-Forced - Postponed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2088.8333 | 83 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 12743.5 | 770 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 7893.333 | 925 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2013 | Oil | DI | 100 | Fossil-Steam | SERC | Winter | 426.3 | 58 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 1552.5 | 45 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3.25 | 5 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 8.0373 | 10.96 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 18 | 27 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 21.6 | 6 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 30 | 30 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 36.132 | 90.33 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 39.0833 | 35 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 60 | 12 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 85.4667 | 8 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 97.75 | 23 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 189 | 135 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 458.1999 | 174 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 487.5 | 30 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 885 | 295 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 945 | 270 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1117.5999 | 264 | 2 | 2 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1180 | 295 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2186.7999 | 132 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3553.1163 | 529 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5486 | 211 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9232.6665 | 220 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 11.6667 | 1 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 381 | 127 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 859.4999 | 270 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1402.2333 | 62 | 2 | 2 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1419.7332 | 352 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1494.2 | 241 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1567.5 | 330 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1719 | 191 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2298.3333 | 20 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3.85 | 11 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 63.9 | 71 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 293.5333 | 119 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 407.7333 | 88 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 463.25 | 85 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 637.5 | 250 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 662 | 165.5 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 730.3333 | 28 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1206.3333 | 220 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3949.4 | 282.1 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 872 | 218 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Oil | DI | 100 | Fossil-Steam | SERC | Summer | 75.85 | 37 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 2.04 | 2.04 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 675 | 150 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 810 | 135 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1657.7 | 242 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1874.25 | 153 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 26.6667 | 32 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 158.2333 | 94 | 1 | 1 | 0030-Coal conveyors and feeders | D3-Forced - Postponed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 738.15 | 133 | 1 | 1 | 0030-Coal conveyors and feeders | D3-Forced - Postponed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 626564.3 | 577 | 1 | 1 | 0030-Coal conveyors and feeders | U2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6.5 | 6 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 10.9667 | 47 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 12 | 10 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 13.25 | 5 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 35.2 | 66 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 47.0049 | 82.95 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 80 | 40 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 120.75 | 161 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 139.3999 | 102 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 201.2499 | 105 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 213.3 | 54 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 364.5 | 243 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 387.9333 | 92 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 542.2499 | 135 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1458 | 243 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1838.8333 | 118 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1988.91 | 40.59 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2204 | 464 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4543.8331 | 398 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10854.9999 | 300 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 12.9988 | 33.91 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 31 | 31 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 92.4999 | 150 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 152.95 | 19 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 182.6666 | 137 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 301.8166 | 91 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1408.1664 | 355 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1493.3331 | 320 | 2 | 2 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 7590 | 460 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2.6833 | 7 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3.5 | 7 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4.8 | 9 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 5 | 12 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 6.3333 | 10 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 16.83 | 37.4 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 20 | 25 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 142.45 | 33 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 308.5333 | 89 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 338.8 | 84 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 354.1666 | 170 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 415.9999 | 120 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 449.9998 | 270 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 694.1666 | 170 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1261.6999 | 222 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2499.9333 | 77 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3157.4833 | 59 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 3622.5833 | 145 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 5100 | 170 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 155.3999 | 133.2 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 57.4166 | 53 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 43 | 21.5 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 2756.9716 | 312.11 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 223.2 | 93 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2293.5 | 417 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 67.7666 | 107 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2013 | Oil | DI | 100 | Fossil-Steam | SERC | Off-Peak | 175.9333 | 58 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 94.7333 | 58 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5409.1332 | 469 | 1 | 1 | 0030-Coal conveyors and feeders | U3-Forced - Postponed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 650 | Fluidized Bed | SERC | Winter | 2007 | 180 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 650-Fluidized Bed
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 2232.75 | 13 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 800-Miscellaneous
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 196.6667 | 20 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 50.6 | 92 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 1524.3332 | 269 | 2 | 2 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 541.3666 | 218 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 580.1666 | 118 | 2 | 2 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 69 | 69 | 2 | 2 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 265.9999 | 168 | 2 | 2 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 399.7499 | 369 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Winter | 265.3333 | 20 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 15 | 18 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 285.1999 | 138 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 582.9999 | 318 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 861.6666 | 188 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 932.5332 | 269 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 2111.65 | 269 | 2 | 2 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 51 | 18 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 490.5 | 218 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 640.9333 | 88 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 54.25 | 93 | 2 | 2 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 210.4333 | 118 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 323.9166 | 169 | 2 | 2 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 545 | 218 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Winter | 230.6666 | 80 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Winter | 663.3333 | 50 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 1241 | 68 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 2040.4998 | 318 | 2 | 2 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 109 | 218 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 291.9999 | 219 | 2 | 2 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 361 | 38 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 472.3332 | 218 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 179.55 | 133 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 102 | 68 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 267.4666 | 118 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 313.2 | 348 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 450.5332 | 218 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 1135.633 | 434 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 1366.4665 | 398 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 1125 | 90 | 1 | 1 | 0030-Coal conveyors and feeders | D3-Forced - Postponed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 233.4666 | 68 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 376.5 | 18 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 378 | 168 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0035 | Metal detector/collector (including magnetic separator) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 348.4 | 134 | 1 | 1 | 0035-Metal detector/collector (including magnetic separator) | D1-Forced - Immediate | 100-Fossil-Steam
0040 | Coal elevators | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 23.8333 | 22 | 1 | 1 | 0040-Coal elevators | D1-Forced - Immediate | 100-Fossil-Steam
0040 | Coal elevators | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 142.5 | 150 | 1 | 1 | 0040-Coal elevators | D1-Forced - Immediate | 100-Fossil-Steam
0040 | Coal elevators | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 181.9166 | 185 | 1 | 1 | 0040-Coal elevators | D1-Forced - Immediate | 100-Fossil-Steam
0040 | Coal elevators | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6716.6658 | 1300 | 1 | 1 | 0040-Coal elevators | U1-Forced - Immediate | 100-Fossil-Steam
0040 | Coal elevators | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 2457.2666 | 62 | 1 | 1 | 0040-Coal elevators | D1-Forced - Immediate | 800-Miscellaneous
0050 | Coal storage fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 489 | 45 | 1 | 1 | 0050-Coal storage fires | D1-Forced - Immediate | 100-Fossil-Steam
0050 | Coal storage fires | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 593.5831 | 419 | 2 | 2 | 0050-Coal storage fires | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 202.4 | 33 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 725.3332 | 170 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 779.1666 | 170 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1390.9499 | 297 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 24 | 24 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 134.3333 | 124 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 141.3166 | 61 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2221.8499 | 111 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 281.9166 | 85 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 402.3333 | 34 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 611.6666 | 100 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 313.2 | 24 | 1 | 1 | 0060-Coal crushers including motors | D2-Forced - Delayed | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 280.8 | 117 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 90 | 36 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 726 | 121 | 1 | 1 | 0060-Coal crushers including motors | D2-Forced - Delayed | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 100 | 100 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 152 | 76 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 95.6666 | 82 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1044.9999 | 132 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2074.1665 | 262 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 10 | 24 | 1 | 1 | 0060-Coal crushers including motors | D2-Forced - Delayed | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 336.8333 | 94 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 50.1666 | 43 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 165.6 | 27 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 2901.8166 | 227 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | U2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5923.25 | 95 | 1 | 1 | 0060-Coal crushers including motors | U2-Forced - Delayed | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | U3 | Forced - Postponed | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 31850 | 455 | 1 | 1 | 0060-Coal crushers including motors | U3-Forced - Postponed | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 37.2 | 93 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 64.2 | 18 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 770.6666 | 170 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1952.8998 | 354 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 81.9 | 63 | 3 | 3 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1567.7 | 61 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1964.7 | 111 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 15.8333 | 19 | 1 | 1 | 0060-Coal crushers including motors | D2-Forced - Delayed | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 708 | 118 | 1 | 1 | 0060-Coal crushers including motors | D2-Forced - Delayed | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 782.3833 | 157 | 1 | 1 | 0060-Coal crushers including motors | D3-Forced - Postponed | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2013 | Coal | CC | 650 | Fluidized Bed | WECC | Summer | 1933.3333 | 100 | 1 | 1 | 0060-Coal crushers including motors | U1-Forced - Immediate | 650-Fluidized Bed
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Winter | 405 | 60 | 2 | 2 | 0060-Coal crushers including motors | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 888 | 444 | 2 | 2 | 0060-Coal crushers including motors | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 276 | 69 | 2 | 2 | 0060-Coal crushers including motors | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0070 | Coal samplers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 32 | 4 | 1 | 1 | 0070-Coal samplers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1380.3832 | 277 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1394.6667 | 20 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 841.1333 | 124 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 8.6333 | 37 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 628.6665 | 184 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 56.25 | 75 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 268.3333 | 70 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 877.5 | 150 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 110 | 110 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 32.6667 | 7 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 314622 | 420 | 1 | 1 | 0075-Storage silos/hoppers | U1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 0 | 0 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 336 | 140 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2136.8 | 8 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 210 | 350 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2012.5 | 250 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 6435.8248 | 605.25 | 1 | 1 | 0075-Storage silos/hoppers | U1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 185.1666 | 110 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 16.5 | 16.5 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 38.95 | 41 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 617.5 | 130 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 110.6667 | 8 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 14.6 | 73 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 70.2 | 117 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 250.1 | 61 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 60 | 10 | 1 | 1 | 0075-Storage silos/hoppers | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 360 | 160 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 58.3 | 22 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1424.3666 | 173 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2358.1831 | 287 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Oil | DI | 100 | Fossil-Steam | SERC | Off-Peak | 12.0333 | 38 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2567.2832 | 289 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1489.8 | 191 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 3 | 1.2 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 5843.25 | 265 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 52.8 | 22 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 607.1333 | 28 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 37.5667 | 23 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | U2 | Forced - Delayed | 2013 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 446.25 | 63 | 1 | 1 | 0080-Stackers/reclaimers | U2-Forced - Delayed | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 644.9999 | 180 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 650-Fluidized Bed
0084 | Coal conveyor scales-storage coal pile | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1308.7498 | 225 | 1 | 1 | 0084-Coal conveyor scales-storage coal pile | D2-Forced - Delayed | 100-Fossil-Steam
0084 | Coal conveyor scales-storage coal pile | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 15.85 | 3 | 1 | 1 | 0084-Coal conveyor scales-storage coal pile | D1-Forced - Immediate | 100-Fossil-Steam
0084 | Coal conveyor scales-storage coal pile | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 165 | 11 | 3 | 3 | 0084-Coal conveyor scales-storage coal pile | D1-Forced - Immediate | 100-Fossil-Steam
0084 | Coal conveyor scales-storage coal pile | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1497.1 | 66 | 1 | 1 | 0084-Coal conveyor scales-storage coal pile | D1-Forced - Immediate | 100-Fossil-Steam
0084 | Coal conveyor scales-storage coal pile | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 296 | 4 | 1 | 1 | 0084-Coal conveyor scales-storage coal pile | D1-Forced - Immediate | 100-Fossil-Steam
0084 | Coal conveyor scales-storage coal pile | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 475.1667 | 5 | 1 | 1 | 0084-Coal conveyor scales-storage coal pile | D1-Forced - Immediate | 100-Fossil-Steam
0084 | Coal conveyor scales-storage coal pile | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 528.6666 | 130 | 1 | 1 | 0084-Coal conveyor scales-storage coal pile | D1-Forced - Immediate | 100-Fossil-Steam
0084 | Coal conveyor scales-storage coal pile | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 845.75 | 51 | 1 | 1 | 0084-Coal conveyor scales-storage coal pile | D1-Forced - Immediate | 100-Fossil-Steam
0084 | Coal conveyor scales-storage coal pile | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 898.4 | 3 | 1 | 1 | 0084-Coal conveyor scales-storage coal pile | D1-Forced - Immediate | 100-Fossil-Steam
0084 | Coal conveyor scales-storage coal pile | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 679.8 | 66 | 1 | 1 | 0084-Coal conveyor scales-storage coal pile | D1-Forced - Immediate | 100-Fossil-Steam
0084 | Coal conveyor scales-storage coal pile | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1197.9333 | 4 | 1 | 1 | 0084-Coal conveyor scales-storage coal pile | D1-Forced - Immediate | 100-Fossil-Steam
0084 | Coal conveyor scales-storage coal pile | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 770 | 66 | 1 | 1 | 0084-Coal conveyor scales-storage coal pile | D1-Forced - Immediate | 100-Fossil-Steam
0084 | Coal conveyor scales-storage coal pile | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 168.1333 | 8 | 1 | 1 | 0084-Coal conveyor scales-storage coal pile | D1-Forced - Immediate | 100-Fossil-Steam
0085 | Bunker feeder coal scales | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 311.3 | 6 | 1 | 1 | 0085-Bunker feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0085 | Bunker feeder coal scales | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 181.7333 | 47 | 1 | 1 | 0085-Bunker feeder coal scales | D2-Forced - Delayed | 100-Fossil-Steam
0085 | Bunker feeder coal scales | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 27.1833 | 7 | 1 | 1 | 0085-Bunker feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 393.75 | 45 | 1 | 1 | 0090-Bunker fires | D1-Forced - Immediate | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 21.25 | 51 | 1 | 1 | 0090-Bunker fires | D1-Forced - Immediate | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 56.3333 | 20 | 1 | 1 | 0090-Bunker fires | D1-Forced - Immediate | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 178.25 | 115 | 1 | 1 | 0090-Bunker fires | D1-Forced - Immediate | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 564.75 | 45 | 1 | 1 | 0090-Bunker fires | D3-Forced - Postponed | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 81.75 | 109 | 1 | 1 | 0090-Bunker fires | D1-Forced - Immediate | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 285 | 57 | 1 | 1 | 0090-Bunker fires | D1-Forced - Immediate | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 553.0667 | 17 | 1 | 1 | 0090-Bunker fires | D1-Forced - Immediate | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 177.7333 | 31 | 1 | 1 | 0090-Bunker fires | D1-Forced - Immediate | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 277.5 | 50 | 1 | 1 | 0090-Bunker fires | D1-Forced - Immediate | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 134.1666 | 115 | 1 | 1 | 0090-Bunker fires | D1-Forced - Immediate | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 18.6667 | 8 | 1 | 1 | 0090-Bunker fires | D1-Forced - Immediate | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1304.9999 | 135 | 1 | 1 | 0090-Bunker fires | D1-Forced - Immediate | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 62 | 31 | 1 | 1 | 0090-Bunker fires | D1-Forced - Immediate | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 38.75 | 31 | 1 | 1 | 0090-Bunker fires | D1-Forced - Immediate | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 82.7667 | 13 | 1 | 1 | 0090-Bunker fires | D1-Forced - Immediate | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 658.3333 | 100 | 1 | 1 | 0090-Bunker fires | D1-Forced - Immediate | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 12999.1665 | 190 | 1 | 1 | 0090-Bunker fires | U1-Forced - Immediate | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 693.3333 | 20 | 1 | 1 | 0090-Bunker fires | D1-Forced - Immediate | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 800 | 50 | 1 | 1 | 0090-Bunker fires | D1-Forced - Immediate | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1755.6 | 228 | 1 | 1 | 0090-Bunker fires | D1-Forced - Immediate | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 86.45 | 39 | 1 | 1 | 0090-Bunker fires | D2-Forced - Delayed | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 23.01 | 7.67 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 162.5 | 25 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 224 | 56 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 237.2066 | 167.44 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 292.5 | 30 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 2236.6666 | 110 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6.7833 | 37 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 60.5666 | 79 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 210 | 50 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 516.6665 | 250 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1930.5 | 117 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3038.6666 | 53 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 33.6833 | 47 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 46.6666 | 70 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 90.8333 | 50 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 106.68 | 12.6 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Oil | DI | 100 | Fossil-Steam | SERC | Summer | 22.8666 | 28 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Oil | DI | 100 | Fossil-Steam | SERC | Summer | 23.4667 | 22 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 96 | 24 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 76.5 | 25.5 | 1 | 1 | 0095-Bunker flow problems | D2-Forced - Delayed | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2013 | Oil | DI | 100 | Fossil-Steam | SERC | Summer | 150.8 | 58 | 1 | 1 | 0095-Bunker flow problems | U1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 34.6666 | 80 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 191.3333 | 205 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 237.5 | 19 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 0.8833 | 53 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 42.5833 | 35 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 117 | 26 | 3 | 3 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 221.6667 | 50 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 84.0999 | 87 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 231.1165 | 283 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1683.2 | 263 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 355.84 | 9.6 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Oil | DI | 100 | Fossil-Steam | SERC | Summer | 290.0667 | 38 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 1.26 | 1.26 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 18 | 9 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 21.605 | 44.7 | 1 | 1 | 0095-Bunker flow problems | D2-Forced - Delayed | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 193.6666 | 83 | 1 | 1 | 0095-Bunker flow problems | D2-Forced - Delayed | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6.6 | 18 | 1 | 1 | 0095-Bunker flow problems | D2-Forced - Delayed | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 61.75 | 19 | 1 | 1 | 0095-Bunker flow problems | D2-Forced - Delayed | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2013 | Oil | DI | 100 | Fossil-Steam | SERC | Summer | 1917.8666 | 58 | 1 | 1 | 0095-Bunker flow problems | U1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 101.3333 | 80 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 30.8333 | 50 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1562.5 | 50 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 129 | 90 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 190.7666 | 118 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 224.1 | 54 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 269.2333 | 82 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 86.92 | 10.6 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 48 | 2 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 23.3933 | 24.2 | 1 | 1 | 0095-Bunker flow problems | D2-Forced - Delayed | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 10.4433 | 24.1 | 1 | 1 | 0095-Bunker flow problems | D2-Forced - Delayed | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2013 | Oil | DI | 100 | Fossil-Steam | SERC | Summer | 649.6 | 58 | 1 | 1 | 0095-Bunker flow problems | U1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2013 | Oil | DI | 100 | Fossil-Steam | SERC | Summer | 706.6333 | 58 | 1 | 1 | 0095-Bunker flow problems | U1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 694.4333 | 83 | 1 | 1 | 0095-Bunker flow problems | U1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 11.5 | 69 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 53.3333 | 50 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 68.75 | 55 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 111.35 | 51 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1224 | 240 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 32.5 | 30 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 48.75 | 15 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 222.4667 | 47 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 8 | 4 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 104.5 | 38 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 9.5 | 38 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3.2067 | 14.8 | 1 | 1 | 0095-Bunker flow problems | D2-Forced - Delayed | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 60.7466 | 54.4 | 1 | 1 | 0095-Bunker flow problems | D2-Forced - Delayed | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1336.1333 | 44 | 1 | 1 | 0095-Bunker flow problems | D2-Forced - Delayed | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 34.2733 | 21.2 | 1 | 1 | 0095-Bunker flow problems | D2-Forced - Delayed | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 95.6667 | 14 | 1 | 1 | 0095-Bunker flow problems | D2-Forced - Delayed | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2013 | Oil | DI | 100 | Fossil-Steam | SERC | Summer | 63.8 | 58 | 1 | 1 | 0095-Bunker flow problems | U1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5 | 20 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 17.4113 | 37.31 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 828.75 | 85 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4535.5999 | 204 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 83.4166 | 91 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 116.9 | 167 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 375.8333 | 110 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 412.5332 | 221 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 688.05 | 99 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 1005.7333 | 15.2 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 273.8333 | 21.2 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Oil | DI | 100 | Fossil-Steam | SERC | Summer | 36.7333 | 38 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Oil | DI | 100 | Fossil-Steam | SERC | Summer | 672.6 | 38 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 24 | 8 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 264 | 22 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 304 | 38 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 80.4 | 20.1 | 1 | 1 | 0095-Bunker flow problems | D2-Forced - Delayed | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 26 | 12 | 1 | 1 | 0095-Bunker flow problems | D2-Forced - Delayed | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 1481.366 | 238.93 | 1 | 1 | 0095-Bunker flow problems | U1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1621.6662 | 700 | 1 | 1 | 0095-Bunker flow problems | U1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 38.1833 | 29 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 42 | 24 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 58.6845 | 51.03 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 567.5999 | 198 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 597.6667 | 44 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2183.9999 | 180 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 27.3 | 3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 888.3 | 126 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1584 | 144 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 23.8333 | 22 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 34.8 | 24 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 230.0164 | 373 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 512.9 | 22.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 599.8666 | 88 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 52.7 | 10.2 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Oil | DI | 100 | Fossil-Steam | SERC | Summer | 11.1167 | 23 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Oil | DI | 100 | Fossil-Steam | SERC | Summer | 575.0667 | 38 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 100.8 | 11.2 | 1 | 1 | 0095-Bunker flow problems | D2-Forced - Delayed | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4171.6667 | 50 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 75.3333 | 40 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 238 | 14 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 689 | 52 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1.9833 | 17 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4.3167 | 7 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 22.9166 | 55 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 189 | 54 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 254.9999 | 225 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 275.7332 | 188 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 356.25 | 75 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1579.7166 | 299 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 65.8667 | 38 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5.2567 | 16.6 | 1 | 1 | 0095-Bunker flow problems | D2-Forced - Delayed | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8.7467 | 16.4 | 1 | 1 | 0095-Bunker flow problems | D2-Forced - Delayed | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 38.4266 | 52.4 | 1 | 1 | 0095-Bunker flow problems | D2-Forced - Delayed | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 38.5 | 33 | 1 | 1 | 0095-Bunker flow problems | D2-Forced - Delayed | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9.75 | 45 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 30 | 25 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 89.5 | 30 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2579.85 | 189 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 71.4 | 21 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 142.91 | 138.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 34.5 | 30 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 41.6 | 26 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 199.8333 | 110 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 633.6 | 198 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 28 | 7 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 72.6 | 18 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 968 | 44 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9.8933 | 21.2 | 1 | 1 | 0095-Bunker flow problems | D2-Forced - Delayed | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 50.74 | 17.2 | 1 | 1 | 0095-Bunker flow problems | D2-Forced - Delayed | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 424.6667 | 39.2 | 1 | 1 | 0095-Bunker flow problems | D2-Forced - Delayed | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 342 | 38 | 1 | 1 | 0095-Bunker flow problems | D2-Forced - Delayed | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 249.6833 | 71 | 1 | 1 | 0095-Bunker flow problems | U1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2013 | Oil | DI | 100 | Fossil-Steam | SERC | Summer | 142.1 | 58 | 1 | 1 | 0095-Bunker flow problems | U1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | LI | 650 | Fluidized Bed | MRO | Off-Peak | 268.8 | 11.2 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 650-Fluidized Bed
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 33.3667 | 26 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0100 | Bunker gates | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 5036.2666 | 112 | 1 | 1 | 0100-Bunker gates | D1-Forced - Immediate | 100-Fossil-Steam
0100 | Bunker gates | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 4.8 | 12 | 1 | 1 | 0100-Bunker gates | D1-Forced - Immediate | 100-Fossil-Steam
0100 | Bunker gates | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 93.3333 | 70 | 1 | 1 | 0100-Bunker gates | D2-Forced - Delayed | 100-Fossil-Steam
0100 | Bunker gates | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 328.6 | 212 | 1 | 1 | 0100-Bunker gates | D1-Forced - Immediate | 100-Fossil-Steam
0100 | Bunker gates | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 910 | 130 | 1 | 1 | 0100-Bunker gates | D1-Forced - Immediate | 100-Fossil-Steam
0100 | Bunker gates | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 200.6 | 68 | 1 | 1 | 0100-Bunker gates | D1-Forced - Immediate | 100-Fossil-Steam
0100 | Bunker gates | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 645.8333 | 62 | 1 | 1 | 0100-Bunker gates | D1-Forced - Immediate | 100-Fossil-Steam
0100 | Bunker gates | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 149.3333 | 80 | 1 | 1 | 0100-Bunker gates | D1-Forced - Immediate | 100-Fossil-Steam
0100 | Bunker gates | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 525.6666 | 332 | 1 | 1 | 0100-Bunker gates | D1-Forced - Immediate | 100-Fossil-Steam
0100 | Bunker gates | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 1358.7 | 14 | 1 | 1 | 0100-Bunker gates | D1-Forced - Immediate | 800-Miscellaneous
0105 | Bunker structures | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8.5 | 51 | 1 | 1 | 0105-Bunker structures | D1-Forced - Immediate | 100-Fossil-Steam
0105 | Bunker structures | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 41.4 | 23 | 1 | 1 | 0105-Bunker structures | D1-Forced - Immediate | 100-Fossil-Steam
0105 | Bunker structures | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 0 | 0 | 1 | 1 | 0105-Bunker structures | D1-Forced - Immediate | 100-Fossil-Steam
0105 | Bunker structures | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8.8167 | 23 | 1 | 1 | 0105-Bunker structures | D1-Forced - Immediate | 100-Fossil-Steam
0105 | Bunker structures | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5511.1166 | 53 | 1 | 1 | 0105-Bunker structures | D1-Forced - Immediate | 100-Fossil-Steam
0105 | Bunker structures | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 199.5 | 42 | 1 | 1 | 0105-Bunker structures | D1-Forced - Immediate | 100-Fossil-Steam
0105 | Bunker structures | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 110.9333 | 26 | 1 | 1 | 0105-Bunker structures | D1-Forced - Immediate | 100-Fossil-Steam
0105 | Bunker structures | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 627.0833 | 35 | 1 | 1 | 0105-Bunker structures | D1-Forced - Immediate | 100-Fossil-Steam
0105 | Bunker structures | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 30.0833 | 19 | 1 | 1 | 0105-Bunker structures | D1-Forced - Immediate | 100-Fossil-Steam
0106 | Coal drying system (see additional codes 0125-0127) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 163.8 | 14 | 1 | 1 | 0106-Coal drying system (see additional codes 0125-0127) | D1-Forced - Immediate | 100-Fossil-Steam
0106 | Coal drying system (see additional codes 0125-0127) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 21.0833 | 11 | 1 | 1 | 0106-Coal drying system (see additional codes 0125-0127) | D1-Forced - Immediate | 100-Fossil-Steam
0106 | Coal drying system (see additional codes 0125-0127) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 66 | 33 | 1 | 1 | 0106-Coal drying system (see additional codes 0125-0127) | D1-Forced - Immediate | 100-Fossil-Steam
0106 | Coal drying system (see additional codes 0125-0127) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 422.4333 | 38 | 1 | 1 | 0106-Coal drying system (see additional codes 0125-0127) | D1-Forced - Immediate | 100-Fossil-Steam
0106 | Coal drying system (see additional codes 0125-0127) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 458.5333 | 38 | 1 | 1 | 0106-Coal drying system (see additional codes 0125-0127) | D1-Forced - Immediate | 100-Fossil-Steam
0106 | Coal drying system (see additional codes 0125-0127) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 348.5 | 123 | 1 | 1 | 0106-Coal drying system (see additional codes 0125-0127) | D1-Forced - Immediate | 100-Fossil-Steam
0106 | Coal drying system (see additional codes 0125-0127) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 28 | 14 | 1 | 1 | 0106-Coal drying system (see additional codes 0125-0127) | D1-Forced - Immediate | 100-Fossil-Steam
0106 | Coal drying system (see additional codes 0125-0127) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 124 | 48 | 1 | 1 | 0106-Coal drying system (see additional codes 0125-0127) | D1-Forced - Immediate | 100-Fossil-Steam
0106 | Coal drying system (see additional codes 0125-0127) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 152.9 | 33 | 1 | 1 | 0106-Coal drying system (see additional codes 0125-0127) | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 21.3 | 18 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 50.3333 | 10 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 186 | 45 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 143.3333 | 25 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 276.2499 | 255 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 381 | 20 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 637.5 | 255 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 792.3166 | 137 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1125 | 150 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4176.6662 | 700 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 109.2 | 104 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 354.1666 | 170 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 406 | 58 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 2603.3333 | 110 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 33 | 33 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 168.4667 | 38 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 136 | 85 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D2-Forced - Delayed | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1167.95 | 141 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D2-Forced - Delayed | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2416 | 302 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D2-Forced - Delayed | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 903.4166 | 185 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D2-Forced - Delayed | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4028.25 | 205 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D2-Forced - Delayed | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 46.6666 | 25 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 225.2499 | 159 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 476.5832 | 215 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1973.3332 | 370 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2192.8332 | 295 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 14.9333 | 112 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 507 | 33.8 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1689.9999 | 390 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 94 | 120 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D2-Forced - Delayed | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2441 | 60 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | U1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 882.2166 | 43 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | U1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 90.65 | 49 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 119.6667 | 20 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 269.25 | 45 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1065.4665 | 262 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1.2166 | 73 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 8.4999 | 255 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 24.6999 | 78 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 29.0666 | 109 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 120 | 120 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 325 | 50 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1447.9329 | 587 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 71.9326 | 63.47 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 195.8333 | 94 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 725 | 100 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 17.6333 | 23 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 193 | 60 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D2-Forced - Delayed | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 390 | 260 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D2-Forced - Delayed | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | U2 | Forced - Delayed | 2013 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 77.3333 | 58 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | U2-Forced - Delayed | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 25.4999 | 153 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 99.5 | 15 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 833.333 | 500 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1074.4664 | 454 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 56.2033 | 64.85 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 114 | 38 | 1 | 2 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2017.483 | 437 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4601 | 43 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 30 | 8 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 517.5 | 115 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D2-Forced - Delayed | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1696.2 | 257 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D2-Forced - Delayed | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 320 | 320 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D2-Forced - Delayed | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 940 | 470 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D2-Forced - Delayed | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 987 | 63 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | U1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 201.9 | 18 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 351.8666 | 104 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 550 | 250 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 646.7499 | 195 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 946.6664 | 400 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 9.1667 | 10 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 92.75 | 53 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 241.2666 | 308 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 280 | 140 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 410.8 | 158 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 627.1665 | 530 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1131.6666 | 140 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 21.6667 | 25 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 201.6 | 48 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D2-Forced - Delayed | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1717.0833 | 65 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D3-Forced - Postponed | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8615.9999 | 180 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | U1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1169.45 | 57 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | U1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | U2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 218652 | 570 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | U2-Forced - Delayed | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 32.745 | 21.83 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 36.8 | 46 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 95.9999 | 90 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 277.6666 | 49 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 336.0832 | 185 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 653.25 | 195 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2.1 | 3 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 11.4 | 228 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 394.9998 | 300 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 700 | 50 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 857.6666 | 124 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2516.6665 | 500 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3 | 15 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 60.3333 | 10 | 1 | 2 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 145.6666 | 95 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 243 | 16.2 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1872 | 78 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 190.8 | 53 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1 | 4 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D2-Forced - Delayed | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 125.5 | 30 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D2-Forced - Delayed | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 7.8 | 13 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 9 | 18 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 17.3333 | 13 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 51 | 17 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 87.3999 | 228 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 106.3333 | 10 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 408.3333 | 100 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 659.7499 | 195 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 14.3333 | 20 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 20.3999 | 153 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 260.2333 | 211 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 303.1 | 433 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 700 | 100 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5631.8165 | 243.1 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 19.2666 | 34 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 74.7499 | 195 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 119.4163 | 106.94 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 261 | 145 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 380 | 40 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1638 | 78 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 122.1 | 18 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 288.5 | 15 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 16.4833 | 23 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 90 | 100 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D2-Forced - Delayed | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 740 | 370 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D2-Forced - Delayed | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1413.9165 | 235 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D2-Forced - Delayed | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1778 | 254 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D2-Forced - Delayed | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4432.9999 | 330 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | U1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2013 | Oil | DI | 100 | Fossil-Steam | SERC | Winter | 1111.6666 | 58 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | U1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 124.1333 | 49 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1481.6666 | 70 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 20.6833 | 73 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 69.7666 | 91 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 91.75 | 91.75 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 125.75 | 15 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 395.9998 | 270 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 403.8199 | 99.3 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 970 | 120 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 21 | 70 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 85.3333 | 40 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 109.0833 | 119 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2014.25 | 35 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 269.75 | 65 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D2-Forced - Delayed | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 351 | 195 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D2-Forced - Delayed | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 377.5833 | 115 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D2-Forced - Delayed | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 450 | 450 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D2-Forced - Delayed | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2080.75 | 145 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D2-Forced - Delayed | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3000 | 250 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D2-Forced - Delayed | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 4.1666 | 25 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 650-Fluidized Bed
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 429.3331 | 368 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 118 | 118 | 2 | 2 | 0110-Other coal fuel supply problems up through bunkers | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 872 | 218 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 1485.1664 | 469 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 3584.6999 | 378 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 7.8667 | 8 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 49.1666 | 118 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 99.7333 | 88 | 2 | 2 | 0110-Other coal fuel supply problems up through bunkers | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 4289.3665 | 434 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 60.6666 | 40 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 110 | 88 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 1844.4 | 318 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 993.4499 | 333 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 1885.5 | 419 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 74.8 | 68 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 185.9 | 338 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 370.9998 | 318 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 139.6665 | 419 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2013 | Other | WD | 650 | Fluidized Bed | RFC | Winter | 2493.3333 | 50 | 1 | 1 | 0111-Solid fuel feeder conveyors | U1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 16.5 | 5.5 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 650 | Fluidized Bed | WECC | Off-Peak | 3154.8423 | 33.82 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 650 | Fluidized Bed | WECC | Off-Peak | 1812.58 | 36.3 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 6.5917 | 3.5 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 191 | 47.75 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | U2 | Forced - Delayed | 2013 | Other | WD | 800 | Miscellaneous | WECC | Summer | 798.9367 | 17.9 | 1 | 1 | 0111-Solid fuel feeder conveyors | U2-Forced - Delayed | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Other | WD | 800 | Miscellaneous | WECC | Winter | 34.9867 | 3.28 | 2 | 2 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 14 | 14 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 6 | 6 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 88 | 15 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 650 | Fluidized Bed | SERC | Winter | 7.0833 | 5 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 130 | 10 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 650 | Fluidized Bed | SERC | Winter | 1.75 | 5 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | OS | 650 | Fluidized Bed | RFC | Off-Peak | 22.4 | 16 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 650 | Fluidized Bed | SERC | Winter | 5.25 | 5 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 0.41667 | 5 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 650 | Fluidized Bed | SERC | Winter | 8.75 | 15 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 650 | Fluidized Bed | SERC | Winter | 13.75 | 15 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | OS | 650 | Fluidized Bed | SERC | Summer | 145.0333 | 38 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | OS | 650 | Fluidized Bed | RFC | Winter | 23 | 23 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0119 | Solid fuel crushers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 11.9 | 10.5 | 1 | 1 | 0119-Solid fuel crushers | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 36 | 4.5 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 137.5 | 12.5 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 12.5 | 2.5 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 40.5 | 4.5 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 7.5 | 2.5 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2013 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 41.7083 | 32.5 | 1 | 1 | 0121-Other solid fuel feed problems | U1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 4 | 0.5 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 4.5 | 1.5 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 6 | 0.5 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 20 | 2.5 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 49.5 | 4.5 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 6 | 3 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 14 | 3.5 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 35.175 | 4.5 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 3 | 1.5 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Gas | GG | 650 | Fluidized Bed | SERC | Winter | 2957.5 | 338 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 460.7 | 34 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0125 | Coal crusher dryer hammers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3697.5 | 170 | 1 | 1 | 0125-Coal crusher dryer hammers | D1-Forced - Immediate | 100-Fossil-Steam
0126 | Coal crusher lube oil system | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 614.1666 | 110 | 1 | 1 | 0126-Coal crusher lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0126 | Coal crusher lube oil system | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 110.5 | 34 | 1 | 1 | 0126-Coal crusher lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0126 | Coal crusher lube oil system | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 73.35 | 27 | 1 | 1 | 0126-Coal crusher lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0126 | Coal crusher lube oil system | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 330 | 120 | 1 | 1 | 0126-Coal crusher lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0126 | Coal crusher lube oil system | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 642 | 120 | 1 | 1 | 0126-Coal crusher lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0126 | Coal crusher lube oil system | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 103.4166 | 85 | 1 | 1 | 0126-Coal crusher lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0127 | Other coal crusher dryer problems (see code 0106) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 106.1333 | 32 | 1 | 1 | 0127-Other coal crusher dryer problems (see code 0106) | D1-Forced - Immediate | 100-Fossil-Steam
0127 | Other coal crusher dryer problems (see code 0106) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 272.2667 | 16 | 1 | 1 | 0127-Other coal crusher dryer problems (see code 0106) | D1-Forced - Immediate | 100-Fossil-Steam
0127 | Other coal crusher dryer problems (see code 0106) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1507.3333 | 119 | 1 | 1 | 0127-Other coal crusher dryer problems (see code 0106) | D1-Forced - Immediate | 100-Fossil-Steam
0127 | Other coal crusher dryer problems (see code 0106) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2164.05 | 27 | 1 | 1 | 0127-Other coal crusher dryer problems (see code 0106) | D1-Forced - Immediate | 100-Fossil-Steam
0127 | Other coal crusher dryer problems (see code 0106) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 234 | 45 | 1 | 1 | 0127-Other coal crusher dryer problems (see code 0106) | D1-Forced - Immediate | 100-Fossil-Steam
0127 | Other coal crusher dryer problems (see code 0106) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 732.1874 | 123.75 | 1 | 1 | 0127-Other coal crusher dryer problems (see code 0106) | D1-Forced - Immediate | 100-Fossil-Steam
0127 | Other coal crusher dryer problems (see code 0106) | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 753.8666 | 128.5 | 1 | 1 | 0127-Other coal crusher dryer problems (see code 0106) | D2-Forced - Delayed | 100-Fossil-Steam
0127 | Other coal crusher dryer problems (see code 0106) | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 309.9999 | 150 | 1 | 1 | 0127-Other coal crusher dryer problems (see code 0106) | D2-Forced - Delayed | 100-Fossil-Steam
0127 | Other coal crusher dryer problems (see code 0106) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 266 | 105 | 1 | 1 | 0127-Other coal crusher dryer problems (see code 0106) | D1-Forced - Immediate | 100-Fossil-Steam
0127 | Other coal crusher dryer problems (see code 0106) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 596.1 | 9 | 1 | 1 | 0127-Other coal crusher dryer problems (see code 0106) | D1-Forced - Immediate | 100-Fossil-Steam
0127 | Other coal crusher dryer problems (see code 0106) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 994.5832 | 155 | 1 | 1 | 0127-Other coal crusher dryer problems (see code 0106) | D1-Forced - Immediate | 100-Fossil-Steam
0127 | Other coal crusher dryer problems (see code 0106) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 398.9333 | 44 | 1 | 1 | 0127-Other coal crusher dryer problems (see code 0106) | D1-Forced - Immediate | 100-Fossil-Steam
0127 | Other coal crusher dryer problems (see code 0106) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 216 | 120 | 1 | 1 | 0127-Other coal crusher dryer problems (see code 0106) | D1-Forced - Immediate | 100-Fossil-Steam
0127 | Other coal crusher dryer problems (see code 0106) | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2.4667 | 4 | 1 | 1 | 0127-Other coal crusher dryer problems (see code 0106) | D2-Forced - Delayed | 100-Fossil-Steam
0127 | Other coal crusher dryer problems (see code 0106) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 960 | 120 | 1 | 1 | 0127-Other coal crusher dryer problems (see code 0106) | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2290 | 100 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 472.35 | 141 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 428.8 | 128 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 630 | 60 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1882.9999 | 420 | 1 | 1 | 0129-Other coal processing system problems | D2-Forced - Delayed | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 14.4431 | 45.61 | 1 | 2 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 25 | 100 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 44.75 | 15 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2928.3332 | 140 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 223.2517 | 46.19 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 325 | 32.5 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 570.8333 | 50 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Oil | DI | 100 | Fossil-Steam | SERC | Winter | 87.3 | 18 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 8.3618 | 45.61 | 1 | 2 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 19.7643 | 45.61 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 31.1668 | 45.61 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 63.9498 | 132.31 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 64.225 | 91.75 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 118.6 | 59.3 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6.9366 | 41.62 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9.0176 | 41.62 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9.7113 | 41.62 | 1 | 2 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 15.9543 | 41.62 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 41.7 | 18 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 170.8333 | 50 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1213.1666 | 251 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2 | 1 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5.3211 | 45.61 | 1 | 2 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 18.244 | 45.61 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3.4167 | 5 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 11.7923 | 41.62 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 274.7065 | 177.23 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 317 | 2 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9279.9994 | 870 | 1 | 1 | 0129-Other coal processing system problems | U1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4.561 | 45.61 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 133.2945 | 46.77 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3824.3332 | 140 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3 | 1 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6.243 | 41.62 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 13.8733 | 41.62 | 1 | 2 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 36.3333 | 20 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 60.9999 | 183 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 152.9 | 11 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 190 | 95 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 172.8 | 128 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1223.4165 | 265 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 32.2733 | 20.6 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1660 | 415 | 1 | 1 | 0129-Other coal processing system problems | D2-Forced - Delayed | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 44.5 | 89 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 55.4921 | 45.61 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 139.9295 | 41.77 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 35 | 10 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 137.5 | 25 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 242.8425 | 58.05 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4 | 2 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 49.0967 | 20.6 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 90.1 | 53 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9.8821 | 45.61 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 30.4066 | 45.61 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 44.8673 | 51.77 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 133.8948 | 67.51 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2291.6666 | 100 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 14.567 | 41.62 | 1 | 3 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 21.15 | 9 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 29.8276 | 41.62 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 64.75 | 185 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 213.3332 | 128 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1210.1665 | 265 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3673.5997 | 492 | 1 | 1 | 0129-Other coal processing system problems | U1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9700 | 200 | 1 | 1 | 0129-Other coal processing system problems | U1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 94.4868 | 50.17 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 206 | 20 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 13.1796 | 41.62 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 17.3416 | 41.62 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 31.9306 | 59.87 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 167.7736 | 55.31 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 263.8333 | 10 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 7456 | 24 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | LI | 650 | Fluidized Bed | MRO | Winter | 77.22 | 32.4 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 650-Fluidized Bed
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2013 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 9 | 9 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 650-Fluidized Bed
0131 | Sorbent handling conveyors | Boiler | Sorbent Supply (fbc) | D1 | Forced - Immediate | 2013 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 854 | 85.4 | 1 | 1 | 0131-Sorbent handling conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0131 | Sorbent handling conveyors | Boiler | Sorbent Supply (fbc) | U1 | Forced - Immediate | 2013 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 19474.9996 | 570 | 1 | 1 | 0131-Sorbent handling conveyors | U1-Forced - Immediate | 650-Fluidized Bed
0131 | Sorbent handling conveyors | Boiler | Sorbent Supply (fbc) | D1 | Forced - Immediate | 2013 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 941.005 | 289.54 | 1 | 1 | 0131-Sorbent handling conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0131 | Sorbent handling conveyors | Boiler | Sorbent Supply (fbc) | D1 | Forced - Immediate | 2013 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 603 | 268 | 1 | 1 | 0131-Sorbent handling conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0132 | Sorbent handling feeders | Boiler | Sorbent Supply (fbc) | D1 | Forced - Immediate | 2013 | Gas | GG | 650 | Fluidized Bed | SERC | Winter | 61.8333 | 53 | 1 | 1 | 0132-Sorbent handling feeders | D1-Forced - Immediate | 650-Fluidized Bed
0160 | Bed material tanks/hoppers | Boiler | Bed Material Preparation System (fbc) | U1 | Forced - Immediate | 2013 | Gas | PC | 862 | CoG steam units | SERC | Summer | 1348.62 | 34.58 | 1 | 1 | 0160-Bed material tanks/hoppers | U1-Forced - Immediate | 862-CoG steam units
0168 | Bed material blowers/fans | Boiler | Bed Material Preparation System (fbc) | D1 | Forced - Immediate | 2013 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 784.75 | 129 | 1 | 1 | 0168-Bed material blowers/fans | D1-Forced - Immediate | 650-Fluidized Bed
0173 | Bed material pneumatic transport system including piping and valves | Boiler | Bed Material Preparation System (fbc) | D1 | Forced - Immediate | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Winter | 561.1667 | 35 | 1 | 1 | 0173-Bed material pneumatic transport system including piping and valves | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0174 | Other bed material handling equipment | Boiler | Bed Material Preparation System (fbc) | U1 | Forced - Immediate | 2013 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 12540 | 570 | 1 | 1 | 0174-Other bed material handling equipment | U1-Forced - Immediate | 650-Fluidized Bed
0174 | Other bed material handling equipment | Boiler | Bed Material Preparation System (fbc) | U1 | Forced - Immediate | 2013 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 6060.2499 | 105 | 1 | 1 | 0174-Other bed material handling equipment | U1-Forced - Immediate | 650-Fluidized Bed
0174 | Other bed material handling equipment | Boiler | Bed Material Preparation System (fbc) | D1 | Forced - Immediate | 2013 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 2844 | 316 | 1 | 1 | 0174-Other bed material handling equipment | D1-Forced - Immediate | 650-Fluidized Bed
0174 | Other bed material handling equipment | Boiler | Bed Material Preparation System (fbc) | U1 | Forced - Immediate | 2013 | Gas | PC | 862 | CoG steam units | SERC | Summer | 4668.3 | 34.58 | 1 | 1 | 0174-Other bed material handling equipment | U1-Forced - Immediate | 862-CoG steam units
0174 | Other bed material handling equipment | Boiler | Bed Material Preparation System (fbc) | U1 | Forced - Immediate | 2013 | Gas | PC | 862 | CoG steam units | SERC | Summer | 311.22 | 34.58 | 1 | 1 | 0174-Other bed material handling equipment | U1-Forced - Immediate | 862-CoG steam units
0174 | Other bed material handling equipment | Boiler | Bed Material Preparation System (fbc) | U1 | Forced - Immediate | 2013 | Gas | PC | 862 | CoG steam units | SERC | Summer | 760.76 | 34.58 | 1 | 1 | 0174-Other bed material handling equipment | U1-Forced - Immediate | 862-CoG steam units
0174 | Other bed material handling equipment | Boiler | Bed Material Preparation System (fbc) | U1 | Forced - Immediate | 2013 | Gas | PC | 862 | CoG steam units | SERC | Summer | 276.64 | 34.58 | 1 | 1 | 0174-Other bed material handling equipment | U1-Forced - Immediate | 862-CoG steam units
0174 | Other bed material handling equipment | Boiler | Bed Material Preparation System (fbc) | U1 | Forced - Immediate | 2013 | Gas | PC | 862 | CoG steam units | SERC | Summer | 276.0637 | 34.58 | 1 | 1 | 0174-Other bed material handling equipment | U1-Forced - Immediate | 862-CoG steam units
0174 | Other bed material handling equipment | Boiler | Bed Material Preparation System (fbc) | U1 | Forced - Immediate | 2013 | Gas | PC | 862 | CoG steam units | SERC | Off-Peak | 1659.84 | 34.58 | 1 | 1 | 0174-Other bed material handling equipment | U1-Forced - Immediate | 862-CoG steam units
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 9 | 36 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 72.9167 | 35 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 25 | 25 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 62 | 124 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 105 | 105 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 380 | 80 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 543.4 | 143 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 950 | 50 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1056.25 | 25 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1.9833 | 7 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 75 | 75 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 379.5 | 69 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 502.0166 | 91 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D2-Forced - Delayed | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 43.75 | 21 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D3-Forced - Postponed | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 193 | 60 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3470.8667 | 44 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 13.3333 | 40 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 656.8333 | 10 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 47 | 47 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 49.8166 | 61 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 274 | 137 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 221.6333 | 109 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 290 | 58 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2168.3333 | 25 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5000 | 40 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 32.6667 | 8 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 274.1666 | 70 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 403.2 | 96 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D3-Forced - Postponed | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 78 | 78 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 653.3333 | 70 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 885 | 60 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2525 | 50 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 939.25 | 85 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 168 | 28 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 52.6666 | 40 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1578.5 | 35 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3650.1666 | 55 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 112.7 | 49 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D2-Forced - Delayed | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 125.2 | 24 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D2-Forced - Delayed | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 26.025 | 62.46 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 31.2499 | 75 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 525.6667 | 20 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 239.4166 | 65 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D2-Forced - Delayed | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9295 | 55 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D3-Forced - Postponed | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4502.1666 | 34 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10884.15 | 57 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 458.45 | 53 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D2-Forced - Delayed | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 35.55 | 27 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1185.9166 | 95 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 878.7333 | 49 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D2-Forced - Delayed | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1116 | 72 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 187.2 | 48 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1339 | 30 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 11759 | 30 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 25.6667 | 7 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 136.275 | 39.5 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 255.8333 | 25 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 821.675 | 34.5 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1706.8333 | 95 | 1 | 2 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 72.0833 | 25 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 297.6666 | 94 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 21.6667 | 20 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 94.8 | 8 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 150 | 40 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 2750.6666 | 40 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0220 | Pulverizer system cyclone separator | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 196.6667 | 20 | 1 | 1 | 0220-Pulverizer system cyclone separator | D1-Forced - Immediate | 100-Fossil-Steam
0220 | Pulverizer system cyclone separator | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 360 | 20 | 1 | 1 | 0220-Pulverizer system cyclone separator | D1-Forced - Immediate | 100-Fossil-Steam
0220 | Pulverizer system cyclone separator | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 168 | 112 | 1 | 1 | 0220-Pulverizer system cyclone separator | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 66.8666 | 59 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 275.1666 | 130 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 673.8333 | 130 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 5 | 50 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 200 | 50 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 304 | 12 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3.6667 | 22 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 655.6666 | 140 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7 | 42 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 100.75 | 65 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 51.6666 | 50 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 20.5333 | 44 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 80.1666 | 74 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 120.6 | 67 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 506.6665 | 304 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 222.75 | 99 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 65.0833 | 11 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 647.8999 | 93 | 1 | 1 | 0240-Pulverized coal bin | D2-Forced - Delayed | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 12.3333 | 74 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 14.3 | 22 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 32.9 | 94 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 424.6666 | 130 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 814.1667 | 50 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 88 | 88 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 403.3333 | 88 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 624 | 104 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 90.9333 | 22 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 8662 | 71 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 29.4 | 28 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 176 | 88 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 36.7333 | 116 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 292.5 | 54 | 1 | 1 | 0240-Pulverized coal bin | U1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 78.75 | 63 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 171.6 | 104 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 550 | 25 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 44.95 | 29 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 550 | 125 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Oil | DI | 100 | Fossil-Steam | SERC | Summer | 130.5 | 58 | 1 | 1 | 0240-Pulverized coal bin | U1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 168.6666 | 88 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 513 | 54 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 830.1333 | 88 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 14.3 | 26 | 1 | 1 | 0240-Pulverized coal bin | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3 | 12 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3.2667 | 7 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4.45 | 89 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5.1667 | 10 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9.1 | 7 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 11 | 22 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 11.05 | 39 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 12 | 10 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 18.2 | 9.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 20.1667 | 22 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 25.8333 | 31 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 26.1 | 87 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 28.65 | 47.75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 31.0333 | 38 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 31.5 | 21 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 34.2 | 22.8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 39.4833 | 103 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 40.5999 | 87 | 1 | 2 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 40.6 | 116 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 47 | 47 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 54.8333 | 47 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 57.9735 | 29.73 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 58.82 | 34.6 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 59.5833 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 66.7 | 58 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 67.2 | 126 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 68.895 | 275.58 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 72.4 | 6 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 76.6666 | 115 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 77.3333 | 116 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 79.0833 | 73 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 80.1666 | 74 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 96 | 24 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 100.8666 | 68 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 101.5 | 145 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 116.9166 | 115 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 116.9999 | 135 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 123.25 | 17 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 133.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 148.005 | 42.9 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 161.25 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 182 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 224.5832 | 245 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 227.5 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 235 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 259 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 261.75 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 273.6 | 72 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 279.4333 | 101 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 280 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 300 | 200 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 320 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 365.75 | 33.25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 376 | 94 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 426.6666 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 430 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 433.35 | 107 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 441 | 180 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 462.25 | 43 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 511.85 | 87 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 530.25 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 541.7333 | 34 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 560.9333 | 56 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 589 | 19 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 682.5 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 731.6333 | 94 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 752.9166 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 760 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 791.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 792 | 144 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 849.85 | 69 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 859.3643 | 215.74 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1160 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1178.3332 | 140 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1212.9164 | 355 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1508.8333 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1800 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2.3333 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3.9667 | 17 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 8.6666 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9.5 | 57 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 14 | 14 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 14.0833 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 15 | 15 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 15.8333 | 95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 17.4 | 87 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 19 | 19 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 20.7083 | 35.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 21.6667 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 23 | 115 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 26 | 39 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 26 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 28.75 | 115 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 29.5833 | 71 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 30.3333 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 38 | 38 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 39.6667 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 41.7083 | 71.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 44.25 | 59 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 45.5 | 78 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 46.6666 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 47.5 | 19 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 47.6666 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 49 | 49 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 51.5 | 103 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 54.2098 | 250.2 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 58.9666 | 122 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 60 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 64.4 | 28 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 67.648 | 24.16 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 67.7833 | 83 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 73.6666 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 76.6833 | 43 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 80.4167 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 80.8333 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 83.95 | 69 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 84.1667 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 96.2499 | 165 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 98.05 | 111 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 117.45 | 87 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 117.4999 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 127.0999 | 93 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 137.5 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 149.8 | 84 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 162.1333 | 64 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 198.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 221.8666 | 128 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 235.2 | 48 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 250.25 | 105 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 271.4 | 92 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 277.5 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 285 | 190 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 313.5 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 341.25 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 349.7333 | 244 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 356.2499 | 225 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 400 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 406.25 | 125 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 419.3332 | 170 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 447.3 | 142 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 518.9999 | 180 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 522.6666 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 533.3333 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 583.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 659.0833 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 678.3333 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 711.0833 | 115 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 731.6 | 124 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 828.6166 | 83 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1050.9 | 113 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2689.9999 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3.8333 | 10 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4.1666 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 6 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6.8833 | 59 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 8.5333 | 16 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 8.7 | 6 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 10 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 11.5 | 23 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 12.5 | 10 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 14.4 | 144 | 1 | 2 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 14.895 | 33.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 20.6833 | 73 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 24.4 | 244 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 25.6 | 32 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 30.8 | 88 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 32.6666 | 98 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 39.5999 | 216 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 40 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 43.5 | 87 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 49.8333 | 115 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 50.6666 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 60.6666 | 52 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 67.5 | 5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 68.2333 | 23 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 70.2333 | 14 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 71.7833 | 59 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 75.8333 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 78.3 | 58 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 81.5833 | 89 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 81.935 | 234.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 82.3499 | 81 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 87.7333 | 14 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 93.5 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 103.3332 | 155 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 109.5 | 73 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 109.6 | 48 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 115.4999 | 126 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 117.1666 | 74 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 135.3333 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 140 | 70 | 2 | 2 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 151.6666 | 140 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 168 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 169.95 | 103 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 176 | 48 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 177.0833 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 200 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 210 | 105 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 210.8333 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 216.2 | 92 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 230.3 | 98 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 231.4 | 52 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 235 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 248.2883 | 46.7 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 249.6 | 144 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 254 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 259.1667 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 265.35 | 87 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 266 | 26.6 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 278.4 | 87 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 281.6666 | 52 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 282.15 | 31.35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 354.1666 | 170 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 386.9 | 73 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 398.25 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 435 | 87 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 472 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 659.85 | 83 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 695.5 | 107 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 732.25 | 101 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 793 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 870 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 903.4666 | 154 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 945 | 63 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 955 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1720 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1741.6666 | 125 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2087.5 | 167 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2632.0331 | 281 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3460.7999 | 126 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 54.25 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 100.4667 | 44 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 324 | 135 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 337.3333 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 544.95 | 63 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 582.0832 | 275 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1603.8166 | 233 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 18.6 | 31 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 85 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 151.3667 | 38 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 317 | 79.25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 747.48 | 124.58 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 748.9166 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Oil | DI | 100 | Fossil-Steam | SERC | Summer | 6.1666 | 37 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3.0683 | 26.3 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3.8 | 3.8 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 50 | 50 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 70.8333 | 34 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 158 | 30 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 448.5 | 117 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 16.3 | 16.3 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 29.5 | 15 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 182.4165 | 199 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 237.6666 | 124 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 276 | 23 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2.1 | 21 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 58.5 | 90 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 77.6833 | 79 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 80.85 | 147 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 300.2 | 158 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 683.1999 | 336 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 910 | 91 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1331.25 | 213 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 27.0833 | 65 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 17.3333 | 80 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 33 | 165 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 82.9331 | 311 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 144.8332 | 158 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 230.0999 | 117 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 313.1833 | 43 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 693.3333 | 160 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 712.5543 | 82.06 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 508 | 127 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 633.2333 | 121 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 656.8333 | 70 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 659.9999 | 99 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 376.1666 | 122 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 872.6665 | 476 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1524 | 635 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3.4667 | 1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6.8 | 51 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 10.1499 | 87 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 13.05 | 87 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 14.4999 | 87 | 1 | 2 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 14.5166 | 67 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 16 | 24 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 16.8703 | 46.01 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 17 | 170 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 17.3333 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 20.1833 | 7 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 20.2667 | 38 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 20.9666 | 34 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 24.3333 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 24.7 | 12.35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 26 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 27 | 21.6 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 27.6667 | 10 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 29 | 29 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 29.0966 | 60.2 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 32.0333 | 62 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 37.5 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 42.6666 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 46.6666 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 48.6666 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 51.2 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 62.5 | 125 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 63.3333 | 95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 65.55 | 69 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 67.3333 | 101 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 70 | 14 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 80.75 | 16.15 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 100.7706 | 97.52 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 101.25 | 5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 102 | 17 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 103.75 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 110 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 110 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 117.2 | 12 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 122.1999 | 141 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 128.1 | 122 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 144 | 240 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 161.7 | 98 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 162.5 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 168.0333 | 71 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 196 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 204.05 | 53 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 207.4333 | 98 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 224.1667 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 240.6666 | 152 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 282.8558 | 32.45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 286.6667 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 334.3333 | 118 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 340.2666 | 176 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 344.85 | 31.35 | 1 | 2 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 351.45 | 33 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 362.6833 | 47 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 405 | 135 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 434.3 | 101 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 439.4666 | 64 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 448.5333 | 116 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 508.3333 | 250 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 523.4999 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 527.5 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 625 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 650 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 695 | 139 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 722 | 152 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 844.4333 | 94 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 894.25 | 73 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 913.3333 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1082.4 | 33 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1630.4666 | 148 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1729.4333 | 169 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1841.4166 | 95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2310 | 220 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2581.2499 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3440.9832 | 137 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1.4 | 7 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2.05 | 3 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3.1667 | 5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3.75 | 9 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5.4833 | 47 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7.59 | 41.4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8.3233 | 9.08 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 13.3 | 57 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 13.7 | 137 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 14.5833 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 17.25 | 115 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 18.3333 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 21.4 | 64.2 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 22.6666 | 34 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 24 | 24 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 24 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 26.37 | 29.3 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 26.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 27.5333 | 59 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 29.3333 | 5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 35 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 35.9667 | 26 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 37 | 37 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 37.3333 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 42 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 43.3333 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 44.1666 | 106 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 51.6666 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 54.1666 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 56.0666 | 58 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 59.6167 | 7 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 64.1666 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 66 | 66 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 72 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 80.8333 | 97 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 96 | 64 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 100 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 110.8333 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 115.15 | 49 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 120.25 | 37 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 124.95 | 119 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 134 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 141.8333 | 115 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 144.0833 | 91 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 156.4 | 34 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 187.2 | 36 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 191.5833 | 121 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 193.6666 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 200 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 216.75 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 221.6667 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 233.3333 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 241.5 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 268.5 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 275 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 287.1 | 33 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 331.3333 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 349.9999 | 84 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 370.5 | 78 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 378 | 108 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 400.05 | 21 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 432.9 | 111 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 442.5 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 470.25 | 31.35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 660.8333 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 663.1333 | 98 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 787.5 | 450 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 832.5 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 891.6667 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 978.9999 | 165 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1016 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1592.0666 | 143 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1693.9999 | 165 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 0 | 0 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2.9333 | 8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3.15 | 63 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 6.5 | 13 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 11 | 1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 12.8 | 12.8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 13.05 | 87 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 13.75 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 14.6666 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 15.95 | 87 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 20.6666 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 21.0833 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 26 | 26 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 27.8667 | 44 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 28.5 | 114 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 29.1667 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 31.0333 | 19 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 36.45 | 81 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 40.0833 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 41.2533 | 22.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 43.3333 | 52 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 45 | 75 | 2 | 2 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 45.991 | 24.86 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 57.0333 | 59 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 57.6 | 144 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 61.5 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 64.6666 | 97 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 70.5833 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 80.75 | 16.15 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 92 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 95 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 97.5333 | 19 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 102.6 | 17.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 131.3333 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 152.7833 | 103 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 162.75 | 63 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 178.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 191.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 198 | 99 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 198.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 222.4166 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 275.3333 | 56 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 292 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 348.8333 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 382.1166 | 56.75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 383.7166 | 143 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 498.1666 | 122 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 528 | 22 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 558.0416 | 56.75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 672.5 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 715 | 220 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 755.1333 | 94 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 898.35 | 113 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 906 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1043.2499 | 117 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1088.7499 | 195 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1119.3333 | 115 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 1530.0173 | 362.85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1704 | 12 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1787.5 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1901.9166 | 145 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 2496.875 | 93.75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5295.9998 | 240 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 4.5833 | 11 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 6.5333 | 7 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 8.9833 | 11 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 12.7333 | 4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 15.25 | 61 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 89.3333 | 67 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 218.5 | 69 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 317.078 | 68.93 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1868.5 | 202 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2003.07 | 87.09 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 118.95 | 39 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 176 | 22 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 27.9 | 31 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 35.65 | 31 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 43.8 | 36 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 89.5833 | 43 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 333.4 | 83.35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 340.9666 | 106 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 637.5666 | 62 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 19.836 | 16.53 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 35.1249 | 84.3 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 38.75 | 25 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 143.5 | 21 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 0.9 | 0.9 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 15.8 | 15.8 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 49.22 | 42.8 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 86.6667 | 50 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 89.375 | 37.5 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 442.15 | 111 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 12.1 | 12.1 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 18.1 | 36.2 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 45.815 | 56.1 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 47.6067 | 14.8 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 348.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 423.3999 | 174 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 82.3333 | 52 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 126.4666 | 28 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 510 | 120 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 609.5 | 53 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 669.6666 | 140 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 81.4666 | 104 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 107.95 | 127 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 180.2666 | 104 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 183.3333 | 220 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 371.8332 | 230 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1184.55 | 149 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 92 | 92 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 230 | 20 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 67.5 | 90 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 301 | 60 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 453.3333 | 40 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 58.825 | 18.1 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 90.95 | 107 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 410.7999 | 156 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1938.75 | 825 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2.1 | 2.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2.5833 | 31 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3.2667 | 14 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 7.3333 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9.3333 | 10 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9.8 | 49 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 11.4 | 19 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 11.6667 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 13.2999 | 114 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 15.7333 | 4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 18.75 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 19.1333 | 82 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 20.3 | 87 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 21.25 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 22.1 | 51 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 22.5 | 15 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 28.2 | 94 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 31.9665 | 274 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 38 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 40 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 41.25 | 33 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 50 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 51.3333 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 54 | 54 | 1 | 2 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 56.0907 | 16.18 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 60 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 62 | 62 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 64.1666 | 77 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 66 | 132 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 66.9666 | 98 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 67.8 | 18 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 68.6097 | 18.46 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 69.4166 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 71.4999 | 78 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 73.2333 | 169 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 85 | 170 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 92.0833 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 94.1633 | 106.6 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 98 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 103.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 103.9999 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 104.5333 | 98 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 105 | 126 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 108.3333 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 109 | 109 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 113.75 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 132.3409 | 74.91 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 133.5 | 89 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 142.3499 | 117 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 152.5333 | 52 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 156.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 160.3333 | 148 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 174.25 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 182.91 | 87.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 184.95 | 27 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 185.1666 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 186.3333 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 200 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 218.5 | 46 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 219.8 | 42 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 220.3999 | 174 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 243 | 81 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 246.1667 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 262.752 | 54.74 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 264 | 88 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 268.25 | 87 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 280.8 | 144 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 304.8083 | 39.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 306 | 170 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 329.3333 | 19 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 330 | 165 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 357.3333 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 360 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 367.5 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 380 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 394.1666 | 215 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 396.3333 | 116 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 414 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 485 | 97 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 541.45 | 147 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 550 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 559.6666 | 73 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 580.9997 | 498 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 582 | 97 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 592.8 | 48 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 766.3332 | 209 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 843.75 | 225 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1081.1666 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1152.6666 | 140 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1184 | 37 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1404.6 | 36 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2918 | 12 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 5146.5833 | 151 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 10913.9166 | 113 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 0.66667 | 1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2.75 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3.2666 | 49 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3.45 | 9 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 4.6666 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4.83 | 41.4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5.7 | 9 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5.8667 | 22 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 6.6667 | 8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8.3333 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9.6666 | 58 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 11 | 11 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 11.6667 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 12.25 | 15 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 13.4167 | 23 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 14.6666 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 16 | 8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 16.65 | 27 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 17.3333 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 19.25 | 15 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 20.6 | 103 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 21.2667 | 22 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 21.6667 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 24.1667 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 36 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 38.3999 | 144 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 40.4166 | 97 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 50 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 55 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 56.4667 | 22 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 59.4166 | 115 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 62.001 | 7.47 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 64.1667 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 66.6666 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 68.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 79.1667 | 19 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 90.25 | 95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 104 | 104 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 105 | 300 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 108.3333 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 109.2 | 168 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 118 | 118 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 123 | 41 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 124.1333 | 98 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 130 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 142.1999 | 108 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 145.6666 | 115 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 215 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 220.5 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 228 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 230 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 300 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 310.05 | 159 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 311.6666 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 326.3999 | 144 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 354.6666 | 152 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 376 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 440 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 458.3333 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 493.0833 | 97 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 527 | 170 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 562.4999 | 135 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 628.35 | 71 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 764.8333 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 820.25 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 858.3333 | 125 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 885 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1116.25 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1209 | 39 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1362.75 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1466.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9272.4999 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3 | 9 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6 | 9 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 7 | 28 | 1 | 2 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 7.25 | 87 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 7.5 | 10 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 7.5533 | 41.2 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 11.6667 | 2 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 12.4 | 24 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 15 | 18 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 17.29 | 9.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 18.2 | 78 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 23.8 | 68 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 24.7999 | 93 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 27.5 | 5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 29.4666 | 68 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 35.1 | 39 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 42 | 42 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 46.1332 | 173 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 46.6666 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 50.4 | 84 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 50.4833 | 13 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 52 | 8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 55 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 55.55 | 101 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 67.1333 | 76 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 67.9999 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 70 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 71.5 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 92.5 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 98.3333 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 99.4989 | 81.78 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 103.5 | 34.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 104.1666 | 125 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 105 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 109.2 | 63 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 112.5 | 18 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 133.9999 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 141.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 157.5 | 105 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 158.7 | 23 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 187.9166 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 192.15 | 183 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 202.5 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 203.3 | 38 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 214 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 222.0833 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 233.5 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 261 | 290 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 270.4 | 104 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 293.75 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 300 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 304.7999 | 144 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 309 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 309.8333 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 310 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 314.1666 | 145 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 316 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 326.6333 | 82 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 351.1666 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 361.7999 | 81 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 367.65 | 40.85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 368.3333 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 441.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 539.4 | 87 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 584.0832 | 215 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 588 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 617.5 | 95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 676.5833 | 176.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 824.585 | 26.7 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 874 | 95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1026.6666 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 1039.4999 | 113.4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1130.6666 | 160 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1186 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1791 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 2075.8333 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 29.5 | 118 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 72 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 73.8 | 41 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 130.65 | 67 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 198.3333 | 68 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 229.0166 | 91 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 410.2333 | 31 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 420.3 | 54 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 5.85 | 13 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 31.9 | 29 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 35.5 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 50 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 115.0333 | 34 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 194 | 97 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 585 | 117 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 2 | 2 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 14.4 | 18 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | SERC | Winter | 51 | 68 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 115.7666 | 46 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 140.8 | 88 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 209.7333 | 52 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 214.9333 | 124 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 653.2 | 46 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 25.645 | 22.3 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 29.75 | 105 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 62.4 | 2.6 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 74.0433 | 45.8 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 907.8333 | 130 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 1230.25 | 111 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1250 | 250 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3.21 | 21.4 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3.9 | 13 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 15.42 | 25.7 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 19.6 | 4.9 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 20.2 | 10.1 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 29 | 29 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 35 | 5 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 315.1 | 274 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 930 | 25 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 32 | 60 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 75 | 75 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 92.7333 | 107 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 284.9 | 37 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 312 | 26 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 871.25 | 85 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1055.5999 | 174 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1085.7 | 47 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 3.3333 | 50 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 4.75 | 95 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 44.4333 | 43 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 64 | 60 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 22.6666 | 136 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 36.45 | 81 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 40.95 | 63 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 319.1999 | 144 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1616.083 | 473 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 54.1666 | 25 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 38.6 | 19.3 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 243.8333 | 95 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 97.5 | 50 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 462.9333 | 56 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 855.6 | 72 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 16900.5 | 285 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 622.5832 | 155 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1031.7998 | 231 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1764.7496 | 585 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5859 | 155 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 0 | 0 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1.0167 | 1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1.1 | 3 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3.625 | 14.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9.6 | 36 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10.1616 | 60.97 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10.3332 | 155 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 10.9417 | 10.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 12.6 | 14 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 14.6666 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 17.2833 | 17 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 17.4 | 87 | 1 | 2 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 17.4166 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 24.6165 | 211 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 26.6667 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 27 | 27 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 27.5167 | 13 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 29.4 | 7 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 34.1666 | 82 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 34.5666 | 61 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 40.3333 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 50 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 58.75 | 15 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 60 | 6 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 60.099 | 26.91 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 64 | 30 | 2 | 2 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 65.3333 | 98 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 68.4 | 76 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 69 | 69 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 69.3333 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 73.3333 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 73.6666 | 68 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 76.5 | 18 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 79.9999 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 82.4166 | 115 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 85.3999 | 84 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 108 | 36 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 112.5 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 114.0666 | 58 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 119.0016 | 129.82 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 122.5583 | 9.55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 126 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 142 | 71 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 143.4999 | 123 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 148.8333 | 19 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 151.4166 | 79 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 151.4666 | 142 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 159.005 | 32.45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 163.3332 | 245 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 165 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 168.5332 | 158 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 180 | 24 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 206.0583 | 39.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 218.3333 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 219.45 | 31.35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 227.55 | 41 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 230.0666 | 68 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 250 | 125 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 262.5 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 273.75 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 291.6665 | 250 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 297.25 | 145 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 326.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 329.3333 | 38 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 359.3333 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 376 | 235 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 411.6666 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 450.0833 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 472.5 | 81 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 481 | 52 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 500 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 525 | 140 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 610.6666 | 160 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 649.3333 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 693.3333 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 795.5 | 74 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 870.1333 | 52 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1074.9999 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1588.5333 | 112 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1704.9332 | 152 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2687.4999 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 7167.5 | 122 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1.6667 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2.0833 | 5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3.9 | 13 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7.5 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 9 | 18 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 9.8 | 14 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 13.3333 | 8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 14 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 15.3333 | 115 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 16 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 16.7875 | 4.25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 18.25 | 15 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 20.6833 | 73 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 24.8 | 124 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 24.84 | 41.4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 28 | 140 | 1 | 2 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 28.8405 | 59.67 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 29.45 | 31 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 30.4833 | 59 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 39 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 46 | 23 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 47.5 | 95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 47.5 | 95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 48.3 | 9 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 52.5 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 60 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 61.25 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 67.6 | 104 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 69.3333 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 70.2883 | 23.3 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 72 | 24 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 75 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 78 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 80.85 | 77 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 84 | 12 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 89.0166 | 109 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 93.75 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 101.3833 | 79 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 103.35 | 117 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 106.1666 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 107 | 107 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 112.1333 | 58 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 112.2 | 102 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 128.75 | 103 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 131.7499 | 93 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 132.1833 | 103 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 132.9166 | 145 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 136.6666 | 200 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 150 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 152.9999 | 108 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 154 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 154.0833 | 43 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 154.8 | 24 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 170.6666 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 172.6666 | 185 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 192.8333 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 218.9999 | 180 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 245 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 254.9999 | 225 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 273 | 140 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 281.6667 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 284 | 71 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 290 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 297.5999 | 288 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 319 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 349.1667 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 351.6667 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 374.0333 | 98 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 411.8333 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 424.6667 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 432 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 435.75 | 21 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 483.3333 | 145 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 492 | 48 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 527.35 | 53 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 533.1666 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 605.9833 | 103 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 625.5 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 663.1666 | 115 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 720 | 180 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 731.2499 | 135 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 812 | 58 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 825 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 862.9166 | 95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1046.3999 | 144 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1097.9166 | 155 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1112.5828 | 845 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1318 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 1834.8833 | 44.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2433.3332 | 200 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2644.4 | 88 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4035.4166 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2 | 40 | 1 | 2 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 10.6667 | 32 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 10.8333 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 11 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 12.5 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 12.9833 | 19 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 13.0333 | 17 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 15 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 16.4667 | 13 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 16.5 | 15 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 16.7999 | 144 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 20 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 23.1833 | 13 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 23.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 33.6 | 144 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 37.7166 | 73 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 42 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 44.605 | 24.33 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 45.3333 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 51.1833 | 83 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 52.2 | 87 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 55.2 | 144 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 56.6666 | 200 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 56.6667 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 58.6666 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 59.4166 | 115 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 59.5035 | 56.67 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 64.4833 | 73 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 68.15 | 87 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 69.6666 | 95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 70 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 73 | 73 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 75 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 77.8166 | 203 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 78.75 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 80.6666 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 89.0931 | 334.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 92.796 | 84.36 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 95.9999 | 144 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 102.35 | 69 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 107.25 | 39 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 112.5 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 113.62 | 43.7 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 116.5666 | 269 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 132 | 66 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 132 | 66 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 135.6 | 18 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 151.9999 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 153 | 102 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 157.0833 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 158.1666 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 188.6 | 123 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 207 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 221 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 345.8 | 52 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 356.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 440 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 440.8333 | 115 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 446.3333 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 462.5833 | 91 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 519.5833 | 145 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 540 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 585 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 623.392 | 49.28 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 624.0666 | 46 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 668.85 | 49 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 985.7166 | 71 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1032 | 86 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1068 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1164.9167 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1173 | 276 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1217.0833 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1841.5833 | 205 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2050.1332 | 128 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 4105.5 | 238 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 79.55 | 43 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 122.4166 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 183.6833 | 107 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 279.5 | 86 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 324.3 | 46 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 715 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 65.1166 | 78.14 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 170.8333 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1385.4333 | 89 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 63.5166 | 37 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 72.8333 | 46 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 80 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 212.8 | 32 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1143 | 95.25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1.8 | 1.8 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7 | 3.5 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10.85 | 18.6 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 11 | 5.5 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 20.75 | 15 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 40.8517 | 19.3 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 76.8 | 6.4 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 101.75 | 55 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 104.16 | 18.6 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 348.7166 | 49 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 385.5 | 128.5 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 859.9999 | 129 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 17.2 | 17.2 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 78.9483 | 46.9 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 163.6667 | 20 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 800.7999 | 168 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7.24 | 18.1 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 23.12 | 40.8 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 473.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2085.3833 | 211 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 4 | 16 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 10.1 | 101 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 85.5666 | 34 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 92.0833 | 65 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 96.2 | 78 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 233.75 | 33 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 397.6 | 71 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 470 | 200 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1568.65 | 137 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 13.9999 | 84 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 25 | 125 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 122.4 | 34 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 26.25 | 45 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 28 | 80 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 84.4999 | 195 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 162.6666 | 160 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 590 | 295 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 40 | 120 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 225 | 60 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 75.05 | 57 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 60.9367 | 18.1 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1823.0498 | 303 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 576.0832 | 155 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 640.3332 | 340 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 5.0667 | 38 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7.5533 | 41.2 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 7.65 | 27 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9.1667 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 10 | 24 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10.2 | 102 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 10.6666 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 14 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 17 | 17 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 18.8499 | 87 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 23.2 | 48 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 31 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 33.3333 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 33.6666 | 101 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 42.6667 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 44.9166 | 49 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 47.95 | 7 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 58.6667 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 62.5 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 63.9167 | 13 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 75.8333 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 78.8666 | 91 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 84.2333 | 19 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 89.75 | 15 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 90.6646 | 87.74 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 90.6667 | 2 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 91.5167 | 19 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 94.5 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 97.5 | 26 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 101.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 103 | 103 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 111.3333 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 117.3333 | 220 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 122.592 | 51.08 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 123.2 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 123.5 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 134 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 135.705 | 12.45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 142.5 | 19 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 142.5833 | 59 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 180 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 198.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 205.3166 | 97 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 242.1166 | 73 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 275 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 280 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 286 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 302.25 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 309.0081 | 337.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 330 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 348.0166 | 133 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 358.5833 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 393.3333 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 478.75 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 529.8332 | 170 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 660 | 220 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 675 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 718.4166 | 37 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 736 | 160 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 789.75 | 39 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 795.8333 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 806 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 871.65 | 149 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 924 | 33 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 940.3332 | 155 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1092.6666 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1883.4 | 516 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3276.8 | 128 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6757.6667 | 19 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 0.6 | 4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3.2667 | 7 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 8 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 11.3333 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 11.75 | 15 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 16.3332 | 140 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 16.3333 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 17.5 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 21.7 | 93 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 23 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 25.3333 | 76 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 31.7333 | 47.6 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 32 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 34.3333 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 37.3333 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 40 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 40 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 44.3332 | 140 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 45.6 | 7.6 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 46.6667 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 47.8866 | 65.3 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 49.05 | 109 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 50 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 51.3333 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 51.35 | 79 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 51.7 | 66 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 54 | 8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 55.93 | 7.99 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 60 | 72 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 69.3333 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 70 | 17.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 73.95 | 43.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 76.5 | 34 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 77.35 | 39 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 81.6 | 68 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 81.6666 | 140 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 87.2451 | 78.13 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 90 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 92 | 115 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 104.004 | 38.52 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 107.5 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 109.2 | 56 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 110 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 110.33 | 129.8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 113.3333 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 129.1999 | 102 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 130 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 136.5 | 210 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 137.5 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 138.6 | 108 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 143.9833 | 53 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 153.6667 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 177.8666 | 116 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 196 | 14 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 198.3331 | 350 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 204.1666 | 125 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 204.1666 | 98 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 215.4167 | 47 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 229.1666 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 240 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 245.3332 | 128 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 256.4333 | 157 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 262.5 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 281.75 | 115 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 319.9999 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 325 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 384.9999 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 391 | 102 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 414.3333 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 436.5832 | 155 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 511.3667 | 23 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 526.3333 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 537.3333 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 675.45 | 79 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 676 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 678.8666 | 34 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1096.6666 | 140 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1133.1833 | 77 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1311.3332 | 140 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1343.55 | 117 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1352 | 169 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1711.6666 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2.6833 | 23 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3.9 | 18 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 6.4533 | 12.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 8.5 | 17 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 8.85 | 59 | 2 | 2 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 12.5 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 13.8333 | 5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 15.6 | 9 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 21.6667 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 45.0665 | 208 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 45.6 | 7.6 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 56 | 16 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 58 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 63.3333 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 68.4 | 17.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 75.7083 | 39.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 77 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 80.925 | 58.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 88.75 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 90.0703 | 24.79 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 108 | 72 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 110.5 | 51 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 111.6667 | 10 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 120.6 | 36 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 126.6666 | 76 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 136.8 | 17.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 140 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 140 | 200 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 217.7333 | 46 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 222.3333 | 92 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 230 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 232.05 | 63 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 254.9946 | 86.93 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 265.3333 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 267.85 | 33 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 276.65 | 33 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 282.9079 | 79.32 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 286 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 302.6666 | 227 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 304.3333 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 315 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 330.2 | 127 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 349.8666 | 128 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 416 | 104 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 454.9999 | 84 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 506.9166 | 79 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 513 | 95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 557.2666 | 52 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 629.3666 | 158 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 831.9024 | 278.85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 885.95 | 87 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 987.5 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1014.75 | 123 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1151.4999 | 105 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5175 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 16 | 24 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 29.7 | 33 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 44 | 44 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 64.2333 | 82 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 120.6333 | 47 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 136.9 | 37 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 51.75 | 23 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 135.2166 | 61 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 26.25 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 100.25 | 120.3 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 120.8333 | 58 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 164.8333 | 23 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 192.75 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1247 | 29 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 27.6 | 6.9 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 27.61 | 25.1 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 35.015 | 14.1 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 59 | 59 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4.29 | 28.6 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 823.2 | 168 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 28 | 14 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 42.25 | 39 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 343 | 70 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 473.3333 | 20 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 677.25 | 129 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 10.4167 | 25 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 36.25 | 25 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 53.2 | 84 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 53.6666 | 70 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 63.6 | 36 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 138.75 | 185 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 145.2 | 88 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 179.3166 | 203 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 381.25 | 75 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 809.02 | 85.16 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 333.6666 | 91 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 147.5999 | 108 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 153.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 272.4666 | 67 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 729.1666 | 125 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 897.4666 | 127 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 3194.5831 | 275 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 345.45 | 63 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 625.3332 | 140 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 0.9 | 2 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4.221 | 12.06 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5.11 | 43.8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5.5 | 15 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7.4 | 37 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 11.6 | 87 | 1 | 3 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 12 | 144 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 12 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 13.3333 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 18 | 27 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 18.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 18.6667 | 20 | 2 | 2 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 21.0006 | 37.06 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 21.75 | 87 | 1 | 2 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 23.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 26.1 | 58 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 29.125 | 23.3 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 29.5 | 59 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 29.9766 | 52.9 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 31.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 31.8999 | 87 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 34.6666 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 36.1 | 19 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 41.25 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 42.4 | 8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 48 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 48.5833 | 53 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 55 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 57 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 58.6666 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 64.1666 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 69 | 46 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 73.4 | 367 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 86.5666 | 98 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 91.8333 | 19 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 92.5 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 93 | 93 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 95.55 | 49 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 105 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 108.4999 | 93 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 109.25 | 115 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 112.5 | 225 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 113.5833 | 145 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 129.4999 | 210 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 133.75 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 148.1883 | 32.45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 157.3 | 121 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 163.3333 | 98 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 163.3666 | 58 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 175.9333 | 14 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 182.6666 | 137 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 209.9166 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 210.9 | 18 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 271.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 329.3999 | 162 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 338 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 357.5 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 388 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 392.9833 | 73 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 412.5333 | 56 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 416.25 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 466.2666 | 52 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 494 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 536.665 | 59.3 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 555.4166 | 155 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 632 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 647.5 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 666.5 | 62 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 697.1667 | 47 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 733.15 | 93 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 842.9166 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 850.5 | 126 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 902.4 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 925.65 | 187 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1274.1666 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1361.65 | 113 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1385.4833 | 97 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1402.9999 | 138 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1828 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1905.75 | 99 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2275.5 | 82 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2812 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 0.8833 | 53 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3.7 | 3.7 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4.5 | 10 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 6.7167 | 13 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 9.9667 | 23 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10.8 | 8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 12 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 16.9333 | 127 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 18.4166 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 19.1666 | 115 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 19.2 | 24 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 20.6667 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 26.4 | 44 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 27.5 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 27.8 | 139 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 30 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 31.7333 | 112 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 35.9999 | 135 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 38.4 | 24 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 40.5 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 42.9 | 66 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 47.6666 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 48.18 | 80.3 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 54.6333 | 22 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 54.6666 | 82 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 56 | 160 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 57.1667 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 59.8 | 26 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 60.4166 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 64 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 69.6667 | 19 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 69.7166 | 89 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 69.9833 | 19 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 72.3332 | 140 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 73 | 73 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 73.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 74.4167 | 19 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 80 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 90 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 95 | 57 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 99.1667 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 102.6666 | 88 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 108.5 | 62 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 108.8666 | 71 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 116.6667 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 126 | 21 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 130.7333 | 37 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 134 | 134 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 135.6666 | 185 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 136.6666 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 147 | 49 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 147.6 | 82 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 173.3333 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 177.0833 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 177.75 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 180.6 | 28 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 181.0666 | 28 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 182.6666 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 184.3333 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 196.5832 | 337 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 210.6666 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 222.3333 | 115 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 265.35 | 29 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 281.25 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 286 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 313.2 | 36 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 324.9 | 36.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 325.3333 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 351 | 108 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 383.3333 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 459.4333 | 77 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 487.5 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 525.9833 | 151 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 538.4266 | 132.4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 604.6125 | 51.75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 643.5 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 698.3333 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 721.5 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 762.1666 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 907.8333 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1035 | 115 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1341.9 | 14 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 6336 | 352 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 5.95 | 21 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 7.5 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 8.25 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 10.4 | 52 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 11.3333 | 10 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 15.1666 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 15.5 | 5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 15.8333 | 95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 17.4 | 87 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 18 | 12 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 35 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 35.75 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 37.5 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 50.8666 | 109 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 60 | 300 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 63.7499 | 153 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 67.2 | 64 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 70.3083 | 64.9 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 70.3998 | 264 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 73.0999 | 258 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 83.3333 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 96 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 97.2649 | 119.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 102.85 | 51 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 103.1999 | 144 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 103.95 | 77 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 116.6666 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 119 | 68 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 122.4166 | 113 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 127.4073 | 34.28 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 132.6 | 117 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 148 | 74 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 162 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 174 | 87 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 188.4166 | 95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 250 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 374.1 | 87 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 400 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 432.6666 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 434.9999 | 180 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 478.8331 | 338 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 500.3333 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 505 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 507 | 260 | 1 | 2 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 699.5833 | 115 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 817.65 | 39.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 997.5 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1047.4999 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1193.3165 | 253 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1292 | 170 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 4094.1666 | 170 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4828.5 | 145 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 10.5 | 10 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 27 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 58.3333 | 28 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 75.25 | 43 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 396.1749 | 206.7 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 581.6999 | 126 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 5542.5999 | 444 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 121.6833 | 49 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 594.4666 | 37 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 5.6333 | 13 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 10.5 | 7 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 20.5333 | 22 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 51.3266 | 76.99 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 89.4829 | 124.86 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 121.8 | 58 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 229.5666 | 71 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 356.88 | 118.96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 446.25 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 540 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1186.0243 | 88.73 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 11.6667 | 2 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 29.8 | 0.6 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7.5 | 18 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 42.8 | 21.4 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 115 | 11.5 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 126.35 | 57 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 210.835 | 28.3 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 293.8333 | 86 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1062 | 12 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5.8967 | 12.2 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9.6333 | 28.9 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 67.9 | 9.7 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 93 | 20 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 368.75 | 147.5 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 639.1666 | 130 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1387.245 | 20.7 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 39.825 | 17.7 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 158.8533 | 36.8 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1064.65 | 107 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2.1333 | 16 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 15.45 | 103 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 104 | 96 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 807.9999 | 96 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 223.3332 | 134 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 366.3 | 99 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 33.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 70.5833 | 55 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 92.4 | 132 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 110 | 132 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 112.7 | 161 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 222.3333 | 116 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 228.9165 | 205 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 603.4166 | 65 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 570.95 | 57 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 151.6664 | 650 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 137.8666 | 176 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 0.93333 | 4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1.75 | 7 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1.83 | 18.3 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2.25 | 9 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3.5 | 105 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5.8 | 29 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6 | 24 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6.749 | 3.97 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 8.2833 | 71 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10.7033 | 24.7 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 11 | 44 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 12.8 | 64 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 13.9333 | 22 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 14.0665 | 211 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 18.6666 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 22.5 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 22.9167 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 23.25 | 5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 24 | 32 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 26 | 78 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 26.5 | 30 | 2 | 2 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 30 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 31.5 | 42 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 39.375 | 52.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 43.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 43.6667 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 47.5 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 47.85 | 87 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 49.1666 | 118 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 53.8833 | 53 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 66.7 | 29 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 69.3333 | 104 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 72 | 36 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 74.5167 | 17 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 74.6666 | 128 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 74.8 | 102 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 90.6666 | 320 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 93.3332 | 400 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 95.8333 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 101 | 202 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 101.9758 | 77.45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 103.5 | 27 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 105 | 105 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 116.25 | 93 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 120 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 122.5 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 142.0833 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 142.5 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 148.125 | 39.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 149.6167 | 47 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 150.1 | 79 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 153.9 | 17.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 157.5 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 178.1 | 137 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 183.5999 | 81 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 184 | 138 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 190.6667 | 22 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 215.5999 | 147 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 231.1666 | 73 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 248.1416 | 135.35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 248.4 | 108 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 261.1 | 373 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 328.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 424.6666 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 576 | 144 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 583 | 212 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 603.9 | 61 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 606.8 | 123 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 679.4166 | 155 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 691.6 | 38 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 712.8333 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 737.0833 | 145 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 868.2333 | 122 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 980 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 993.1666 | 118 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1462 | 170 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1541 | 115 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2088.8333 | 151 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 0 | 0 | 2 | 2 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1.5 | 5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2.0667 | 4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2.5333 | 4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7.2 | 144 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 11 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 16 | 15 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 20 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 20.4167 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 21.25 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 23 | 69 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 23.9999 | 144 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 26.5833 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 29.9 | 78 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 30 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 30.3332 | 140 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 33 | 18 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 33.8666 | 127 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 33.9 | 113 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 37.2666 | 43 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 37.5 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 39 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 52.5 | 21 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 53.6666 | 140 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 54.2666 | 74 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 57.6 | 144 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 57.9666 | 94 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 71.1333 | 44 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 88 | 66 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 88 | 88 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 95.0516 | 53.3 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 101.25 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 104.5 | 19 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 107.4666 | 104 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 135 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 137.75 | 145 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 138 | 138 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 140 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 141.1666 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 142.5 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 143.264 | 38.72 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 144.4666 | 197 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 145.3333 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 149.5 | 39 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 153.6667 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 170 | 170 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 172.8 | 54 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 174.4833 | 19 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 178.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 183.4833 | 109 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 186.6666 | 112 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 187 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 189.75 | 9 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 201.8333 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 213.5666 | 86 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 214.4 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 219.9499 | 249 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 224.2499 | 117 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 232.5 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 237.5 | 95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 245.6667 | 22 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 250.8333 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 253.8666 | 64 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 258.9999 | 105 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 259.2 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 269.4999 | 105 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 330 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 363 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 374.5 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 407.9999 | 180 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 408.4167 | 29 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 460 | 115 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 500 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 541.15 | 137 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1248.75 | 185 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1516.8665 | 244 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 2845.8997 | 447 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2887.2166 | 107 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4718.3333 | 190 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1.7967 | 7.7 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2.7 | 2 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 8.4 | 7 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 9.8166 | 31 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 12 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 12.8333 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 13.0333 | 34 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 13.2 | 88 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 16.5 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 18.6667 | 16 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 19.2 | 144 | 1 | 2 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 22.002 | 36.67 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 23.9999 | 144 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 28.8 | 144 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 29.3333 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 38.55 | 257 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 39.5833 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 40.6665 | 244 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 44.7333 | 244 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 47.25 | 105 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 50 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 50.6 | 92 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 50.6667 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 50.75 | 87 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 51.6466 | 50.8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 53.2933 | 57.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 55 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 55.5 | 15 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 57 | 76 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 72.0833 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 92 | 115 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 104.3232 | 184.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 112 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 136 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 140 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 150 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 161.1999 | 78 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 162.75 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 194.6 | 139 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 210.8333 | 23 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 211.5 | 94 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 214.2 | 102 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 226.8666 | 83 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 252.8 | 64 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 263.9333 | 107 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 264.1833 | 121 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 279.5 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 281.75 | 161 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 282.1667 | 5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 287.8499 | 171 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 290.0333 | 77 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 302.9167 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 316.5 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 356.6667 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 370 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 422.45 | 119 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 422.5 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 422.625 | 103.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 498.3333 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 503.9999 | 108 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 625 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 715 | 143 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 741.4166 | 31 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 756.1666 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 1065.7923 | 61.37 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1732.5 | 105 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2690.5833 | 103.75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 5026.2666 | 88 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 3.25 | 13 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 15 | 15 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 23.2333 | 17 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 33.3667 | 26 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 42.8833 | 31 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 49.6 | 32 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 99.75 | 57 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 126.6666 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 135 | 54 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 365.75 | 77 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 779 | 76 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 929.5056 | 89.09 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 28.75 | 23 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 29.7667 | 19 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 59.85 | 63 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 72.6666 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 580 | 116 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 3 | 9 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 5.8667 | 11 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 45.6333 | 37 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 48.4 | 33 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 52.3166 | 73 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 70.9333 | 38 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 96.35 | 47 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 693 | 44 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Oil | DI | 100 | Fossil-Steam | SERC | Summer | 242.5667 | 38 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5.005 | 27.3 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 12.1333 | 28 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 22.1667 | 14 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 54.8 | 13.7 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 72.8 | 18.2 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 123 | 60 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 192 | 64 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 229.35 | 139 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5 | 2.5 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5.85 | 19.5 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 12.8 | 3 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 16.8 | 16.8 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 78.1667 | 17.5 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 717.4999 | 210 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3301.1 | 33 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 58.6667 | 44 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 67 | 67 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 99.47 | 29.4 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 189.3333 | 5 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 518 | 20 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 20 | 20 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 128.9167 | 35 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 201.5833 | 205 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 93.9166 | 115 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 157.5 | 105 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 206.5 | 295 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 214.5 | 110 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 696.6665 | 190 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 229.5 | 81 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 843.3333 | 55 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 23.3333 | 70 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 25 | 50 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 958.7997 | 846 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 751.1 | 406 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1.1333 | 4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1.95 | 9 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2.1667 | 10 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4.3333 | 26 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7.6667 | 10 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8.4058 | 3.85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 10.5 | 2 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 11.9375 | 47.75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 12.25 | 49 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 12.35 | 57 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 12.6667 | 10 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 12.9499 | 111 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 15.3533 | 13.16 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 15.95 | 87 | 1 | 2 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 16.2499 | 195 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 23.1083 | 29.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 23.8333 | 10 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 29.233 | 9.43 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 31.13 | 42.45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 32 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 32.4999 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 33 | 33 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 35.1 | 81 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 38.5 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 42 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 42.21 | 40.2 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 50.6666 | 95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 51.3333 | 77 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 52.5 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 53.3333 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 56 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 63 | 63 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 63.9166 | 59 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 66.6999 | 87 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 72.75 | 97 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 82.5 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 84.3333 | 92 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 84.5833 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 90 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 90 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 95 | 95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 95.6666 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 117.4167 | 5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 128.8833 | 19 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 130.15 | 57 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 136.3333 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 143.1 | 53 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 145.5499 | 213 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 151.3333 | 10 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 154.8 | 43 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 161.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 169.95 | 103 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 178.6666 | 160 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 178.8333 | 37 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 186.6666 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 227.1 | 18 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 234 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 244.0833 | 101 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 284.1666 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 320.6666 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 328.5 | 15 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 391 | 68 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 397.75 | 43 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 415.6666 | 86 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 428.75 | 245 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 433.3333 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 446.6666 | 200 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 457.3333 | 112 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 481.6666 | 170 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 514.5 | 98 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 518 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 652.5166 | 119 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 706.8833 | 83 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 801.6666 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 816 | 68 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1117.4166 | 53 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1218 | 87 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1234.9999 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 3896 | 160 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4.3166 | 37 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5.8333 | 10 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 7.5 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8.1667 | 7 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8.5 | 15 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 9.5 | 4.75 | 1 | 2 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 10.95 | 73 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 15.5 | 15.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 15.6667 | 47 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 18 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 34.2 | 76 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 34.6666 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 38.7943 | 12.86 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 41.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 42.4666 | 98 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 42.75 | 14.25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 43.9166 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 52 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 57.6 | 32 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 63 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 65.1666 | 115 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 65.25 | 145 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 65.9166 | 113 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 68.0833 | 95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 71.25 | 15 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 78.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 79.2166 | 97 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 88 | 22 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 88.6666 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 100.4333 | 46 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 114.4 | 208 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 118.8999 | 87 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 121.992 | 39.78 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 127 | 127 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 130 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 131.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 133.3333 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 140 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 159.9999 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 163.3333 | 10 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 169.1666 | 145 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 170.2 | 69 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 179.8667 | 38 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 223.72 | 263.2 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 236.8333 | 49 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 254.5833 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 257.8333 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 270 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 271.7999 | 108 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 287.4999 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 303.6833 | 19 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 343.3333 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 350.8667 | 19 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 373.7499 | 195 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 377.5667 | 47 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 437.8333 | 142 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 496 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 592 | 64 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 593.75 | 125 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 624 | 312 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 635.9999 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 637.2 | 36 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 655.5 | 21.85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 902.8 | 74 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1409 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1694.9999 | 180 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1714.1666 | 170 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1822.9166 | 125 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2066.6666 | 248 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2282.5833 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2485.75 | 163 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3486 | 249 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4859.5166 | 161 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7312.8 | 48 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 0 | 0 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 0.46666 | 7 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3.9667 | 14 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 10.1499 | 87 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 11.1293 | 39.28 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 11.4333 | 7 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 11.6667 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 11.75 | 47 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 15.2 | 7.6 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 20.3 | 87 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 21.75 | 87 | 1 | 2 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 28.5 | 19 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 28.9666 | 79 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 31.0333 | 49 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 31.5 | 21 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 33.0666 | 64 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 36 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 36.75 | 15 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 37.3333 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 39.5833 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 45.6166 | 119 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 52.1833 | 101 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 55.9166 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 64.35 | 27 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 65 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 65 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 65.6 | 123 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 70.2 | 78 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 74.97 | 44.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 75.3333 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 79.3625 | 27.21 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 88.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 90.85 | 34.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 98.8999 | 258 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 110 | 88 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 119.7 | 17.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 120 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 124 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 128.2833 | 43 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 129.9999 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 136.64 | 29.28 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 142.1 | 87 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 152.1666 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 160 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 161.9088 | 90.79 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 182.46 | 304.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 196.3333 | 76 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 216.6666 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 221.85 | 87 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 222.3 | 17.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 224.25 | 195 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 231.9999 | 87 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 244.85 | 83 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 245.5833 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 248 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 259.2498 | 255 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 270.8333 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 299 | 46 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 307.8 | 51.3 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 317.3333 | 119 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 348.3333 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 365.5 | 43 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 406.4 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 444.0485 | 30.73 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 534.9999 | 300 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 552.2 | 44 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 601.9999 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 758 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 760 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 923.8332 | 230 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 930.6 | 99 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1804.9166 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1891.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1945 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4072.3499 | 153 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 16291.1 | 119 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 13.6 | 17 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 36.6833 | 31 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 83 | 83 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 105.4666 | 56 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 325.3333 | 160 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 349.6 | 76 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 5964.5 | 79 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 23.7667 | 23 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 30.4833 | 31 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 59.1066 | 64.48 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 287.0333 | 79 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 388 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 417.5 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 439.1667 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 3.3333 | 8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 53.3 | 41 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 74.4 | 36 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 118.3666 | 53 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 150 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 180.17 | 180.17 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 219.45 | 33 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 249.0166 | 67 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 355 | 71 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Oil | DI | 100 | Fossil-Steam | SERC | Summer | 6.9667 | 38 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5.39 | 23.1 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 73.5 | 21 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 81 | 27 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 87.5 | 15 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 106.9866 | 47.2 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 107.9666 | 79 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 228 | 30 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 255.9999 | 96 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6.81 | 22.7 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 21 | 21 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 22.445 | 20.1 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 79.8 | 13.3 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 908.355 | 21.1 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7.6266 | 35.2 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 57.96 | 21.6 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 105.3266 | 25.9 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 308.3333 | 148 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 2803.6832 | 149 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 357 | 140 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 906.7143 | 75.77 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 985.3666 | 287 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 2729.9165 | 205 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 7048.5 | 222 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 27 | 135 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 47.6665 | 220 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 100 | 100 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 121.0166 | 137 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 189 | 140 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 205.4665 | 184 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 719.4333 | 113 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 166 | 24 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 410.8333 | 145 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 1008.1666 | 115 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 61.3333 | 80 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 218.6666 | 80 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2776.6664 | 340 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 107 | 107 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Oil | DI | 100 | Fossil-Steam | SERC | Summer | 208.8 | 58 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 2 | 2 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 4 | 4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 9 | 9 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 12 | 4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 16 | 16 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 2008.3333 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 201.55 | 29 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 2 | 2 | 1 | 2 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 5 | 5 | 1 | 4 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 8 | 8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 26 | 13 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 64 | 32 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 51 | 17 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 9 | 3 | 1 | 2 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 2.3333 | 4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 20.1667 | 11 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 57.1667 | 14 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 3 | 3 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 3 | 3 | 1 | 5 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 6 | 2 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 22 | 11 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 50 | 10 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 210 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 8 | 8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 23.1 | 11 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 315.4 | 19 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 15 | 5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 32 | 32 | 1 | 2 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 46 | 23 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 90 | 18 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 9 | 9 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 1 | 1 | 1 | 5 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 10 | 10 | 1 | 2 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 36 | 18 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 91.6167 | 23 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 0.33333 | 2 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 9.35 | 11 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 33.8333 | 29 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 90 | 15 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 28 | 15 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 12 | 6 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 71.7833 | 73 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 72 | 24 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 80 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 120 | 24 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 10 | 10 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 2 | 1 | 1 | 2 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 6 | 6 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 13 | 13 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 120 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 135.45 | 21 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 800-Miscellaneous
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 8.8167 | 23 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 800-Miscellaneous
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 319.0833 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 800-Miscellaneous
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 26.4333 | 26 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 800-Miscellaneous
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 47.6667 | 11 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 800-Miscellaneous
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 91.8333 | 38 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 449.6 | 12 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 155.3333 | 8 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 37.3667 | 38 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 73.4666 | 58 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 81.6666 | 98 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Off-Peak | 342 | 76 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 53.2 | 28 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 815.1 | 38 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Off-Peak | 290.0666 | 76 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 86.6666 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 34.8 | 58 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 238.7667 | 13 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 1901.25 | 65 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 119.0667 | 38 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 37.1 | 42 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 123.75 | 45 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 322.2 | 54 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 380.25 | 117 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 728 | 104 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 12.6 | 18 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 191.25 | 45 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 225.4 | 46 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 405.3333 | 19 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 409.5 | 91 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 788.9 | 161 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 540 | 45 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1762.95 | 161 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2002 | 88 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 74.9599 | 112.44 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 215.3333 | 38 | 1 | 1 | 0253-Pulverizer feeder motor | D2-Forced - Delayed | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 642.6 | 68 | 1 | 1 | 0253-Pulverizer feeder motor | D2-Forced - Delayed | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 19.39 | 19.39 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 297.5 | 70 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4 | 8 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 8.1667 | 5 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 14.4667 | 14 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 736 | 120 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 870 | 20 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 11570 | 130 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 53.4195 | 13.19 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 65 | 39 | 1 | 1 | 0253-Pulverizer feeder motor | D2-Forced - Delayed | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 518.4 | 27 | 1 | 1 | 0253-Pulverizer feeder motor | D2-Forced - Delayed | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 392.4333 | 122 | 1 | 1 | 0253-Pulverizer feeder motor | D2-Forced - Delayed | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 175.5833 | 49 | 1 | 1 | 0253-Pulverizer feeder motor | D3-Forced - Postponed | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 9.6 | 64 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 34.35 | 9 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 105 | 12 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 185.3666 | 166 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 246.75 | 47 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 893.2333 | 211 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 198.3333 | 238 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 373.3332 | 140 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 379.7332 | 128 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 385.7333 | 88 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1383.3333 | 25 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1991.7333 | 88 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 34.8333 | 19 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 48.5833 | 55 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 80 | 80 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 181.2 | 36 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 601.5 | 30 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 720.07 | 55.39 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 74.165 | 27.3 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1085 | 105 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 66 | 88 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 800.0667 | 4 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1216.6666 | 73 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2107.3332 | 218 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 607.464 | 116.82 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 151.965 | 29.7 | 1 | 1 | 0253-Pulverizer feeder motor | D2-Forced - Delayed | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 523.045 | 21.9 | 1 | 1 | 0253-Pulverizer feeder motor | D2-Forced - Delayed | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 700 | 100 | 1 | 1 | 0253-Pulverizer feeder motor | D2-Forced - Delayed | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 27.3 | 63 | 1 | 1 | 0253-Pulverizer feeder motor | U1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7.6667 | 10 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 12.0333 | 19 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 73.6666 | 52 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 82.6 | 84 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 182.7499 | 129 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 199.5 | 19 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 273 | 91 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 347.6667 | 20 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 20.6667 | 20 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 22.2 | 12 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 39.1666 | 94 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 73.3333 | 100 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 111.6667 | 20 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 127.5 | 102 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 192 | 128 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 259.9 | 69 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 301 | 86 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 318.5 | 130 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 680 | 40 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 912 | 228 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 31.3333 | 47 | 1 | 2 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 85.8333 | 25 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 308.3167 | 13 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6.597 | 14.66 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 32.6728 | 45.59 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 862 | 120 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1603.9999 | 120 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 165.3332 | 248 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 220 | 11 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 298.2 | 63 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1564.2 | 198 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 235.8225 | 60.21 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 150.2666 | 32.2 | 1 | 1 | 0253-Pulverizer feeder motor | D2-Forced - Delayed | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 531.1333 | 24.8 | 1 | 1 | 0253-Pulverizer feeder motor | D2-Forced - Delayed | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 42 | 8 | 1 | 1 | 0253-Pulverizer feeder motor | D2-Forced - Delayed | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 104.1833 | 19 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 230.6666 | 80 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 288.1666 | 95 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 397.4167 | 19 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1122 | 88 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 478 | 120 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1283.3332 | 140 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 15.3 | 18 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 25.8333 | 50 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 40.5333 | 16 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 88 | 88 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 199.1333 | 4 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 301.3333 | 40 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 386.6665 | 232 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 13.4599 | 80.76 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | RFC | Winter | 40.25 | 35 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | RFC | Winter | 95.0833 | 35 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 14.76 | 36.9 | 1 | 1 | 0253-Pulverizer feeder motor | D2-Forced - Delayed | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 135.2 | 52 | 1 | 1 | 0253-Pulverizer feeder motor | D2-Forced - Delayed | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 52 | 13 | 1 | 1 | 0253-Pulverizer feeder motor | D3-Forced - Postponed | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Oil | DI | 100 | Fossil-Steam | SERC | Summer | 720.1666 | 58 | 1 | 1 | 0253-Pulverizer feeder motor | U1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 52 | 65 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 472.5 | 45 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 55.4167 | 19 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 149.6 | 88 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 198 | 22 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 205.6 | 48 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 264 | 22 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 281.5167 | 19 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 624 | 104 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3837.1666 | 115 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 33 | 3 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 104.9999 | 90 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 139.3333 | 88 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 37.4183 | 14.3 | 1 | 1 | 0253-Pulverizer feeder motor | D2-Forced - Delayed | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 232.3999 | 168 | 1 | 1 | 0253-Pulverizer feeder motor | U1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 91 | 13 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 800-Miscellaneous
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 370.7666 | 98 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1032.3333 | 95 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1430.6666 | 80 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 51.75 | 23 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 76.3333 | 20 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 44.5 | 30 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 139.5833 | 25 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 27.2 | 17 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 410.5666 | 113 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8825.6665 | 638 | 1 | 1 | 0255-Pulverizer feeder coal scales | U1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 25 | 20 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 59.3333 | 20 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 165 | 132 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 7.3333 | 40 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 614.4 | 48 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1552.4999 | 405 | 1 | 1 | 0255-Pulverizer feeder coal scales | D2-Forced - Delayed | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 175 | 50 | 1 | 1 | 0255-Pulverizer feeder coal scales | D2-Forced - Delayed | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 354.1666 | 170 | 1 | 1 | 0255-Pulverizer feeder coal scales | D2-Forced - Delayed | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1.2499 | 75 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1039.15 | 21 | 1 | 1 | 0255-Pulverizer feeder coal scales | D2-Forced - Delayed | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 269.5 | 70 | 1 | 1 | 0255-Pulverizer feeder coal scales | D2-Forced - Delayed | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 992.3333 | 130 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 280 | 40 | 1 | 1 | 0255-Pulverizer feeder coal scales | D3-Forced - Postponed | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 406.5833 | 35 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 860 | Co-generator Block | RFC | Summer | 485.4499 | 219 | 1 | 1 | 0255-Pulverizer feeder coal scales | U1-Forced - Immediate | 860-Co-generator Block
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 860 | Co-generator Block | RFC | Summer | 616.8499 | 219 | 1 | 1 | 0255-Pulverizer feeder coal scales | U1-Forced - Immediate | 860-Co-generator Block
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 860 | Co-generator Block | RFC | Winter | 372.3 | 219 | 1 | 1 | 0255-Pulverizer feeder coal scales | U1-Forced - Immediate | 860-Co-generator Block
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4.9 | 49 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 375 | 100 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1213.3332 | 140 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 128.25 | 19 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 12348 | 840 | 1 | 1 | 0256-Seal air system (air to pulverizers) | U1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 17.05 | 93 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 233.402 | 99.32 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 58.3333 | 50 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 290 | 60 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 84.1667 | 25 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 31.6667 | 10 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 125.3333 | 20 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D2-Forced - Delayed | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 37.5 | 25 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 137.75 | 15 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1382.3333 | 145 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D2-Forced - Delayed | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 186 | 40 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 311.2166 | 71 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 75 | 20 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 296.8333 | 65 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 103.9999 | 240 | 1 | 1 | 0256-Seal air system (air to pulverizers) | U1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 158.6666 | 40 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 366.9167 | 35 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1219.65 | 173 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 13.3333 | 10 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 17 | 34 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 25.15 | 50.3 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 25.5833 | 5 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 45 | 45 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 51.3333 | 35 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 120 | 60 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 130 | 120 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 174 | 60 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 283.3333 | 85 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 296 | 96 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 417.625 | 128.5 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 713 | 31 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 720 | 45 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 965.8916 | 128.5 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 1641.0665 | 362 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1911.6666 | 100 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 36.2746 | 35.68 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 88.1667 | 5 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 93.7333 | 76 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 435 | 30 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 459.75 | 15 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1608.6666 | 127 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1802.25 | 45 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 20591 | 349 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 22349.0666 | 76 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 27.2667 | 2 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 99.6667 | 23 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 144.5 | 15 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 230 | 50 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 251.25 | 15 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 428.1667 | 35 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 727.9999 | 420 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 985.5 | 270 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1258 | 370 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1508.75 | 85 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1865.8 | 57 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 347.945 | 30.3 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 40.2 | 20.1 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 122.1 | 74 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 306.195 | 41.1 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 961.4 | 69 | 1 | 1 | 0260-Primary air fan | U1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3866.6664 | 800 | 1 | 1 | 0260-Primary air fan | U1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5576.4998 | 570 | 1 | 1 | 0260-Primary air fan | U1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1956.9998 | 570 | 1 | 1 | 0260-Primary air fan | U1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 30866 | 220 | 1 | 1 | 0260-Primary air fan | U2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 42.4666 | 49 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 75 | 15 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 83 | 83 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 105.0333 | 46 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 111.25 | 15 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 130 | 52 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 136 | 68 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 141.8166 | 67 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 213.75 | 15 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 240 | 15 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 365.3333 | 40 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 374 | 55 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 492.65 | 167 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 500 | 50 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 829.7331 | 392 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 840 | 35 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2508.3333 | 25 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3.1333 | 1 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 28.3333 | 5 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 42 | 42 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 46.25 | 37 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 55 | 20 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 158.3332 | 125 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 220 | 110 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 245 | 5 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 364 | 28 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 378.75 | 45 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 454.0333 | 128.5 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 686.5333 | 76 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1426.3667 | 14 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1454.8333 | 58 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1850 | 74 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3317 | 107 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 32.5333 | 32 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 210 | 30 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 250.2 | 27 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 602.5 | 30 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 991.1665 | 190 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1480 | 370 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 686.375 | 32.3 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 80.6517 | 22.3 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 262.9667 | 14 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 319.8333 | 38 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 373.5 | 415 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 27.5 | 55 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 34.1 | 62 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 46.6666 | 56 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 66 | 66 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 92 | 92 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 116.1 | 18 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 508 | 80 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1136 | 71 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1640.6666 | 115 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1682 | 10 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2582.5 | 25 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4450.8333 | 25 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 6.6667 | 20 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 38 | 19 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 67.3333 | 20 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 67.8499 | 177 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 151 | 30 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 232 | 40 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 300 | 30 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 406.2 | 36 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 460.4166 | 85 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 612.5 | 25 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 810.1333 | 56 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 829.25 | 107 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 47.15 | 41 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 60.3333 | 20 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 162.9333 | 13 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 200.9833 | 31 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 202.25 | 15 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 445.25 | 15 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 476.5 | 15 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 496.9999 | 420 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 630.18 | 24.3 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 265.0666 | 224 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 572.025 | 26.3 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 306.8333 | 35 | 1 | 1 | 0260-Primary air fan | D3-Forced - Postponed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1244.0499 | 417 | 1 | 1 | 0260-Primary air fan | U1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2145.2331 | 278 | 1 | 1 | 0260-Primary air fan | U1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 74.7333 | 118 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 225 | 25 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 260 | 20 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 360 | 10 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 420 | 35 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 502.8333 | 70 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 650.6666 | 61 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1287.45 | 286.1 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1980 | 100 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2048.8 | 394 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 171.6666 | 100 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 250 | 40 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 287.5 | 25 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 312 | 156 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 362.8333 | 70 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 406.25 | 25 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 463.5 | 90 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 474.1667 | 50 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1129.9999 | 75 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1174.5 | 54 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1480 | 60 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5671 | 107 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 13940 | 80 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 42.75 | 9 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 165 | 55 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 210 | 100 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 616 | 28 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 950 | 25 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 6408 | 60 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 10109.9999 | 360 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 32.6667 | 20 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 43677.25 | 239 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 608.9416 | 51.1 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 1528.0998 | 354 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 31969.6665 | 220 | 1 | 1 | 0260-Primary air fan | U1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5164.2664 | 842 | 1 | 1 | 0260-Primary air fan | U1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5622.1663 | 610 | 1 | 1 | 0260-Primary air fan | U1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10 | 10 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 72.5 | 15 | 1 | 2 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 106 | 60 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 147.8833 | 19 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 152.4375 | 203.25 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 212.75 | 37 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 314.25 | 45 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 562.5 | 45 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 577.9166 | 95 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 620.5833 | 55 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 640 | 60 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 841 | 15 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1122.4 | 61 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2524.6333 | 46 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3746.1667 | 35 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8669.5 | 35 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 12841.5 | 35 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 42654.4166 | 85 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 424819.0665 | 362 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4.5833 | 25 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 23.6 | 24 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 33 | 11 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 36 | 12 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 66.5 | 114 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 76 | 8 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 348.8332 | 182 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 354.1666 | 125 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 505.2333 | 46 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 595.4666 | 56 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2497.8333 | 70 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 41.5166 | 53 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 47.2 | 48 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 75 | 25 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 331.5 | 15 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 377.3 | 42 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 429 | 39 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 442 | 51 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 888.635 | 117.7 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 923 | 71 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1041.75 | 15 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 4621 | 60 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 7193.3331 | 332 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 9886.3331 | 380 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 63 | 4.2 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 623.1 | 9.3 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 321.875 | 12.5 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 237.9667 | 23.6 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 9 | 27 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 24.9999 | 150 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3430.6997 | 507 | 1 | 1 | 0260-Primary air fan | U1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9259.25 | 407 | 1 | 1 | 0260-Primary air fan | U2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4 | 5 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 53.2 | 21 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 100.1 | 22 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 101.25 | 75 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 104.5 | 19 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 116.25 | 15 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 177.9667 | 19 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 310.4 | 96 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 344.3 | 66 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 362.0833 | 25 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1168.75 | 25 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3397.3333 | 70 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6220.45 | 28.2 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8538.8333 | 35 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 83.7499 | 75 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 132 | 33 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 266 | 19 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 325 | 65 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 805 | 35 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1547 | 70 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5652.5 | 85 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 13217.5 | 25 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 19170.6665 | 208 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 11.75 | 15 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 40.482 | 46.71 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 51 | 51 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 72.9 | 81 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 75 | 15 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 89.6667 | 20 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 130 | 13 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 186.6667 | 35 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 192 | 32 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 232.5 | 30 | 2 | 2 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 540 | 45 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1868.3331 | 380 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3895 | 41 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 6489 | 60 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 13737 | 60 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 17390.9167 | 35 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 17876.8333 | 35 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 45750 | 250 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 16.6667 | 20 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 55.3333 | 20 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 84.71 | 12.9 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4037 | 220 | 1 | 1 | 0260-Primary air fan | U1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 24389.3332 | 170 | 1 | 1 | 0260-Primary air fan | U1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 227.4999 | 390 | 1 | 1 | 0260-Primary air fan | U1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10 | 24 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 27.5 | 15 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 30.5 | 30 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 43.0666 | 68 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 65.5 | 15 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 87.5 | 35 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 140.8333 | 50 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 141 | 20 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 175 | 10 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 280 | 20 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 388.5 | 111 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 410 | 20 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 440.4167 | 35 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 708.75 | 45 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2461.6667 | 35 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 36607.9999 | 384 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 0.69999 | 21 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 53.3 | 82 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 125.6667 | 13 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 210.1 | 33 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 742 | 60 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1950.75 | 17 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 10547.9164 | 415 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 24.7332 | 212 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 57.5 | 10 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 59 | 59 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 60 | 40 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 63.75 | 17 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 87.9167 | 25 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 104.8 | 48 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 198.5 | 15 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 468.75 | 15 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 480 | 30 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 598.8 | 18 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1161.4166 | 55 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1248 | 96 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1339.7332 | 128 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1545 | 15 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1676.5833 | 55 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3020.3999 | 108 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 5124.9164 | 445 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 24 | 20 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1038.4499 | 387 | 1 | 1 | 0260-Primary air fan | U1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5940 | 594 | 1 | 1 | 0260-Primary air fan | U1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 28386.5331 | 844 | 1 | 1 | 0260-Primary air fan | U1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 37.5 | 25 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 70.4166 | 65 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 135 | 15 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 140 | 40 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 310.5 | 27 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 371.2 | 32 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 406.3333 | 46 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 420 | 105 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 423 | 18 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1167.7499 | 81 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1400.5333 | 101 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2316.25 | 85 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5886.6664 | 400 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 7212.7999 | 384 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 30.6 | 51 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 263.25 | 39 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 309.9999 | 150 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 477 | 212 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 681.3333 | 80 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1043.25 | 107 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1240 | 80 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1317.5667 | 47 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1432 | 60 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1639 | 110 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1750 | 25 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4203.3166 | 107 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4471.5 | 90 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 8922.3333 | 58 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 18392.0833 | 25 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 109.9999 | 150 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 247.05 | 61 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 350 | 100 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 605 | 20 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 987.5 | 125 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5711.6666 | 100 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 9620 | 80 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2177.42 | 41.2 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3250.0433 | 41.9 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 65 | 13 | 1 | 1 | 0260-Primary air fan | D3-Forced - Postponed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 650 | Fluidized Bed | WECC | Summer | 4005.75 | 105 | 1 | 1 | 0260-Primary air fan | U1-Forced - Immediate | 650-Fluidized Bed
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 650 | Fluidized Bed | SERC | Winter | 43800 | 5 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 650-Fluidized Bed
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 313.3333 | 20 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 800-Miscellaneous
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Winter | 1058.3333 | 100 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 3222.6666 | 80 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 560.9 | 6 | 1 | 1 | 0262-Primary air fan lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 929.25 | 531 | 1 | 1 | 0262-Primary air fan lube oil system | SF-Startup Failure | 100-Fossil-Steam
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 675 | 45 | 1 | 1 | 0262-Primary air fan lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 294.4998 | 465 | 1 | 1 | 0262-Primary air fan lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 90.95 | 25.5 | 1 | 1 | 0262-Primary air fan lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 77.9999 | 117 | 1 | 1 | 0262-Primary air fan lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 6.6 | 44 | 1 | 1 | 0262-Primary air fan lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 369.6 | 18 | 1 | 1 | 0262-Primary air fan lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 438.9 | 18 | 1 | 1 | 0262-Primary air fan lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 30 | 15 | 1 | 1 | 0262-Primary air fan lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 726.9 | 6 | 1 | 1 | 0262-Primary air fan lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2557.25 | 53 | 1 | 1 | 0262-Primary air fan lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 109.46 | 54.73 | 1 | 1 | 0262-Primary air fan lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 616.1998 | 284.4 | 1 | 1 | 0262-Primary air fan lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 38.7697 | 21.74 | 1 | 1 | 0262-Primary air fan lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 91 | 35 | 1 | 1 | 0262-Primary air fan lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 97.4167 | 35 | 1 | 1 | 0262-Primary air fan lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 119.6 | 6 | 1 | 1 | 0262-Primary air fan lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 113.834 | 19.74 | 1 | 1 | 0262-Primary air fan lube oil system | D3-Forced - Postponed | 100-Fossil-Steam
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 847.9 | 6 | 1 | 1 | 0262-Primary air fan lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 151.725 | 25.5 | 1 | 1 | 0262-Primary air fan lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 4305.1995 | 687 | 1 | 1 | 0262-Primary air fan lube oil system | U1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 7804.2499 | 285 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 12013.3332 | 272 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 57.3333 | 20 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 118.3333 | 20 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 261.8 | 47.6 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 582.2833 | 49 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 63.6667 | 20 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 111.3333 | 20 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 268.6663 | 520 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 897.5999 | 198 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1440 | 64 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 55.1073 | 12.62 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 834.25 | 47 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 170.7666 | 109 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 860 | 20 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 107.3333 | 20 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 118 | 20 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2235.6 | 243 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 5439.3331 | 820 | 1 | 1 | 0263-Primary air fan drives | U1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5.25 | 45 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 321.4167 | 19 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4003.8 | 18 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 7780.4164 | 355 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 72.0666 | 94 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 13.8 | 12 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 29.3333 | 20 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 240.5083 | 21.7 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 742.14 | 55.8 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 209 | 44 | 1 | 1 | 0263-Primary air fan drives | D3-Forced - Postponed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 4789 | 60 | 1 | 1 | 0263-Primary air fan drives | U1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 37249.9995 | 750 | 1 | 1 | 0263-Primary air fan drives | U3-Forced - Postponed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 76.6667 | 20 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 90.1 | 53 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6451.25 | 75 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 25.3333 | 16 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 45.5 | 65 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 88.8666 | 62 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 339.255 | 18.9 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 5998.3329 | 590 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 400.9663 | 523 | 1 | 1 | 0263-Primary air fan drives | SF-Startup Failure | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 7463.0832 | 415 | 1 | 1 | 0263-Primary air fan drives | U1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 24916.6665 | 575 | 1 | 1 | 0263-Primary air fan drives | U3-Forced - Postponed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 133.6667 | 20 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 218.6667 | 20 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 230.3 | 14 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 265.1667 | 10 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2112.25 | 85 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 83.0667 | 14 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 95 | 19 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 219.3332 | 140 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 435.4666 | 284 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 445.9999 | 120 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 968.75 | 25 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1101.9998 | 285 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 64.3333 | 20 | 2 | 2 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 78.6667 | 20 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 183.6667 | 20 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 828 | 180 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 60600 | 750 | 1 | 1 | 0263-Primary air fan drives | U1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 38266 | 530 | 1 | 1 | 0263-Primary air fan drives | U1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 60 | 20 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 121 | 20 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 134.6667 | 20 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 207.0832 | 355 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 50.6 | 33 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 53.6667 | 20 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5273.3331 | 565 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 115.5 | 110 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 161 | 140 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 64.6667 | 20 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 154.3333 | 20 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 198.6667 | 20 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 101.6667 | 20 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 229.7633 | 30.1 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 56.6667 | 20 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1710.8805 | 38.49 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3037.3332 | 272 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 150 | 50 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 209 | 19 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 457.65 | 81 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5782.25 | 505 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 193 | 20 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 58 | 14.5 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2902.1166 | 68.5 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 50 | 20 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 80.8583 | 31.3 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 672.75 | 69 | 1 | 1 | 0263-Primary air fan drives | U1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 41.6667 | 20 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 100 | 20 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4605.3333 | 160 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4660.9999 | 177 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 75.6 | 42 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 108 | 120 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 41.3333 | 20 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 69.6667 | 20 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 2.5 | 5 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 650-Fluidized Bed
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1184 | 48 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 7650 | 50 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 143.9333 | 127 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 217 | 30 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 123.2 | 56 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 178.5999 | 228 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 688.2 | 444 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1093.6666 | 68 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1224.25 | 83 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2255.8333 | 25 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 5769.8833 | 83 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4589.25 | 29 | 1 | 1 | 0264-Other primary air fan problems | D2-Forced - Delayed | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1065.8998 | 342 | 1 | 1 | 0264-Other primary air fan problems | U1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 90.2625 | 62.25 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 129.5167 | 19 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 144.6666 | 70 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 202.5333 | 196 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 553.9999 | 120 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 635.8333 | 175 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1627.4 | 316 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 18518.6665 | 190 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 12097.5 | 75 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 14.7 | 18 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 210.4666 | 164 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 13497 | 60 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | OS | 100 | Fossil-Steam | NPCC | Off-Peak | 5.8333 | 10 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 274.905 | 14.9 | 1 | 1 | 0264-Other primary air fan problems | D2-Forced - Delayed | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2228.1667 | 29 | 1 | 1 | 0264-Other primary air fan problems | D2-Forced - Delayed | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 189 | 189 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 269.4833 | 218.5 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 648.6664 | 695 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 771.6666 | 100 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1803.0833 | 55 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2022.0997 | 438 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 13089 | 60 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 49.8666 | 68 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 54.4 | 68 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 75 | 30 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1386 | 22 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 747.2165 | 419 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 783 | 108 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 3005.8 | 28 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 3305.3667 | 38 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 12212.6666 | 70 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 64659.4998 | 510 | 1 | 1 | 0264-Other primary air fan problems | U1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 73.6 | 184 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 77 | 77 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 248 | 48 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 818.7998 | 267 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6156.8333 | 53 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 3757.6 | 48 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 5248 | 82 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 5733.6666 | 103 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2732 | 60 | 1 | 1 | 0264-Other primary air fan problems | D3-Forced - Postponed | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5.1333 | 11 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 30.654 | 68.12 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 187 | 60 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 253.3332 | 400 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1099.4166 | 167 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1530.75 | 157 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 172.2 | 41 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1071.4666 | 56 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 42.4667 | 13 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 325 | 25 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 15018.4333 | 53 | 1 | 1 | 0264-Other primary air fan problems | D3-Forced - Postponed | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 22304.1666 | 125 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 77.998 | 19.83 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1047.9166 | 25 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1199.3333 | 56 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2059.3166 | 157 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2262 | 120 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2887.8 | 18 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4509.9166 | 115 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 21742 | 60 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 170.5 | 341 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 177 | 177 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 220.15 | 259 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1128.75 | 43 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1429.1 | 62 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1447.3332 | 167 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6068 | 185 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 37.3333 | 17.5 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 674.5 | 19 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 144 | 48 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 163.5 | 218 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 255 | 90 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 209.52 | 21.6 | 1 | 1 | 0264-Other primary air fan problems | D2-Forced - Delayed | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 12956.0999 | 342 | 1 | 1 | 0264-Other primary air fan problems | U1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1015.8333 | 50 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2493.3333 | 187 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3005 | 100 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3876 | 95 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 5826.6666 | 40 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 5830.4165 | 175 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 508 | 127 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 92.8 | 8 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 705.3 | 18 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 4767.7999 | 93 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 793.32 | 13.2 | 1 | 1 | 0264-Other primary air fan problems | D2-Forced - Delayed | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Gas | GG | 861 | CoG GT units | TRE | Off-Peak | 72.4999 | 75 | 1 | 1 | 0264-Other primary air fan problems | U1-Forced - Immediate | 861-CoG GT units
0265 | Primary air heater | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 16.1333 | 44 | 1 | 1 | 0265-Primary air heater | D1-Forced - Immediate | 100-Fossil-Steam
0265 | Primary air heater | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 80 | 80 | 1 | 1 | 0265-Primary air heater | D1-Forced - Immediate | 100-Fossil-Steam
0265 | Primary air heater | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 49.3333 | 74 | 1 | 1 | 0265-Primary air heater | D2-Forced - Delayed | 100-Fossil-Steam
0265 | Primary air heater | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 10577.8165 | 497 | 1 | 1 | 0265-Primary air heater | U1-Forced - Immediate | 100-Fossil-Steam
0265 | Primary air heater | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 729.4832 | 253 | 1 | 1 | 0265-Primary air heater | D1-Forced - Immediate | 100-Fossil-Steam
0265 | Primary air heater | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4854.2333 | 107 | 1 | 1 | 0265-Primary air heater | U1-Forced - Immediate | 100-Fossil-Steam
0265 | Primary air heater | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 290777.9333 | 124 | 1 | 1 | 0265-Primary air heater | D1-Forced - Immediate | 100-Fossil-Steam
0265 | Primary air heater | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 84.6 | 94 | 1 | 1 | 0265-Primary air heater | D1-Forced - Immediate | 100-Fossil-Steam
0265 | Primary air heater | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 238.4665 | 196 | 1 | 1 | 0265-Primary air heater | D1-Forced - Immediate | 100-Fossil-Steam
0265 | Primary air heater | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 4634 | 105 | 1 | 1 | 0265-Primary air heater | D1-Forced - Immediate | 100-Fossil-Steam
0265 | Primary air heater | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 591.5 | 13 | 1 | 1 | 0265-Primary air heater | D1-Forced - Immediate | 800-Miscellaneous
0266 | Primary air heater fouling | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 488.4 | 44 | 1 | 1 | 0266-Primary air heater fouling | D1-Forced - Immediate | 100-Fossil-Steam
0266 | Primary air heater fouling | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 44.2 | 13 | 1 | 1 | 0266-Primary air heater fouling | D1-Forced - Immediate | 100-Fossil-Steam
0266 | Primary air heater fouling | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 216.9999 | 186 | 1 | 1 | 0266-Primary air heater fouling | D1-Forced - Immediate | 100-Fossil-Steam
0266 | Primary air heater fouling | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 280.4499 | 237 | 1 | 1 | 0266-Primary air heater fouling | D1-Forced - Immediate | 100-Fossil-Steam
0266 | Primary air heater fouling | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1921 | 20 | 1 | 1 | 0266-Primary air heater fouling | D1-Forced - Immediate | 100-Fossil-Steam
0266 | Primary air heater fouling | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 4601.6667 | 44 | 1 | 1 | 0266-Primary air heater fouling | D1-Forced - Immediate | 100-Fossil-Steam
0266 | Primary air heater fouling | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 44.7333 | 11 | 1 | 1 | 0266-Primary air heater fouling | D1-Forced - Immediate | 100-Fossil-Steam
0266 | Primary air heater fouling | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 178.8499 | 219 | 1 | 1 | 0266-Primary air heater fouling | D1-Forced - Immediate | 100-Fossil-Steam
0266 | Primary air heater fouling | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5601.2166 | 53 | 1 | 1 | 0266-Primary air heater fouling | D1-Forced - Immediate | 100-Fossil-Steam
0266 | Primary air heater fouling | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2056.4331 | 323 | 1 | 1 | 0266-Primary air heater fouling | D1-Forced - Immediate | 100-Fossil-Steam
0266 | Primary air heater fouling | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1744.6 | 44 | 1 | 1 | 0266-Primary air heater fouling | D1-Forced - Immediate | 100-Fossil-Steam
0266 | Primary air heater fouling | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 8521.3333 | 44 | 1 | 1 | 0266-Primary air heater fouling | D1-Forced - Immediate | 100-Fossil-Steam
0266 | Primary air heater fouling | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8.8 | 16 | 1 | 1 | 0266-Primary air heater fouling | D1-Forced - Immediate | 100-Fossil-Steam
0266 | Primary air heater fouling | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 85.5 | 38 | 1 | 1 | 0266-Primary air heater fouling | D1-Forced - Immediate | 100-Fossil-Steam
0266 | Primary air heater fouling | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1370 | 40 | 1 | 1 | 0266-Primary air heater fouling | D1-Forced - Immediate | 100-Fossil-Steam
0266 | Primary air heater fouling | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 18480 | 110 | 1 | 1 | 0266-Primary air heater fouling | D1-Forced - Immediate | 100-Fossil-Steam
0266 | Primary air heater fouling | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 881.6165 | 313 | 1 | 1 | 0266-Primary air heater fouling | D1-Forced - Immediate | 100-Fossil-Steam
0266 | Primary air heater fouling | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 6248 | 44 | 1 | 1 | 0266-Primary air heater fouling | D1-Forced - Immediate | 100-Fossil-Steam
0266 | Primary air heater fouling | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 202.4 | 24 | 1 | 1 | 0266-Primary air heater fouling | D1-Forced - Immediate | 100-Fossil-Steam
0266 | Primary air heater fouling | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 499.3333 | 214 | 1 | 1 | 0266-Primary air heater fouling | D1-Forced - Immediate | 100-Fossil-Steam
0266 | Primary air heater fouling | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 55791.5999 | 342 | 1 | 1 | 0266-Primary air heater fouling | U1-Forced - Immediate | 100-Fossil-Steam
0266 | Primary air heater fouling | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 131.4666 | 34 | 1 | 1 | 0266-Primary air heater fouling | D1-Forced - Immediate | 100-Fossil-Steam
0266 | Primary air heater fouling | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 447.5 | 15 | 1 | 1 | 0266-Primary air heater fouling | D1-Forced - Immediate | 100-Fossil-Steam
0266 | Primary air heater fouling | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1494.7166 | 341 | 1 | 1 | 0266-Primary air heater fouling | D1-Forced - Immediate | 100-Fossil-Steam
0266 | Primary air heater fouling | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1710.8667 | 44 | 1 | 1 | 0266-Primary air heater fouling | D1-Forced - Immediate | 100-Fossil-Steam
0266 | Primary air heater fouling | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 4171.9333 | 44 | 1 | 1 | 0266-Primary air heater fouling | D1-Forced - Immediate | 100-Fossil-Steam
0266 | Primary air heater fouling | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 7190.3333 | 44 | 1 | 1 | 0266-Primary air heater fouling | D1-Forced - Immediate | 100-Fossil-Steam
0266 | Primary air heater fouling | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 17 | 2 | 1 | 1 | 0266-Primary air heater fouling | D1-Forced - Immediate | 100-Fossil-Steam
0266 | Primary air heater fouling | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4905.5 | 30 | 1 | 1 | 0266-Primary air heater fouling | D1-Forced - Immediate | 100-Fossil-Steam
0266 | Primary air heater fouling | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 12215.1333 | 44 | 1 | 1 | 0266-Primary air heater fouling | D1-Forced - Immediate | 100-Fossil-Steam
0266 | Primary air heater fouling | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 112.5 | 5 | 1 | 1 | 0266-Primary air heater fouling | D1-Forced - Immediate | 100-Fossil-Steam
0266 | Primary air heater fouling | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 220.0333 | 23 | 1 | 1 | 0266-Primary air heater fouling | D1-Forced - Immediate | 100-Fossil-Steam
0266 | Primary air heater fouling | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 91724.4 | 342 | 1 | 1 | 0266-Primary air heater fouling | U1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 130.1666 | 110 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 22.05 | 147 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 114.6666 | 160 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1198.3999 | 168 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 39.975 | 19.5 | 1 | 1 | 0267-Primary air flow instrumentation | D2-Forced - Delayed | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 150 | 15 | 1 | 1 | 0267-Primary air flow instrumentation | D2-Forced - Delayed | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 184.1666 | 32.5 | 1 | 1 | 0267-Primary air flow instrumentation | D2-Forced - Delayed | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 13.5667 | 22 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 176 | 88 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 739.2 | 88 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 30 | 40 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 136.6667 | 50 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 31.7333 | 136 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 102.95 | 71 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 72 | 48 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 105.3499 | 147 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 261.2498 | 285 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1123.75 | 93 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 42.24 | 28.8 | 1 | 1 | 0267-Primary air flow instrumentation | D3-Forced - Postponed | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 161 | 105 | 1 | 1 | 0267-Primary air flow instrumentation | D3-Forced - Postponed | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 6883.5 | 390 | 1 | 1 | 0267-Primary air flow instrumentation | U1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 154.2665 | 356 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 340.4166 | 95 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 12.25 | 147 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 31.1667 | 22 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 71.9666 | 127 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 172.6667 | 35 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 181.8666 | 341 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 849.3333 | 40 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Other | BM | 100 | Fossil-Steam | WECC | Off-Peak | 177.0906 | 59.36 | 1 | 1 | 0267-Primary air flow instrumentation | U1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Other | BM | 100 | Fossil-Steam | WECC | Off-Peak | 598.5466 | 59.36 | 1 | 1 | 0267-Primary air flow instrumentation | U1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 180 | 40 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 127.4166 | 139 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 24.1667 | 25 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 29.3333 | 55 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 498.3333 | 100 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 71.4 | 102 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 302.225 | 38.5 | 1 | 1 | 0267-Primary air flow instrumentation | D2-Forced - Delayed | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 18 | 27 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 25.2 | 28 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 70.5333 | 92 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 161.5 | 51 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 504.5333 | 172 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 21.9 | 21.9 | 1 | 1 | 0267-Primary air flow instrumentation | D2-Forced - Delayed | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2018.7499 | 75 | 1 | 1 | 0267-Primary air flow instrumentation | D3-Forced - Postponed | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 735.3 | 342 | 1 | 1 | 0267-Primary air flow instrumentation | U1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2.1667 | 26 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 174.9999 | 150 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 62.05 | 25.5 | 1 | 1 | 0267-Primary air flow instrumentation | D2-Forced - Delayed | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Other | BM | 100 | Fossil-Steam | WECC | Off-Peak | 237.44 | 59.36 | 1 | 1 | 0267-Primary air flow instrumentation | U1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 113.75 | 65 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 195.0666 | 152 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 406.85 | 79 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 424 | 120 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1080.4 | 37 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2198.8166 | 329 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 6422 | 260 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 70.3 | 111 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1013.8333 | 110 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 27.0833 | 25 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 253.551 | 40.14 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 814 | 185 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 892.5 | 85 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2932 | 40 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 9975.5333 | 122 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | SERC | Summer | 1684.6666 | 56 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 458.3333 | 220 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 107 | 20 | 1 | 1 | 0270-Primary air duct and dampers | D3-Forced - Postponed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 33.6666 | 101 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 58.9 | 38 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 65 | 30 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 201.6666 | 55 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 225 | 45 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 248 | 48 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 411.2499 | 105 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 565 | 30 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 585 | 90 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 615 | 205 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 621.8333 | 65 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 627 | 132 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 870.8333 | 95 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1125.3333 | 160 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2131.54 | 27.05 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 176 | 160 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 177.3333 | 28 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 288.4 | 84 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 745.9999 | 120 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 783.125 | 52.5 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1171.3332 | 140 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 56.6 | 28.3 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 110.25 | 49 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 127.3333 | 20 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 256.1 | 78 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 416.1666 | 110 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 547.2 | 48 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 583 | 233.2 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 1332.5575 | 64.95 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 187.5 | 75 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 11.6667 | 35 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 11149.485 | 404.7 | 1 | 1 | 0270-Primary air duct and dampers | U1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 352.35 | 261 | 1 | 1 | 0270-Primary air duct and dampers | U1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 30 | 20 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 36.75 | 24.5 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 84 | 105 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 106.9833 | 49 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 170 | 100 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 267.6665 | 220 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 283.3333 | 40 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 399 | 70 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 65.4167 | 25 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 178.2499 | 93 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 180 | 180 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 559 | 130 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2502.72 | 18.96 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3391.6666 | 55 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3762.6666 | 68 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 590 | 295 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 962.5 | 35 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 195.2 | 64 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 316.2499 | 165 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 111 | 36 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 381.65 | 51 | 1 | 1 | 0270-Primary air duct and dampers | D3-Forced - Postponed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 8259.1665 | 530 | 1 | 1 | 0270-Primary air duct and dampers | U2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 75 | 75 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5.3167 | 11 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 58.3333 | 50 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 214.375 | 52.5 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 294.8125 | 66.75 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 619.6666 | 130 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 886.9666 | 82 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 66.6667 | 20 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 119.25 | 45 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 224.7166 | 97 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 289.9166 | 71 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 498.3 | 151 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 531.3166 | 71 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 540 | 48 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3389.8 | 51 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8859.9996 | 600 | 1 | 1 | 0270-Primary air duct and dampers | SF-Startup Failure | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 13722.4997 | 825 | 1 | 1 | 0270-Primary air duct and dampers | U1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 17512.0832 | 325 | 1 | 1 | 0270-Primary air duct and dampers | U3-Forced - Postponed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 58.2667 | 19 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 293.3333 | 55 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 658 | 60 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 942.3333 | 110 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 35.1333 | 31 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 123.5 | 19 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 128.375 | 9.75 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 306 | 120 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 426.6666 | 100 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 867 | 90 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 217.4999 | 90 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 364.5 | 45 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1878.3332 | 490 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1093.1833 | 107 | 1 | 1 | 0270-Primary air duct and dampers | U1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 24.9963 | 36.58 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 190 | 5 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 249.6666 | 70 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1632 | 102 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 24.7 | 57 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 128.248 | 23.46 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 332 | 83 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 346 | 346 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2089.5 | 63 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 27.3333 | 41 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 300 | 120 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 204.7499 | 135 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 3751 | 121 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 45619.9998 | 600 | 1 | 1 | 0270-Primary air duct and dampers | U1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2156.25 | 625 | 1 | 1 | 0270-Primary air duct and dampers | U1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2.85 | 9 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10 | 30 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 102.4999 | 75 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 253.8666 | 128 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 320.8333 | 35 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 357 | 42 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 750.75 | 55 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 849.2333 | 73 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 866.6666 | 100 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 44607.3333 | 130 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 26.9167 | 5 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 106.0833 | 19 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 235 | 60 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 253.8666 | 136 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 266 | 190 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 529.0666 | 124 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1225 | 70 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 33.1866 | 52.4 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 886.5 | 197 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1003 | 20 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 51.964 | 47.24 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 168 | 96 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 389.7333 | 37 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1666.4 | 48 | 1 | 1 | 0270-Primary air duct and dampers | D3-Forced - Postponed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 10337.5999 | 168 | 1 | 1 | 0270-Primary air duct and dampers | U2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 65 | 65 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 77.9999 | 117 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 96.25 | 55 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 140 | 60 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 208.5 | 278 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 210 | 120 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 378.2 | 124 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 587 | 60 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 617.8666 | 112 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 704.7333 | 124 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1067.5 | 175 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1653 | 145 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 223.9999 | 120 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 367.7332 | 197 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 492.8 | 66 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 767 | 295 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 779 | 82 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1605.9999 | 165 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1982.9333 | 52 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 93.75 | 75 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 276.4666 | 58 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 377.8499 | 99 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 384 | 64 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 439.0665 | 178 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 514.8 | 171.6 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 822 | 120 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1181 | 590.5 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 239.1665 | 410 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 169.4 | 42 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 0 | 0 | 1 | 1 | 0270-Primary air duct and dampers | D3-Forced - Postponed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 27765.3999 | 156 | 1 | 1 | 0270-Primary air duct and dampers | U2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 116.6666 | 40 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 383.8 | 38 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 228.6667 | 20 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1060.5 | 35 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1426.6666 | 40 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2721.8666 | 59 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3922.1 | 91 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 35 | 50 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 403.6667 | 14 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 445 | 60 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 577.7 | 106 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1286.3333 | 68 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 47.9602 | 34.67 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 85.1132 | 127.67 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 147 | 49 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 237.6666 | 115 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 281.1667 | 35 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 291.0666 | 37 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 358.55 | 71 | 1 | 1 | 0280-Pulverizer fires | D2-Forced - Delayed | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5 | 18.75 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 100 | 100 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 230.95 | 93 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 817.9166 | 151 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 856.6667 | 20 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 903 | 140 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1004.9166 | 155 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3.6833 | 13 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 165 | 66 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6987.4 | 644 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 100 | 25 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 113.1 | 78 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 387.5 | 50 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1156.6666 | 40 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1679.3666 | 83 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 556.6667 | 50 | 1 | 1 | 0280-Pulverizer fires | D2-Forced - Delayed | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 2826.7665 | 274 | 1 | 1 | 0280-Pulverizer fires | D2-Forced - Delayed | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 425.85 | 167 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 815.6667 | 20 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1058 | 40 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1153.1667 | 22 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 28.9666 | 79 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 72.5 | 25 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5421 | 130 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 12.5 | 25 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 31.6666 | 100 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 194.1556 | 57.67 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 225.6283 | 43.67 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 6307.2 | 72 | 1 | 1 | 0280-Pulverizer fires | D2-Forced - Delayed | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 16.4467 | 24.67 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 55.824 | 104.67 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 77.2666 | 76 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 371.0134 | 155.67 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1391.8333 | 70 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1650.9999 | 78 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 179 | 30 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5841.1666 | 101 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 46.6667 | 14 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 79.7768 | 57.67 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 234 | 120 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 684.5 | 74 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 332.2666 | 224 | 1 | 1 | 0280-Pulverizer fires | D2-Forced - Delayed | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 20.9993 | 96.92 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 25.5126 | 54.67 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 254.3332 | 140 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 292.25 | 167 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 449.5 | 93 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 789.1667 | 50 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2616.3332 | 167 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4884.3 | 54 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 99.75 | 63 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 395.5 | 70 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 8.0062 | 43.67 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 21.25 | 75 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 30 | 100 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 33.761 | 20.67 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 94.4491 | 66.67 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 202.5833 | 13 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 300 | 100 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 576.1333 | 58 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 704 | 64 | 1 | 1 | 0280-Pulverizer fires | D2-Forced - Delayed | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 75.8825 | 303.53 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 95.15 | 11 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 117.6 | 84 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 641.7 | 207 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2073.3332 | 200 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2388.7499 | 117 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4919.4 | 54 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 26 | 65 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 68 | 68 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 905.3332 | 140 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2250 | 100 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 8.8167 | 23 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 15.468 | 38.67 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 36.3917 | 43.67 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 473.3333 | 50 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 503.1 | 78 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1000 | 80 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1104.984 | 35.76 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2591.6666 | 100 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 1881.4665 | 274 | 1 | 1 | 0280-Pulverizer fires | D2-Forced - Delayed | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 11500.5332 | 427 | 1 | 1 | 0280-Pulverizer fires | U1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 18390.6663 | 520 | 1 | 1 | 0280-Pulverizer fires | U1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 9.1667 | 25 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 30.5 | 30 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 106.9441 | 75.49 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 296.3333 | 70 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 320 | 10 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2118.3333 | 100 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2334.5 | 30 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 65.5 | 10 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4.4 | 88 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 25.0845 | 71.67 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 189 | 18 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 192 | 45 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3120.1166 | 59 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 601.6 | 94 | 1 | 1 | 0280-Pulverizer fires | D2-Forced - Delayed | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 111 | 60 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 759.1667 | 25 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 67.5 | 10 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 92.4 | 168 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2409.75 | 135 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 69.9999 | 105 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 308.9667 | 13 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1196.6666 | 100 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 235.8665 | 244 | 1 | 1 | 0280-Pulverizer fires | D2-Forced - Delayed | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 14173.9333 | 214 | 1 | 1 | 0280-Pulverizer fires | D2-Forced - Delayed | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Off-Peak | 5291.7332 | 352 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 9369.6 | 61 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6.8833 | 7 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 43.6333 | 77 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7380 | 90 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 76 | 19 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 126.6667 | 8 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 668.4167 | 13 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 345.6 | 18 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 88 | 11 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D3-Forced - Postponed | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 223.2666 | 68 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7136.6667 | 25 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D3-Forced - Postponed | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 192 | 8 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D3-Forced - Postponed | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 20.1 | 18 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 52.7333 | 28 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 225 | 15 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 696.6 | 36 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3495.7333 | 8 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 194.7 | 18 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 6140.6666 | 151 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 67.6666 | 28 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 315.4667 | 8 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 34.5 | 30 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 67.6 | 13 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 369.4666 | 68 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 638 | 58 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2077.5 | 150 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3.3333 | 8 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 182 | 8 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2243.9999 | 180 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 5764.2 | 26 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 24.0667 | 38 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 61.6 | 28 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 317.0666 | 116 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 324.3333 | 7 | 2 | 2 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 486.6666 | 200 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1686 | 40 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3575.5 | 30 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 0 | 0 | 1 | 2 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 15 | 50 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 25.3333 | 19 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 83.6 | 44 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 138 | 3 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 286.6666 | 200 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1097.8333 | 14 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2207.9167 | 35 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2473.3333 | 80 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3222.4 | 152 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 47.5 | 95 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 99.5667 | 29 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 145.3666 | 49 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 148.68 | 49.56 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 307.8166 | 73 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 395.8333 | 50 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 911.4 | 42 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1189.6666 | 43 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 19075 | 35 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1449 | 27 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 10496.85 | 91 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5760.3333 | 55 | 1 | 1 | 0300-Pulverizer motors and drives | D3-Forced - Postponed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 44.3667 | 22 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 133.25 | 41 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 200.0833 | 49 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 244 | 40 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 253.3332 | 200 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 383.8333 | 49 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 436.3333 | 35 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 809.5833 | 145 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 938.6667 | 32 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1195.8333 | 82 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5447.6666 | 138.5 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10504.0833 | 55 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 36747.7999 | 129 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 99.75 | 95 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 135.5333 | 107 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 422.8746 | 134.96 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 516.75 | 195 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2528.8 | 48 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3066.75 | 70.5 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4060 | 80 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 11.25 | 45 | 1 | 4 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 206.6166 | 49 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 511.4333 | 67 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 523.1333 | 59 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 981.4666 | 136 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1256.25 | 75 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2010.743 | 72.59 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 1215.0999 | 174 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 15.9 | 15.9 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 103.5 | 115 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 3527.5 | 85 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1431.8333 | 55 | 1 | 1 | 0300-Pulverizer motors and drives | D3-Forced - Postponed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 100 | 100 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 278.25 | 45 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 349.8 | 212 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 477.8333 | 5 | 2 | 2 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 668.8 | 44 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1421.2 | 57 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4194 | 60 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 34.6667 | 5 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 73 | 73 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 200.4166 | 185 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 340.0833 | 55 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 340.2666 | 116 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 849.5876 | 77.47 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1514.3333 | 55 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1556.3333 | 58 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3200.4 | 36 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 26.25 | 45 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 486.7666 | 34 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 523.8833 | 43 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 608.3333 | 50 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1338.075 | 51.3 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1698.6666 | 112 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2221.5 | 18 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 16727.0833 | 35 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 210 | 100 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1280 | 40 | 1 | 1 | 0300-Pulverizer motors and drives | D3-Forced - Postponed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 135.4166 | 65 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 243.7499 | 225 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 255.351 | 18.11 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 810 | 20 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 7721.6666 | 100 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 28532.5833 | 35 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6.0833 | 73 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 13.75 | 55 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 29.0333 | 26 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 51 | 6 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 106.6667 | 8 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 290.521 | 16.94 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 413 | 60 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1059.6666 | 110 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1076.6666 | 95 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1080.25 | 145 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1248.5 | 55 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1305 | 54 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2075 | 20 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2384 | 80 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5957.4667 | 26 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7474 | 120 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 11382 | 84 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 199.5333 | 73 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 906.1 | 82 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1101.6666 | 50 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 14051.3333 | 40 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 14496.25 | 75 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 37.3333 | 32 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 18044 | 40 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 164.5 | 30 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 10870 | 40 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 30940 | 425 | 1 | 1 | 0300-Pulverizer motors and drives | U1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 99 | 55 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 118.3333 | 50 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 221 | 60 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1519.5 | 2 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1957.6667 | 7 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5048.325 | 138.5 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 7554.2499 | 165 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 710.6666 | 104 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 884 | 24 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1568.8 | 53 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4477.25 | 15 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 26 | 26 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 99.1667 | 50 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 187.125 | 49.9 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 246.5 | 51 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 675 | 50 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 777.055 | 20.01 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 7975 | 100 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 272.3333 | 20 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 146 | 20 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2838.6 | 24.9 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1400.6666 | 40 | 1 | 1 | 0300-Pulverizer motors and drives | D3-Forced - Postponed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 0.029 | 0.01 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 200 | 100 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 384.4333 | 19 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 403.2 | 72 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 477.651 | 28.18 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 480 | 60 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1911.25 | 55 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5100.5 | 202 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 54.9999 | 150 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 146.25 | 117 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 212.4999 | 150 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 212.6667 | 44 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 234.9105 | 18.57 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 254.9333 | 64 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 366.6666 | 40 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 921.5 | 97 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2500.1 | 69 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3612 | 75.25 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4514.0833 | 19 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5882.1666 | 145 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 80 | 40 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 92 | 46 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 131.7332 | 152 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 218.6666 | 82 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 261 | 27 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2250.6666 | 128 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5485 | 100 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 38.3333 | 25 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 13527.7666 | 61 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 535.7583 | 26.9 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1549.6667 | 20 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 20.7999 | 78 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 32.1667 | 19.3 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 55 | 20 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 98 | 56 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 151.25 | 121 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 227.0833 | 109 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 600 | 30 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 656 | 60 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1292.7833 | 7 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1605.9 | 101 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2924 | 40 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3363.3 | 222 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3588.75 | 495 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2394 | 19 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2740 | 80 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2817.9375 | 84.75 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 54.035 | 15.15 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 633.9925 | 18.35 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 143 | 78 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 543.6667 | 35 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 12.5 | 50 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 14.9999 | 90 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 99.0167 | 13 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 321.914 | 22.67 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 592.0833 | 145 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 876.6667 | 25 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2727.8333 | 130 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 73776.9999 | 114 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 61.5 | 82 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 181 | 30 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 936.6667 | 50 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1017.9 | 87 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1092.4999 | 138 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2317.95 | 101 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2771.0666 | 56 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3838 | 19 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4595.6666 | 85 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 25.36 | 25.36 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 120 | 60 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 208.25 | 3 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 226.5 | 45 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 258 | 129 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 390.25 | 21 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 922.5 | 90 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1004.3332 | 131 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1218.3333 | 43 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1232.4999 | 150 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2363.8 | 22.3 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 41.6667 | 20 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1686 | 120 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 319.8333 | 38 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 833 | 28 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 28884.9999 | 318 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Off-Peak | 428 | 80 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 49 | 28 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 216.8 | 48 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 860 | Co-generator Block | RFC | Summer | 598.5999 | 219 | 1 | 1 | 0300-Pulverizer motors and drives | U1-Forced - Immediate | 860-Co-generator Block
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 0.33332 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3.01 | 30.1 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6.2333 | 22 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 20.67 | 20.67 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 27.8333 | 10 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 36.34 | 27.6 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 41.1666 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 42 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 45.0504 | 245.73 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 45.8333 | 55 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 45.8333 | 25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 53.3333 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 55 | 55 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 58.65 | 51 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 60.4999 | 165 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 68.88 | 33.6 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 75 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 78.65 | 121 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 85 | 15 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 90 | 15 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 92.3 | 39 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 113.3333 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 128.25 | 27 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 145.6 | 39 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 147.4666 | 28 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 154.5333 | 244 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 156 | 78 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 172.3333 | 10 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 179.5 | 10 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 192.4 | 48.1 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 194.8333 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 211.6667 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 213 | 71 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 216.3333 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 231.9999 | 87 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 238.3999 | 447 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 240 | 10 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 265.4666 | 88 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 268.3333 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 274.05 | 81 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 291.8332 | 170 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 316.6666 | 200 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 327.9167 | 25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 333.0833 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 362.6666 | 64 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 373.3332 | 140 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 412.5 | 165 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 466.1 | 59 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 490.4166 | 55 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 519.75 | 45 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 536.75 | 95 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 549 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 554.8666 | 287 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 604.75 | 15 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 637.5 | 75 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 655.6666 | 140 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 680 | 200 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 752.521 | 23.59 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 775.6 | 56 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 778.3333 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 924.8332 | 310 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 946.6666 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1000 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1082.9 | 119 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1818.6666 | 155 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3552.6667 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5768.75 | 355 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1.5 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5.1675 | 20.67 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5.3667 | 23 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 12 | 36 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 12 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 17.997 | 17.14 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 24.5 | 105 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 43.4 | 62 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 49 | 49 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 57.5167 | 7 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 72 | 72 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 73.2 | 61 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 75 | 25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 108.3333 | 25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 110.4999 | 78 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 120 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 138.6666 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 141.6666 | 85 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 150 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 164 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 180 | 90 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 230.2666 | 88 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 261 | 116 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 281.4 | 134 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 315 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 324 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 331.1833 | 31 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 376 | 80 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 536.875 | 85.9 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 585 | 45 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 747.5 | 150 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 901 | 68 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 903 | 210 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1124.2667 | 8 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1274 | 104 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 4380.45 | 87 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6510.8333 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 0.46666 | 7 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6.9997 | 38.18 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 35 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 37.95 | 9 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 41 | 12 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 43.8666 | 28 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 48.2821 | 36.67 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 58.5833 | 95 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 76.25 | 25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 91.5 | 45 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 108.3332 | 260 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 113.3333 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 134.1666 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 144.8333 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 180.8333 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 188.8333 | 103 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 191.7333 | 16 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 216.6666 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 238.39 | 76.9 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 344.9333 | 52 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 357.7 | 42 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 368.6667 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 392 | 96 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 458.4999 | 210 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 492.2666 | 142 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 522.6666 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 605 | 150 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 677.4999 | 150 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 697.6666 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 703.3333 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 795.6666 | 62 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 816 | 102 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 968.5 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1245.62 | 36.6 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1296.2499 | 255 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1300 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1460.4167 | 5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1480 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1528.3333 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1627.5 | 90 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2072.5333 | 116 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2558.3333 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4040 | 202 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5709.6 | 122 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 30 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 64.75 | 37 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 88.1833 | 37 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 965 | 193 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1125.8333 | 175 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2847 | 780 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 12 | 16 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 13.0333 | 17 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 387 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 91.2666 | 148 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 183.9333 | 89 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 136.2999 | 87 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 151.6666 | 52 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 505 | 101 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1056.6667 | 20 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1364 | 110 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 46 | 23 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 400 | 100 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 527.5 | 211 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4372.3333 | 130 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 80 | 80 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2850 | 150 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 7764.3499 | 156.75 | 1 | 1 | 0310-Pulverizer mills | U1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2.75 | 5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3.5567 | 10.67 | 2 | 2 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 11.1833 | 11 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 15.1667 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 15.8333 | 10 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 18 | 54 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 23.3333 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 24.05 | 37 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 26 | 39 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 37.3333 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 40.2167 | 19 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 45 | 45 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 45.8333 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 47.5 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 50 | 15 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 83.8666 | 37 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 96.6666 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 99.7333 | 17 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 112 | 56 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 115.5833 | 73 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 116.9315 | 206.35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 125.0667 | 8 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 141 | 94 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 147.3333 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 168.6666 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 180 | 45 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 183.6666 | 95 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 206.4 | 36 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 220.9999 | 102 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 312.8667 | 13 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 327.7999 | 447 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 336.6 | 68 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 345 | 230 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 368.8 | 48 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 378.75 | 45 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 380.9999 | 180 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 387.8333 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 415.1333 | 26 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 440 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 457.6 | 64 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 582.7499 | 135 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 594.6666 | 160 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 654.1 | 93 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 744.1665 | 190 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 765.7 | 93 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 920 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1196.0313 | 45.02 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1300 | 250 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1420.8332 | 250 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3430.85 | 59 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5237.3333 | 160 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 9073.3333 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9656.6666 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 10185 | 97 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 10.5 | 15 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 11.5 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 17 | 68 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 32.4999 | 78 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 33.761 | 20.67 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 45 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 47.996 | 20.28 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 52 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 58.6666 | 80 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 67.9999 | 102 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 82 | 10 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 97.1499 | 87 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 108.3333 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 110.7 | 123 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 117.4875 | 60.25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 125.7333 | 92 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 137.5 | 55 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 155.8333 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 189.3333 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 198 | 66 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 201.6666 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 218.2499 | 135 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 234 | 13 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 243 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 267.75 | 119 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 277.3333 | 64 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 278 | 1 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 286 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 322 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 348 | 87 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 376.3 | 106 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 575 | 115 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 586.6666 | 55 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 589.22 | 173.3 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 595 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 767.25 | 31 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1641.9166 | 85 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1668.3333 | 175 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1748.5 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1770 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2000 | 80 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2379 | 26 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3817.3333 | 80 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 6765 | 150 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1 | 3.75 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 12.2833 | 11 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 18.0833 | 7 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 20.1832 | 173 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 23.1 | 77 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 24.75 | 27 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 29.7666 | 94 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 60.8 | 114 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 64 | 48 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 71 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 71.5 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 86.4 | 144 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 100 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 104.31 | 18.3 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 125 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 137.4 | 11.45 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 145.0667 | 16 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 150 | 150 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 179.6666 | 49 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 198.1833 | 47 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 201.0666 | 116 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 254.2 | 93 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 274.6667 | 16 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 284.4833 | 101 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 325 | 75 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 345 | 23 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 362.6333 | 46 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 420 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 475 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 547 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 739.6666 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 803.8333 | 106 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 854.1 | 117 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1012.8333 | 59 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1680.25 | 65 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1962.9999 | 195 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5254 | 24 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 8130 | 36 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 222.6 | 42 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 281.3333 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 761.6 | 119 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 3936.7997 | 444 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 30.0833 | 19 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 67.4666 | 46 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 116.5333 | 46 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 120.2666 | 82 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 140.8333 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 403.2666 | 46 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 28.75 | 115 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 225.3333 | 65 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 252.6499 | 93 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 316.3833 | 41 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 591.6665 | 250 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 41 | 20 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 55.7333 | 19 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 365.5 | 102 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 111.9333 | 23 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 26 | 24 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 123.2 | 22 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 125 | 125 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 132 | 132 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 460.1333 | 56 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 368.8 | 48 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 480 | 50 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1519.1666 | 50 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 2577.1666 | 70 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 427 | 427 | 1 | 1 | 0310-Pulverizer mills | U1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1123.5 | 90 | 1 | 1 | 0310-Pulverizer mills | U1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3.3 | 11 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 8.6125 | 20.67 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 19.95 | 19 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 23.616 | 34.56 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 29.9 | 39 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 32.1 | 9 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 33.5667 | 38 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 34.9167 | 5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 36 | 18 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 37.6833 | 17 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 41.8 | 44 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 45.3333 | 80 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 47.4833 | 77 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 47.9999 | 180 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 60 | 200 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 62.5333 | 8 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 71.3 | 23 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 75 | 25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 83.5833 | 59 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 87.4999 | 210 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 109.0833 | 77 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 112.5 | 25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 119.1666 | 65 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 141.2667 | 26 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 150 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 180.5 | 190 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 187.2 | 39 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 195 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 226.75 | 15 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 234 | 52 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 256.6667 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 305.5 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 370 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 372.6666 | 260 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 383.4 | 108 | 2 | 2 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 493.3333 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 500 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 510 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 520 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 562.5 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 614.883 | 467 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 669.5 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 720 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 757.3558 | 77.15 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 819.9998 | 240 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 870 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 895.3332 | 340 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1239.3332 | 143 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1394 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2184.6666 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2289.75 | 215 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2383.3333 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 2958.6665 | 280 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3490 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3727.25 | 51 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3788.8 | 64 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5372.4999 | 210 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 8055 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 10359.6 | 97 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 14953.3333 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 21600 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10.8 | 9 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 24 | 36 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 24.6 | 123 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 32.6666 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 36.5 | 146 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 46.2333 | 73 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 54 | 10 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 60.9166 | 43 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 65.1666 | 115 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 66.3333 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 71.05 | 49 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 75.8332 | 182 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 80.6666 | 88 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 121.6666 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 146.2333 | 107 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 165.3 | 19 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 166 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 187.0666 | 61 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 190 | 190 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 255.9999 | 96 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 262 | 262 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 283.8333 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 287.5 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 300 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 302.4167 | 19 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 352.5 | 75 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 353.6667 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 432 | 96 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 444.73 | 85.8 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 528.4533 | 7.6 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 660 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 700 | 112 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 717.5 | 205 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 792.9966 | 131.8 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 795.5 | 86 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 845.3 | 214 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 889.9999 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1040 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1256.6666 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1588.3333 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1930.5 | 165 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2842.6666 | 82 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3701.9999 | 180 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7552.8362 | 30.83 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 7843.05 | 87 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4.58 | 2.29 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6.6 | 9 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 21.3333 | 160 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 33.335 | 66.67 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 51.2 | 96 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 55.4666 | 64 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 69.85 | 127 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 76.85 | 87 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 95.9999 | 144 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 100.3333 | 28 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 105.05 | 11 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 109.2 | 104 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 114.4 | 66 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 126.5 | 11 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 145 | 145 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 155.2666 | 137 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 162.8667 | 14 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 180 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 190.1333 | 46 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 196.3333 | 19 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 199.9998 | 300 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 206 | 12 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 209 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 211.3331 | 317 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 226.3332 | 140 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 273.3333 | 82 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 289.1667 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 294.2166 | 127 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 300 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 335.75 | 17 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 339.3333 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 352.75 | 85 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 374.92 | 133.9 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 401.5 | 146 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 437 | 38 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 456.5166 | 91 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 546.6666 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 646 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 695.5 | 39 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 916 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 999.25 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1353 | 3 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 2080 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2170 | 140 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2849.4265 | 176.8 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6600 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 8634.7 | 158 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 9316.7333 | 122 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 181.3 | 37 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 236.9833 | 59 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 477.75 | 65 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 277.75 | 33 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1193.7499 | 75 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 91.6666 | 110 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 872.6666 | 68 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 42.05 | 87 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 52 | 52 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 216.6667 | 20 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2779.5 | 54.5 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 560 | 140 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6574.1666 | 115 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 34 | 60 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 151.1999 | 81 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1184.1666 | 203 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 59.81 | 59.81 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 13.8 | 69 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 484 | 48 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1643.3332 | 340 | 1 | 1 | 0310-Pulverizer mills | U1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 731 | 340 | 1 | 1 | 0310-Pulverizer mills | U1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3.6667 | 22 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6.5613 | 5.18 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 8.8 | 22 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 13.3333 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 13.5 | 27 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 16.3333 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 23.3333 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 35.8333 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 41.25 | 55 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 52.1166 | 59 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 53.3333 | 64 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 58.8 | 56 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 59.25 | 79 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 59.9833 | 59 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 65 | 65 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 77 | 21 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 100.8333 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 102.5 | 123 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 165.2167 | 23 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 218.3 | 59 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 221.5 | 15 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 222.6833 | 31 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 229.1666 | 125 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 230.9497 | 447 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 234.6666 | 160 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 288 | 64 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 288.6667 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 302.9833 | 53 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 307.6666 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 307.9999 | 210 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 382.0906 | 202.88 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 388 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 439.5499 | 447 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 463.9999 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 480 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 490 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 531.0717 | 12.7 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 543.8333 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 599.5833 | 25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 718.9333 | 64 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 742.1 | 82 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 750.2833 | 109 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 775.5 | 235 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 779.4165 | 235 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 873.3333 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1241.6 | 64 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1894 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2090.8333 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2190 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2275 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2560 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 4252.8333 | 190 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 10081.5333 | 97 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 0 | 0 | 2 | 2 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2.889 | 57.78 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8.4333 | 23 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 8.5333 | 32 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9.15 | 30.5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 14.1833 | 23 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 14.8333 | 10 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 20.5 | 4.1 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 35.3833 | 11 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 39.3333 | 10 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 40.1333 | 86 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 42.5 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 43 | 43 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 43.9999 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 48.5 | 97 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 48.6667 | 10 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 53.1666 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 55 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 73.6666 | 170 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 83.9942 | 42.35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 85.2833 | 119 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 87.5 | 175 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 91.4999 | 90 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 95.3333 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 99.268 | 57.27 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 109.2 | 78 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 117 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 169 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 169.2 | 24 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 175.9999 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 179.8333 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 187 | 85 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 197.8 | 92 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 227.3333 | 220 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 229.8333 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 250.6666 | 160 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 259.5 | 45 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 259.9999 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 265.9935 | 34.47 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 275 | 150 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 325.1667 | 10 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 340.6666 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 388 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 500 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 559 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 565.2 | 108 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 595.9 | 101 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 634.2666 | 71 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 817.5 | 90 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 873.3332 | 131 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2153.3333 | 68 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3305.5 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4813.9212 | 49.13 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 6667 | 113 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7109.1666 | 95 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4.2 | 9 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 15.4 | 44 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 20.6833 | 17 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 23.4333 | 19 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 24.9167 | 23 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 44.6667 | 10 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 45.5 | 13 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 52.6166 | 77 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 57.5 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 69.3332 | 260 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 75.8333 | 10 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 82.5 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 84.5325 | 7.65 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 88.5 | 9 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 91 | 13 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 94.7333 | 98 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 95 | 95 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 101.5 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 110.0666 | 52 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 121.1166 | 43 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 132 | 55 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 148.5 | 45 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 151.6666 | 91 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 152.0154 | 100.23 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 153.55 | 111 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 202.6666 | 128 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 234 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 248.3333 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 261.66 | 22.05 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 277.5 | 370 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 286.6666 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 314.5833 | 125 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 327.75 | 115 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 344.1666 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 368 | 184 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 371.8333 | 46 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 406 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 411.16 | 54.1 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 423 | 94 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 459.8167 | 47 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 465.65 | 67 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 536.6666 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 605.4999 | 210 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 647.4 | 52 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 816.6666 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 864 | 160 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 973.9999 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1072.5 | 45 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1162.5 | 150 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1454.8333 | 145 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2130 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2258.6666 | 55 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2400 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3378.8333 | 95 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 12811.9999 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 14.9333 | 16 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 16.7833 | 19 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 111.8333 | 55 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 126.6333 | 29 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 251.1 | 162 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 259 | 74 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 393.3 | 54 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 702.9999 | 228 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 252.5 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 16.6667 | 20 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 44.4 | 18 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 60.8 | 7.6 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 644.9333 | 56 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 778.1666 | 115 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 88.4499 | 87 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 672 | 96 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 694.4999 | 90 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 251.0833 | 23 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 334.9486 | 54.76 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 91 | 91 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 92.25 | 61.5 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 178.15 | 21 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 290.605 | 50.54 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 417.69 | 59.67 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 419.15 | 101 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 23.6833 | 49 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1041.95 | 39 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 366.8 | 42 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3849.9999 | 132 | 1 | 1 | 0310-Pulverizer mills | U1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 0.3 | 3 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2.5667 | 14 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 7.6667 | 10 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7.8333 | 1 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 13.05 | 27 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 20.2 | 101 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 20.371 | 15.67 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 23.3333 | 25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 25.8667 | 8 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 27.5 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 41.2417 | 10.1 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 44.505 | 29.67 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 53.3 | 82 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 72 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 79 | 79 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 79.3333 | 28 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 129.75 | 45 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 141.25 | 75 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 153.75 | 45 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 155.8333 | 55 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 163.8 | 9.1 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 169 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 202.4167 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 221.6665 | 190 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 256.3166 | 91 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 288.3833 | 121 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 351.75 | 45 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 370.9999 | 210 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 437.4166 | 145 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 442.6666 | 80 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 449.25 | 45 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 487.9999 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 513.4 | 34 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 566.6666 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 577.9999 | 102 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 594 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 800 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 803.25 | 85 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 852 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 861.3333 | 80 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 896 | 64 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1087.6666 | 52 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1173.3333 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1433.3332 | 200 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1824 | 228 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2049.8333 | 98 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2752 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 11792.0833 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 16298.3833 | 53 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6.9 | 2 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 11.2 | 14 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 27.3916 | 86.5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 30.4 | 38 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 34.1333 | 64 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 39.42 | 59.13 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 40 | 80 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 46.75 | 55 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 56.6666 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 67 | 67 | 1 | 2 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 67.3666 | 86 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 94.992 | 39.58 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 97 | 97 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 102 | 51 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 103 | 103 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 103.4166 | 73 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 105.4166 | 55 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 148 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 151.4666 | 142 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 162 | 18 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 260.25 | 45 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 270.6 | 123 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 285.1333 | 94 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 307.9999 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 329.3333 | 80 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 364 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 377.6666 | 103 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 379.6666 | 170 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 400 | 80 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 474.9792 | 32.57 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 580 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 614.9 | 78 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 991.6 | 37 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1167.8333 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1287.7333 | 16 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2213.5 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3125.8333 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3930.6666 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 14973.75 | 45 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 0 | 0 | 1 | 2 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 9.3167 | 13 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 9.6 | 18 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 12 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 21.3 | 18 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 28.5 | 114 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 33.75 | 25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 37.196 | 43.76 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 43.5 | 18 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 55 | 44 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 78.8 | 24 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 79.3551 | 24.67 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 83.6 | 38 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 85.7666 | 83 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 95.6667 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 140.76 | 122.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 159.4558 | 46.67 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 159.65 | 31 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 159.8 | 47 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 170.8333 | 41 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 171.55 | 47 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 181.7 | 39.5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 189 | 63 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 228.125 | 109.5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 238.1166 | 91 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 240.2917 | 39.5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 292.5 | 65 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 305.8 | 66 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 309.8333 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 346.8 | 102 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 373.5 | 83 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 373.9999 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 400 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 444 | 37 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 462 | 77 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 489.1 | 67 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 514.2498 | 255 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 534 | 178 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 548.8166 | 149 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 710.2666 | 56 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1902.9999 | 165 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2425.3333 | 80 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2915.4 | 258 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3441.75 | 15 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4400 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4603.9999 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7305.6666 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 13295.9999 | 180 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 504.8333 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 998.4 | 208 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2755.6329 | 722 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 43.7333 | 41 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 231.1166 | 49 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1878.4999 | 102 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 106.6667 | 32 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 42.3566 | 26.2 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 125.4 | 114 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 433.4937 | 32.27 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1103 | 20 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 30.8 | 24 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 36.6667 | 20 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 37.4 | 18.7 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1520 | 48 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 120.0833 | 55 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 490.6665 | 184 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 54 | 108 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 106.4833 | 63.89 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 168 | 84 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 198.6666 | 40 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 215 | 86 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 478.6666 | 40 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 47.4 | 12 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 102.9 | 63 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 121 | 121 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 158 | 79 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 273 | 63 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 560.6667 | 29 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2587.5 | 150 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1201.3332 | 340 | 1 | 1 | 0310-Pulverizer mills | U1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 384.0375 | 156.75 | 1 | 1 | 0310-Pulverizer mills | U1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 11.6666 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 15 | 25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 28.4167 | 11 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 42.5333 | 44 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 42.5833 | 73 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 48 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 52.2 | 29 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 53.0833 | 13 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 56.7667 | 13 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 57 | 95 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 59.5833 | 65 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 75.5333 | 44 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 82.7667 | 13 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 102 | 85 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 106.65 | 27 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 107.6666 | 76 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 117.3332 | 128 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 120 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 126.6666 | 95 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 138.7 | 38 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 140.4 | 36 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 158.1666 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 204 | 34 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 210 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 257.6 | 184 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 292.2666 | 64 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 304 | 48 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 357 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 417.5999 | 108 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 438.75 | 135 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 440 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 476 | 119 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 500 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 506.5999 | 102 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 540 | 432 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 583 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 616.2 | 36 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 643.5 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 665 | 150 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 759.5 | 98 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 921.3333 | 10 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 925.1666 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 937.6666 | 194 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 960 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1058.8667 | 14 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 1140 | 190 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1305 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1305.8666 | 118 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2070 | 72 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2154.6 | 26.6 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 2563.3333 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 2726.6666 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2775.75 | 45 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3960 | 528 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4573 | 34 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 10323 | 180 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6.2333 | 22 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 7.6667 | 23 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 21.1621 | 115.43 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 22.4041 | 70.75 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 40 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 46.2 | 63 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 48.5666 | 94 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 49.5833 | 85 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 51 | 36 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 63 | 63 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 64.9167 | 41 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 88 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 99.5 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 110 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 114 | 114 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 121.5 | 90 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 122.6666 | 115 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 127.9999 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 131.7666 | 67 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 136.6667 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 147.5833 | 55 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 156.3333 | 67 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 185.6667 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 213.9666 | 49 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 227.5 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 234.0758 | 12.71 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 303 | 202 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 340 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 354.6667 | 38 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 357 | 119 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 358.8 | 92 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 380.6667 | 8 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 404.1666 | 97 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 515.6666 | 170 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 749 | 214 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 861.25 | 75 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 891 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1329.1665 | 250 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1420 | 80 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1549.1666 | 65 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1850.6666 | 80 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2408.4 | 108 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2800 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3313.6 | 57 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3641 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3680 | 115 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3933.75 | 25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9371.4 | 36 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 13832.1 | 47 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 23.4 | 13 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 28 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 52.4166 | 85 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 56.0333 | 82 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 66 | 132 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 81.9 | 27 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 87.5 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 89.011 | 15.99 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 97.2 | 81 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 104.2167 | 13 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 115.5 | 165 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 136 | 34 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 137.6666 | 140 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 142.5 | 90 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 144.7333 | 52 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 165.4666 | 68 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 182.8999 | 93 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 205.8999 | 213 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 206 | 103 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 252.5 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 275.3332 | 280 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 295.8 | 58 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 307.6666 | 142 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 361.8333 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 423.3 | 102 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 485.55 | 83 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 676.6666 | 200 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 825.55 | 0.95 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 934.5333 | 86 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 953.3333 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1239.9999 | 96 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1399.6666 | 170 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1409.4 | 36 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1573.9999 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1837.5333 | 86 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 2738.85 | 19 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3022.5 | 90 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3594 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3837.1666 | 91 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 12822.4667 | 19 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 14430 | 65 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 223.1 | 46 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 928.7 | 251 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1350 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 161.6667 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 219.1667 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 256.2 | 122 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 265.35 | 61 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 332.15 | 39 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 245.1 | 114 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 649.8333 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 15.8666 | 68 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 115.2 | 14.4 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 156 | 4 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 553.5833 | 91 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 151.25 | 75 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 270 | 90 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 350.6467 | 35.3 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1553.2833 | 107 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 193.7 | 149 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 293.3333 | 20 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 485.8333 | 110 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 13920 | 120 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 45.05 | 53 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 54.6975 | 59.67 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 36 | 10 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 39.3333 | 118 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 864 | 96 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 723.6 | 108 | 1 | 1 | 0310-Pulverizer mills | U1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3.8683 | 21.1 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6.5 | 26 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6.6666 | 200 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 15.0667 | 8 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 17.25 | 115 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 24.6666 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 28 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 39.55 | 21 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 45.26 | 37.2 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 54.395 | 29.67 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 56.6666 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 78 | 26 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 81.25 | 125 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 84 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 87.5 | 105 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 95.8333 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 102 | 102 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 103.75 | 75 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 133.3333 | 80 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 136 | 68 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 138.008 | 39.81 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 142.1333 | 8 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 175 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 180.9 | 81 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 182.25 | 45 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 203.5 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 216.75 | 85 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 220 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 240 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 249.6 | 128 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 253.3333 | 38 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 302.0333 | 41 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 322.0213 | 39.92 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 342 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 344.25 | 27 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 348.6 | 14 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 356.25 | 75 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 375 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 385.4 | 9.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 400 | 64 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 414.9999 | 300 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 425 | 150 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 453.3333 | 25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 463.5 | 45 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 468.8333 | 97 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 508.25 | 107 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 561.6 | 144 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 633.3333 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 795.1666 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 800 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 810 | 180 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 985.1666 | 128.5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1027.8333 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1052.5 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1220.6667 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1450 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1633.3331 | 350 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1651 | 260 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1843.75 | 75 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2065.9999 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2584.0833 | 55 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2592 | 216 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 7800 | 200 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 7840.6665 | 190 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 17920.55 | 87 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 30.9963 | 40.43 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 34.6667 | 1 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 45.2333 | 59 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 51.5667 | 47.6 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 53.6667 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 54.6666 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 63.6999 | 78 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 75.8333 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 86 | 86 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 100 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 104.0125 | 39.75 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 105.3333 | 8 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 128.25 | 135 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 130.9 | 22 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 143 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 144.45 | 107 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 146.9333 | 38 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 153.3666 | 86 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 182.5 | 75 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 198 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 199.3333 | 92 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 221.6666 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 239 | 239 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 264.9166 | 85 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 272.65 | 41 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 283.8 | 129 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 298 | 149 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 304.5 | 87 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 396 | 11 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 535 | 75 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 579.6666 | 94 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 632 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 659.8333 | 107 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 980 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1678.0833 | 65 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3276.6667 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5195.6666 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5224.6666 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 29.1833 | 103 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 42 | 42 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 42 | 42 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 56.25 | 25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 56.6667 | 17 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 64.5 | 129 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 109.8667 | 32 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 125.6666 | 52 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 173.2393 | 98.06 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 180.0833 | 5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 193.4166 | 55 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 216.3333 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 217.9667 | 26 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 245 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 268.6666 | 260 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 276 | 69 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 360 | 72 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 477.3766 | 49.9 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 486.0833 | 95 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 510 | 170 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 584.495 | 84.1 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 585.9 | 63 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 631.8332 | 170 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 863 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 931.5 | 69 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1157.3333 | 56 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1185.3332 | 140 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 1412.0167 | 19 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2176 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2479.8666 | 28 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 2829.3333 | 160 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2904.1831 | 341 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3173.3333 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4729.6666 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 12857 | 34.5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 6.7667 | 7 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 30.15 | 27 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 132.3 | 63 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 466.6666 | 200 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 662.3 | 179 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 52.4166 | 37 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 72.3333 | 28 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 151 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 133.4666 | 91 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 87.4 | 19 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 413.7 | 18 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1018.4 | 13.4 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3459.1999 | 138 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 14911.8 | 116 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 48 | 24 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 75.6 | 12.6 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 199 | 60 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 312.5 | 125 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 320 | 80 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 445.5 | 55 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 480 | 48 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 122.4 | 108 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2949.9999 | 150 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 150 | 120 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 780 | 520 | 1 | 1 | 0310-Pulverizer mills | U1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 21501.6663 | 475 | 1 | 1 | 0310-Pulverizer mills | U2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3.3833 | 7 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5.2 | 12 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 10 | 10 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 10.1333 | 8 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 11.7433 | 27.1 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 14.6667 | 22 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 16.3333 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 21.1808 | 36.31 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 22.9167 | 25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 24.5833 | 5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 25.6667 | 11 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 37.8 | 63 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 38.35 | 39 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 51.35 | 39 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 58.75 | 15 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 68.25 | 39 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 80.855 | 47.1 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 89.5999 | 84 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 94 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 105.75 | 47 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 106.6666 | 160 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 109.2 | 8 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 110.5167 | 19 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 113.3333 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 118.0667 | 23 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 121.7333 | 83 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 128.3333 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 132.5 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 134.3666 | 139 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 150 | 10 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 180.5533 | 37.1 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 200.6666 | 140 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 221.6666 | 140 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 229.9999 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 243.8 | 10.6 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 247.5 | 25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 260.7499 | 447 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 318.4666 | 34 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 332.5 | 95 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 337.3666 | 58 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 354.5 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 357.75 | 45 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 417.6 | 48 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 479.9999 | 180 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 494.25 | 15 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 601.9999 | 84 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 620 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 777.5 | 75 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 792 | 88 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 897.1667 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 912.9333 | 41.75 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1074.1 | 69 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1100 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1599.9999 | 300 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1640 | 80 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1709.4 | 148 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2043.3333 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2485.9999 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2609.3832 | 331 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3664.2833 | 121 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3691.3332 | 245 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 4012.5 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8500 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 0 | 0 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 5.75 | 23 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8.75 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9.1 | 22.75 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 12.7 | 6 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 20.2667 | 16 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 22 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 22.5 | 45 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 22.6666 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 30.305 | 9.57 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 32.55 | 7 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 33 | 36 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 35.4 | 1 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 36 | 12 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 42 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 47.9121 | 27.91 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 68.7999 | 96 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 72.3333 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 82.65 | 87 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 83 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 86.9999 | 90 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 89.25 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 94.5 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 108 | 108 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 131.25 | 25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 150.2666 | 92 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 158.1666 | 73 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 167.4167 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 180 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 188 | 94 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 188.5 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 190 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 190.6666 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 196.8375 | 65.25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 201 | 67 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 226.4166 | 55 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 248.75 | 75 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 262.5 | 175 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 270.425 | 186.5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 276 | 92 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 305.5 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 317.4167 | 13 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 323.25 | 45 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 333.6667 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 350.9 | 87 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 422.9167 | 25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 427.5 | 45 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 437.4278 | 43.67 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 643.25 | 83 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 668.175 | 88.5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 678.3333 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 854.9999 | 108 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 979.6 | 39.5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1005.3333 | 80 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 1382.4999 | 150 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1563.3332 | 140 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2517.6667 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3700 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 6568.5 | 87 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7442.1666 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6.3333 | 10 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 8.8 | 33 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 15.1667 | 14 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 18.1333 | 34 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 24.0185 | 43.67 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 45 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 46.6666 | 56 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 48.9 | 18 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 50.75 | 21 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 55 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 60 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 61.8833 | 79 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 68.4 | 114 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 83.5666 | 46 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 98.7499 | 75 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 102 | 102 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 105 | 15 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 128.4 | 12 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 136 | 51 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 144 | 72 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 145.8 | 162 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 149.8333 | 31 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 155 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 167.4 | 54 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 170 | 200 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 177.55 | 53 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 177.7333 | 62 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 195.8333 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 200 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 206.72 | 40.8 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 238 | 8 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 250 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 261.3333 | 64 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 275 | 25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 386.1667 | 2 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 483 | 23 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 489.3333 | 80 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 502.9166 | 71 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 529.7849 | 164.7 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 572.8 | 64 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 633.85 | 21 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 653.3333 | 112 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 673.6666 | 94 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 719.95 | 77 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 774.5667 | 38 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 846.0666 | 98 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 882.9 | 162 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 999.7333 | 23 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1057.0999 | 93 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1331.2 | 104 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1369.1667 | 10 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1419 | 215 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 1581 | 102 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1704 | 36 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1807.3 | 106 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1916.0667 | 41 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1981.9999 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2043 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 5618.4499 | 111 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 22230 | 200 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 67472.9166 | 125 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 492.7999 | 231 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 759.3333 | 67 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 73.45 | 39 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 80.2333 | 58 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 173.3333 | 65 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 29.3333 | 20 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 454.0333 | 106 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2537.1666 | 65 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 21.6667 | 20 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 248 | 96 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 380 | 20 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 436.8 | 112 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 7.2865 | 23.01 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 27.95 | 13 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 163.48 | 36.6 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 270.6833 | 29.8 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 531.5333 | 68 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 729.75 | 63 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 2.9333 | 11 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 7.3333 | 40 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 222.5 | 89 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 280 | 40 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 336 | 84 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 100 | 25 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4.5333 | 8 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 20.5833 | 13 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 208.3332 | 125 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 221.6 | 48 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 9408.75 | 325 | 1 | 1 | 0310-Pulverizer mills | U2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 105.4167 | 5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 120 | 5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 538.1667 | 5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 885 | 10 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 962.4167 | 5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 42 | 3 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Winter | 600 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 294 | 63 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 563.1666 | 218 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 962.8 | 8 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 4552.8 | 168 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 1180 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 0 | 0 | 1 | 3 | 0310-Pulverizer mills | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 60.6667 | 8 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 238.6664 | 358 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 791.8667 | 8 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 2651.1333 | 38 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 925.1 | 58 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 240 | 10 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 103.5 | 138 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 373 | 373 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 31.75 | 5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 40 | 5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 670 | 10 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 259 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 518 | 28 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 3367.2 | 368 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 810 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 2760 | 15 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 62.1833 | 13 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 91.2 | 48 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 1069.2 | 88 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 38 | 38 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 639 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 4.8333 | 58 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 79.1667 | 38 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 0 | 0 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 423 | 188 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 220 | 10 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 1839.8333 | 10 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 35 | 5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Winter | 450 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 27.2333 | 38 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 420 | 15 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 21.8987 | 20.53 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 238.467 | 82.23 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 1313.25 | 255 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 24.0007 | 19.46 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 219.0467 | 20.6 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 277.5 | 30 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 136.0666 | 52 | 1 | 1 | 0312-Pulverizer mill classifiers | D2-Forced - Delayed | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 777.3332 | 265 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 60 | 10 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 90 | 10 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 97.9167 | 25 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 381.0473 | 40.04 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 914.6666 | 160 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 92.004 | 27.06 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 177.829 | 217.75 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 1365.3333 | 80 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 368.6666 | 140 | 1 | 1 | 0312-Pulverizer mill classifiers | D2-Forced - Delayed | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 178.7664 | 346 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 247.9664 | 346 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1862.4999 | 150 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 521.7 | 47 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1796.1666 | 130 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 39.004 | 41.79 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 498.8332 | 146 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 8.5 | 85 | 1 | 1 | 0312-Pulverizer mill classifiers | D2-Forced - Delayed | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 596.4166 | 85 | 1 | 1 | 0312-Pulverizer mill classifiers | D2-Forced - Delayed | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 105 | 14 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 563.3333 | 100 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1270.5 | 154 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1.3333 | 40 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 104.25 | 15 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 133.8542 | 31.25 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 350.1333 | 104 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 117.75 | 157 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 337.5 | 150 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 1100.75 | 85 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 56.8333 | 62 | 1 | 1 | 0312-Pulverizer mill classifiers | D2-Forced - Delayed | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3135.9166 | 121 | 1 | 1 | 0312-Pulverizer mill classifiers | D2-Forced - Delayed | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 3840.3 | 306 | 1 | 1 | 0312-Pulverizer mill classifiers | D2-Forced - Delayed | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 60.4166 | 25 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 208.1567 | 40.55 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1105 | 170 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 56.6666 | 85 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1100 | 200 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5231.6667 | 50 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1746.75 | 137 | 1 | 1 | 0312-Pulverizer mill classifiers | D2-Forced - Delayed | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 886.9166 | 145 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 79.0833 | 13 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1044.4 | 42 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1188.6 | 84 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 751.1166 | 60.25 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 837.4333 | 97 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1056 | 48 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 427.5 | 57 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D1-Forced - Immediate | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 800 | 160 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D1-Forced - Immediate | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 128.3333 | 100 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D1-Forced - Immediate | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 276 | 69 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D1-Forced - Immediate | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 17.7332 | 152 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D1-Forced - Immediate | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3534 | 120 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D1-Forced - Immediate | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1011.0046 | 119.41 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D1-Forced - Immediate | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 481.6666 | 85 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D3-Forced - Postponed | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1420.8332 | 155 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D3-Forced - Postponed | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 8129.9999 | 180 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D1-Forced - Immediate | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 966 | 184 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D1-Forced - Immediate | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1174.4166 | 85 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D2-Forced - Delayed | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 216.05 | 87 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D2-Forced - Delayed | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 512 | 60 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D1-Forced - Immediate | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1129.3333 | 77 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D1-Forced - Immediate | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 355.7333 | 92 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4 | 16 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 152.0833 | 25 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 276.4166 | 155 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 26.8 | 12 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 85.5 | 18 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 48.8 | 24 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 94.5 | 42 | 1 | 1 | 0315-Pulverizer mill coal level controls | D2-Forced - Delayed | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3 | 12 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 95 | 25 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 608 | 60 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 166.5 | 74 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 748.75 | 75 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1162.6666 | 320 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 147.5833 | 35 | 1 | 1 | 0315-Pulverizer mill coal level controls | D2-Forced - Delayed | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 62.8999 | 102 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 257.8333 | 91 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 5.0667 | 16 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 134.7 | 18 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 466.2 | 37 | 1 | 1 | 0315-Pulverizer mill coal level controls | D2-Forced - Delayed | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 20 | 10 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 30 | 10 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 18.5 | 15 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 30.8 | 24 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 101.2 | 138 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 772.5 | 150 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 42 | 7 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 86 | 86 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 310.5 | 81 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 82.95 | 79 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 41.1667 | 13 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 115.5 | 77 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4276.5332 | 316 | 1 | 1 | 0315-Pulverizer mill coal level controls | U1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 14.7333 | 68 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 23.25 | 93 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 24.9333 | 68 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 28.9999 | 174 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 47 | 188 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 49.6832 | 271 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 57 | 57 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1068.3333 | 50 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 78 | 39 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 216.6666 | 260 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 704.0666 | 118 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1347.4999 | 165 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1945.9 | 122 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 312.5 | 50 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 377.6 | 64 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3204 | 180 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 189.7499 | 99 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 358.0666 | 164 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 579.9665 | 274 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 770.4 | 144 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 2686.2 | 74 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 2717.2999 | 174 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 79.2166 | 49 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 104.4 | 54 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 612.95 | 299 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 651.6 | 24 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 33.0666 | 64 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 42.9 | 99 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 76.4666 | 124 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 82.9999 | 249 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 224.1999 | 114 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 243 | 324 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 391.5 | 174 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 454.3833 | 199 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 459.2 | 224 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 791.7 | 174 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 1216.8332 | 149 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 2009.7 | 99 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 2303.4666 | 224 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 242.782 | 63.89 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D3-Forced - Postponed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 413.6166 | 83 | 1 | 1 | 0320-Foreign object in Pulverizers mill | U1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4.8333 | 58 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 18.1333 | 68 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 20.1499 | 93 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 27.6498 | 237 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 31.3332 | 188 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 46.8331 | 281 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 83.5833 | 17 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1083.208 | 106.72 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3.1667 | 38 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 24 | 24 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 61.8332 | 265 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 156.6667 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6.8 | 68 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 21.9 | 73 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 36.6666 | 55 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 238 | 28 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 308.0998 | 234 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 30.3333 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 35.3333 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 145.3333 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 1889.25 | 99 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 41.3333 | 124 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 42.4 | 24 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 83 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 151.4333 | 154 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 243.3666 | 149 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 463.7333 | 74 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 530.3998 | 234 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 599.2 | 214 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 655.6 | 149 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 842.4499 | 249 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 1255.7998 | 234 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 3771.2998 | 234 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3.8666 | 58 | 1 | 2 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 17.8333 | 107 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 125 | 15 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 58.5833 | 19 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 82.5 | 45 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 145.0333 | 38 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 156.6666 | 40 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 397 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 13.6 | 68 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 15.4999 | 93 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 212.1666 | 95 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1890 | 18 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 22 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 56.3333 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 143.3333 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 151.6667 | 50 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 316.0999 | 174 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8.19 | 27.3 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 55.6667 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 69.6 | 144 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 86.92 | 32.8 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 117 | 19.5 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 1278.9 | 174 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 21.41 | 64.23 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 26.95 | 49 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 41.65 | 49 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 60.6333 | 214 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 63.2 | 24 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 121.3333 | 91 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 142.0999 | 174 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 142.2667 | 44 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 153.0666 | 224 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 191.8 | 274 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 208.8 | 174 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 243.8666 | 124 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 598.5332 | 134 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 973.6666 | 254 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 987.9665 | 214 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 1496 | 374 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 2325 | 124 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 2525.3665 | 274 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 3224.2665 | 214 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1.7 | 34 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6.8 | 68 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 12.4666 | 68 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 28.0333 | 58 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 30.15 | 201 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 44.1332 | 331 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 126 | 63 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 209 | 60 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 334.8333 | 98 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 536.6666 | 70 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 6.5167 | 23 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10.6666 | 64 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 83.3 | 47.6 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 284.1666 | 110 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 840 | 35 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1024.1 | 114 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 3430 | 140 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 108.1 | 23 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 310.2 | 99 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 33.3333 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 65 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 833.0666 | 284 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 34.5333 | 74 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 62 | 124 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 112.5 | 54 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 122.5 | 49 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 135.9833 | 199 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 247.9 | 74 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 298.6999 | 174 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 471.7333 | 244 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 511.4999 | 99 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 600.3 | 54 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 835.2 | 174 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 908.1333 | 49 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 1162.2665 | 184 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 1328.7 | 309 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 2163.4665 | 244 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7.9333 | 68 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 8.9999 | 135 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 19.7499 | 237 | 1 | 2 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 24.7999 | 93 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 480 | 40 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 831.6667 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5.75 | 69 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 17.0917 | 29.3 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 95.3333 | 55 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 124.1333 | 98 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 154.6666 | 40 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 166.75 | 69 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 215.3333 | 85 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 500 | 150 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2929.1665 | 190 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 7.9333 | 68 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 73.4999 | 90 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 240.9 | 99 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 262.2 | 114 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 477 | 159 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 2874.6666 | 224 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 11644.0665 | 389 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 76.2666 | 88 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 428.4 | 204 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 4861.8666 | 344 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2.42 | 12.1 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 82.4 | 24 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 136.5666 | 34 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 177.65 | 209 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 217.0666 | 74 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 232.9 | 274 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 295.2333 | 34 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 431.5665 | 214 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 492.9 | 159 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 1029.4999 | 174 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 1534.0999 | 174 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 1750.9333 | 49 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 1927.1332 | 274 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 2904.5332 | 224 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2.8333 | 85 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 10.8333 | 65 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 11.3333 | 68 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 12.4 | 93 | 1 | 2 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 21.7 | 93 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 22.6666 | 68 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 52.1333 | 68 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 70.8 | 236 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 96 | 30 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 520 | 60 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2002 | 182 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 15.3 | 102 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 19.5 | 15 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 87.4333 | 122 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 294.8333 | 58 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 388 | 48 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1579.9 | 122 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2115.75 | 93 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2956 | 80 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 10.95 | 73 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 67.0833 | 115 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 86.25 | 115 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 269.9667 | 26 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 306.25 | 35 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 396.43 | 68.35 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 312.8666 | 76 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 25.6667 | 20 | 2 | 2 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 39.3333 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 176.2333 | 34 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 889 | 254 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 15.6667 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 18.7833 | 49 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 52.6667 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 338.6667 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 349.7333 | 244 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 921.2 | 49 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 1108.2166 | 49 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 37.95 | 99 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 63.7 | 49 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 80.1666 | 74 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 164.0333 | 74 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 197.8666 | 224 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 198.5666 | 74 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 237.6 | 99 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 278.5665 | 274 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 356.4333 | 74 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 476.0666 | 74 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 553.8666 | 124 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 572.2666 | 74 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 639.9 | 54 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 1112.4666 | 74 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 1411.1 | 274 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 90.6666 | 40 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D3-Forced - Postponed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3.1 | 93 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9.5 | 57 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 15.8666 | 68 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 16.8 | 21 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 24.9999 | 150 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 26 | 40 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 41.3332 | 248 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 52.25 | 19 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 53.6 | 12 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 67.4333 | 47.6 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 139.7 | 33 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 288.75 | 165 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 348.3999 | 78 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 549.9999 | 165 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6.0833 | 73 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 48.6666 | 73 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 73 | 73 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 166.725 | 51.3 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 280 | 224 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 615.8666 | 124 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 730.7332 | 194 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 24.6667 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 90.7499 | 99 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 109.9332 | 194 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 947.2 | 74 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 30.3999 | 114 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 35.1333 | 124 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 44.6666 | 134 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 169.6 | 64 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 252.3 | 174 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 333.4999 | 174 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 513.9 | 54 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 533.9833 | 199 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 554.4 | 154 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 741.4666 | 134 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 792 | 144 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 2511.3999 | 174 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4.65 | 93 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7 | 42 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 17 | 68 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 19.2666 | 68 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 34 | 68 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 35.7666 | 58 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 43.4499 | 237 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 274.3333 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 580 | 24 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1621.55 | 123 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 27.7667 | 47.6 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 29.8276 | 41.62 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 68.9 | 53 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 186.4333 | 47.6 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 196.2 | 43.6 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1018.7333 | 148 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2459.3332 | 140 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7.0833 | 17 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 23.1 | 18 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 108.1666 | 118 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 440 | 60 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 943 | 69 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 860.295 | 69.1 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1831.3166 | 77 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 26.6667 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 205.2 | 34.2 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 638.6 | 124 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 84.3333 | 44 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 84.7333 | 124 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 110.21 | 10.7 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 123.3 | 274 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 145.9333 | 199 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 165.3 | 174 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 201.15 | 149 | 2 | 2 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 276.2666 | 224 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 516.1999 | 174 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 564.2 | 124 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 604.8 | 224 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 632.1999 | 174 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 902.8 | 74 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 1765.8666 | 224 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 2404.2665 | 184 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 2762.8332 | 274 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 650 | Fluidized Bed | SERC | Winter | 13.6667 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 650-Fluidized Bed
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 86.3333 | 28 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 800-Miscellaneous
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 141.0667 | 23 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 434 | 105 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2299.9998 | 300 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 16 | 48 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 301.95 | 33 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 93 | 93 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 50.1666 | 43 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3430.6666 | 31 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 174.1666 | 55 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 603.3333 | 50 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 706.25 | 75 | 1 | 1 | 0325-Pulverizer skidding | D3-Forced - Postponed | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 120 | 50 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 445 | 50 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 460 | 75 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1156 | 170 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 381.6667 | 50 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 54 | 54 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 11.7 | 18 | 1 | 1 | 0325-Pulverizer skidding | D2-Forced - Delayed | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 600.65 | 123 | 1 | 1 | 0325-Pulverizer skidding | D3-Forced - Postponed | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 265 | 530 | 1 | 1 | 0325-Pulverizer skidding | U1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 485.8333 | 55 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 875 | 50 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 216.6667 | 50 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 882.75 | 55 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 37.8933 | 20.3 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 63.3333 | 190 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 76 | 19 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 116.25 | 31 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 366.8333 | 31 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2999.0666 | 166 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 267.05 | 109 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 21.4 | 51.36 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 181.3333 | 68 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 42.9 | 13 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 184.1666 | 85 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1615 | 60 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 165 | 33 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 346.6666 | 40 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 33.3333 | 80 | 1 | 1 | 0325-Pulverizer skidding | D2-Forced - Delayed | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 811.25 | 55 | 1 | 1 | 0325-Pulverizer skidding | D3-Forced - Postponed | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 781.5833 | 83 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 384 | 128 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 32 | 32 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 350 | 56 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 1.5 | 5 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 62.5 | 50 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 150.8333 | 50 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 173.3333 | 65 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 222 | 120 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1047.3333 | 40 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 66.5 | 19 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 107.6667 | 38 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6262.6666 | 77 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 31.5 | 27 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 66.5 | 57 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 142.5 | 95 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 317.9167 | 35 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 364 | 112 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 467.4999 | 150 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1268.75 | 145 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 88.8333 | 41 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 121.5 | 27 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 461.9893 | 119.48 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 113.1666 | 97 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 319 | 66 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 502.7833 | 97 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 69.3333 | 32 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1377.5 | 145 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D3-Forced - Postponed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1610.2639 | 194.79 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D3-Forced - Postponed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 69 | 60 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 100 | 30 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 750 | 100 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 24.3333 | 73 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 91 | 35 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 183.3333 | 50 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 194.25 | 37 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 300 | 150 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 457.5 | 91.5 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1094.75 | 145 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 22.5 | 45 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 63 | 108 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 78.6 | 36 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 237.5 | 150 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 454.4165 | 205 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 578.45 | 69 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1220.4166 | 145 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1230 | 120 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2450 | 100 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 197.8 | 43 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 350.6666 | 40 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 187.6 | 42 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6.5 | 13 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 37.4999 | 90 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 39.3333 | 5 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 68.3333 | 100 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 77.6666 | 233 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 87 | 58 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 265.8333 | 79.75 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 330 | 75 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 331.5666 | 49 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 63.9999 | 96 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 222.8333 | 70 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 293.3333 | 80 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 414.5166 | 119 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 857.9166 | 145 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1035 | 92 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 29 | 60 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 36.3333 | 20 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 384.25 | 145 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 93 | 36 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 105.1333 | 38 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 131.4666 | 58 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 294.5 | 95 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 265.4166 | 65 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 339.5 | 97 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 374.5832 | 155 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 411.2499 | 105 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 415 | 83 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 694.1666 | 85 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1040.0333 | 82 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1695.2 | 78 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 91.5 | 91.5 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 102.6666 | 80 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 136.6833 | 59 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 191.6666 | 100 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 390 | 130 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 785.4166 | 145 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 804.1666 | 125 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 206.15 | 133 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 520 | 200 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 540.4 | 14 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 543.6666 | 140 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 727.8333 | 110 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2016.6666 | 100 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 200 | 50 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 215 | 100 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 270 | 90 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 308.3333 | 50 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 380 | 30 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 467.5 | 50 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1494.45 | 123 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2079 | 55 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 52.8833 | 19 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 225 | 25 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 237.5 | 150 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 384.25 | 145 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 652.5 | 145 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 61 | 30 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 108 | 48 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 159 | 36 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 178.2499 | 93 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 195 | 60 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 268.3333 | 100 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 109.55 | 31.3 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 413.565 | 34.9 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 4.0833 | 49 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 130.15 | 57 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 4 | 120 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 440 | 40 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D3-Forced - Postponed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 17.6 | 33 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D3-Forced - Postponed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 224.9666 | 34 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 230 | 230 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 347.6666 | 70 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 471 | 20 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 627 | 60 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1211.1666 | 130 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9 | 3 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 331.5 | 90 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 391.4166 | 77 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6.6666 | 100 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 42.5 | 30 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 44.6333 | 103 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 180 | 100 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 733.5 | 90 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 776.8999 | 102 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 975 | 100 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1342.5 | 150 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2368.3333 | 145 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1183.1457 | 166.25 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 28.325 | 30.9 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 65.9633 | 25.7 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 727.5666 | 73 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1455.8166 | 113 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 30.4833 | 29.5 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 59.25 | 39.5 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 90 | 30 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 109.5 | 9 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 179.1667 | 10 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 730.5 | 10 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 221.3166 | 49 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 265.2332 | 146 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 592.2 | 47 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 697.6666 | 140 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1595 | 145 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 90.9999 | 78 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 129.5 | 70 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 136 | 102 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 145 | 145 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 157.5 | 45 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 169.1999 | 108 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 177.6666 | 65 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 210 | 60 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 654.4999 | 102 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 45.6333 | 37 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 280.6 | 69 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 208.8 | 58 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 212.5 | 50 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 330 | 132 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 200.3166 | 119 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 234.4 | 48 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1.3333 | 5 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 63 | 30 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 69.3333 | 64 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 69.6666 | 76 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 81.3333 | 80 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 408 | 144 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4116.6666 | 100 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 15.4 | 42 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 52.2 | 29 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 109.3333 | 40 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 173 | 86.5 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 202 | 120 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 469 | 93.8 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 679.9999 | 120 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 821.6666 | 145 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2118.3332 | 155 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 10.4167 | 5 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 172.0019 | 94.68 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 813.75 | 155 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 63.96 | 98.4 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 101.5 | 30 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7050.9999 | 165 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D3-Forced - Postponed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 306.25 | 35 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 83.1999 | 78 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 73.6666 | 65 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 125 | 60 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 175 | 35 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 307.6666 | 52 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 55 | 55 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 142.6 | 93 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 350 | 70 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 472.8666 | 173 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1107.1665 | 365 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2921.15 | 37 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 45.5 | 10 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 115 | 60 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 189 | 18 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 547.4 | 161 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 571.9999 | 120 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6120.8333 | 130 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 44.65 | 11.4 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 203.45 | 39 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 292.3833 | 53 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 95.7 | 29 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 100.8333 | 55 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 150 | 25 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 196.3333 | 124 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 197.0833 | 55 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 272.5 | 30 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 443.6666 | 55 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 641.6666 | 55 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 144.7833 | 73 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 178 | 120 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 243.4667 | 44 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 310 | 124 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 334.25 | 15 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 346.6666 | 260 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1041.8333 | 35 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1080 | 120 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2055 | 30 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 410.8333 | 85 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 255 | 10 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 70.2666 | 31 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D3-Forced - Postponed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 0 | 0 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6.8333 | 10 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 246.4 | 42 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 406.25 | 65 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 440.2999 | 102 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 526.5 | 78 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1539 | 45 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 290.7 | 34 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 444.1666 | 82 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 632.5 | 110 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 640 | 100 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1080 | 160 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1175.8333 | 83 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 14.6667 | 44 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 172.6666 | 70 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 375.8333 | 110 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 389.1667 | 50 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 400.5 | 18 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1202.4 | 108 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1629.1666 | 115 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 44 | 44 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 133.7 | 42 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 239.8 | 44 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 75.9 | 11 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 865 | 15 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2011.6 | 47 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3165 | 100 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 99.6666 | 52 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 172.0833 | 35 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 737.5832 | 265 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 131.4166 | 95 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 152 | 96 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 264.075 | 50.3 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 274.1666 | 70 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 614.8333 | 62 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 640 | 160 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 115.4833 | 41 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 22 | 44 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D3-Forced - Postponed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1936.6666 | 50 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D3-Forced - Postponed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 31.6667 | 20 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 107.3333 | 46 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 108.5 | 42 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 130 | 65 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 339.1666 | 37 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 352 | 22 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 666.6666 | 125 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 712.2499 | 165 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2282.5 | 50 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8.1 | 27 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 22.5333 | 52 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 80.5 | 70 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1381.65 | 151 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 85 | 102 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 183.3333 | 88 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 375 | 45 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1912.4999 | 135 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3206.25 | 225 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 50.5667 | 41 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 55.6566 | 28.3 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 82 | 82 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1844.75 | 47 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 393.6 | 82 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D3-Forced - Postponed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 29.5 | 10 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 50.6333 | 31 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 113.6 | 48 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 199.5 | 21 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 408.8 | 112 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 610 | 120 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 72 | 18 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 72.8333 | 19 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 102.9166 | 95 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 495 | 55 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 641.6666 | 55 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2860 | 52 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 59.9958 | 29.75 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 79.5 | 9 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 230.75 | 65 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 829.9999 | 120 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1406 | 74 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 9970 | 60 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 7.5833 | 13 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 464.7416 | 128.5 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 725.3667 | 47 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 890.2666 | 88 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D3-Forced - Postponed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 61.25 | 35 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D3-Forced - Postponed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 33.3333 | 50 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 71.55 | 53 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 102.4666 | 116 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 140 | 30 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 450.45 | 59.4 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 965.8331 | 305 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1966.6666 | 50 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 7188.75 | 355 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 40.6666 | 40 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 88 | 120 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 104.8333 | 85 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 212.85 | 99 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 2746.3332 | 140 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 13.8333 | 10 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 28.6667 | 20 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 48 | 24 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 424.4333 | 107 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 151.8 | 25.3 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D3-Forced - Postponed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 17.6 | 24 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 19.4333 | 11 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 180 | 120 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 415 | 50 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 528.9166 | 55 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 727.5 | 97 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1647.9166 | 125 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 141.7833 | 47 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 253.45 | 37 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 8.6667 | 20 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 56.3333 | 52 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 67.1 | 122 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 767.25 | 135 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 823.3999 | 138 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 148.2 | 57 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 311.2 | 48 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 123.2499 | 87 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D3-Forced - Postponed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 9878.2666 | 278 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | U2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 161.7 | 18 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 88.8 | 18 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 102.6666 | 80 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 134 | 60 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 135.4166 | 125 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 153.75 | 45 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1015 | 145 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1254 | 120 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 9.45 | 63 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 90.9 | 54 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 175.5 | 90 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 410 | 100 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1.6667 | 20 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 54 | 108 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 65 | 260 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 70.6667 | 20 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 99 | 99 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 152 | 152 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 173.3333 | 80 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 176 | 110 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 297.2333 | 74 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 352 | 110 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 550 | 88 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1792.5 | 45 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 17.5 | 35 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 376.25 | 215 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 466.9333 | 136 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 256.6665 | 175 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 520 | 65 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 184.1666 | 130 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 262.1666 | 55 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 317.3333 | 80 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 597.8333 | 85 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 3080 | 110 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 91.8666 | 104 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 97.5333 | 44 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 145.5 | 97 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 967.5999 | 123 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 20.7999 | 78 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 37.2666 | 86 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 193 | 20 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 250.1332 | 268 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 692.5 | 138.5 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1892.25 | 145 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4539.1666 | 65 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 57 | 90 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 138.45 | 39 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 16.6666 | 100 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 4.6666 | 70 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 114.2332 | 149 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 202.5 | 270 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 495.4166 | 145 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 24.5 | 30 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 45.8333 | 55 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 54.6666 | 80 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 81.5 | 30 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 108.75 | 145 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 166.8333 | 70 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 421.0832 | 155 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1416 | 120 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 112 | 28 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 141 | 20 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 160.1035 | 26.61 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 244.4999 | 90 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 274.35 | 93 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 427.5 | 95 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 616.25 | 145 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 786.6666 | 80 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1317.3332 | 260 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2261.6666 | 100 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 35.5667 | 22 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2588.6665 | 220 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3976.5833 | 35 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 214.1667 | 50 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 232.9 | 51 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 174.097 | 91.63 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 181.05 | 51 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 252 | 144 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 85.5 | 90 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 237.85 | 67 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 796.5 | 270 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 26.55 | 59 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 40.1333 | 28 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 100 | 200 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 145.5 | 45 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 174.9999 | 105 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 437.4999 | 150 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2082.6666 | 88 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 47.1683 | 9.1 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 395.9 | 107 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 429.3333 | 20 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 701.6667 | 50 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 701.95 | 101 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 950.95 | 133 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1051.85 | 109 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1659.3333 | 19 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1675 | 60 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 51.5667 | 22.1 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 84.5833 | 145 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 130 | 20 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 303 | 101 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 362.5 | 145 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 399.9 | 86 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 533.6667 | 20 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 597.85 | 33 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 12 | 4 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 84 | 16.8 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 283.5 | 70 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 423.0333 | 98 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 2243.6 | 284 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 553.4166 | 145 | 1 | 1 | 0335-Pulverizer lube oil system | D3-Forced - Postponed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 406.6666 | 100 | 1 | 1 | 0335-Pulverizer lube oil system | D3-Forced - Postponed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 34.1 | 62 | 1 | 1 | 0335-Pulverizer lube oil system | D3-Forced - Postponed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 88.3333 | 53 | 1 | 2 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 171.1666 | 130 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 175.5 | 78 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 550.4999 | 90 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 13.3833 | 73 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 13.8333 | 83 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 24.9333 | 88 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 28 | 8 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 41.0833 | 85 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 76 | 38 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 147.5 | 75 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 280 | 100 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1.4 | 14 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4.9 | 14 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 12.8333 | 70 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 58.3333 | 25 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 114.5833 | 25 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 116 | 116 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 140 | 70 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 185.3666 | 67 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 536.6666 | 100 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2547.4999 | 150 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 56 | 56 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 55 | 25 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 793 | 130 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2497.55 | 119.5 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 97.1333 | 62 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 59.5 | 30 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 76.3666 | 158 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 128.3333 | 55 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 150 | 45 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 189.5833 | 175 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 236.1666 | 130 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 270 | 50 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 483.4025 | 60.05 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 525 | 70 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 627.15 | 111 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 696.8 | 39 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 906.6666 | 100 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 18.1333 | 68 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 64.5667 | 13 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 170 | 150 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 401.25 | 107 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 508.25 | 107 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 520 | 104 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 653.6666 | 106 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 845.5 | 19 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2754.2666 | 104 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 14.6 | 12 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 27.5 | 110 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 72.5 | 145 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 166.25 | 95 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 266.25 | 75 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 340 | 85 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 667.2083 | 119.5 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1089.3333 | 20 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1111.6666 | 230 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4280.4 | 72 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 9435.8333 | 50 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 108.7833 | 61 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 801.1666 | 115 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 20 | 60 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 22.6666 | 68 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 221.35 | 57 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 906.4999 | 210 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 31.7917 | 17.5 | 1 | 1 | 0335-Pulverizer lube oil system | D3-Forced - Postponed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 17.3333 | 80 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 42.5 | 15 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 74 | 74 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 207.5 | 50 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 231.8333 | 130 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 264 | 66 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 328.8 | 48 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 332 | 103.75 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 345 | 230 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 755.7 | 99 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 935 | 85 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 26.2833 | 83 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 278.0666 | 172 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 675 | 90 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 26.25 | 63 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 66.5 | 30 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 68.8333 | 35 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 75 | 50 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 135 | 135 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 233.6667 | 20 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 270.3 | 53 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 9.6 | 72 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 482.6 | 254 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 500.85 | 81 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 13.75 | 55 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2582.3329 | 635 | 1 | 1 | 0335-Pulverizer lube oil system | U1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 18.75 | 75 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 39.0833 | 33.5 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 91 | 35 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 167.9166 | 155 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 216.6666 | 130 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 255.1333 | 178 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 259 | 70 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 414.6666 | 80 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6348.1665 | 205 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 25.6666 | 110 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 42.9 | 78 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 90.0666 | 28 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 119.25 | 53 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 136.5 | 130 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 184 | 46 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1.1667 | 14 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 46.6666 | 80 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 95 | 20 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 555 | 300 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 83.3667 | 41 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 76.6833 | 43 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 156 | 26 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 273 | 20 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1827.9166 | 133.75 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 225.4999 | 165 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 149.25 | 45 | 1 | 1 | 0335-Pulverizer lube oil system | D3-Forced - Postponed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 109.8666 | 64 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 232 | 48 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 2031.9166 | 185 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 110 | 55 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 24.25 | 15 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5 | 20 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 26 | 8 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 27.5 | 33 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 49.5 | 18 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 50 | 20 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 71.9999 | 108 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1435 | 175 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 3267.7972 | 355.84 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 84.6666 | 40 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 91.3 | 83 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 376.2 | 11 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1989.1666 | 110 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 314.4166 | 77 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 54.5832 | 131 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D2-Forced - Delayed | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 48 | 90 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D2-Forced - Delayed | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 8 | 40 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5520 | 184 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 19.575 | 43.5 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 39.6333 | 58 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 55.7999 | 108 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 226 | 30 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 263.7833 | 119 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 270 | 90 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 444.5 | 42 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 35.7666 | 37 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 127 | 20 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 163.1667 | 22 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 119.25 | 135 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D2-Forced - Delayed | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 10 | 120 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D2-Forced - Delayed | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 0.58333 | 7 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 63 | 108 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 114.6667 | 20 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 28.6666 | 40 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 37.3333 | 112 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 100 | 100 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 200.75 | 73 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 13.3333 | 40 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 91 | 65 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 273.4666 | 56 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 393.3333 | 80 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 426.0667 | 44 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 76.6667 | 20 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 691.6666 | 100 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 8 | 40 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 17.1 | 27 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 56 | 40 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1750.75 | 149 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 6 | 6 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 56.8333 | 55 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 276.2499 | 195 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 586.3 | 33 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 43.654 | 37.96 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3021 | 530 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | U1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 24.9166 | 65 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 36.25 | 75 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 48.3 | 69 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 161.4332 | 167 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 182.25 | 45 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 29 | 58 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 53.0333 | 37 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 33.3333 | 80 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 42 | 24 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3195 | 180 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | U1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 258.5 | 47 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 36.3999 | 78 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 103.9999 | 240 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 150 | 30 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 286 | 143 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 43.5 | 87 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 349.8133 | 93.7 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D2-Forced - Delayed | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 966 | 140 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D2-Forced - Delayed | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1278 | 120 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D2-Forced - Delayed | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 20.8 | 16 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 42.6667 | 32 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 111.9166 | 85 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 126.9646 | 88.58 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9 | 18 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 57 | 19 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 111.25 | 25 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 146.9333 | 38 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1178 | 30 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 171.95 | 57 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 502.25 | 105 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 203.6666 | 65 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 508.6666 | 109 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D2-Forced - Delayed | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Gas | GG | 850 | Combined Cycle Block | WECC | Off-Peak | 44.6193 | 43.18 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 850-Combined Cycle Block
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 21679 | 60 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 122.4 | 68 | 1 | 1 | 0339-Pulverizer System Puff | U1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4906 | 30 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1708 | 35 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 213.5833 | 55 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 475 | 100 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 76 | 80 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 209.3333 | 80 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 39484.9998 | 318 | 1 | 1 | 0339-Pulverizer System Puff | U2-Forced - Delayed | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 23.85 | 27 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2252.584 | 57.66 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 70.2 | 78 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 5.8333 | 25 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 101.7 | 27 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6130.25 | 155 | 1 | 1 | 0339-Pulverizer System Puff | U1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 306.25 | 175 | 1 | 1 | 0339-Pulverizer System Puff | U1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 889.9999 | 120 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 190.8 | 212 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 11.75 | 47 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 5.6666 | 170 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 16606.0832 | 505 | 1 | 1 | 0339-Pulverizer System Puff | U2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9.8333 | 10 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 40.8333 | 14 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 58.3333 | 50 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 62 | 31 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 71.1 | 54 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 72 | 24 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 75.8333 | 35 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 86 | 86 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 89.6667 | 20 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 94.2333 | 22 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 97.3333 | 73 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 98.3333 | 50 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 151.6666 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 192 | 96 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 195.3333 | 20 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 225 | 75 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 248 | 80 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 257.25 | 245 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 377 | 58 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 400 | 50 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 433.3333 | 100 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 435 | 87 | 1 | 2 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 609.5833 | 55 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 840 | 80 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 860 | 20 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 868 | 140 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 885 | 20 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 894.1667 | 50 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 915 | 305 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1091.25 | 45 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1574 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1787.5 | 55 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3515.5 | 79 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5128.1998 | 297 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 6605.6666 | 149 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 7.3 | 73 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 18 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 24.75 | 99 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 25.6166 | 53 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 36 | 18 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 40.8 | 102 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 41 | 4 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 58.8333 | 5 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 67.3 | 6 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 77.3333 | 232 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 92 | 23 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 93.15 | 9 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 147.3333 | 13 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 339.5666 | 167 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 341 | 62 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 406.6666 | 40 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 410.6664 | 352 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 452.4 | 312 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 767.25 | 465 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1093.95 | 187 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 1702.8 | 132 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 6.4167 | 5 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 42.8333 | 5 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 47 | 60 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 51.94 | 5.88 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 61 | 60 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 75.9 | 66 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 94 | 40 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 161.25 | 45 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 169.5833 | 37 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 233.3333 | 80 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 245.8333 | 50 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 315 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 336 | 210 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 337.3333 | 80 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 345 | 20 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 357.6 | 144 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 359.3333 | 110 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 519.9999 | 150 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 554.4 | 88 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 566.8333 | 95 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 590.3333 | 55 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 591.9999 | 222 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 638 | 58 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 657.3333 | 80 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 741.6666 | 100 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1033.5 | 159 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 2939.5831 | 425 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4400 | 250 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 5702.9333 | 68 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 180387.3332 | 370 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 30 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 100 | 50 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 168.6 | 84.3 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 765 | 50 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 16.0008 | 73.85 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 90.3 | 12.9 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 100.1 | 77 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 9232.1666 | 65 | 1 | 1 | 0340-Other pulverizer problems | D3-Forced - Postponed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 231.7332 | 176 | 1 | 1 | 0340-Other pulverizer problems | U1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 34.3 | 98 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 37.05 | 39 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 71.1318 | 24.67 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 112.2333 | 14 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 128.5 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 136.5 | 18 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 177.8833 | 13 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 259 | 259 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 285.8333 | 35 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 308.3332 | 370 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 350 | 140 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 442.9666 | 97 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 584.25 | 95 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 763.75 | 65 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 770.6666 | 80 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 840 | 140 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1182.4999 | 75 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1511.35 | 181 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1797.4999 | 150 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2287.5 | 15 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5042.7 | 27 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5167.5 | 50 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 6672.7166 | 149 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4 | 24 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 28.2333 | 7 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 41 | 10 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 51.9167 | 7 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 56.6666 | 100 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 57 | 57 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 58 | 5 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 60.8666 | 83 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 90 | 180 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 91.9333 | 7 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 111.9 | 9 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 114 | 152 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 164.1667 | 50 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 166.4 | 52 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 228.0667 | 11 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 232 | 40 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 386.6666 | 160 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 430.6666 | 40 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 795 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 900 | 180 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4519.9166 | 73 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 1.0833 | 1 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 6 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 26.2 | 6 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 40.5 | 9 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 57 | 45 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 72 | 36 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 96.75 | 15 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 107.5 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 226.6666 | 170 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 307.4998 | 225 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 326.3333 | 220 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 336.6 | 68 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 348.3333 | 100 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 400.05 | 127 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 518.3333 | 100 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 561 | 68 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 684.6666 | 40 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1256 | 48 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1302.1666 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1405 | 20 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1695.1 | 134 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2152.0833 | 125 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3880.8 | 84 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6151.3663 | 574 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | SERC | Summer | 347.1 | 178 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 29.3333 | 8 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 992 | 64 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 414.8333 | 95 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 292 | 48 | 1 | 1 | 0340-Other pulverizer problems | D3-Forced - Postponed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 330.2 | 39 | 1 | 1 | 0340-Other pulverizer problems | D3-Forced - Postponed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 9.825 | 4.5 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 11.6667 | 35 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 12 | 12 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 17.5 | 42 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 84.065 | 29.67 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 95 | 25 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 107 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 118.34 | 59.17 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 120.1333 | 53 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 130.6667 | 8 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 140.1666 | 145 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 148.3333 | 100 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 152 | 19 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 153.3333 | 50 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 180 | 40 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 187.5 | 15 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 210 | 210 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 215.8 | 26 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 216.6666 | 65 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 253.3333 | 40 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 270.3999 | 78 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 276.6666 | 200 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 285.1333 | 26 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 327 | 45 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 351.3332 | 310 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 390.4 | 122 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 450 | 20 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 512.3 | 94 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 552 | 160 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 568.75 | 75 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 606.8 | 82 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 812 | 58 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1019.6666 | 161 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1274.226 | 80.14 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1734 | 289 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1856.7999 | 132 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2016 | 36 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2326.5 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8060.25 | 45 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8448 | 165 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3.3333 | 20 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 34.2 | 54 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 35.2 | 88 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 68.7499 | 75 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 69 | 9 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 88.9333 | 8 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 114.6708 | 94.25 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 132.4 | 24 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 145.3666 | 49 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 160 | 120 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 161.7667 | 23 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 174 | 87 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 180 | 180 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 185 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 186.6667 | 25 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 197.55 | 27 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 219.05 | 13 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 222 | 6 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 264.3333 | 65 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 275 | 110 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 306.8167 | 41 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 355.5 | 45 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 496.5 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 710.3333 | 20 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1286.3833 | 79 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1414.5 | 246 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1570 | 120 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1890 | 150 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 7.9333 | 17 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 8 | 32 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 51.3333 | 110 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 69 | 92 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 75 | 20 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 93.5999 | 108 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 154.5 | 45 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 170 | 20 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 189.5 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 198.1666 | 290 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 250 | 50 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 281.7833 | 53 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 372 | 80 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 381 | 60 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 550.8 | 68 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 678.3332 | 370 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 718 | 120 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 805 | 230 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1368.5 | 391 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2430 | 60 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2591.0833 | 85 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 3298.3333 | 100 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 10490 | 100 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 20449.3331 | 392 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 253.5 | 65 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 26.8667 | 26 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 477 | 53 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 21.85 | 23 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 48.75 | 15 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 878.9416 | 72.74 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 537.88 | 76.84 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 237.65 | 49 | 1 | 1 | 0340-Other pulverizer problems | D3-Forced - Postponed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 401.1666 | 58 | 1 | 1 | 0340-Other pulverizer problems | D3-Forced - Postponed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7387.1 | 427 | 1 | 1 | 0340-Other pulverizer problems | U1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3 | 18 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3.1407 | 6.73 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4 | 4 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8 | 40 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 29.5166 | 77 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 34.0083 | 37.1 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 38.5 | 14 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 46.1833 | 17 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 55 | 50 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 58 | 58 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 74.6666 | 70 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 90 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 111.8333 | 110 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 190.8 | 53 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 205.2333 | 94 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 207 | 46 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 229.7583 | 39.5 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 266.49 | 197.4 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 277.5 | 37 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 315 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 351.25 | 75 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 445.7666 | 43 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 517.9999 | 120 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 540 | 120 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 550 | 100 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 591.6666 | 100 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 648.2833 | 97 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 716.1375 | 84.75 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 886.6666 | 112 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 944.6666 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1036.6667 | 20 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 1091.0665 | 392 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 3724.9999 | 447 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 0 | 0 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 13.5667 | 11 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 30.8 | 56 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 43.3333 | 52 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 45 | 45 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 45.8333 | 50 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 49.4 | 57 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 75.5 | 6 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 88 | 44 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 88.5 | 90 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 89.5833 | 25 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 130.5 | 9 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 166.5 | 90 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 212 | 106 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 255.3333 | 40 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 384 | 192 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 390 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 445.5 | 54 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 630 | 14 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 760 | 120 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 815 | 60 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1425.3167 | 19 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2740.4665 | 202 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4276.85 | 69 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 7418.6666 | 40 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 22 | 24 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 22.3405 | 34.37 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 52.5 | 90 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 62.1833 | 41 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 63 | 18 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 74.1 | 78 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 88 | 40 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 88 | 110 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 162.1166 | 137 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 188.3333 | 20 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 190 | 19 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 273.3666 | 139 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 294.6 | 18 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 300 | 50 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 326.2 | 84 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 379.1667 | 50 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 408.3333 | 100 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 443.3333 | 100 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 515.6666 | 68 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 679.4665 | 392 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 957.6666 | 68 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1117.3333 | 80 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1183.75 | 15 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 1319.6664 | 370 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1818.9666 | 197 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2975 | 250 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4071.6666 | 100 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6622 | 440 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 143.2167 | 13 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 55 | 20 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 87.0833 | 55 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 100.3333 | 35 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 179.6666 | 49 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 32 | 20 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 80 | 60 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 8312.7496 | 615 | 1 | 1 | 0340-Other pulverizer problems | SF-Startup Failure | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 16128.75 | 425 | 1 | 1 | 0340-Other pulverizer problems | U1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1218.3332 | 340 | 1 | 1 | 0340-Other pulverizer problems | U1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 23.1133 | 34.67 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 25.3333 | 20 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 30.3333 | 70 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 69.9 | 18 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 88.9666 | 157 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 89.3333 | 40 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 123.3332 | 200 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 143.1 | 18 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 151.6666 | 140 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 168.3333 | 100 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 169.8498 | 237 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 188.9999 | 162 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 194.3333 | 53 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 220.4167 | 25 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 260 | 100 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 315 | 60 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 326.6667 | 50 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 335 | 335 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 336.6666 | 100 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 383.3999 | 162 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 463.8666 | 98 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 478.75 | 75 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 497.4999 | 150 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 552.5 | 425 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 620 | 100 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 731.6666 | 100 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 948 | 120 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1094.75 | 145 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1471.2 | 48 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2781.9 | 66 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4336 | 80 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 26482.0833 | 65 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 9.5 | 19 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 12.5 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 35.4666 | 76 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 49 | 28 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 67.5833 | 5 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 71.9333 | 52 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 73.84 | 62.4 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 75 | 6 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 75.6 | 7 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 79.7333 | 104 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 100 | 100 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 100.4667 | 44 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 102.75 | 9 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 148.8667 | 44 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 153 | 54 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 165.3333 | 40 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 222.1333 | 98 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 251.3333 | 232 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 314.1667 | 50 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 438 | 73 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 443.22 | 73.87 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 642.4 | 44 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 1044.05 | 157 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1150 | 115 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1200.6167 | 41 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1237.5 | 66 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 6369.75 | 447 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6.8 | 68 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 16.8667 | 23 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 18.0167 | 23 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 22.6666 | 40 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 24.0333 | 14 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 25 | 60 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 30 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 34.9998 | 300 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 50 | 25 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 56.8828 | 16.33 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 77.5 | 75 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 90.25 | 57 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 92.2833 | 113 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 103.5 | 23 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 105.4 | 124 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 161.0666 | 302 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 172.6664 | 370 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 210 | 100 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 216.6666 | 260 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 271.9999 | 120 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 297 | 33 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 303.5333 | 29 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 499.8 | 40.8 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 504.7 | 49 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 559 | 39 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 570.3499 | 183 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 851.5 | 65 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1137.3333 | 80 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 1288.6 | 102 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1874.6666 | 74 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 2125 | 425 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2356 | 124 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2447.5 | 89 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 2613.1998 | 282 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 4628.5666 | 191 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 5315.3333 | 68 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 5423 | 187 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 10894.5333 | 202 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | SERC | Summer | 17.3333 | 16 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 26.3333 | 20 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 61.92 | 21.6 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 67.68 | 21.6 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 306.1333 | 64 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 255 | 20 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 156.6833 | 79 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 218.5833 | 61 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 483.03 | 71.56 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3865.3333 | 65 | 1 | 1 | 0340-Other pulverizer problems | D3-Forced - Postponed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 161.2666 | 164 | 1 | 1 | 0340-Other pulverizer problems | SF-Startup Failure | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2994.84 | 84.6 | 1 | 1 | 0340-Other pulverizer problems | U1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2.9645 | 25.41 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 7.7035 | 14.91 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 8.3333 | 10 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 8.4166 | 101 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 23.3333 | 40 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 37.23 | 43.8 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 60.75 | 135 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 64 | 80 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 67.5 | 15 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 128 | 8 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 143 | 260 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 187.5 | 45 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 198 | 44 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 247.4665 | 232 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 266.6666 | 100 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 283.5 | 210 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 312.05 | 79 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 325 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 370.8 | 72 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 411.6 | 49 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 450 | 180 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 454 | 120 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 482.2333 | 74 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 510 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 728 | 28 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1072.5 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2160 | 108 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3161.25 | 27 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5909.75 | 15 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 11206 | 60 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 12100.8333 | 65 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 13256.6833 | 127 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 12.1333 | 52 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 13.6 | 12 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 25 | 25 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 48.0667 | 7 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 69.1667 | 5 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 75 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 78.75 | 105 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 85.2 | 72 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 87.75 | 39 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 158.65 | 167 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 162.1332 | 152 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 168 | 9 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 408.3333 | 175 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 481.5333 | 62 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 597.3 | 33 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 807.8666 | 332 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 827.75 | 215 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 843.75 | 125 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 990 | 75 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 992.8 | 48 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1113.6 | 64 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 1127.4666 | 302 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 1173.9 | 182 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3938.9999 | 180 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5083.7333 | 64 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 5606.6665 | 232 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 20 | 24 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 30.6 | 108 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 31 | 60 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 46 | 23 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 58.1667 | 5 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 68.3333 | 100 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 99 | 27 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 100.3333 | 20 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 129 | 45 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 135.6667 | 44 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 146.6666 | 200 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 152 | 160 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 167.4999 | 150 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 168 | 28 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 173.5 | 2 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 198 | 108 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 211.1999 | 144 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 227.9999 | 180 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 260.3333 | 220 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 325.2667 | 41 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 366.6666 | 100 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 532.1665 | 310 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 562.5 | 50 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 645 | 100 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 847.9999 | 120 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 990 | 110 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 1332 | 370 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1749.583 | 425 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 2230.2666 | 172 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2524.5 | 18 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 4532.5333 | 92 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5448.5 | 170 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 10580 | 20 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 12358.6666 | 92 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 44609.0833 | 73 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 214.6 | 74 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1497.2499 | 84.75 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9.1667 | 22 | 1 | 1 | 0340-Other pulverizer problems | D3-Forced - Postponed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 49250 | 50 | 1 | 1 | 0340-Other pulverizer problems | D3-Forced - Postponed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 41.6666 | 50 | 1 | 1 | 0340-Other pulverizer problems | D3-Forced - Postponed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 471.2 | 48 | 1 | 1 | 0340-Other pulverizer problems | D3-Forced - Postponed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 624.075 | 15.9 | 1 | 1 | 0340-Other pulverizer problems | D3-Forced - Postponed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3600 | 15 | 1 | 1 | 0340-Other pulverizer problems | D3-Forced - Postponed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 901.17 | 500.65 | 1 | 1 | 0340-Other pulverizer problems | U1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1015.6665 | 220 | 1 | 1 | 0340-Other pulverizer problems | U1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 23.6 | 12 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 33 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 49.1167 | 7 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 50 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 63.6667 | 20 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 72 | 18 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 77.5 | 31 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 78 | 78 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 80.75 | 51 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 126.6667 | 20 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 183.9333 | 62 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 210.6 | 54 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 219.9999 | 150 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 245 | 35 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 275.3333 | 70 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 296.3333 | 70 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 338.4 | 72 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 338.8 | 77 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 425 | 75 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 576 | 180 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 939.9333 | 92 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1008 | 252 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 1064.9331 | 392 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1369.9999 | 120 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1503.65 | 87 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1715.9164 | 349 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1970.3333 | 20 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 2487.3331 | 410 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 3400 | 425 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 3930 | 300 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5779.3333 | 20 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4.4 | 22 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 6.9667 | 22 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 16 | 16 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 16.6667 | 25 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 19.5 | 19.5 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 21.5 | 43 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 42 | 14 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 42.4999 | 75 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 55.3333 | 40 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 72.6833 | 7 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 78.6666 | 80 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 110.39 | 23.24 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 159.1667 | 10 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 163.8 | 28 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 168 | 20 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 270 | 180 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 294.4333 | 73 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 328.6 | 212 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 333.5 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 349.25 | 127 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 606.6667 | 25 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1502.0833 | 175 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1651.9999 | 84 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1890 | 108 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5793.5 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 50974.2 | 27 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 22.5 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 34.4 | 43 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 52 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 71.9666 | 34 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 83.3333 | 100 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 93.5 | 85 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 95.8333 | 115 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 106.3333 | 220 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 145.8 | 108 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 146.4167 | 35 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 159.5 | 110 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 161.6667 | 20 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 177.1 | 138 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 245 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 313.9999 | 120 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 450 | 75 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 450 | 120 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 457.9167 | 35 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 475.3332 | 310 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 617.5 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1033.3332 | 400 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1086.8666 | 68 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1270.5 | 154 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1346.0833 | 145 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1487.5 | 125 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1539.6665 | 310 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1935 | 150 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 15281.6667 | 20 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 175 | 70 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 71.4666 | 64 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 255 | 30 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2305 | 20 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 100.8167 | 23 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 601.875 | 133.75 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 39.5832 | 125 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 147.3333 | 52 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 290 | 145 | 1 | 1 | 0340-Other pulverizer problems | D3-Forced - Postponed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3.6665 | 220 | 1 | 1 | 0340-Other pulverizer problems | U1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 187 | 170 | 1 | 1 | 0340-Other pulverizer problems | U1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 18.4 | 23 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 21.0027 | 39.38 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 27.9434 | 128.97 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 31.6583 | 14.5 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 63 | 63 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 66 | 11 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 74 | 74 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 93.8667 | 8 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 112 | 20 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 117 | 18 | 2 | 2 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 170.5 | 310 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 183.3333 | 100 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 213.75 | 45 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 227.5 | 10 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 268.6666 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 294 | 49 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 324.9999 | 150 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 371.2333 | 86 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 400 | 50 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 457.7 | 46 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 685.9999 | 120 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 754 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 1042.1664 | 370 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1120 | 28 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1256.7 | 177 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1300 | 50 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1677.0833 | 115 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 2918.3331 | 425 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7025 | 60 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 30908.2666 | 68 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 39.6667 | 7 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 64.35 | 117 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 72.6667 | 4 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 74.1667 | 10 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 110.5 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 115.3 | 6 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 145 | 58 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 179.6666 | 98 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 197.5 | 158 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 244.5667 | 23 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 256 | 128 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 441.8166 | 49 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 642.1166 | 59 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 934.83 | 103.87 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 993.3333 | 80 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 1026.1333 | 52 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 13246.4 | 108.8 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 13.3333 | 40 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 18.3333 | 110 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 37.4999 | 90 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 50.1166 | 31 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 94.4666 | 218 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 98.4 | 6 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 118.5 | 79 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 137.6666 | 140 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 139 | 60 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 154 | 88 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 156 | 48 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 162.9167 | 23 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 180 | 120 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 217.7333 | 46 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 245.8333 | 50 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 277.3332 | 128 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 280.8 | 208 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 325 | 100 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 345.3332 | 280 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 376 | 15 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 433.3332 | 200 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 451.5 | 35 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 493 | 17 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 500 | 25 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 550 | 50 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 550 | 110 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 575.1667 | 35 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 669.6666 | 82 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 703.3332 | 200 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1027.3333 | 92 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1302.95 | 253 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1322.9166 | 25 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1652.3 | 82 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 2318.3333 | 100 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 61.5 | 82 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1100.5166 | 94.33 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 154 | 22 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 344.3499 | 213 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 183.4666 | 64 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 58.5 | 13 | 1 | 1 | 0340-Other pulverizer problems | D3-Forced - Postponed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 357 | 119 | 1 | 1 | 0340-Other pulverizer problems | D3-Forced - Postponed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1617.6667 | 20 | 1 | 1 | 0340-Other pulverizer problems | D3-Forced - Postponed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 8.1666 | 98 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 224 | 70 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 75.3333 | 113 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 50.6667 | 38 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 3067.5 | 75 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 345.1667 | 38 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 753.9166 | 83 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 18.6666 | 28 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 244 | 48 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 52.2666 | 64 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 89.3333 | 8 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0341 | Pulverizer deluge system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 460 | 92 | 1 | 1 | 0341-Pulverizer deluge system | D2-Forced - Delayed | 100-Fossil-Steam
0341 | Pulverizer deluge system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 483 | 92 | 1 | 1 | 0341-Pulverizer deluge system | D2-Forced - Delayed | 100-Fossil-Steam
0341 | Pulverizer deluge system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1791.1666 | 110 | 1 | 1 | 0341-Pulverizer deluge system | D1-Forced - Immediate | 100-Fossil-Steam
0341 | Pulverizer deluge system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 195.8 | 22 | 1 | 1 | 0341-Pulverizer deluge system | D2-Forced - Delayed | 100-Fossil-Steam
0341 | Pulverizer deluge system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 108 | 72 | 1 | 1 | 0341-Pulverizer deluge system | U1-Forced - Immediate | 100-Fossil-Steam
0341 | Pulverizer deluge system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 639 | 142 | 1 | 1 | 0341-Pulverizer deluge system | D2-Forced - Delayed | 100-Fossil-Steam
0342 | Pulverizer inert system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1770.6 | 156 | 1 | 1 | 0342-Pulverizer inert system | D1-Forced - Immediate | 100-Fossil-Steam
0342 | Pulverizer inert system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 129.5633 | 82.7 | 1 | 1 | 0342-Pulverizer inert system | D1-Forced - Immediate | 100-Fossil-Steam
0342 | Pulverizer inert system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1356.6 | 399 | 1 | 1 | 0342-Pulverizer inert system | D1-Forced - Immediate | 100-Fossil-Steam
0342 | Pulverizer inert system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 320 | 40 | 1 | 1 | 0342-Pulverizer inert system | D1-Forced - Immediate | 100-Fossil-Steam
0342 | Pulverizer inert system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 940 | 235 | 1 | 1 | 0342-Pulverizer inert system | D1-Forced - Immediate | 100-Fossil-Steam
0342 | Pulverizer inert system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9.25 | 15 | 1 | 1 | 0342-Pulverizer inert system | D1-Forced - Immediate | 100-Fossil-Steam
0342 | Pulverizer inert system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 5624.2666 | 161 | 1 | 1 | 0342-Pulverizer inert system | D1-Forced - Immediate | 100-Fossil-Steam
0342 | Pulverizer inert system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2898.0666 | 116 | 1 | 1 | 0342-Pulverizer inert system | D1-Forced - Immediate | 100-Fossil-Steam
0342 | Pulverizer inert system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 333 | 111 | 1 | 1 | 0342-Pulverizer inert system | D1-Forced - Immediate | 100-Fossil-Steam
0342 | Pulverizer inert system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2.4666 | 148 | 1 | 1 | 0342-Pulverizer inert system | D1-Forced - Immediate | 100-Fossil-Steam
0342 | Pulverizer inert system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 630 | 70 | 1 | 1 | 0342-Pulverizer inert system | D1-Forced - Immediate | 100-Fossil-Steam
0342 | Pulverizer inert system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7.5833 | 65 | 1 | 1 | 0342-Pulverizer inert system | D1-Forced - Immediate | 100-Fossil-Steam
0342 | Pulverizer inert system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 2296.9846 | 266.06 | 1 | 1 | 0342-Pulverizer inert system | D1-Forced - Immediate | 100-Fossil-Steam
0342 | Pulverizer inert system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 265.4 | 132.7 | 1 | 1 | 0342-Pulverizer inert system | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 15 | 10 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 58.5 | 18 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 401.25 | 15 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 412.5 | 150 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2704.6333 | 41 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2788.5 | 90 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 90.0833 | 47 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 106.6667 | 20 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 696.6666 | 100 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1595.9999 | 126 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6910.7333 | 92 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 22 | 11 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 139.2 | 87 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 620 | 155 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1202.0666 | 146 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 896.375 | 75.75 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 50 | 25 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 52 | 13 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 70 | 30 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 353.0166 | 59 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 608 | 152 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 114 | 20 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 349.0833 | 59 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 695 | 50 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 702.0833 | 125 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 997.5 | 70 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 48 | 12 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3200.5166 | 49 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 542.5 | 155 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 461.1 | 58 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1725.3333 | 160 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 958 | 120 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1508.4166 | 115 | 1 | 1 | 0344-Pulverizer inspection | D3-Forced - Postponed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 72 | 27 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 205 | 20 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 315.7333 | 37 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 324 | 81 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 445.5 | 99 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 761.25 | 87 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1076.8 | 32 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1183 | 91 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1595 | 50 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 84.3333 | 23 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 107.9167 | 35 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 222.6 | 63 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 291.6417 | 39.5 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 322 | 120 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 604.1667 | 50 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 354.6 | 54 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1545.6 | 24 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 728 | 104 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 300 | 150 | 1 | 1 | 0344-Pulverizer inspection | D3-Forced - Postponed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 18 | 9 | 2 | 2 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 75 | 30 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 883.7833 | 13 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1200.3333 | 65 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1458.5833 | 115 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 19439.25 | 45 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 99 | 54 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 136 | 102 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 162.5 | 50 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 198.3333 | 20 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 399.0999 | 78 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2408.25 | 95 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4764.6666 | 140 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 144 | 18 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 169 | 52 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 551.25 | 63 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 587.05 | 59 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 483.8666 | 152 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1299.6333 | 127 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 20 | 8 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 35.75 | 11 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 296 | 37 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 427.8333 | 34 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1008 | 12 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3142.15 | 29 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 6401.2 | 104 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 196.6667 | 20 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 256.6666 | 110 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 345 | 12 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1035.6666 | 65 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2542.5 | 90 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 26870 | 40 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 84.5 | 78 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 755.7333 | 104 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 6107.4 | 324 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 6547.2 | 248 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 39.5 | 30 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 333.25 | 155 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 637.5 | 45 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3.75 | 9 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 132.9999 | 105 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 145 | 29 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 174 | 58 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 291.6666 | 140 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1070.1 | 87 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6090 | 60 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 788 | 80 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 896.4666 | 68 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 117.4999 | 75 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 456 | 38 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 748.0208 | 71.81 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 386.25 | 309 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 16 | 4 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 32 | 16 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 135.4167 | 25 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 545.4166 | 275 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 225 | 45 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 481 | 111 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 481.9999 | 120 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1016.6667 | 50 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 167.6333 | 94 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 273 | 78 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1284.9999 | 150 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1575 | 100 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2686.6666 | 100 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 409.7033 | 64.69 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 5708.5 | 233 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 749.1666 | 58 | 1 | 1 | 0344-Pulverizer inspection | D3-Forced - Postponed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 386.4 | 56 | 1 | 1 | 0344-Pulverizer inspection | D3-Forced - Postponed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2159 | 34 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 12.35 | 19 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 66.3875 | 16.95 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 67.2 | 12 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 105 | 45 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 182.75 | 51 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 278.25 | 21 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1818.6666 | 80 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2166.6166 | 49 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1084.2666 | 76 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 495.4166 | 145 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 1235 | 65 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 2914.3333 | 35 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 260 | 65 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 10873.75 | 75 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 165 | 3 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 612.1167 | 19 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1962.6666 | 40 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 48.3333 | 2 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 70 | 5 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7320.3333 | 20 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 11101.5667 | 26 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 14 | 1 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 155 | 100 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 25 | 100 | 1 | 1 | 0345-Pulverizer overhaul | D2-Forced - Delayed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 17.85 | 7 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1032 | 8 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 111 | 3 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3300 | 60 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 46.3667 | 13 | 1 | 1 | 0345-Pulverizer overhaul | D2-Forced - Delayed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 415.6 | 24 | 1 | 1 | 0345-Pulverizer overhaul | D3-Forced - Postponed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 16893.5 | 130 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 23861.25 | 35 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 25100 | 100 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 159.8333 | 7 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 672 | 28 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 22700 | 50 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 144 | 12 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 198 | 3 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1640.3333 | 37 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 596.2 | 66 | 1 | 1 | 0345-Pulverizer overhaul | D3-Forced - Postponed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1978.05 | 9 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 451.5833 | 5 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 573.8 | 38 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1403.5 | 14 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2086.6666 | 80 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3300 | 50 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5610 | 60 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5784.2333 | 38 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 66216 | 89 | 1 | 1 | 0345-Pulverizer overhaul | D3-Forced - Postponed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 111.6667 | 20 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 470.1333 | 82 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 673.75 | 5 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1470 | 30 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10325 | 140 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 37895 | 55 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 530.9167 | 5 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5340 | 18 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 14412 | 60 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 49265 | 50 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 803.8333 | 35 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1085 | 35 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 11628.9066 | 58.3 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1380 | 20 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3870 | 30 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 89 | 30 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 144 | 8 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 214.3333 | 2 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1092 | 7 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 220 | 40 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3559.2 | 36 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2019.3 | 106 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 440 | 8 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5705.4167 | 25 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4995 | 27 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2348.4 | 30.9 | 1 | 1 | 0345-Pulverizer overhaul | D2-Forced - Delayed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1293.75 | 27 | 1 | 1 | 0345-Pulverizer overhaul | D2-Forced - Delayed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 744 | 8 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 93.8667 | 32 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 95 | 60 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 117.8666 | 68 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 129.9999 | 150 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 219.3333 | 40 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 841.6666 | 100 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 528 | 44 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 60.5 | 55 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 127.9999 | 120 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 233.3333 | 40 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2194.3999 | 156 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 387.6 | 20.4 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 121.52 | 33.6 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 9.9667 | 23 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 22 | 110 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 96.9 | 51 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 36.2167 | 41 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 48.75 | 39 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 63.25 | 69 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 103.4 | 47 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 7.25 | 145 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 166.75 | 115 | 1 | 1 | 0346-Pulverizer pyrite removal system | D3-Forced - Postponed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 505 | 100 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 573.0666 | 56 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 694.6667 | 20 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 169.456 | 105.91 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 119.2167 | 23 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 344.5866 | 46.15 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 217.5 | 45 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 28.5833 | 35 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 42 | 40 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 59.5 | 34 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1033.5 | 117 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 105.6 | 44 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 220.8 | 276 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 36 | 40 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 43.75 | 35 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 36.25 | 145 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 79.2 | 48 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 93.4999 | 165 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 109.6666 | 94 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 162.5333 | 184 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 288.3999 | 168 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 274.5 | 90 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 357 | 18 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1880.6666 | 140 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 47.6 | 68 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 314.3333 | 92 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 37.1 | 14 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 50 | 40 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3293.3333 | 160 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 181.25 | 125 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 428.7999 | 96 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 65.0667 | 8 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 725.5183 | 64.3 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 108.1 | 47 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 58.5 | 54 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 75 | 45 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 99.75 | 63 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 28.75 | 115 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 40.85 | 43 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 25.9667 | 19 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 193.9666 | 46 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 666.25 | 41 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 16.1 | 14 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 50 | 60 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 92.8 | 24 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 203 | 105 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 45.0166 | 73 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 408 | 68 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 467.4166 | 71 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 589.9999 | 120 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 736 | 160 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 804 | 268 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 180.5833 | 55 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 117 | 117 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 57.05 | 16.3 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 190.6666 | 143 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 102.75 | 45 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 191.6666 | 100 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 930.7 | 227 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 187.5333 | 58 | 1 | 1 | 0346-Pulverizer pyrite removal system | D3-Forced - Postponed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 308.3333 | 100 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 427.35 | 111 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4 | 30 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 44.8708 | 30.25 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 46.6666 | 40 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 50 | 50 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 77.7 | 63 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 129.2 | 19 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 59.1999 | 96 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 90 | 50 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 374.8333 | 65 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 57.4 | 42 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 232.5 | 150 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 881.9999 | 108 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 613.8333 | 127 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 39.6333 | 29 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 41.0833 | 29 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 90.2 | 44 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 122.2 | 94 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 46.2167 | 47 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 74.7333 | 38 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 184.8 | 176 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 25 | 30 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 27.3333 | 40 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 117 | 108 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 151.7666 | 58 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 6.0666 | 28 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 18.6666 | 40 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 83.3 | 47.6 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 303.3333 | 35 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 735 | 70 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 802.5 | 53.5 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1422.4999 | 75 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 540.5 | 94 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 3.75 | 15 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 95.2 | 42 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 98 | 98 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 39.6667 | 35 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 52 | 120 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 548.9333 | 184 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 13.3333 | 40 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 108.5 | 14 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 565 | 75 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 682.5 | 52.5 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1540 | 66 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 426.8333 | 65 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 627.3 | 123 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1814.1666 | 50 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 19.9333 | 23 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 486.8333 | 127 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 541.3666 | 149 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 59.5 | 30 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 89.4166 | 145 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 218.8333 | 65 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 298.6666 | 140 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 53.6666 | 46 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 87.1 | 39 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 215 | 50 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 38 | 57 | 1 | 2 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 50 | 60 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 179.6666 | 245 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 346.5 | 165 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 117.1667 | 38 | 1 | 1 | 0346-Pulverizer pyrite removal system | D3-Forced - Postponed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 92.4 | 28 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 598 | 149.5 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 628.05 | 79 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1054.7 | 106 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1235 | 380 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 392.25 | 45 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 704.9999 | 180 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 33.4825 | 34.05 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 240.75 | 107 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 612.3541 | 61.75 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 733.95 | 233 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 63 | 31.5 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 277.5 | 50 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 58.9167 | 35 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 667.3333 | 110 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 25.4166 | 61 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 63 | 70 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 65.8667 | 38 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 79.2166 | 97 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 174.0333 | 46 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 25 | 100 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 81.6333 | 62 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 58.3333 | 100 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 86.0333 | 58 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 553.2833 | 89 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 253 | 55 | 1 | 1 | 0346-Pulverizer pyrite removal system | D3-Forced - Postponed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 8 | 48 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 73.3333 | 80 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 85.2 | 142 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 151.8 | 44 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 158.3333 | 50 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 217.5 | 45 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 247.5 | 150 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1095.0288 | 23.11 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 5.3333 | 10 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 47 | 47 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 119.0666 | 94 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 280 | 35 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 312.55 | 57 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 760 | 152 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 1063.9166 | 85 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 249 | 83 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 288 | 96 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 498.1666 | 49 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 520.6667 | 44 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 831.2499 | 105 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1625 | 100 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2611.6667 | 50 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 3415.6667 | 20 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 395 | 79 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 134.1667 | 50 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D3-Forced - Postponed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 189.5832 | 125 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D3-Forced - Postponed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2641.8 | 238 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | U1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2.5833 | 5 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 8 | 1 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 28.9333 | 56 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 62 | 20 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 70 | 100 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 94.8 | 79 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 492.5 | 50 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 682.5 | 70 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 946.6666 | 160 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1303.3333 | 100 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1328 | 60 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 31 | 31 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 95.3333 | 65 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 24.0667 | 1 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 42.05 | 29 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 55.3667 | 22 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 331.6667 | 20 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 883.75 | 175 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 3236.6667 | 20 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 59.5 | 30 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 176.1666 | 151 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 278 | 30 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D3-Forced - Postponed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 30 | 40 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 108.5 | 70 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 176.3333 | 46 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 276.2499 | 195 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 943.25 | 33 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1361.5144 | 106.23 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 9308.6667 | 20 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6.6667 | 5 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 70.8333 | 50 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 94.4 | 59 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 120 | 50 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 244.4167 | 35 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 353.8333 | 110 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2089.9998 | 300 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 51.3333 | 22 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 99 | 90 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 152.5 | 122 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 269.4333 | 59 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 312.5 | 125 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 813.75 | 35 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 28026.6667 | 20 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 431.6667 | 50 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 200 | 50 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 858 | 66 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 484.05 | 32.27 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 171.45 | 127 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 187.0333 | 62 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 78439.9993 | 1110 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | U1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 5.4 | 1 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 111.9999 | 210 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 140.8333 | 65 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 155.7999 | 246 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 210 | 175 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 235.2 | 32 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 600 | 100 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 756.25 | 75 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2092.6666 | 146 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 92.9167 | 25 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 254.1667 | 50 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 413.5833 | 35 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1207.1166 | 67 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 12.0333 | 19 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 94.7333 | 58 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 97.5 | 30 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 103.3333 | 100 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 112 | 24 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 360 | 72 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 366.3333 | 20 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 368 | 96 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1136.6666 | 124 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 56.48 | 112.96 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 292.8 | 73.2 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 57.96 | 6.44 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 148.5 | 74.25 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 19.92 | 16.6 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 240 | 80 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 1424.8 | 274 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 1495.9999 | 204 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 16604.4665 | 644 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | U1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 0.75 | 1 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 69.2333 | 67 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 202 | 20 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 343.9999 | 120 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 422.5 | 65 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 455 | 65 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 507.5 | 70 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1592.5 | 65 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2071.6958 | 137.35 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 52.5 | 9 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 116.6666 | 175 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 187.8333 | 46 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 219 | 146 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 355.2 | 96 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 400 | 50 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 5.7833 | 1 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 34 | 68 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 110 | 60 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 214.2 | 102 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 609.15 | 121.83 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 84.917 | 51.99 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 298.5906 | 74.96 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 320 | 80 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 534.08 | 33.38 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 125 | 62.5 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 109.0833 | 55 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 2239.8665 | 214 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 28 | 21 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D3-Forced - Postponed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 30 | 30 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D3-Forced - Postponed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 38.9333 | 32 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 145.5 | 18 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 183.6 | 102 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 311.6666 | 55 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 524.3165 | 193 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8860 | 50 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 155.4 | 111 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 280 | 120 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2713.9999 | 177 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 47.25 | 1 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 62.3333 | 22 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 365.7999 | 177 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 532 | 112 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 173.7 | 54 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 253.98 | 42.33 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 63.0333 | 24.4 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 637.0413 | 54.76 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1274.7266 | 71.48 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 52.5 | 30 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D3-Forced - Postponed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 20.65 | 21 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D3-Forced - Postponed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 72 | 27 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 200.9 | 123 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 256.6666 | 100 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 214.5 | 110 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 326.6666 | 245 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 331.5 | 34 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 658.75 | 17 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 745.5 | 70 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1375 | 125 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1497.7 | 51 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 17.5 | 30 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 67.8333 | 10 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 964.8 | 67 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2567.2666 | 194 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 54 | 72 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 486.9478 | 79.61 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 825.68 | 103.21 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1120 | 80 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 6.0833 | 1 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 38 | 10 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 38.5 | 70 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 74.4166 | 95 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 200 | 80 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 850.6667 | 44 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1115.8333 | 103 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 11.2666 | 52 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 86.4166 | 85 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 135.8833 | 31 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 284.9166 | 65 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 420 | 35 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3.9993 | 8.57 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 6.0667 | 1 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 304 | 76 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 272 | 80 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 172.3333 | 94 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 303.75 | 135 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D3-Forced - Postponed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 295.1666 | 230 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | U1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 40 | 5 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0358 | Oil burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 948.3833 | 77 | 1 | 1 | 0358-Oil burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0358 | Oil burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 3551.1666 | 110 | 1 | 1 | 0358-Oil burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0358 | Oil burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2013 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 18013.9664 | 803 | 1 | 1 | 0358-Oil burner piping and valves | SF-Startup Failure | 100-Fossil-Steam
0358 | Oil burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 381.6 | 318 | 1 | 1 | 0358-Oil burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0358 | Oil burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4191.6665 | 500 | 1 | 1 | 0358-Oil burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0358 | Oil burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 126.3332 | 379 | 1 | 1 | 0358-Oil burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0358 | Oil burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 98 | 280 | 1 | 1 | 0358-Oil burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0358 | Oil burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 320 | 40 | 1 | 1 | 0358-Oil burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0358 | Oil burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 111.6666 | 335 | 1 | 1 | 0358-Oil burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0358 | Oil burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 3657.5 | 110 | 1 | 1 | 0358-Oil burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0358 | Oil burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 163.3332 | 140 | 1 | 1 | 0358-Oil burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0358 | Oil burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 16.5 | 330 | 1 | 1 | 0358-Oil burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0358 | Oil burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 214.7664 | 379 | 1 | 1 | 0358-Oil burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 245.9666 | 94 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 12049.5467 | 50.6 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 35.6573 | 45.52 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2013 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 2741.5996 | 552 | 1 | 1 | 0359-Gas burner piping and valves | SF-Startup Failure | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 154.5833 | 175 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 1524.25 | 91 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 61.1416 | 63.25 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 655 | 30 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Oil | DI | 100 | Fossil-Steam | RFC | Off-Peak | 7.8 | 52 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Oil | DI | 100 | Fossil-Steam | RFC | Off-Peak | 42 | 12 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 180.9 | 67 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2013 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 489.9583 | 106.9 | 1 | 1 | 0359-Gas burner piping and valves | SF-Startup Failure | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2459.1665 | 650 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 261.9997 | 393 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 532.5 | 75 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6754.5 | 27 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 1571.2666 | 182 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 75.1666 | 82 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 235.8333 | 25 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 821.25 | 75 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 1084.8832 | 547 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 183.2999 | 117 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 5.6666 | 170 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6.75 | 5 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 89.9166 | 83 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1652 | 472 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 63 | 420 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 2768.7833 | 169 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 312.0333 | 74 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 2219.5828 | 761 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 50 | 25 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 68.8333 | 70 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 3324.0665 | 476 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 382.3333 | 74 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 2905.29 | 509.7 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 66 | 165 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 41.5166 | 53 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 374.9999 | 180 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2013 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 15029.9498 | 741 | 1 | 1 | 0359-Gas burner piping and valves | SF-Startup Failure | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 1515 | 404 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 1573 | 220 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 3039.6666 | 110 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5503.6667 | 22 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 180 | 90 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 11.935 | 23.87 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 34.65 | 63 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 100 | Fossil-Steam | SERC | Off-Peak | 199.5 | 2 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 4087.8495 | 741 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 150 | 100 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 746.1 | 54 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Oil | DI | 100 | Fossil-Steam | RFC | Off-Peak | 151.9 | 62 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Oil | DI | 100 | Fossil-Steam | RFC | Off-Peak | 249.3333 | 20 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 654.9997 | 393 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 302.8667 | 23.6 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2013 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 121.6 | 76 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D2 | Forced - Delayed | 2013 | Gas | GG | 850 | Combined Cycle Block | TRE | Summer | 20.79 | 29.7 | 1 | 1 | 0359-Gas burner piping and valves | D2-Forced - Delayed | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | SF | Startup Failure | 2013 | Gas | GG | 850 | Combined Cycle Block | TRE | Summer | 59040 | 60 | 1 | 1 | 0359-Gas burner piping and valves | SF-Startup Failure | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2013 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 41.0667 | 44 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2013 | Gas | GG | 850 | Combined Cycle Block | WECC | Summer | 253.7083 | 60.89 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2013 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 98.05 | 111 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | U1 | Forced - Immediate | 2013 | Gas | GG | 851 | CC GT units | RFC | Winter | 1333.6166 | 161 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 851-CC GT units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | U1 | Forced - Immediate | 2013 | Gas | GG | 851 | CC GT units | SERC | Winter | 365 | 75 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 851-CC GT units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 196 | 49 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 220 | 50 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 2.6 | 12 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 4280.25 | 65 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 441.25 | 75 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 7.0833 | 85 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 62 | 31 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 54.6 | 18 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 115.9666 | 49 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 26.95 | 49 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 985.7166 | 119 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 14.7 | 21 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | SERC | Winter | 154.1667 | 50 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | SERC | Winter | 200 | 50 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 2975.9166 | 65 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | U1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | SERC | Winter | 184.9333 | 38 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 852-CC steam units
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 0.56664 | 34 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 32.55 | 31 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 295.8 | 51 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 387.6 | 12 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 406.5 | 54.2 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 562.5 | 250 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1229.25 | 45 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4199.7998 | 249 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 82.25 | 105 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 175 | 50 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4.2083 | 10.1 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 30.3333 | 65 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 48.5 | 97 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 52.8908 | 90.67 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 134.85 | 87 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 193.2333 | 17 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 270.3999 | 96 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 414.1 | 101 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 743.1666 | 65 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 15.7333 | 8 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 88.3707 | 212.09 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 31.6 | 15.8 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6.6733 | 14.3 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 178.8499 | 147 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 111.3333 | 5 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 115.832 | 144.79 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 175 | 175 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 909.5833 | 25 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1202.6666 | 110 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7657.4167 | 35 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 20519.4166 | 65 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2754.5833 | 5 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 104 | 80 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 178.35 | 87 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 188.7 | 111 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 294.6666 | 68 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 352 | 110 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 454.6666 | 110 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1935 | 50 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 4500 | 225 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 123.9291 | 151.75 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 22088.7 | 303 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 80233.4833 | 199 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Oil | OO | 100 | Fossil-Steam | WECC | Summer | 33.7333 | 44 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 29.1667 | 25 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2059 | 29 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3793.0999 | 249 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 15962 | 60 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 200.75 | 73 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 300 | 50 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 371.0833 | 73 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 403 | 60 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 435.4166 | 95 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 53 | 53 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 184.1499 | 87 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 282.75 | 87 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 164.85 | 157 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 100 | Fossil-Steam | SERC | Summer | 28.35 | 21 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 57.125 | 45.7 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2013 | Oil | OO | 100 | Fossil-Steam | RFC | Winter | 19130.0999 | 153 | 1 | 1 | 0360-Burners | SF-Startup Failure | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 5435.8662 | 691 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 14.0167 | 29 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 31.1666 | 55 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 831.3333 | 58 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1584.3333 | 98 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3081 | 13 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2172.5 | 110 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6697.8333 | 5 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 211.5 | 45 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 100 | Fossil-Steam | SERC | Summer | 47.25 | 21 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 57.3617 | 12.7 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1184 | 74 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 5908.9164 | 731 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 25.6666 | 70 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 55 | 55 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 81.0666 | 128 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 138.6 | 63 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 336.4166 | 55 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9980.3333 | 10 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1554.6666 | 80 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 4.5367 | 13.61 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 110.4999 | 78 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 242.0833 | 175 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 308 | 77 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 9274.6333 | 13 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 98.8333 | 10 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 13.585 | 20.9 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 38.2 | 19.1 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 51.9167 | 35 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 80 | 40 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 512 | 60 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 514.75 | 71 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 83.5833 | 85 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 707.6666 | 55 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 5.8917 | 10.1 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 75.3999 | 87 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 223.2999 | 87 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 296.5666 | 82 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 673.1333 | 92 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2910 | 10 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 181.6 | 12 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | RFC | Winter | 168.75 | 81 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Oil | DI | 100 | Fossil-Steam | NPCC | Winter | 17 | 34 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 119.5275 | 159.37 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 181.5 | 121 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 95.3333 | 104 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 263.4666 | 104 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 18.6666 | 70 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 33.3333 | 40 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1092.5 | 95 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2075.32 | 30.7 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 60.9166 | 85 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1025 | 100 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 59.0333 | 77 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 233.3333 | 175 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 240 | 192 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 339.5 | 97 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 379.2 | 96 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 386.3333 | 190 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 718.5333 | 68 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2109.75 | 29 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3533.3333 | 160 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 25637 | 62 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 36 | 27 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 27 | 27 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 661.5 | 441 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 38.35 | 59 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 41.3333 | 80 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 89.4666 | 88 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 212.1333 | 74 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 475.8333 | 50 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 678.9332 | 268 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 55.5333 | 68 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 58.3333 | 175 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 105.8499 | 87 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 118.4 | 96 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 180 | 120 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1225 | 140 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 91.9666 | 62 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 69 | 69 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1979.685 | 26.1 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 12718.75 | 55 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 1188 | 45 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4205.25 | 35 | 1 | 1 | 0360-Burners | D3-Forced - Postponed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1602.2999 | 441 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 37184 | 830 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 24.2535 | 63.27 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 184 | 230 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Gas | GG | 800 | Miscellaneous | MRO | Off-Peak | 49.9383 | 36.1 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 800-Miscellaneous
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Gas | GG | 800 | Miscellaneous | MRO | Off-Peak | 85.9733 | 41.6 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 800-Miscellaneous
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Gas | GG | 800 | Miscellaneous | MRO | Off-Peak | 24.825 | 33.1 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 800-Miscellaneous
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2013 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 10.67 | 9.7 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2013 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 19.65 | 9 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2013 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 2826.62 | 23.7 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2013 | Gas | GG | 850 | Combined Cycle Block | MRO | Off-Peak | 12.9167 | 25 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2013 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 1.7667 | 1 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2013 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 14.25 | 9 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2013 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 61.5 | 73.8 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2013 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 428.5667 | 23 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | U2 | Forced - Delayed | 2013 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 6678.7 | 58 | 1 | 1 | 0360-Burners | U2-Forced - Delayed | 851-CC GT units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2013 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 93.25 | 15 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 851-CC GT units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | U2 | Forced - Delayed | 2013 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 27183.6333 | 58 | 1 | 1 | 0360-Burners | U2-Forced - Delayed | 851-CC GT units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2013 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 992.8666 | 53 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 851-CC GT units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2013 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 104 | 26 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 851-CC GT units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2013 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 1102.8333 | 26 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 851-CC GT units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 146.9999 | 126 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 86.3833 | 73 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2013 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 216.2667 | 8 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2013 | Gas | GG | 852 | CC steam units | WECC | Winter | 4578.5333 | 23 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 4.1 | 82 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2013 | Gas | GG | 852 | CC steam units | SERC | Summer | 0.53333 | 8 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2013 | Gas | GG | 852 | CC steam units | WECC | Summer | 36.3333 | 20 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 234.85 | 61 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2013 | Gas | GG | 852 | CC steam units | WECC | Summer | 286.3333 | 20 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2013 | Gas | GG | 852 | CC steam units | SERC | Summer | 15.5 | 30 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2013 | Gas | GG | 852 | CC steam units | SERC | Winter | 96.4167 | 5 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 680.8333 | 95 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 186.5 | 30 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 5.4666 | 82 | 1 | 4 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Gas | GG | 860 | Co-generator Block | RFC | Summer | 26.25 | 15 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 860-Co-generator Block
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Gas | GG | 860 | Co-generator Block | RFC | Summer | 2.75 | 15 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 860-Co-generator Block
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Gas | GG | 860 | Co-generator Block | RFC | Summer | 7.5 | 15 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 860-Co-generator Block
0361 | Burner orfices | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 85 | 17 | 1 | 1 | 0361-Burner orfices | D1-Forced - Immediate | 100-Fossil-Steam
0361 | Burner orfices | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 216 | 90 | 1 | 1 | 0361-Burner orfices | D1-Forced - Immediate | 100-Fossil-Steam
0361 | Burner orfices | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 110.3833 | 37 | 1 | 1 | 0361-Burner orfices | D1-Forced - Immediate | 100-Fossil-Steam
0361 | Burner orfices | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 107.8 | 28 | 1 | 1 | 0361-Burner orfices | D1-Forced - Immediate | 100-Fossil-Steam
0361 | Burner orfices | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6354.7 | 66 | 1 | 1 | 0361-Burner orfices | D1-Forced - Immediate | 100-Fossil-Steam
0361 | Burner orfices | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 50.6666 | 80 | 1 | 1 | 0361-Burner orfices | D1-Forced - Immediate | 100-Fossil-Steam
0361 | Burner orfices | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 72.5 | 87 | 1 | 1 | 0361-Burner orfices | D1-Forced - Immediate | 100-Fossil-Steam
0361 | Burner orfices | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 64.6 | 51 | 1 | 1 | 0361-Burner orfices | D1-Forced - Immediate | 100-Fossil-Steam
0366 | Duct burners (FBC only) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 289 | 102 | 1 | 1 | 0366-Duct burners (FBC only) | D1-Forced - Immediate | 850-Combined Cycle Block
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3.1667 | 5 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3.75 | 5 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 43.1666 | 70 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1187.3333 | 130 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 32 | 80 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 40 | 120 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 48 | 60 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1592.99 | 227.57 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 78.8333 | 110 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 131.6666 | 100 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 648.2831 | 401 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1174.6 | 84 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 359.9 | 122 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 1711.2 | 552 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 314.1333 | 38 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 78.1666 | 70 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 140.8328 | 845 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 258.3333 | 100 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 238.6666 | 80 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 68.6667 | 20 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5301.5994 | 846 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 7634.7329 | 638 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 25.5 | 90 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 96.8333 | 70 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 173.2665 | 226 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 615.7 | 131 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 55.4999 | 90 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 435.6 | 242 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 399.1 | 307 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 345.3332 | 370 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 89.3333 | 80 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 162.5 | 50 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 210 | 168 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 179.1999 | 168 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 163.1666 | 110 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 1123.4664 | 421.3 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Oil | OO | 100 | Fossil-Steam | WECC | Winter | 27.8667 | 44 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 350 | 200 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 976 | 80 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 15.1667 | 26 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 38.3333 | 50 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 45 | 90 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 45.3333 | 80 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 126 | 105 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 98.7999 | 156 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 77.2666 | 122 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1102.0666 | 122 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 1124.6814 | 339.1 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 17.25 | 23 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 691.68 | 31.44 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Oil | OO | 100 | Fossil-Steam | WECC | Winter | 18.3333 | 44 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Oil | OO | 100 | Fossil-Steam | WECC | Winter | 48.4 | 44 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Oil | OO | 100 | Fossil-Steam | WECC | Winter | 82.1333 | 44 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4 | 5 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 46.6666 | 80 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 48 | 80 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 233.3333 | 100 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 41.3166 | 67 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 81.99 | 27.33 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 220 | 110 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 297 | 330 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 85.2983 | 83.9 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 254.8 | 84 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2.0833 | 5 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 29.1666 | 70 | 1 | 2 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 45.1 | 82 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 72.318 | 241.06 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 257.5999 | 168 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 510.45 | 123 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7.75 | 155 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 40.8333 | 70 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 10.8267 | 23.2 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 884.5 | 305 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 62.4 | 48 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D2-Forced - Delayed | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 101.8349 | 83.7 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 500.2665 | 536 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 888.7666 | 91 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 2927.75 | 245 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5 | 5 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 59.5 | 70 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 64 | 80 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 345 | 230 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2007.9998 | 240 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5746.9 | 202 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 21.875 | 17.5 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D2-Forced - Delayed | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 91 | 84 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 300 | 200 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 142.1333 | 104 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Oil | OO | 100 | Fossil-Steam | WECC | Winter | 23.4667 | 44 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Oil | OO | 100 | Fossil-Steam | WECC | Winter | 127.6 | 44 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Gas | GG | 800 | Miscellaneous | MRO | Summer | 18.78 | 31.3 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 800-Miscellaneous
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2013 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 37.7667 | 22 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 850-Combined Cycle Block
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2013 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 3.08 | 23.1 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 850-Combined Cycle Block
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2013 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 22.1667 | 14 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 850-Combined Cycle Block
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | U1 | Forced - Immediate | 2013 | Gas | GG | 850 | Combined Cycle Block | WECC | Winter | 57 | 38 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 850-Combined Cycle Block
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | U1 | Forced - Immediate | 2013 | Gas | GG | 851 | CC GT units | WECC | Summer | 112 | 70 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 851-CC GT units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2013 | Gas | GG | 851 | CC GT units | TRE | Summer | 398.2333 | 26 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 851-CC GT units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 161.2 | 93 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2013 | Gas | GG | 852 | CC steam units | SERC | Winter | 74.8333 | 5 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 180 | 90 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 9.9667 | 26 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 521.5833 | 55 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 770.4 | 18 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 2133.6 | 18 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 40 | 75 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 143.9166 | 55 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | U1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 630.3 | 382 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 149.9999 | 90 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 220 | 55 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2013 | Gas | GG | 852 | CC steam units | SERC | Summer | 12.8 | 48 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2013 | Gas | GG | 852 | CC steam units | WECC | Summer | 77.92 | 48.7 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2013 | Gas | GG | 852 | CC steam units | SERC | Winter | 25 | 5 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2013 | Gas | GG | 852 | CC steam units | SERC | Winter | 29.1667 | 5 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2013 | Gas | GG | 852 | CC steam units | SERC | Winter | 41.6667 | 5 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2013 | Gas | GG | 852 | CC steam units | SERC | Winter | 138.8333 | 5 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 83.1999 | 96 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | U1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 107.6666 | 170 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 209.9333 | 67 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 17.3333 | 26 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 17.5 | 42 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | U1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 104.8332 | 170 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 12.8 | 32 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2013 | Gas | GG | 852 | CC steam units | SERC | Winter | 18.3333 | 5 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 4.1 | 82 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 171 | 45 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 60.6665 | 280 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 78.2999 | 162 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 160 | 160 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 251.25 | 67 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 372.2999 | 153 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 79 | 79 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 244.8333 | 130 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 232 | 116 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 412.3 | 93 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | SF-Startup Failure | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 20.3333 | 244 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 51.6666 | 100 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 100 | 100 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 163.3332 | 200 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 802.4999 | 90 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 69.0166 | 101 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 480.1999 | 147 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1705.0833 | 37 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4254.2498 | 357 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 37.3333 | 56 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 215.4166 | 55 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 433.3333 | 130 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 168.5665 | 389 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D2-Forced - Delayed | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 2095.8 | 499 | 2 | 2 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 103.2 | 129 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 186.6666 | 70 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 360.4999 | 210 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 607.7331 | 344 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3946.2499 | 165 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1530.2665 | 184 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 164.6667 | 13 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 594.5333 | 49 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1699.4998 | 495 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | SF-Startup Failure | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 68.3333 | 100 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 93.3333 | 100 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 306.483 | 497 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 165.75 | 195 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 13.9993 | 19.09 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 29.4667 | 17 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 55.1 | 57 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 72 | 72 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 92.1666 | 79 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 103.2 | 344 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1099.9999 | 375 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 183.3333 | 88 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 92.4 | 63 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 274.85 | 69 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 372.75 | 63 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 858.0661 | 844 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1873.25 | 635 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 66.74 | 56.4 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9496.133 | 536 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 128.38 | 31.44 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 261.6666 | 100 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 518.4665 | 404 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 103.5 | 90 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 36.2166 | 53 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 36.9 | 54 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 524 | 131 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1671 | 557 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 498.3333 | 100 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D2-Forced - Delayed | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3003.2498 | 615 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | SF-Startup Failure | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 558.25 | 385 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 176 | 96 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 354.1999 | 84 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 271.25 | 105 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 436.5 | 97 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 120.6667 | 20 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 1281.25 | 205 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 227.3332 | 155 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | SF-Startup Failure | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1241.733 | 536 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 16.5 | 330 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2812.5 | 750 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 767.8666 | 104 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2252.3664 | 394 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 7.3666 | 34 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 84.8 | 424 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D2-Forced - Delayed | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 8.68 | 37.2 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 62.5 | 25 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 70 | 60 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 808.1666 | 130 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1982.1998 | 561 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 6139 | 140 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 3178.3333 | 50 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1294.25 | 155 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | SF-Startup Failure | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 8904.2 | 844 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | SF-Startup Failure | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2959.9998 | 300 | 2 | 2 | 0380-Light-off (igniter) systems (including fuel supply) | SF-Startup Failure | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 549.0497 | 417 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 852.75 | 45 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 91.65 | 84.6 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 146.5331 | 314 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 445.5 | 330 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 14410 | 131 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 56.122 | 51.02 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 198.3333 | 119 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 38.75 | 15 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 850-Combined Cycle Block
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 26.5817 | 38.9 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 850-Combined Cycle Block
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 13.3316 | 42.1 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 850-Combined Cycle Block
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 2.3417 | 28.1 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 850-Combined Cycle Block
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 246.5 | 15 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 850-Combined Cycle Block
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 5.0933 | 19.1 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 850-Combined Cycle Block
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2013 | Gas | GG | 851 | CC GT units | WECC | Summer | 83.79 | 37.24 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | SF-Startup Failure | 851-CC GT units
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Gas | GG | 852 | CC steam units | SERC | Off-Peak | 38.4167 | 5 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 852-CC steam units
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Gas | GG | 852 | CC steam units | SERC | Summer | 85.4167 | 5 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 852-CC steam units
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 2.0833 | 25 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 852-CC steam units
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 141.421 | 31.78 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 852-CC steam units
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 3552.4999 | 75 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 852-CC steam units
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Gas | GG | 852 | CC steam units | SERC | Winter | 144.1667 | 5 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 852-CC steam units
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 15 | 25 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 852-CC steam units
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 61.6666 | 25 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 852-CC steam units
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 110 | 100 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 852-CC steam units
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 64.1667 | 25 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 852-CC steam units
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 57.5 | 25 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 852-CC steam units
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 50 | 25 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 852-CC steam units
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 10.8333 | 25 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 852-CC steam units
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 22.9167 | 25 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 852-CC steam units
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 45 | 30 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 268 | 67 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 80 | 80 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 89 | 178 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 686.5833 | 55 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 245.3625 | 196.29 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 4497.675 | 85.67 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 750 | 500 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 915.25 | 523 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 218.3333 | 100 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 138.8333 | 98 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 152.25 | 87 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 283.4 | 78 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7663.3331 | 760 | 1 | 1 | 0385-Igniters | SF-Startup Failure | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1360.6666 | 260 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 20.3666 | 94 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 200.1 | 138 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 510 | 120 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 287.5833 | 119 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 375 | 125 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 100 | 200 | 1 | 1 | 0385-Igniters | SF-Startup Failure | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 3147.083 | 455 | 1 | 1 | 0385-Igniters | SF-Startup Failure | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 238.3333 | 220 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 176 | 220 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 41.6666 | 100 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 81.75 | 109 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 149.25 | 45 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 45.4666 | 88 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 291 | 291 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 506.6667 | 20 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Oil | OO | 100 | Fossil-Steam | NPCC | Off-Peak | 302.8332 | 158 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 260.3333 | 220 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1500 | 200 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 24.25 | 97 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 27.9167 | 5 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 68.3333 | 20 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 945 | 35 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 154.4166 | 85 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 305.4333 | 154 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 8.55 | 27 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 57.0666 | 107 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 84.5 | 30 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 96.2499 | 105 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 107.5 | 75 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 147.9166 | 71 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 220 | 50 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 336 | 168 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 42.0333 | 97 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1936 | 60 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 450.9999 | 165 | 1 | 1 | 0385-Igniters | SF-Startup Failure | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 110 | 220 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 128.3333 | 220 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 17.25 | 45 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 20.1166 | 71 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 127.5999 | 87 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 288.6 | 222 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 392.6667 | 20 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 533.5 | 55 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 123.6563 | 34.67 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 211.6 | 138 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 21 | 63 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 37.5 | 18 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 5.8333 | 7 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6169.9998 | 300 | 2 | 2 | 0385-Igniters | SF-Startup Failure | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 546.345 | 404.7 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 579.5 | 114 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 19.55 | 51 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 130.6666 | 49 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 56.6667 | 5 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 160.0665 | 196 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 427.9333 | 98 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 866.6666 | 80 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1201.9666 | 107 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 34.5167 | 19 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 910.4375 | 145.67 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 687.5 | 125 | 1 | 1 | 0385-Igniters | SF-Startup Failure | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2013 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 1399.9999 | 420 | 1 | 1 | 0385-Igniters | SF-Startup Failure | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 17.6666 | 106 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 149.5 | 23 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0385 | Igniters | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 53.7833 | 46.1 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 850-Combined Cycle Block
0385 | Igniters | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 1.7333 | 4 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 851-CC GT units
0385 | Igniters | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2013 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 85.2 | 72 | 1 | 1 | 0385-Igniters | SF-Startup Failure | 851-CC GT units
0385 | Igniters | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2013 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 53.0333 | 74 | 1 | 1 | 0385-Igniters | SF-Startup Failure | 851-CC GT units
0385 | Igniters | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Gas | GG | 852 | CC steam units | WECC | Summer | 10.3333 | 20 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 852-CC steam units
0385 | Igniters | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 39.5833 | 25 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 852-CC steam units
0385 | Igniters | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 725.7 | 18 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 852-CC steam units
0385 | Igniters | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 312 | 26 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 852-CC steam units
0385 | Igniters | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 6260.8 | 26 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 852-CC steam units
0385 | Igniters | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 5314.8333 | 26 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 852-CC steam units
0385 | Igniters | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 82.2 | 18 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 852-CC steam units
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 41.5 | 83 | 1 | 1 | 0390-Burner wind boxes and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 18 | 4.5 | 1 | 1 | 0390-Burner wind boxes and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 87.25 | 15 | 1 | 1 | 0390-Burner wind boxes and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 3511 | 20 | 1 | 1 | 0390-Burner wind boxes and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 157.2333 | 106 | 1 | 1 | 0390-Burner wind boxes and dampers | U1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 41.8667 | 16 | 1 | 1 | 0390-Burner wind boxes and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 885.4999 | 210 | 1 | 1 | 0390-Burner wind boxes and dampers | U1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 97788 | 580 | 1 | 1 | 0390-Burner wind boxes and dampers | U2-Forced - Delayed | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1752.0833 | 145 | 1 | 1 | 0390-Burner wind boxes and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1425.6 | 162 | 1 | 1 | 0390-Burner wind boxes and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 116.2 | 42 | 1 | 1 | 0390-Burner wind boxes and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 241.5 | 70 | 1 | 1 | 0390-Burner wind boxes and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 167.3833 | 83 | 1 | 1 | 0390-Burner wind boxes and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1815.8333 | 50 | 1 | 1 | 0390-Burner wind boxes and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 240 | 10 | 1 | 1 | 0390-Burner wind boxes and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 1038.6667 | 20 | 1 | 1 | 0390-Burner wind boxes and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2013 | Oil | OO | 100 | Fossil-Steam | WECC | Winter | 74.0667 | 44 | 1 | 1 | 0390-Burner wind boxes and dampers | SF-Startup Failure | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 40 | 30 | 1 | 1 | 0390-Burner wind boxes and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 858.3333 | 100 | 1 | 1 | 0390-Burner wind boxes and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 890.1667 | 35 | 1 | 1 | 0390-Burner wind boxes and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 437.7332 | 268 | 1 | 1 | 0390-Burner wind boxes and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 59.1666 | 50 | 1 | 1 | 0390-Burner wind boxes and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 80 | 25 | 1 | 1 | 0390-Burner wind boxes and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Gas | GG | 852 | CC steam units | SERC | Off-Peak | 13.75 | 5 | 1 | 1 | 0390-Burner wind boxes and dampers | D1-Forced - Immediate | 852-CC steam units
0400 | Burner wind box fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 242 | 55 | 1 | 1 | 0400-Burner wind box fires | D1-Forced - Immediate | 100-Fossil-Steam
0400 | Burner wind box fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1239.3333 | 104 | 1 | 1 | 0400-Burner wind box fires | D3-Forced - Postponed | 100-Fossil-Steam
0400 | Burner wind box fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 17632.9996 | 660 | 1 | 1 | 0400-Burner wind box fires | U2-Forced - Delayed | 100-Fossil-Steam
0400 | Burner wind box fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 686.1333 | 166 | 1 | 1 | 0400-Burner wind box fires | SF-Startup Failure | 100-Fossil-Steam
0400 | Burner wind box fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 123824.7999 | 264 | 1 | 1 | 0400-Burner wind box fires | U2-Forced - Delayed | 100-Fossil-Steam
0400 | Burner wind box fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 308.3333 | 100 | 1 | 1 | 0400-Burner wind box fires | D1-Forced - Immediate | 100-Fossil-Steam
0400 | Burner wind box fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 208295.1999 | 372 | 1 | 1 | 0400-Burner wind box fires | U1-Forced - Immediate | 100-Fossil-Steam
0400 | Burner wind box fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 870 | 40 | 1 | 1 | 0400-Burner wind box fires | D1-Forced - Immediate | 100-Fossil-Steam
0400 | Burner wind box fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 10366.601 | 510.67 | 1 | 1 | 0400-Burner wind box fires | U1-Forced - Immediate | 100-Fossil-Steam
0400 | Burner wind box fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 24353.55 | 299 | 1 | 1 | 0400-Burner wind box fires | U1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 40.5 | 27 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 116.6666 | 100 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1947.9166 | 125 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 110 | 110 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 182 | 70 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 279.9999 | 105 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 804.1 | 22 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 7.3935 | 8.37 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | OS | 100 | Fossil-Steam | MRO | Winter | 140.7458 | 19.87 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | OS | 100 | Fossil-Steam | MRO | Winter | 154.9295 | 16.57 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2013 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 3520.89 | 495.9 | 1 | 1 | 0410-Other burner problems | SF-Startup Failure | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 504.1663 | 550 | 1 | 1 | 0410-Other burner problems | U1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 122.85 | 63 | 1 | 1 | 0410-Other burner problems | U1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 700.505 | 24.87 | 1 | 1 | 0410-Other burner problems | U1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 680.6166 | 97 | 1 | 1 | 0410-Other burner problems | U1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 1383.9998 | 480 | 1 | 1 | 0410-Other burner problems | U1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 801.3333 | 80 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1062.6666 | 80 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 78.6666 | 80 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 145.1666 | 65 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 245 | 70 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 69.6666 | 110 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 16.0032 | 12.47 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 125.8333 | 25 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3325.3999 | 156 | 1 | 1 | 0410-Other burner problems | U1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1020 | 340 | 1 | 1 | 0410-Other burner problems | U1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 189.15 | 97 | 1 | 1 | 0410-Other burner problems | U1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 375.9998 | 480 | 1 | 1 | 0410-Other burner problems | U1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 28.5 | 30 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 200 | 60 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 348.5 | 170 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 793.4999 | 90 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1014 | 65 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 516 | 103.2 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 50.2623 | 16.57 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 50.3035 | 14.17 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 7.5 | 5 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 80 | 24 | 1 | 1 | 0410-Other burner problems | D2-Forced - Delayed | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1418.6666 | 80 | 1 | 1 | 0410-Other burner problems | D3-Forced - Postponed | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 101 | 12 | 1 | 1 | 0410-Other burner problems | D3-Forced - Postponed | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | OS | 100 | Fossil-Steam | MRO | Winter | 20.2012 | 19.87 | 1 | 1 | 0410-Other burner problems | D3-Forced - Postponed | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 597.6 | 72 | 1 | 1 | 0410-Other burner problems | U1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 197.7165 | 24.87 | 1 | 1 | 0410-Other burner problems | U1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 542.7998 | 552 | 1 | 1 | 0410-Other burner problems | U1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 14.7 | 14 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 121.5999 | 96 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1107.8332 | 170 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 755.25 | 95 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 66 | 110 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 150.0778 | 15.77 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | OS | 100 | Fossil-Steam | MRO | Winter | 16.8345 | 12.47 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 482.1767 | 13.4 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 239.0333 | 71 | 1 | 1 | 0410-Other burner problems | U1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 2410.3999 | 138 | 1 | 1 | 0410-Other burner problems | U1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 137.0833 | 175 | 1 | 1 | 0410-Other burner problems | U1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 832.3333 | 44 | 1 | 1 | 0410-Other burner problems | U1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 85.3333 | 80 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1210 | 60 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 364 | 35 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2183.0833 | 115 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 49160.3 | 42 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 7438.35 | 10.2 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 20.923 | 4.27 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 62.5842 | 14.17 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | OS | 100 | Fossil-Steam | MRO | Winter | 111.272 | 19.87 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 32.5 | 65 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 142.4 | 96 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 186 | 62 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1144.5833 | 205 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3159 | 180 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 181.4999 | 90 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 528 | 110 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2530.8 | 76 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 28.1492 | 19.87 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | OS | 100 | Fossil-Steam | NPCC | Off-Peak | 34.6667 | 10 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 153.2685 | 13.27 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 44.1666 | 25 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 11.7167 | 19 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1322.25 | 205 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 180.3333 | 10 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 188.6666 | 40 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 79.1488 | 19.87 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | OS | 100 | Fossil-Steam | NPCC | Off-Peak | 83.5833 | 17 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | OS | 100 | Fossil-Steam | NPCC | Off-Peak | 195.5 | 17 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 20.3677 | 12.47 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 28.0575 | 12.47 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 12.4 | 24 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 446.7683 | 18.1 | 1 | 1 | 0410-Other burner problems | U1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 281.6 | 96 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 17598.4333 | 37 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 37.9166 | 65 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 415.3333 | 10 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 822.25 | 55 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 871.1 | 62 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | OS | 100 | Fossil-Steam | MRO | Winter | 14.0845 | 16.57 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | OS | 100 | Fossil-Steam | MRO | Winter | 124.8498 | 19.87 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 40.2999 | 78 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Oil | OO | 100 | Fossil-Steam | NPCC | Off-Peak | 8.3333 | 50 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 775.15 | 111 | 1 | 1 | 0410-Other burner problems | SF-Startup Failure | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 387.9165 | 175 | 1 | 1 | 0410-Other burner problems | U1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 106 | 106 | 1 | 1 | 0410-Other burner problems | U1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2013 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 367.5 | 14 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 850-Combined Cycle Block
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2013 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 814 | 37 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 850-Combined Cycle Block
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2013 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 419.7667 | 14 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 850-Combined Cycle Block
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2013 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 1272 | 106 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 851-CC GT units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2013 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 123.6666 | 106 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 851-CC GT units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | U1 | Forced - Immediate | 2013 | Gas | GG | 851 | CC GT units | WECC | Winter | 2996.2499 | 153 | 1 | 1 | 0410-Other burner problems | U1-Forced - Immediate | 851-CC GT units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | SERC | Winter | 10654.9333 | 64 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 305.225 | 7.25 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 121.3333 | 65 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 479.3333 | 10 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 2051.9833 | 101 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 554.2625 | 7.25 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | SERC | Winter | 9401.6 | 64 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | SERC | Winter | 9321.6 | 64 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2013 | Gas | GG | 852 | CC steam units | WECC | Winter | 1880 | 96 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 66.7 | 7.25 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 2815 | 6 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 5697.6 | 6 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3 | 10 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 3.1667 | 38 | 1 | 2 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3.6667 | 22 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 31.2499 | 75 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 35 | 5 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 39.4666 | 64 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 52.9 | 69 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 82.5 | 30 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 199.8 | 27 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 220.8333 | 106 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1400 | 60 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2783.6667 | 20 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 7.3333 | 44 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10.7 | 6 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 13.4167 | 35 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 22.1666 | 70 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 22.5 | 45 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 278.25 | 53 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 4.4333 | 38 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5.25 | 21 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 5.5 | 33 | 1 | 2 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 5.7 | 38 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 9.3333 | 28 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 12.6666 | 76 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 95.3333 | 110 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 199.5 | 133 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 250.8333 | 35 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 287.5 | 50 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 444.1666 | 65 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 493.35 | 99 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 711 | 60 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 776 | 97 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 917.5 | 30 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 3.9667 | 14 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 46.25 | 37 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 29.75 | 51 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 48.1833 | 59 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 76.8 | 64 | 1 | 2 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 300 | 90 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 34.1333 | 64 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 65.0666 | 122 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 85.3333 | 64 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 136 | 16 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 137.5 | 75 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 198.45 | 81 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 505.6666 | 74 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 740 | 100 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 29.1667 | 35 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 57.75 | 45 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 84 | 21 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 255.3333 | 40 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 424.6666 | 56 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 480.25 | 51 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3 | 1.5 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5 | 5 | 2 | 2 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 6.6 | 33 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 15.1666 | 70 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 16 | 32 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 17.05 | 33 | 1 | 2 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 33 | 33 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 142.5 | 10 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 162.6666 | 40 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 177.5 | 50 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 837.5 | 50 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 161.55 | 27 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 481.6666 | 68 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 87.4666 | 64 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 147 | 49 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1631.4999 | 78 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 7.6 | 38 | 1 | 2 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 14.6667 | 44 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 151.5 | 101 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 166.5 | 54 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 295.8333 | 25 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 431.6667 | 50 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 578.04 | 48.17 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1170 | 18 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5405 | 100 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 35968.3333 | 50 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 6.6 | 33 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 12.6 | 36 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 19.6 | 84 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 29.1333 | 76 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 53.0833 | 35 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 67.0833 | 35 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 108.3333 | 50 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 572.65 | 39 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 948.75 | 69 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1342 | 40 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1 | 1 | 2 | 4 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 2.5333 | 38 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 10.6667 | 32 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 32.25 | 45 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 40 | 40 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 68.25 | 65 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 126.5 | 46 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 170.9999 | 270 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 369 | 45 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 597.5 | 50 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 856.8333 | 97 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 961.9166 | 97 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1031.2833 | 43 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1041.6666 | 100 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1222.8333 | 115 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 214.2 | 63 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 42 | 63 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 2.1333 | 8 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 24.6666 | 74 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 73.5 | 49 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 77.5833 | 49 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 86.25 | 69 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 116.15 | 69 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 483.4 | 24.17 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 408.3333 | 100 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 83 | 30 | 1 | 1 | 0415-Cyclone feeders | D3-Forced - Postponed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 343.9333 | 77 | 1 | 1 | 0415-Cyclone feeders | U1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 4.8333 | 29 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 5.1333 | 44 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 10.4 | 26 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 12.6667 | 38 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 15 | 50 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 16 | 64 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 23 | 46 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 25.6667 | 44 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 40.5 | 54 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 42.55 | 69 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 124.3667 | 41 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 203.3333 | 50 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 598 | 60 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 745.8333 | 10 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 800 | 64 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1508 | 116 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1754.5 | 15.95 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1.8667 | 16 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 9.9 | 33 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 26.95 | 49 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 49.6667 | 20 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 207.2 | 56 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 472.4666 | 76 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1254.1666 | 50 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1450 | 50 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2.5 | 6 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6 | 6 | 2 | 2 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 8.2333 | 38 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 12.0333 | 38 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 13.6166 | 43 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 17.1 | 38 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 57.5 | 50 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 245 | 60 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 341.3333 | 80 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2530 | 60 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3101.6666 | 100 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 4678.8 | 36 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 85.5 | 54 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 816.9 | 63 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 25.6 | 64 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 26.8667 | 26 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 57.1666 | 70 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 106.1666 | 49 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 106.5 | 71 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 34.1666 | 50 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 119.0667 | 47 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 0.4 | 6 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 8.5333 | 32 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 41 | 41 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 45.6333 | 74 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 57.9666 | 74 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 93.5 | 11 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 148 | 16 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 169.3333 | 5 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 193.5 | 45 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 235.6833 | 79 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 504.1666 | 55 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 513.6833 | 119 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 612 | 60 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1215.5 | 55 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2015.4167 | 35 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3878.9166 | 89 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 14914.25 | 65 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 5.25 | 21 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 18.0833 | 35 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 60.2667 | 32 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 69.1667 | 50 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 213.3 | 81 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1337.8499 | 81 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4 | 2 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5.8333 | 50 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6.6666 | 80 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 20 | 60 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 83.95 | 69 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 91.5 | 45 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 132 | 60 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 148.1666 | 70 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 997.3333 | 55 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1128 | 40 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1236.4 | 44 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 40.5 | 54 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 45 | 50 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 98 | 49 | 1 | 3 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 110.25 | 49 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 266.8 | 69 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 137.4333 | 62 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3.0667 | 23 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 5.75 | 69 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 11.7333 | 44 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 33.0666 | 64 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 36.6666 | 40 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 40.25 | 69 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 57.1666 | 49 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 84.7 | 21 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 165.6667 | 35 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 196 | 28 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 198.3333 | 70 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 248.7333 | 41 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 567.5 | 50 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 11.4 | 38 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 11.55 | 33 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 12.65 | 33 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 18.7 | 33 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 42.6667 | 20 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 54 | 10.8 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 60.6666 | 91 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 110.7333 | 44 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 244.8 | 51 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 526.4 | 42 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 646.8 | 56 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 660.5 | 15 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1 | 6 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 13.9333 | 38 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 32.4 | 54 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 204.4 | 73 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 15.3333 | 23 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 40.7333 | 47 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 11.5 | 69 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 19.2 | 72 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 45 | 60 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 48 | 16 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 62.3333 | 68 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 79.5 | 90 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 104.5333 | 64 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 113.0833 | 59 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 114 | 45 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 156.75 | 57 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 48.8 | 48 | 1 | 1 | 0415-Cyclone feeders | U1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2.1667 | 13 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 17.6333 | 46 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 65.0666 | 64 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 75.8333 | 10 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 116.25 | 5 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 298.6667 | 20 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 362 | 30 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 811.25 | 55 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1806 | 43 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 10597.9333 | 71 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 5.5 | 33 | 1 | 2 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9 | 9 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10 | 10 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 22.55 | 33 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 68.4 | 76 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 76.9166 | 71 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 144 | 45 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2023.3333 | 20 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2407.2 | 236 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 3 | 36 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 13.3333 | 32 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 22 | 22 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 35 | 60 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 41 | 60 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 54.25 | 15 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 128.3333 | 50 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 147.5 | 10 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 300 | 50 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 345.7999 | 84 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 909.5 | 30 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1820 | 175 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 178.5 | 63 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 52.0832 | 125 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 136 | 48 | 1 | 1 | 0415-Cyclone feeders | U1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 567 | 108 | 1 | 1 | 0415-Cyclone feeders | U1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1 | 6 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 8.75 | 21 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 10 | 10 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 11.7 | 78 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 14.2333 | 61 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 14.3 | 78 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 20.5833 | 65 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 38.3833 | 49 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 41.6 | 64 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 41.7 | 6 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 64.1333 | 74 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 65.31 | 9.33 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 91 | 70 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 104.8333 | 74 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 148 | 74 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 243.3666 | 49 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 245.4333 | 74 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 246.2166 | 79 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 316.7666 | 86 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 687.5 | 13.75 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9 | 4.5 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 37.2666 | 86 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 63 | 45 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 118.75 | 75 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 188.98 | 17.18 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 192.5 | 55 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 256.2 | 42 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 347.15 | 131 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 9.35 | 33 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 14.4 | 32 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 30 | 45 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 59 | 60 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 129.3333 | 20 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 164.01 | 54.67 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 466.6667 | 50 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1087.4333 | 202 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1792.4166 | 157 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2175 | 60 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 3300.9666 | 49 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 443.3667 | 47 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 32.85 | 73 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 74.7333 | 59 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 6.5 | 30 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 12 | 30 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 189.3333 | 71 | 1 | 2 | 0415-Cyclone feeders | D3-Forced - Postponed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 650 | Fluidized Bed | SERC | Winter | 67 | 20 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 650-Fluidized Bed
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Gas | GG | 650 | Fluidized Bed | SERC | Off-Peak | 16.8 | 18 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 650-Fluidized Bed
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 0.81666 | 7 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 650-Fluidized Bed
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 16.15 | 19 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 68.5666 | 34 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 187.85 | 39 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 47.85 | 29 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 3.1667 | 19 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 19.3167 | 19 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 24.7 | 39 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 25.9667 | 19 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 73.4667 | 29 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 4931.4332 | 439 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 93.3333 | 40 | 1 | 1 | 0420-Cyclone crusher | D1-Forced - Immediate | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1588.6666 | 40 | 1 | 1 | 0420-Cyclone crusher | D1-Forced - Immediate | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 42 | 63 | 1 | 1 | 0420-Cyclone crusher | D1-Forced - Immediate | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 126 | 63 | 1 | 1 | 0420-Cyclone crusher | D1-Forced - Immediate | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 20 | 40 | 1 | 1 | 0420-Cyclone crusher | D1-Forced - Immediate | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 52.5 | 35 | 1 | 1 | 0420-Cyclone crusher | D1-Forced - Immediate | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 40 | 40 | 1 | 1 | 0420-Cyclone crusher | D1-Forced - Immediate | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 322.5 | 30 | 1 | 1 | 0420-Cyclone crusher | D1-Forced - Immediate | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2006.6666 | 40 | 1 | 1 | 0420-Cyclone crusher | D1-Forced - Immediate | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 915.75 | 37 | 1 | 1 | 0420-Cyclone crusher | D1-Forced - Immediate | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 9 | 54 | 1 | 1 | 0420-Cyclone crusher | D1-Forced - Immediate | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 46.25 | 37 | 1 | 1 | 0420-Cyclone crusher | D1-Forced - Immediate | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 78.2 | 68 | 1 | 1 | 0420-Cyclone crusher | D1-Forced - Immediate | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1940 | 40 | 1 | 1 | 0420-Cyclone crusher | D1-Forced - Immediate | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 292 | 73 | 1 | 1 | 0420-Cyclone crusher | D1-Forced - Immediate | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 18.75 | 45 | 1 | 1 | 0420-Cyclone crusher | D3-Forced - Postponed | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 289.8 | 63 | 1 | 1 | 0420-Cyclone crusher | D1-Forced - Immediate | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 56.25 | 45 | 1 | 1 | 0420-Cyclone crusher | D1-Forced - Immediate | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 71.7833 | 73 | 1 | 1 | 0420-Cyclone crusher | D1-Forced - Immediate | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 84 | 63 | 1 | 1 | 0420-Cyclone crusher | D1-Forced - Immediate | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 193.45 | 73 | 1 | 1 | 0420-Cyclone crusher | D1-Forced - Immediate | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 225.75 | 63 | 1 | 1 | 0420-Cyclone crusher | D1-Forced - Immediate | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 17.5666 | 34 | 1 | 1 | 0420-Cyclone crusher | D2-Forced - Delayed | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1008 | 28 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2941.5 | 111 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5.25 | 45 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 59.5833 | 65 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 45.3333 | 68 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 599.1333 | 38 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 920 | 23 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6.6666 | 40 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 16 | 16 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 56.6666 | 40 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 704 | 40 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3000.4332 | 334 | 1 | 1 | 0425-Cyclone dampers | SF-Startup Failure | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2092.5 | 15 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 20.3333 | 61 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 41.4167 | 35 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2243.2666 | 46 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1269.3333 | 28 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2726.65 | 23 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6.75 | 45 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3743 | 38 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 173.25 | 45 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 208.3333 | 100 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 17175 | 50 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 149.6 | 68 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 728 | 28 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4.2 | 36 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 54 | 18 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 32.0833 | 55 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 207 | 41.4 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 18.3333 | 44 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4.5333 | 68 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 552.5 | 30 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1120 | 28 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1606 | 33 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3486 | 28 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9000 | 20 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 31.05 | 81 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 19.1667 | 50 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 261.5833 | 73 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 750.75 | 45 | 1 | 1 | 0425-Cyclone dampers | D2-Forced - Delayed | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9.6666 | 58 | 1 | 2 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 484.1666 | 83 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4.8 | 36 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 13 | 13 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 270 | 40 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 16.5 | 45 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 14310 | 50 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 325.5 | 63 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0426 | Cyclone air ducts | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 119.1666 | 55 | 1 | 1 | 0426-Cyclone air ducts | D1-Forced - Immediate | 100-Fossil-Steam
0426 | Cyclone air ducts | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 283.05 | 111 | 1 | 1 | 0426-Cyclone air ducts | D1-Forced - Immediate | 100-Fossil-Steam
0426 | Cyclone air ducts | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 434 | 30 | 1 | 1 | 0426-Cyclone air ducts | D1-Forced - Immediate | 100-Fossil-Steam
0426 | Cyclone air ducts | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 51 | 60 | 1 | 1 | 0426-Cyclone air ducts | D1-Forced - Immediate | 100-Fossil-Steam
0426 | Cyclone air ducts | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 154 | 30 | 1 | 1 | 0426-Cyclone air ducts | D1-Forced - Immediate | 100-Fossil-Steam
0426 | Cyclone air ducts | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 87.5 | 25 | 1 | 1 | 0426-Cyclone air ducts | D2-Forced - Delayed | 100-Fossil-Steam
0426 | Cyclone air ducts | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 192.6666 | 40 | 1 | 1 | 0426-Cyclone air ducts | D1-Forced - Immediate | 100-Fossil-Steam
0426 | Cyclone air ducts | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 687.5 | 30 | 1 | 1 | 0426-Cyclone air ducts | D1-Forced - Immediate | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 0 | 0 | 1 | 1 | 0430-Cyclone furnace | D1-Forced - Immediate | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 8998.75 | 115 | 1 | 1 | 0430-Cyclone furnace | D1-Forced - Immediate | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 60.5 | 22 | 1 | 1 | 0430-Cyclone furnace | D1-Forced - Immediate | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 11778.0832 | 427 | 1 | 1 | 0430-Cyclone furnace | U1-Forced - Immediate | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2 | 2 | 1 | 3 | 0430-Cyclone furnace | D1-Forced - Immediate | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7 | 3.5 | 1 | 1 | 0430-Cyclone furnace | D1-Forced - Immediate | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 200.8666 | 46 | 1 | 1 | 0430-Cyclone furnace | D1-Forced - Immediate | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 513.3333 | 16 | 1 | 1 | 0430-Cyclone furnace | D1-Forced - Immediate | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1 | 1 | 1 | 1 | 0430-Cyclone furnace | D1-Forced - Immediate | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 90 | 40 | 1 | 1 | 0430-Cyclone furnace | D1-Forced - Immediate | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 464 | 116 | 1 | 1 | 0430-Cyclone furnace | D1-Forced - Immediate | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5463.85 | 469 | 1 | 1 | 0430-Cyclone furnace | U1-Forced - Immediate | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 80.55 | 3 | 1 | 1 | 0430-Cyclone furnace | D1-Forced - Immediate | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8 | 8 | 1 | 1 | 0430-Cyclone furnace | D1-Forced - Immediate | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 122.6667 | 16 | 1 | 1 | 0430-Cyclone furnace | D1-Forced - Immediate | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 25 | 12.5 | 1 | 1 | 0430-Cyclone furnace | D1-Forced - Immediate | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 10568.3333 | 25 | 1 | 1 | 0430-Cyclone furnace | D1-Forced - Immediate | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 112.05 | 27 | 1 | 1 | 0430-Cyclone furnace | D1-Forced - Immediate | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3 | 3 | 1 | 1 | 0430-Cyclone furnace | D1-Forced - Immediate | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 714.1667 | 50 | 1 | 1 | 0430-Cyclone furnace | D1-Forced - Immediate | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 52.5 | 45 | 1 | 1 | 0430-Cyclone furnace | D3-Forced - Postponed | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 120.6666 | 40 | 1 | 1 | 0430-Cyclone furnace | D1-Forced - Immediate | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 337.5 | 30 | 1 | 1 | 0430-Cyclone furnace | D1-Forced - Immediate | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 1400 | 140 | 1 | 1 | 0430-Cyclone furnace | D1-Forced - Immediate | 650-Fluidized Bed
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2.8666 | 43 | 1 | 7 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3.8666 | 58 | 1 | 6 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5.25 | 45 | 2 | 4 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6.1999 | 93 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6.75 | 45 | 2 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9.35 | 33 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 13.5333 | 58 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 33.3333 | 50 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 42 | 21 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2 | 2 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2.55 | 51 | 1 | 7 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2.8 | 56 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3.4167 | 41 | 1 | 7 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4.1 | 41 | 1 | 4 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4.6 | 46 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4.7833 | 41 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4.8 | 36 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5.9166 | 71 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6 | 40 | 1 | 3 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7.1166 | 61 | 1 | 3 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8 | 8 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 12.2 | 61 | 1 | 5 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 17.7333 | 76 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 27.3333 | 40 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 28 | 56 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 31.7333 | 56 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 44 | 66 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 748.0832 | 191 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 944 | 118 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3703.45 | 51 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1.5 | 45 | 1 | 8 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3 | 45 | 2 | 12 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5.5 | 55 | 1 | 3 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 9.1667 | 50 | 1 | 3 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 17.25 | 45 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 95 | 47.5 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 174.4166 | 65 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 338 | 67.6 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 66.5 | 42 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 86.1 | 63 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 220.5 | 63 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 3.6667 | 44 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 264.1 | 38 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 85.75 | 49 | 1 | 1 | 0435-Other cyclone problems | D3-Forced - Postponed | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1.4333 | 43 | 1 | 4 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3.4 | 68 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4.3 | 43 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4.65 | 93 | 1 | 4 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5.0166 | 43 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5.8 | 58 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6 | 45 | 2 | 3 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6.6 | 33 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7.5 | 45 | 2 | 3 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 8.3333 | 50 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9 | 45 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 14 | 2 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 34 | 68 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 41.25 | 75 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 49.9999 | 75 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 58 | 58 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1.75 | 35 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3 | 3 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3.0666 | 46 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3.4 | 51 | 2 | 4 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3.7333 | 56 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4.6666 | 56 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6.15 | 41 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6.5333 | 56 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7.6666 | 46 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8.4 | 56 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9.15 | 61 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10.1666 | 61 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 11.1833 | 61 | 1 | 3 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 13.6 | 51 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 15.3333 | 46 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 18 | 40 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 18.45 | 41 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 33.3666 | 91 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 47.8333 | 35 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 86 | 86 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 246.5 | 30 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 308.55 | 51 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8234 | 46 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4.5 | 45 | 2 | 11 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5.8333 | 50 | 1 | 7 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 15 | 45 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 17.01 | 5.67 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 21.0833 | 55 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 22.5 | 10 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 23.7499 | 75 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 24.1666 | 145 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 35 | 15 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 398.3333 | 100 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 459.5 | 10 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 135.3333 | 58 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 123.52 | 46.32 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 6.2 | 31 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3818.1666 | 155 | 1 | 1 | 0435-Other cyclone problems | U1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1.5 | 45 | 1 | 5 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4.6 | 46 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6.25 | 75 | 1 | 4 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6.6666 | 50 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7.3 | 73 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 8.25 | 45 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 8.75 | 75 | 1 | 5 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 11.7333 | 88 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 12.65 | 33 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 13.95 | 93 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 50.25 | 45 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 209.5 | 30 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4.6667 | 35 | 1 | 3 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5.3666 | 46 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5.95 | 51 | 1 | 5 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6.1333 | 46 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6.6666 | 40 | 1 | 3 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6.8333 | 41 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7.4666 | 56 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7.65 | 51 | 1 | 3 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8.4 | 36 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10 | 40 | 1 | 5 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10.25 | 41 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 11.5 | 46 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 12.25 | 35 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 12.6666 | 40 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 13.2166 | 61 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 13.6667 | 41 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 14 | 56 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 21 | 35 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 28.4666 | 61 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 39.65 | 61 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 53.0833 | 91 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 63 | 30 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 80.6666 | 121 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 120.9833 | 61 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 121 | 121 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 192 | 40 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 197.6 | 76 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 892.5 | 51 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4.1666 | 50 | 1 | 13 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 7.5833 | 65 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 10.4999 | 90 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 12.5 | 50 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 13.75 | 55 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 14.9999 | 90 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 15.8333 | 50 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 16.6667 | 50 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 18 | 45 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 22.9166 | 55 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 52.5 | 21 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 337.5 | 45 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 3.0833 | 37 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1.8333 | 11 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2.15 | 43 | 1 | 3 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2.5 | 50 | 1 | 14 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3.5833 | 43 | 1 | 6 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3.8333 | 46 | 1 | 6 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5 | 75 | 1 | 6 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 8.25 | 33 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 11.25 | 45 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 14.5666 | 46 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 16.1 | 46 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 21.5 | 43 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 24.9333 | 68 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 25.3 | 46 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 36.5 | 73 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 40 | 60 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 152.7333 | 58 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 900.5333 | 44 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 982.4 | 32 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2.9167 | 35 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4 | 40 | 1 | 4 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4.0666 | 61 | 1 | 5 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5.0833 | 61 | 1 | 3 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5.1 | 51 | 1 | 5 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5.4667 | 41 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6 | 36 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6.1 | 61 | 1 | 3 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7 | 35 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8.75 | 35 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9.2 | 46 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10.0833 | 121 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10.1333 | 76 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10.2 | 51 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 11 | 11 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 11.3333 | 40 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 12.3 | 41 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 14.4 | 96 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 19.8333 | 35 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 20.4 | 51 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 21.35 | 61 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 22.1833 | 121 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 26.8333 | 46 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 40 | 40 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 72.25 | 51 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 119 | 42 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 135 | 30 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9463.9 | 51 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3.75 | 45 | 2 | 10 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6.75 | 45 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 7.5 | 50 | 1 | 5 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 11.9166 | 55 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 11.9166 | 65 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 13.3333 | 50 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 14.25 | 45 | 1 | 3 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 24.75 | 55 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 60.8333 | 50 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1328.6667 | 20 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3245.25 | 45 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 18 | 54 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 7 | 42 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 700 | 140 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 69.1667 | 50 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1.6666 | 50 | 1 | 19 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5.8333 | 50 | 1 | 3 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6.1333 | 46 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7.6666 | 46 | 1 | 5 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9.3166 | 43 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 10 | 75 | 1 | 4 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 11.6667 | 50 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 12 | 45 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 13.75 | 75 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 15.8333 | 50 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 16.2499 | 75 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 17 | 68 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 20 | 50 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 22.5 | 75 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 43.75 | 75 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 53.8666 | 101 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 350.8333 | 50 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 495.25 | 35 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 890 | 30 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1.3667 | 41 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1.8 | 36 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2.3333 | 35 | 1 | 3 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3.3333 | 40 | 1 | 8 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4.55 | 91 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4.6666 | 40 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5.5 | 66 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7 | 7 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8.2 | 41 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8.5 | 51 | 1 | 4 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8.8 | 66 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 15.1666 | 91 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 15.75 | 35 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 17.0833 | 41 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 21.2333 | 91 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 30.3333 | 35 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 42.35 | 121 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 46.75 | 51 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 101.6166 | 91 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 141.1 | 51 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 228.1499 | 81 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 247 | 30 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1585.3333 | 41 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2.25 | 45 | 1 | 13 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4.5 | 90 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4.5833 | 55 | 1 | 6 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5 | 50 | 1 | 5 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 7.5 | 45 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 8.3333 | 50 | 1 | 8 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 9 | 45 | 2 | 3 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 9.1666 | 55 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 10.5 | 45 | 2 | 3 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 10.8333 | 50 | 1 | 3 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 11 | 55 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 12.8333 | 55 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 13.5 | 45 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 80 | 40 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 58.5833 | 37 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 2571.45 | 63 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 126 | 63 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 118.4333 | 38 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 4158.2 | 51 | 1 | 1 | 0435-Other cyclone problems | U2-Forced - Delayed | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2.5 | 75 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3 | 45 | 2 | 13 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3.0666 | 46 | 1 | 5 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3.3333 | 50 | 1 | 7 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4.5 | 45 | 2 | 6 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6.7666 | 58 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7.1666 | 43 | 1 | 3 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7.5 | 75 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7.7333 | 58 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 8.6 | 43 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 12.5 | 75 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 23.2 | 58 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 25 | 75 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 45.75 | 45 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 47.25 | 63 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 52.5 | 75 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 56.25 | 45 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 72.0666 | 46 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 143.0667 | 29 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2.05 | 41 | 1 | 9 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5.6 | 56 | 2 | 3 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5.8333 | 35 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9.3333 | 35 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 11.6667 | 35 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 13.0666 | 56 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 14 | 35 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 14.2333 | 61 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 16.2 | 81 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 16.6833 | 91 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 16.8 | 56 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 19.9499 | 171 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 20.1666 | 121 | 1 | 3 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 32.5333 | 61 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 43 | 8.6 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 90.8833 | 41 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 130.0833 | 35 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 252 | 36 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2 | 2 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3.3333 | 50 | 1 | 17 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6.4166 | 55 | 1 | 3 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 8 | 8 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 21.75 | 45 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 414 | 45 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2037.4999 | 150 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 38.85 | 63 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4.1666 | 50 | 1 | 8 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5.7333 | 43 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6.9 | 46 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7.3333 | 40 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 7.6666 | 115 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7.9333 | 68 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9.1667 | 50 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9.3 | 93 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 10.6333 | 58 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 11.25 | 75 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 13.5 | 45 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 15.4666 | 116 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 18.75 | 75 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 19.1666 | 46 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 20.8333 | 50 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 23.2333 | 41 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 54 | 4.5 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 54.25 | 93 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1.3333 | 40 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2 | 40 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2.6666 | 40 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2.7333 | 41 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3.05 | 61 | 1 | 3 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3.8333 | 46 | 1 | 4 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4.0833 | 35 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5.3333 | 40 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6.8 | 51 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7.5167 | 41 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8.1667 | 35 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9.5667 | 41 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 11 | 66 | 2 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 11.2 | 56 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 12.6666 | 76 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 14.5666 | 46 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 15.8666 | 56 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 16.1 | 46 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 16.15 | 51 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 16.2666 | 61 | 1 | 5 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 19.25 | 35 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 19.3166 | 61 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 21.5833 | 35 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 25.7833 | 91 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 29.8666 | 56 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 35.8333 | 86 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 39.3333 | 40 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 42.5 | 34 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 88.3333 | 106 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 114.8 | 56 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 988 | 30 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1413.8167 | 41 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 7369.0166 | 83 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1 | 1 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2.5 | 50 | 1 | 12 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6.6666 | 50 | 1 | 6 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6.99 | 2.33 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 7.3333 | 55 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 8.75 | 75 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 9.75 | 45 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 18.3333 | 50 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 26.25 | 35 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 32.5 | 50 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 34.1666 | 50 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 29.3333 | 44 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 180 | 54 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 100.8 | 48 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2 | 2 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2.25 | 45 | 2 | 14 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3.75 | 45 | 2 | 11 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3.75 | 75 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5 | 50 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9.0666 | 68 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9.6666 | 58 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 13.6 | 68 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 15 | 75 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 32.5 | 6.5 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 37.5 | 75 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 43.7166 | 43 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 79.95 | 41 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 101 | 60 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 462 | 77 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1 | 1 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1.5333 | 46 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1.7 | 51 | 1 | 4 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4.25 | 51 | 2 | 9 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5.1666 | 31 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6.3333 | 76 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6.4167 | 35 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7.5833 | 91 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8.2833 | 71 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8.6666 | 40 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9.3333 | 56 | 1 | 3 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9.35 | 51 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10 | 10 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 11.8333 | 71 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 12.1333 | 91 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 14.3333 | 86 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 15.0333 | 41 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 17.85 | 51 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 23.3333 | 56 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 24.2 | 121 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 36.2666 | 136 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 39.0833 | 35 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 85 | 51 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 93.4999 | 102 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 210.5 | 30 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2683.9166 | 43 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1.6666 | 50 | 1 | 15 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2.75 | 55 | 1 | 4 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3.6666 | 55 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5.25 | 45 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6 | 45 | 1 | 4 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 11.25 | 45 | 2 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 12 | 45 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 14.1667 | 50 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 14.6666 | 55 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 27.5 | 55 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 42.5 | 50 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 326.6666 | 100 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 510 | 102 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4540 | 100 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 14 | 42 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 341.25 | 63 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 42 | 63 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 8 | 32 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 4.5833 | 25 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 59.85 | 63 | 1 | 1 | 0435-Other cyclone problems | D3-Forced - Postponed | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 9 | 4.5 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 650-Fluidized Bed
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 10 | 2.5 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 650-Fluidized Bed
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 22.5 | 2.5 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 650-Fluidized Bed
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 897.5 | 150 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 650-Fluidized Bed
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 10.4917 | 0.5 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 650-Fluidized Bed
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 16090.6665 | 280 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 650-Fluidized Bed
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 20 | 2.5 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 650-Fluidized Bed
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Gas | GG | 650 | Fluidized Bed | SERC | Off-Peak | 65.2167 | 13 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 650-Fluidized Bed
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 3 | 1.5 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 650-Fluidized Bed
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 4.5 | 1.5 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 650-Fluidized Bed
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 12 | 1.5 | 1 | 3 | 0435-Other cyclone problems | D1-Forced - Immediate | 650-Fluidized Bed
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 7.5 | 2.5 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 650-Fluidized Bed
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 2451 | 285 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 650-Fluidized Bed
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 4 | 0.5 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 650-Fluidized Bed
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 34.5 | 1.5 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 650-Fluidized Bed
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 347.0833 | 119 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 40.4 | 24 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 160.8833 | 49 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 217.75 | 39 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 25.0167 | 19 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 40.85 | 19 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 101.65 | 19 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 52 | 24 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 53.65 | 29 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 13.2 | 44 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 24.6 | 9 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 1641.5 | 469 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 43.65 | 9 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 1246.9497 | 459 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 27.65 | 79 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 39.6333 | 29 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 446.85 | 9 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 138.3833 | 19 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 40.2167 | 19 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 426.8667 | 19 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 1141.4 | 439 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 9.9 | 9 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 51.3 | 19 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 21.85 | 69 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 38 | 19 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 63.8 | 44 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 70.2 | 39 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 79.2166 | 49 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0440 | Fuel oil pumps (general) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Oil | OO | 100 | Fossil-Steam | NPCC | Off-Peak | 695.75 | 605 | 1 | 1 | 0440-Fuel oil pumps (general) | U1-Forced - Immediate | 100-Fossil-Steam
0440 | Fuel oil pumps (general) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 236.25 | 175 | 1 | 1 | 0440-Fuel oil pumps (general) | D1-Forced - Immediate | 100-Fossil-Steam
0440 | Fuel oil pumps (general) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 38.5 | 77 | 1 | 1 | 0440-Fuel oil pumps (general) | U1-Forced - Immediate | 100-Fossil-Steam
0441 | Fuel oil pumps (burner supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 2 | 40 | 1 | 1 | 0441-Fuel oil pumps (burner supply) | D1-Forced - Immediate | 100-Fossil-Steam
0441 | Fuel oil pumps (burner supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 13 | 60 | 1 | 1 | 0441-Fuel oil pumps (burner supply) | D1-Forced - Immediate | 100-Fossil-Steam
0441 | Fuel oil pumps (burner supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9960 | 415 | 1 | 1 | 0441-Fuel oil pumps (burner supply) | SF-Startup Failure | 100-Fossil-Steam
0441 | Fuel oil pumps (burner supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 226.0465 | 437.51 | 1 | 1 | 0441-Fuel oil pumps (burner supply) | U1-Forced - Immediate | 100-Fossil-Steam
0441 | Fuel oil pumps (burner supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 167.712 | 437.51 | 1 | 1 | 0441-Fuel oil pumps (burner supply) | U1-Forced - Immediate | 100-Fossil-Steam
0442 | Fuel oil pumps (forwarding/transfer) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 1740 | 60 | 1 | 1 | 0442-Fuel oil pumps (forwarding/transfer) | U1-Forced - Immediate | 100-Fossil-Steam
0450 | Fuel oil heaters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2013 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 11594.015 | 437.51 | 1 | 1 | 0450-Fuel oil heaters | SF-Startup Failure | 100-Fossil-Steam
0450 | Fuel oil heaters | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Gas | GG | 850 | Combined Cycle Block | WECC | Off-Peak | 111.08 | 277.7 | 1 | 1 | 0450-Fuel oil heaters | D1-Forced - Immediate | 850-Combined Cycle Block
0460 | Fuel oil atomizers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 182.3999 | 144 | 1 | 1 | 0460-Fuel oil atomizers | D1-Forced - Immediate | 100-Fossil-Steam
0460 | Fuel oil atomizers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 583.3275 | 333.33 | 1 | 1 | 0460-Fuel oil atomizers | U1-Forced - Immediate | 100-Fossil-Steam
0460 | Fuel oil atomizers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 43.3333 | 100 | 1 | 1 | 0460-Fuel oil atomizers | U1-Forced - Immediate | 100-Fossil-Steam
0460 | Fuel oil atomizers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 24 | 80 | 1 | 1 | 0460-Fuel oil atomizers | D1-Forced - Immediate | 100-Fossil-Steam
0460 | Fuel oil atomizers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 388.85 | 77 | 1 | 1 | 0460-Fuel oil atomizers | D1-Forced - Immediate | 100-Fossil-Steam
0460 | Fuel oil atomizers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 422.9165 | 175 | 1 | 1 | 0460-Fuel oil atomizers | D1-Forced - Immediate | 100-Fossil-Steam
0460 | Fuel oil atomizers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 65 | 15 | 1 | 1 | 0460-Fuel oil atomizers | D1-Forced - Immediate | 100-Fossil-Steam
0460 | Fuel oil atomizers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 102.0833 | 125 | 1 | 1 | 0460-Fuel oil atomizers | D1-Forced - Immediate | 100-Fossil-Steam
0460 | Fuel oil atomizers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 286.6666 | 80 | 1 | 1 | 0460-Fuel oil atomizers | D1-Forced - Immediate | 100-Fossil-Steam
0460 | Fuel oil atomizers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 139.5833 | 67 | 1 | 1 | 0460-Fuel oil atomizers | D1-Forced - Immediate | 100-Fossil-Steam
0460 | Fuel oil atomizers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 232.9166 | 65 | 1 | 1 | 0460-Fuel oil atomizers | D1-Forced - Immediate | 100-Fossil-Steam
0470 | Oil and gas fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 136.85 | 34.5 | 1 | 1 | 0470-Oil and gas fires | D1-Forced - Immediate | 100-Fossil-Steam
0470 | Oil and gas fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 22944.9999 | 390 | 1 | 1 | 0470-Oil and gas fires | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 942.9074 | 340.81 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 920.8333 | 250 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | SF-Startup Failure | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 19550 | 115 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 1290.7333 | 76 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 106.2 | 177 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 894.9415 | 375.5 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 784.5832 | 376.6 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 9.1 | 13 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 154.3667 | 22 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 1940 | 80 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Oil | DI | 100 | Fossil-Steam | RFC | Summer | 52.0832 | 125 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 3197.0667 | 38 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U2 | Forced - Delayed | 2013 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 370.2333 | 58 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U2-Forced - Delayed | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 100.5 | 67 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | OS | 100 | Fossil-Steam | NPCC | Winter | 61.5 | 18 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 497.4586 | 295.52 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 30.4 | 19 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 20.9333 | 8 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D2-Forced - Delayed | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Oil | DI | 100 | Fossil-Steam | SERC | Off-Peak | 409.8666 | 58 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Oil | DI | 100 | Fossil-Steam | RFC | Winter | 1459.1661 | 850 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Oil | OO | 100 | Fossil-Steam | NPCC | Off-Peak | 28.3333 | 100 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Oil | DI | 100 | Fossil-Steam | SERC | Off-Peak | 221.3666 | 58 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4336.2665 | 404 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 32.3833 | 29 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Oil | DI | 100 | Fossil-Steam | RFC | Winter | 54.1333 | 20.3 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 208.2667 | 22 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2387 | 220 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 65.5 | 31.44 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 1576.7999 | 81 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Oil | DI | 100 | Fossil-Steam | SERC | Off-Peak | 484.3 | 58 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Oil | DI | 100 | Fossil-Steam | RFC | Off-Peak | 27936 | 582 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | OS | 100 | Fossil-Steam | NPCC | Off-Peak | 34.1667 | 10 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 55 | 110 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 1020.9412 | 175.52 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 37.05 | 11.4 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 187.7666 | 43 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Oil | DI | 100 | Fossil-Steam | SERC | Off-Peak | 44.4666 | 58 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 98760.5905 | 437.51 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | OS | 100 | Fossil-Steam | NPCC | Off-Peak | 907.35 | 23 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 2075.5833 | 5 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 777 | 111 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | SF-Startup Failure | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 2351.1499 | 177 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Oil | DI | 100 | Fossil-Steam | RFC | Off-Peak | 28094.4 | 585.3 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Gas | GG | 650 | Fluidized Bed | SERC | Off-Peak | 5310.1964 | 365.8 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 650-Fluidized Bed
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Gas | GG | 650 | Fluidized Bed | SERC | Off-Peak | 6015.52 | 366.8 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 650-Fluidized Bed
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Gas | GG | 650 | Fluidized Bed | SERC | Off-Peak | 9056.4665 | 414.8 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 650-Fluidized Bed
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 444 | 74 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 800-Miscellaneous
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Summer | 63.7543 | 9.91 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Summer | 29.96 | 16.8 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Summer | 23.0228 | 12.91 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Summer | 56.6133 | 8.8 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 5404.3329 | 620 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 850-Combined Cycle Block
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Oil | DI | 851 | CC GT units | SERC | Winter | 96.8333 | 83 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 851-CC GT units
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2013 | Oil | DI | 851 | CC GT units | SERC | Winter | 1470.4833 | 83 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | SF-Startup Failure | 851-CC GT units
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Oil | DI | 851 | CC GT units | SERC | Winter | 13.8333 | 83 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 851-CC GT units
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Gas | GG | 851 | CC GT units | WECC | Summer | 56.4 | 72 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 851-CC GT units
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 93.3333 | 70 | 2 | 2 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 851-CC GT units
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Gas | GG | 852 | CC steam units | WECC | Summer | 24.4243 | 31.18 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 852-CC steam units
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 625 | 25 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 852-CC steam units
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2013 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 460 | 138 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 852-CC steam units
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 21 | 7 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 42 | 14 | 1 | 2 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 45 | 18 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 48 | 16 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 71.4 | 14 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 75 | 45 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 94 | 10 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 112 | 21 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 114.8 | 21 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 142.75 | 5 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 174 | 24 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 182 | 13 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 200 | 30 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 221.1 | 11 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 246.25 | 15 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 260 | 16 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 320.1 | 22 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 348.3333 | 38 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 349.8 | 9 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 532 | 14 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1040 | 40 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1410 | 20 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1621.0833 | 49 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 12 | 3 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 18 | 18 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 58 | 12 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 85 | 20 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 110 | 22 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 346.6667 | 20 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 420 | 20 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 507.5 | 35 | 1 | 2 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 669.3333 | 16 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1071 | 42 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 15.3333 | 23 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 20 | 20 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 52.8 | 2 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 53.1667 | 29 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 58.6667 | 11 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 59.5833 | 11 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 84 | 14 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 88 | 22 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 103.7667 | 22 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 133.3333 | 16 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 191 | 12 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 203.3333 | 20 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 283.5 | 54 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 836906.5829 | 605 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U2-Forced - Delayed | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 8 | 8 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 12 | 16 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 22.1667 | 5 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 26 | 13 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 29.1667 | 25 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 35 | 10 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 36 | 16 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 36.8667 | 14 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 45.2 | 12 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 62.6667 | 8 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 64.5833 | 25 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 75 | 15 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 87.45 | 11 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 114.8333 | 13 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 135 | 30 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 144 | 12 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 163.8 | 26 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 192 | 16 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 192.5 | 5 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 260.1 | 27 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 391.5167 | 13 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 528 | 48 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 532 | 42 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1016 | 30 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2217.6 | 36 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 68.3333 | 20 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 95 | 20 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 99.2 | 32 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 150 | 30 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 192.75 | 15 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 480 | 20 | 1 | 2 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 596.6667 | 20 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 920 | 20 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 980 | 20 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 24.75 | 11 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 28 | 28 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 32.8333 | 10 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 50 | 50 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 130 | 26 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 318.5 | 49 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 507.5 | 29 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 624.75 | 49 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1049 | 30 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1150 | 50 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2090 | 38 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 55.5 | 37 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D2-Forced - Delayed | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 21562.6663 | 520 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 12245.3333 | 205 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U2-Forced - Delayed | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 16 | 16 | 1 | 2 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 32 | 16 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 35 | 20 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 36.75 | 21 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 64.1667 | 11 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 73.4667 | 38 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 75 | 20 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 90 | 10 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 150 | 20 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 160 | 16 | 2 | 2 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 161.25 | 45 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 231 | 44 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 301.5 | 18 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 440 | 22 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 627.3 | 34 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 960.6667 | 44 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 17.5 | 35 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 17.5666 | 62 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 47.6667 | 11 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 632 | 20 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 129 | 36 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 365.5 | 17 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 500.5 | 22 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 630 | 45 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 667.3333 | 52 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1014.3 | 414 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | SF | Startup Failure | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1468.0664 | 361 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | SF-Startup Failure | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 38067.9499 | 249 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 17.8666 | 67 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 20665.4649 | 156.3 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 9 | 9 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 12 | 12 | 1 | 2 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 21 | 30 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 43.5 | 29 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 45.5 | 26 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 56 | 14 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 62.5 | 15 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 120 | 15 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 136 | 8 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 140 | 14 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 164 | 16 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 181.1333 | 22 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 216.4667 | 17 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 257.6667 | 10 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 264 | 11 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 336 | 14 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 368 | 16 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 437.5 | 25 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 609.9333 | 14 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 647.5 | 35 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 800.3333 | 35 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 862.5 | 25 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1550 | 25 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2266.25 | 49 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 48.3333 | 20 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 60 | 4 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 205.8333 | 19 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 263.3333 | 20 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 313.3333 | 20 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 405.3333 | 19 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 429.3333 | 20 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 532.5 | 30 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1885 | 20 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 22 | 11 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 48 | 36 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 90 | 30 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 126.45 | 27 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 137.4167 | 17 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 140.4 | 54 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 156 | 39 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 198.3333 | 14 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 381.6667 | 20 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 423.5833 | 13 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 453.8333 | 10 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 900.2 | 28 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 13451.3662 | 634 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 23885.8664 | 448 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 93465 | 335 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 105256.6666 | 200 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U2-Forced - Delayed | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 13 | 13 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 21 | 21 | 1 | 2 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 25.4333 | 14 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 26.6667 | 25 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 28 | 28 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 28.3333 | 34 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 33 | 22 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 34 | 17 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 40.0833 | 13 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 46.8 | 6 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 53.3333 | 20 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 70 | 7 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 77.5 | 10 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 85.8333 | 5 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 118.25 | 15 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 119.1667 | 22 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 120.4667 | 13 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 138 | 12 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 143 | 11 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 195 | 15 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 213.3333 | 20 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 216.25 | 25 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 232 | 16 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 262.35 | 11 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 378 | 28 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 408 | 16 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 513.3333 | 22 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 90 | 20 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 240 | 15 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 242.5 | 15 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1140 | 20 | 1 | 2 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2700 | 20 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 6.25 | 25 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 64.5833 | 5 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 126 | 15 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 136.8 | 8 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 137.5 | 11 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 140 | 20 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 180.95 | 21 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 212.5 | 30 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 256.25 | 41 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 270.6666 | 28 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 310.5 | 9 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 397.5 | 30 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 581.25 | 45 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | SF | Startup Failure | 2013 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 131699.6497 | 831 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | SF-Startup Failure | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 18745.9999 | 210 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 31893.3332 | 520 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 10369.2 | 72 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 44722.8333 | 145 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 472.5 | 90 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 18.3333 | 55 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 26.8333 | 23 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 33.7333 | 22 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 38.25 | 17 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 43.6667 | 20 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 76.2167 | 17 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 88 | 44 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 101 | 12 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 102 | 17 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 161.5 | 34 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 181.3333 | 32 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 185.5 | 14 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 204 | 15 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 316.5833 | 29 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 330 | 20 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 333.8667 | 16 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 368 | 23 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 805.75 | 11 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 9 | 9 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 12.8333 | 1 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 24.6667 | 8 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 27 | 12 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 30 | 20 | 1 | 2 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 58 | 20 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 73.8 | 18 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 83.4 | 18 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 150 | 15 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 189.5 | 6 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 371.6667 | 20 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1437 | 9 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 22 | 22 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 150.6667 | 16 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 185.8333 | 50 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 259 | 14 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 261.3333 | 20 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 268.75 | 25 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 277.0833 | 35 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 303 | 18 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 325 | 25 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 513 | 57 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 603.5 | 34 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 779 | 19 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1952.1 | 54 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2184 | 28 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 8684 | 52 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3183.0499 | 249 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 50427.8497 | 831 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U2-Forced - Delayed | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 23 | 23 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 33 | 11 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 37.8333 | 10 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 39.6667 | 14 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 52.5 | 30 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 67.0833 | 35 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 73.5 | 6 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 84 | 12 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 106.75 | 7 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 110.8333 | 5 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 155.8333 | 17 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 157.6667 | 22 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 187 | 12 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 196 | 49 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 225 | 30 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 293.3333 | 16 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 305.5 | 39 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 322.25 | 15 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 351 | 13 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 367.5 | 15 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 450 | 15 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 454.1667 | 10 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1819.8833 | 133 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2002 | 44 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 21 | 21 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 45.3333 | 17 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 65.9167 | 7 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 135 | 45 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 140 | 10 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 255 | 20 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 361.6667 | 20 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 436.6667 | 20 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 460 | 40 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 594 | 18 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 770 | 35 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1675 | 20 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 36.8333 | 17 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 37.5 | 18 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 49 | 21 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 124.1667 | 50 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 144 | 9 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 195 | 52 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 228 | 18 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 302.6 | 34 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 337.5 | 25 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 544.4167 | 47 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 837 | 54 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 10164.25 | 109 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 236396.1 | 619 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 33066.7999 | 312 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 16.6667 | 10 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 32.0167 | 17 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 45 | 45 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 46 | 46 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 51.2 | 16 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 60.2333 | 13 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 83 | 12 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 95 | 20 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 100 | 12 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 106.6667 | 5 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 130 | 10 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 147 | 21 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 186.7 | 6 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 210 | 10 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 211.1667 | 7 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 406.6 | 12 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 927.5 | 15 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 960 | 45 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2628 | 24 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 12.9333 | 8 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 30.6667 | 8 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 80 | 8 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 200 | 20 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 493.3333 | 20 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 690 | 30 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 810 | 20 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2.5 | 10 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 13.75 | 55 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 21 | 21 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 38 | 19 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 68 | 8 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 92 | 16 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 133.5 | 9 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 144.7167 | 19 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 208 | 16 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 343 | 49 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 361.6 | 32 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1417.5 | 54 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 997.5 | 570 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1531.25 | 245 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 3885.333 | 470 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 3438.75 | 393 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 144217.5 | 335 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Other | BM | 100 | Fossil-Steam | SERC | Summer | 3226.55 | 47 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1929.1 | 191 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U2-Forced - Delayed | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 373667.5 | 685 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U3-Forced - Postponed | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 17214 | 285 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 650-Fluidized Bed
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 96968.6665 | 280 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 650-Fluidized Bed
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Geothermal | GE | 830 | Geothermal | WECC | Off-Peak | 881.11 | 51.83 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 830-Geothermal
0500 | Main steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U2 | Forced - Delayed | 2013 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 5642 | 260 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U2-Forced - Delayed | 850-Combined Cycle Block
0500 | Main steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 850 | Combined Cycle Block | MRO | Winter | 12972.8331 | 281 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 850-Combined Cycle Block
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2013 | Gas | GG | 860 | Co-generator Block | NPCC | Winter | 855 | 57 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U2-Forced - Delayed | 860-Co-generator Block
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 139.1667 | 10 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 12973.5666 | 94 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 8586 | 106 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 19.6667 | 10 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 51.3333 | 8 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 117.8333 | 5 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 301.5 | 10 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1590 | 10 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 469.3 | 57 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2215.4999 | 90 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 6015.3333 | 14 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 823.4167 | 41 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 99.9998 | 240 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D2-Forced - Delayed | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 93.6 | 4 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1001.25 | 75 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 15040 | 94 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 414 | 138 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 17175.05 | 57 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 330.6333 | 13 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 15333.3329 | 575 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | U1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 70 | 70 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 104 | 104 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 312.5 | 250 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 23.05 | 3 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 109.9333 | 68 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D2-Forced - Delayed | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 131.85 | 27 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D2-Forced - Delayed | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 10 | 30 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 70.5 | 141 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 296.4 | 104 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1260 | 10 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4608.415 | 35.3 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 24.5667 | 22 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1003.9999 | 120 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 202.8 | 52 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 10 | 10 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 11.7 | 13 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 39.25 | 5 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 175 | 10 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 400.9 | 63.3 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 410 | 10 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1570 | 10 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 40 | 40 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 130 | 120 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 326.4 | 272 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D2-Forced - Delayed | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 210 | 300 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 316.8333 | 10 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 828 | 10 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 94168 | 316 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 301.35 | 123 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 31 | 6.2 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D2-Forced - Delayed | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | SF | Startup Failure | 2013 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 9712.1665 | 190 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | SF-Startup Failure | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 10.75 | 5 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 62.5 | 125 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 126.6665 | 190 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3572 | 94 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 73.15 | 57 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 228 | 144 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 481.6667 | 10 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Gas | GG | 650 | Fluidized Bed | SERC | Summer | 110.4999 | 78 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 650-Fluidized Bed
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Gas | GG | 650 | Fluidized Bed | SERC | Summer | 157.6666 | 43 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 650-Fluidized Bed
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 247.95 | 27 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 650-Fluidized Bed
0510 | Main steam relief/safety valves off superheater | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2013 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 38.5 | 22 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 850-Combined Cycle Block
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 396 | 22 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2255 | 22 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Oil | OO | 100 | Fossil-Steam | NPCC | Off-Peak | 536.9164 | 379 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | D3 | Forced - Postponed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 4716.0666 | 218 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D3-Forced - Postponed | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | SF | Startup Failure | 2013 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 1472.5 | 190 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | SF-Startup Failure | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 17566.6664 | 340 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 144 | 108 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | D3 | Forced - Postponed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1885.8665 | 208 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D3-Forced - Postponed | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 947.4999 | 150 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 6514.75 | 115 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7175.5 | 635 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 26349.3331 | 410 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 50032.4996 | 630 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U2-Forced - Delayed | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Oil | OO | 100 | Fossil-Steam | NPCC | Off-Peak | 79.3332 | 280 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 170 | 340 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1811.2 | 64 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4382.9166 | 335 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 309.3333 | 64 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 29723.7663 | 499 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 12738.45 | 156.3 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 3041.5831 | 565 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 194.4833 | 7 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2585 | 22 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Oil | OO | 100 | Fossil-Steam | NPCC | Off-Peak | 344.6664 | 376 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | SF | Startup Failure | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4613.6499 | 159 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | SF-Startup Failure | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 34612.5 | 650 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 31878.3329 | 620 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 5535 | 45 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Oil | OO | 100 | Fossil-Steam | NPCC | Off-Peak | 87.9998 | 330 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | D3 | Forced - Postponed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 4788.3332 | 221 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D3-Forced - Postponed | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 8704.4166 | 335 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6579.9996 | 600 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 6630 | 120 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 799.5166 | 77 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U2-Forced - Delayed | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 3730.4 | 48 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 11668.5331 | 329 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 650-Fluidized Bed
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Geothermal | GE | 830 | Geothermal | WECC | Off-Peak | 21 | 21 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 830-Geothermal
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2013 | Gas | GG | 850 | Combined Cycle Block | TRE | Off-Peak | 65 | 130 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 850-Combined Cycle Block
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2013 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 29926.189 | 443.57 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 850-Combined Cycle Block
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2013 | Gas | GG | 850 | Combined Cycle Block | TRE | Off-Peak | 1004.7666 | 301.43 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 850-Combined Cycle Block
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 12935.162 | 186.52 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 850-Combined Cycle Block
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 851 | CC GT units | MRO | Winter | 180.1999 | 159 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 851-CC GT units
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 851 | CC GT units | TRE | Summer | 199.7499 | 141 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 851-CC GT units
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 851 | CC GT units | TRE | Summer | 7896 | 141 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 851-CC GT units
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 851 | CC GT units | TRE | Summer | 1508.7 | 141 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 851-CC GT units
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 851 | CC GT units | MRO | Summer | 546.1166 | 151 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 851-CC GT units
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | SF | Startup Failure | 2013 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 2100 | 240 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | SF-Startup Failure | 851-CC GT units
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | MRO | Winter | 78.2 | 69 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 852-CC steam units
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 220.6166 | 61 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 852-CC steam units
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1.9667 | 2 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3.25 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 9.9 | 6 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 13.0833 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 25.9333 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 26.25 | 1.25 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 35.9167 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 43.5833 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 106.5 | 10 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 121.5 | 9 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2975.9333 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 0.23333 | 2 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1.4 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2.9 | 2 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3.6333 | 2 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4.3333 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4.5 | 10 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5.1 | 9 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 6.3333 | 2 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 7.7 | 6 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 8.7 | 6 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 10.8667 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 13 | 13 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 13.25 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 13.85 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 14.98 | 2.14 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 16.1333 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 16.5333 | 16 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 16.9333 | 8 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 20.6667 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 22.45 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 23.5833 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 24.8 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 26.6 | 2 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 28.75 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 35.3333 | 10 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 35.4167 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 39.2 | 16 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 46.15 | 13 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 51.8667 | 8 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 64.75 | 7 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 64.9 | 6 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 66.6 | 12 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 70 | 8 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 71 | 6 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 71.3333 | 10 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 74.4 | 6 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 92.5167 | 7 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 94.8 | 18 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 96.45 | 9 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 102.8 | 8 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 107.6 | 12 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 115.6 | 8 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 147.2 | 12 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 172.25 | 13 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 660 | 120 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1.3 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 10.1333 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 11.25 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 33 | 10 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 466.6667 | 50 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 17629.75 | 727 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Other | BM | 100 | Fossil-Steam | WECC | Off-Peak | 92.008 | 59.36 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 28296 | 262 | 1 | 1 | 0530-Other main steam system problems | U2-Forced - Delayed | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 0.25 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 0.4 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 0.53333 | 2 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2.35 | 1 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2.6667 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3.05 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3.3833 | 7 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3.4667 | 2 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4.75 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 5.75 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 7.3 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 9.4167 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 10.9 | 6 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 11.2 | 7 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 22.95 | 9 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 24.3 | 6 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 54.6 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 57.7333 | 8 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 59.9333 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 66.55 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 69.2 | 1.73 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 74.82 | 1.29 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 77.6 | 6 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 126 | 6 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 378 | 9 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1.1667 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1.55 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1.9167 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1.9333 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2 | 40 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3.85 | 11 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4.3 | 6 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4.8333 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4.8333 | 2 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5 | 2.5 | 1 | 2 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 7.15 | 13 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8.01 | 2.67 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 8.8 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 9.4 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 11.6 | 8 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 12.1667 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 13.25 | 15 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 13.5 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 13.5 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 14.25 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 15.4 | 7 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 17.99 | 2.57 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 19.2 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 20.2667 | 8 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 20.7167 | 11 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 21.6 | 6 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 22.3333 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 25 | 12 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 28.96 | 3.62 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 32.35 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 35.2 | 12 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 36 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 38.2667 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 40.9333 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 43.7333 | 8 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 52.9167 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 55.8833 | 7 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 63.8333 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 69.6 | 8 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 71.3167 | 11 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 74.5333 | 8 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 74.85 | 9 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 90.4 | 6 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 94.2499 | 195 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 98.1 | 9 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 99.6 | 8 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 102.05 | 13 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 105.95 | 13 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 107.6667 | 10 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 116.3333 | 10 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 170.9333 | 8 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 193.8 | 19 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 706.6665 | 265 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3601.25 | 215 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 0.099999 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1 | 1 | 2 | 9 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3.7333 | 8 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5.01 | 1.67 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 16.1 | 6 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 67.25 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 0.25 | 5 | 1 | 1 | 0530-Other main steam system problems | D3-Forced - Postponed | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 10638.6663 | 505 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 6052.35 | 771 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 231.3 | 771 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 0.45 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 0.46666 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1.5 | 2 | 1 | 2 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3.2667 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 6.9 | 9 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 6.9 | 2 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 8.1667 | 7 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 8.8333 | 2 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 10.25 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 11.8667 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 14.9333 | 7 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 18.25 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 33 | 82.5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 49.05 | 9 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 63.3333 | 10 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 65.85 | 9 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 70.7 | 14 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 98.8 | 12 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 138.3 | 6 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 153 | 9 | 1 | 2 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 0.33333 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 0.7 | 14 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 0.73333 | 11 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1 | 1 | 1 | 2 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1.1667 | 7 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1.2333 | 2 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1.4167 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2.6667 | 8 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2.85 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2.9167 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2.95 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3.1 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3.1667 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3.3 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4.05 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5.1333 | 11 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 7.95 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 9.1 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 9.7333 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 9.8667 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 10.5 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 12 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 12.5667 | 13 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 12.5833 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 13.75 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 15.0833 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 16.5 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 18.4 | 8 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 18.55 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 19.8333 | 10 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 22.65 | 9 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 22.9 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 23.9167 | 7 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 24.5 | 6 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 24.5667 | 11 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 29.3333 | 10 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 32.8333 | 10 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 32.8667 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 36.25 | 15 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 45.75 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 49.3 | 17 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 50.5333 | 8 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 51.8 | 7 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 58.6667 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 66.9 | 9 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 69.3 | 6 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 78.3 | 9 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 78.4 | 7 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 84.45 | 9 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 91.6667 | 11 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 99.6 | 9 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 109.3333 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 111.4667 | 8 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 118.2 | 12 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 122.2833 | 11 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 130.9 | 17 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 142 | 120 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 175.8167 | 11 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 232.3333 | 20 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1.05 | 7 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1.9 | 2 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3.0667 | 4 | 1 | 2 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 8.5 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 102.0833 | 25 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4680 | 600 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 0.3 | 6 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2.5333 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 10.4 | 6 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 12.8 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 16.65 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 22.1666 | 70 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 28.2 | 9 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 38.1333 | 8 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 44.6 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 46.1667 | 10 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 56.6667 | 10 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 150.1667 | 10 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 0.2 | 2 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 0.36666 | 11 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 0.93333 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1 | 5 | 1 | 2 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1.95 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2.0833 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3 | 1.5 | 1 | 3 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3.4333 | 2 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5.1667 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5.6 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 7.1 | 2 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 8.8833 | 13 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 9 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 9.3333 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 10.9 | 6 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 23 | 6 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 25.25 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 28.98 | 3.22 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 30.6833 | 7 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 31.9167 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 34.1 | 11 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 36 | 15 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 36.75 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 45.4667 | 11 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 46 | 8 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 55 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 61.0167 | 7 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 61.95 | 7 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 76.05 | 13 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 78.5 | 10 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 111.6667 | 10 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 112.75 | 11 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 153.5 | 15 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 163.7333 | 16 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 183.7333 | 8 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 206.5 | 14 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 255.2667 | 14 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2 | 2 | 1 | 4 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2.3333 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 6.0667 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 16.03 | 2.29 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 20.4 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 55 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 65.8333 | 25 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 886.6662 | 760 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Other | BM | 100 | Fossil-Steam | WECC | Off-Peak | 38.584 | 59.36 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 0.95 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1 | 1 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1.2333 | 2 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3.1333 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3.8333 | 2 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 6.15 | 9 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 7.2 | 2 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 31.5 | 1.5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 48.6 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 54.5 | 10 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 55.6833 | 13 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 65.5 | 6 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 80.6667 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 153.2667 | 11 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 0.33333 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2.1 | 1 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3.35 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3.8667 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5.25 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 6.4 | 2 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 6.9 | 9 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 7.3333 | 8 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 7.4 | 6 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 9.4333 | 2 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 10 | 2 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 10.8 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 10.8167 | 11 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 11.0833 | 7 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 11.2 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 12.2 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 14.1167 | 7 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 15.8667 | 7 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 16.1333 | 11 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 16.45 | 7 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 19.4 | 6 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 22.8 | 2 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 23.3333 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 23.7333 | 16 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 30.85 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 32.0833 | 11 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 33.25 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 35.5833 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 36.3 | 11 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 38.6 | 12 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 45.6 | 16 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 47.4 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 49.1 | 6 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 49.6167 | 13 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 50.0333 | 19 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 70.7 | 14 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 71 | 10 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 93.5 | 10 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 107.5 | 6 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 110.3333 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 113 | 10 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 124 | 12 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 174.9333 | 16 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1377.5 | 95 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3335 | 145 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 5557.5 | 190 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1.7 | 2 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2 | 1 | 2 | 2 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 7.7333 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 8.8 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 9 | 1.8 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 17.4 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 19 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 19.7 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 37.15 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 612.3399 | 216.12 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 6540.6497 | 771 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Other | BM | 100 | Fossil-Steam | WECC | Off-Peak | 670.768 | 59.36 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1.2833 | 7 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1.3 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2.75 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3.4 | 6 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3.4167 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3.6667 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3.7 | 2 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3.9 | 6 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4.3 | 6 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4.4 | 6 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 5.5 | 2 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 8.0667 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 12.54 | 1.14 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 14.4667 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 15.2 | 6 | 2 | 2 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 16.5 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 24.9 | 18 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 28.05 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 87.75 | 45 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 117 | 9 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 238 | 14 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 324 | 18 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 0.15 | 3 | 2 | 2 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 0.4 | 2 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1.8667 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2 | 8 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2.6 | 6 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3.3 | 9 | 2 | 2 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3.8333 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4.1 | 2 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4.2 | 9 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4.5333 | 2 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4.9333 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 7.2333 | 14 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 8.0167 | 1 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 8.5333 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 8.6333 | 14 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 9.8333 | 10 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10 | 2.5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 11.1 | 9 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 12.3667 | 2 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 15 | 2.5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 15 | 6 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 15 | 30 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 15.3333 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 22 | 11 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 23.8333 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 24.5 | 14 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 25.7833 | 13 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 27.8 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 28.1333 | 8 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 29 | 10 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 31.4667 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 34.4167 | 7 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 39.3333 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 47.25 | 7 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 50 | 6 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 50.3 | 6 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 53.7167 | 11 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 77.7 | 7 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 81.3167 | 7 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 83.65 | 7 | 1 | 2 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 89.4 | 12 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 89.8333 | 7 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 96.8 | 11 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 101.25 | 9 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 152.75 | 13 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 184.0667 | 11 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 202.6667 | 10 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 219.25 | 15 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 297.05 | 13 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1244.8332 | 194 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 5249.5832 | 215 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3 | 1.5 | 1 | 2 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3.6 | 8 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4 | 2 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 11.0667 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 12 | 6 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 19.25 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 103.75 | 15 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3240.6667 | 20 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 95 | 5 | 1 | 1 | 0530-Other main steam system problems | D3-Forced - Postponed | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | SF | Startup Failure | 2013 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 1156.5 | 771 | 1 | 1 | 0530-Other main steam system problems | SF-Startup Failure | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | SF | Startup Failure | 2013 | Oil | OO | 100 | Fossil-Steam | NPCC | Off-Peak | 1643.5 | 190 | 1 | 1 | 0530-Other main steam system problems | SF-Startup Failure | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 938.0495 | 771 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Other | BM | 100 | Fossil-Steam | WECC | Off-Peak | 37.5946 | 59.36 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 0.2 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1.6 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2.75 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2.8 | 2 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2.9333 | 2 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4.35 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 5 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 5.7 | 2 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 6.4667 | 2 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 6.6667 | 8 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 8.9833 | 7 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 11.25 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 16 | 2 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 16.35 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 29.7 | 6 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 38.55 | 9 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 55.95 | 9 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 206.85 | 9 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 432 | 18 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 0.16667 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 0.7 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2 | 2 | 1 | 2 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2.3 | 2 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4 | 2 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6 | 2 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 6.2 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 7.5 | 10 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 9.1667 | 2 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 11.1667 | 2 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 11.3333 | 8 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 12.6 | 9 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 14.6667 | 8 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 19.4833 | 7 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 21.8333 | 5 | 1 | 2 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 23.8 | 6 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 28.6667 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 35.9167 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 38.2667 | 14 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 39.75 | 9 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 45.8333 | 11 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 46.25 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 61.2 | 12 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 63.6 | 6 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 66.9167 | 11 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 69.5333 | 14 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 72.5 | 6 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 73.85 | 7 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 90.5667 | 19 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 95.6667 | 10 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 97.5333 | 11 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 116.5333 | 8 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 126 | 9 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 131.0833 | 11 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 168.9333 | 14 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 187.4167 | 13 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 0.83333 | 2 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5 | 2.5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 10.55 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 15.2 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 11.3333 | 5 | 1 | 1 | 0530-Other main steam system problems | D3-Forced - Postponed | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 96 | 4 | 1 | 1 | 0530-Other main steam system problems | D3-Forced - Postponed | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 1228.5 | 455 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Other | BM | 100 | Fossil-Steam | WECC | Off-Peak | 34.6266 | 59.36 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1.8667 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3.8333 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4 | 6 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6 | 1 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 6.45 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 12.6333 | 2 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 17 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 17.0667 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 23.2 | 12 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 26.0833 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 31.75 | 15 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 44 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 52.6667 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 63.1167 | 7 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 86.3333 | 70 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 110.3333 | 10 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 125.85 | 9 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 407.1666 | 70 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 0.46666 | 7 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1.3333 | 16 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1.35 | 9 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1.4 | 14 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2.0333 | 2 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2.1333 | 8 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2.6333 | 2 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3.9 | 9 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4.7667 | 11 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4.8 | 8 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 6.05 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 8.4 | 9 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 8.9333 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 13.7333 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 16.8 | 6 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 19.3667 | 7 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 19.5 | 9 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 32.25 | 9 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 33.2667 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 46.3 | 6 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 58.6 | 6 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 59.6167 | 7 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 70.9333 | 14 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 72.6 | 11 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 85.1667 | 14 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 142.8333 | 10 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 206.4833 | 13 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 207.2 | 16 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1237.4999 | 270 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3.1667 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4.65 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 6.1667 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 6.4167 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 10.6 | 4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 11 | 2.75 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 12.4 | 2 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 37.6833 | 7 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3310.6666 | 191 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 266 | 190 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 2729.8333 | 110 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 3060.75 | 77 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 58039.5499 | 393 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 454.4583 | 83.9 | 1 | 1 | 0530-Other main steam system problems | U2-Forced - Delayed | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Geothermal | GE | 830 | Geothermal | WECC | Winter | 5.7517 | 20.3 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 830-Geothermal
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Geothermal | GE | 830 | Geothermal | WECC | Off-Peak | 14 | 2 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 830-Geothermal
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Geothermal | GE | 830 | Geothermal | WECC | Off-Peak | 144 | 18 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 830-Geothermal
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Geothermal | GE | 830 | Geothermal | WECC | Winter | 1.95 | 13 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 830-Geothermal
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Geothermal | GE | 830 | Geothermal | WECC | Winter | 6 | 15 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 830-Geothermal
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Geothermal | GE | 830 | Geothermal | WECC | Off-Peak | 42 | 21 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 830-Geothermal
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Geothermal | GE | 830 | Geothermal | WECC | Off-Peak | 240 | 30 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 830-Geothermal
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Geothermal | GE | 830 | Geothermal | WECC | Winter | 21.6 | 14.4 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 830-Geothermal
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Geothermal | GE | 830 | Geothermal | WECC | Off-Peak | 5.64 | 1.88 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 830-Geothermal
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Geothermal | GE | 830 | Geothermal | WECC | Winter | 18.75 | 12.5 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 830-Geothermal
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Geothermal | GE | 830 | Geothermal | WECC | Winter | 3.25 | 15 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 830-Geothermal
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Geothermal | GE | 830 | Geothermal | WECC | Winter | 4.5717 | 21.1 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 830-Geothermal
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Geothermal | GE | 830 | Geothermal | WECC | Off-Peak | 504 | 42 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 830-Geothermal
0530 | Other main steam system problems | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2013 | Gas | GG | 850 | Combined Cycle Block | TRE | Off-Peak | 241.144 | 301.43 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 850-Combined Cycle Block
0530 | Other main steam system problems | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2013 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 268.3667 | 2 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 850-Combined Cycle Block
0530 | Other main steam system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 7107.4166 | 173 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 850-Combined Cycle Block
0530 | Other main steam system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 1068.1667 | 26 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 850-Combined Cycle Block
0530 | Other main steam system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 1133.6 | 48 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 850-Combined Cycle Block
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 10653.333 | 470 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 23141.25 | 605 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U2-Forced - Delayed | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | U3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 33040.3498 | 459 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U3-Forced - Postponed | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 86739 | 580 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U2-Forced - Delayed | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 21868.2665 | 524 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 165.953 | 18.93 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 78222.6663 | 580 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 24763.05 | 249 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6155.9999 | 243 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 800 | Miscellaneous | SERC | Summer | 21939.9998 | 240 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 800-Miscellaneous
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 6652.6166 | 304.7 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 850-Combined Cycle Block
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U3 | Forced - Postponed | 2013 | Gas | GG | 850 | Combined Cycle Block | MRO | Off-Peak | 9377.9999 | 270 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U3-Forced - Postponed | 850-Combined Cycle Block
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 170066 | 248 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 850-Combined Cycle Block
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2013 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 5061.3331 | 365 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 850-Combined Cycle Block
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 29884.1498 | 249 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 850-Combined Cycle Block
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 851 | CC GT units | WECC | Winter | 4388.1786 | 168.56 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 851-CC GT units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 851 | CC GT units | SERC | Winter | 457.4666 | 188 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 851-CC GT units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 16819.3083 | 108.5 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 852-CC steam units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 852 | CC steam units | TRE | Summer | 7068.5 | 335 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 852-CC steam units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 48922.65 | 108.5 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 852-CC steam units
0541 | Cold reheat steam piping up to boiler | Boiler | Boiler Piping System | U3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1867.0166 | 91 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | U3-Forced - Postponed | 100-Fossil-Steam
0541 | Cold reheat steam piping up to boiler | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Waste Heat | WH | 100 | Fossil-Steam | WECC | Winter | 62.8115 | 289.9 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | U1-Forced - Immediate | 100-Fossil-Steam
0541 | Cold reheat steam piping up to boiler | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 37263.1664 | 710 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | U2-Forced - Delayed | 100-Fossil-Steam
0541 | Cold reheat steam piping up to boiler | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Oil | DI | 100 | Fossil-Steam | NPCC | Winter | 5448.0833 | 107 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | U1-Forced - Immediate | 100-Fossil-Steam
0541 | Cold reheat steam piping up to boiler | Boiler | Boiler Piping System | SF | Startup Failure | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 411977.9165 | 575 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | SF-Startup Failure | 100-Fossil-Steam
0541 | Cold reheat steam piping up to boiler | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 36515.4666 | 152 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | U1-Forced - Immediate | 100-Fossil-Steam
0541 | Cold reheat steam piping up to boiler | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 118660 | 850 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | U1-Forced - Immediate | 100-Fossil-Steam
0541 | Cold reheat steam piping up to boiler | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 14708.3998 | 612 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | U1-Forced - Immediate | 100-Fossil-Steam
0541 | Cold reheat steam piping up to boiler | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 120657.5 | 850 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | U1-Forced - Immediate | 100-Fossil-Steam
0541 | Cold reheat steam piping up to boiler | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2013 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 647.9249 | 146.7 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | D1-Forced - Immediate | 850-Combined Cycle Block
0541 | Cold reheat steam piping up to boiler | HRSG Boiler | HRSG Boiler Piping System | D2 | Forced - Delayed | 2013 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 4440.8 | 364 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | D2-Forced - Delayed | 850-Combined Cycle Block
0541 | Cold reheat steam piping up to boiler | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 5872.425 | 602.3 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | U1-Forced - Immediate | 850-Combined Cycle Block
0541 | Cold reheat steam piping up to boiler | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2013 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 2858.0332 | 358 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | D1-Forced - Immediate | 850-Combined Cycle Block
0541 | Cold reheat steam piping up to boiler | HRSG Boiler | HRSG Boiler Piping System | U2 | Forced - Delayed | 2013 | Gas | GG | 851 | CC GT units | WECC | Summer | 84034.5999 | 156 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | U2-Forced - Delayed | 851-CC GT units
0541 | Cold reheat steam piping up to boiler | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 65180.6833 | 121 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | D1-Forced - Immediate | 852-CC steam units
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 57983.3333 | 56 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 96.8333 | 10 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 1155 | 15 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 576.2165 | 449 | 1 | 1 | 0550-Reheat steam relief/safety valves | D3-Forced - Postponed | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 867.5 | 30 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2317.05 | 271 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 746.9 | 77 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 75 | 50 | 1 | 1 | 0550-Reheat steam relief/safety valves | D3-Forced - Postponed | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 135.3333 | 35 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 65.3333 | 14 | 1 | 1 | 0550-Reheat steam relief/safety valves | D2-Forced - Delayed | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 606.8333 | 110 | 1 | 1 | 0550-Reheat steam relief/safety valves | U1-Forced - Immediate | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4088 | 56 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 142.5 | 15 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 751.75 | 15 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 1136.6666 | 110 | 1 | 1 | 0550-Reheat steam relief/safety valves | U1-Forced - Immediate | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 10 | 40 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 10233.0666 | 56 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 6382.9333 | 88 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1410 | 200 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 227.5 | 35 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 37582 | 760 | 1 | 1 | 0550-Reheat steam relief/safety valves | U1-Forced - Immediate | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 49309.3333 | 110 | 1 | 1 | 0550-Reheat steam relief/safety valves | U1-Forced - Immediate | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 14520 | 528 | 1 | 1 | 0550-Reheat steam relief/safety valves | U1-Forced - Immediate | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 851 | CC GT units | TRE | Summer | 11679.15 | 147 | 1 | 1 | 0550-Reheat steam relief/safety valves | U1-Forced - Immediate | 851-CC GT units
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 12729.1332 | 164 | 1 | 1 | 0550-Reheat steam relief/safety valves | U1-Forced - Immediate | 851-CC GT units
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 851 | CC GT units | TRE | Summer | 11648.3666 | 146 | 1 | 1 | 0550-Reheat steam relief/safety valves | U1-Forced - Immediate | 851-CC GT units
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 26001 | 321 | 1 | 1 | 0550-Reheat steam relief/safety valves | U1-Forced - Immediate | 852-CC steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1857.4999 | 150 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 100-Fossil-Steam
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6624 | 288 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 100-Fossil-Steam
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 58787.2999 | 429 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 650-Fluidized Bed
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2013 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 112 | 320 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 850-Combined Cycle Block
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2013 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 1099.9999 | 375 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 850-Combined Cycle Block
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 851 | CC GT units | TRE | Summer | 12842.75 | 141 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 851 | CC GT units | RFC | Summer | 2190.9166 | 152.5 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 851 | CC GT units | RFC | Summer | 179.4 | 156 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 851 | CC GT units | TRE | Summer | 255.75 | 155 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 851 | CC GT units | RFC | Winter | 40082.7832 | 167 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 851 | CC GT units | SERC | Summer | 7.255 | 145.1 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 851 | CC GT units | TRE | Summer | 521.9999 | 216 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 851 | CC GT units | WECC | Winter | 959.8665 | 184 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 851 | CC GT units | TRE | Winter | 1012.85 | 141 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 851 | CC GT units | WECC | Winter | 524.4 | 184 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 488.75 | 75 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 290.7 | 102 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 235.6249 | 97.5 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 78.3 | 174 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 852-CC steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 140.25 | 85 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2013 | Gas | GG | 852 | CC steam units | RFC | Winter | 30962.1499 | 129 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 76.5 | 127.5 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 1506.6249 | 127.5 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 280.5 | 127.5 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 140.25 | 255 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 852-CC steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 861 | CoG GT units | TRE | Off-Peak | 615.9999 | 165 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 861-CoG GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 862 | CoG steam units | TRE | Off-Peak | 336 | 90 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 862-CoG steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Waste Heat | WH | 862 | CoG steam units | TRE | Off-Peak | 137.8666 | 176 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 862-CoG steam units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 14433.6665 | 380 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 100-Fossil-Steam
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 3223.1 | 167 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 180.9665 | 178 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 1277.55 | 167 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 16.7 | 167 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 98.2665 | 268 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 852-CC steam units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 15.8 | 158 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 95.5666 | 94 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 1208.7 | 158 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 3049.4 | 158 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 20.9999 | 180 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 852-CC steam units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 8.9332 | 268 | 1 | 3 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 852-CC steam units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2013 | Gas | GG | 861 | CoG GT units | TRE | Winter | 13104.5833 | 175 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U2-Forced - Delayed | 861-CoG GT units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2013 | Waste Heat | WH | 862 | CoG steam units | TRE | Winter | 6814.3833 | 91 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | D2-Forced - Delayed | 862-CoG steam units
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 5.8 | 6 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 23 | 10 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 23.5667 | 7 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2 | 2 | 1 | 7 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 6.3 | 9 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8 | 1.6 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8.01 | 2.67 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10 | 2.5 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 18 | 4.5 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 24 | 9 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 69.18 | 11.53 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 71.1667 | 7 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 94.5 | 10 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 95.8848 | 4.13 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 98 | 2.45 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 106.7 | 11 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 156.3833 | 11 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 180.1333 | 14 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 185.7 | 18 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 185.8667 | 17 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4 | 2 | 1 | 3 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 7.4 | 4 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 13.2 | 3 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 14.96 | 1.87 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 17.25 | 3 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 21.4667 | 4 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 71.1 | 9 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 94.0833 | 5 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 502.2 | 18 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 575.7333 | 68 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3628.1 | 511 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 6.65 | 7 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 317.5498 | 261 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 864.1666 | 305 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3.99 | 1.33 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4.8 | 9 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5.01 | 1.67 | 1 | 3 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6 | 2 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7 | 1.75 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9 | 1.5 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 11 | 10 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 11.01 | 3.67 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 14 | 2.8 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 17.7333 | 14 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 18.9 | 7 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 25.25 | 15 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 54.5 | 15 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 66.3833 | 7 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 73.92 | 3.36 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5 | 1.25 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 11 | 2.2 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 11 | 4 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 772.2 | 429 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 8.9332 | 268 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 17.8 | 3 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 48 | 12 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 203.315 | 47.1 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1 | 1 | 1 | 21 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2.6 | 3 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2.8 | 6 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6 | 3 | 1 | 2 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 7.0833 | 17 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9 | 1.8 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 25.75 | 15 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 32.5 | 15 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 48.93 | 2.33 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 52 | 3.25 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 87.9667 | 14 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 122.2833 | 11 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 131 | 6 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 198.9333 | 16 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1 | 1 | 2 | 14 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3 | 3 | 2 | 3 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 7 | 1.4 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 15.8 | 6 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 18.5833 | 5 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 29.5 | 6 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 12.5833 | 5 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 328.35 | 33 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2.3 | 6 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4 | 4 | 1 | 2 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5 | 5 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6 | 6 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 10.2 | 6 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 11.8333 | 10 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 12.3667 | 14 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 21.4667 | 8 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 84.9 | 2.83 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 154.0508 | 4.01 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 288 | 12 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 381.8 | 4 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 0.33333 | 5 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2 | 1 | 1 | 3 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3.4 | 2 | 1 | 2 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4 | 4 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 10 | 2 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 12.5 | 2 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 13 | 3.25 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 144 | 6 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 10073.0664 | 352 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 49444.6331 | 598 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1 | 1 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 41.7 | 6 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 49.4167 | 5 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 52.6999 | 186 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 67 | 268 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 128.05 | 13 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4.5 | 9 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 79.7335 | 3.99 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 107.6 | 12 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 116.2333 | 11 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 141.1 | 6 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 262.6667 | 16 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 363.1333 | 4 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 420.42 | 5.39 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1513.6 | 4 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6 | 3 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 11 | 5.5 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 12.3333 | 5 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 26.8 | 3 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 58.8 | 3 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 104.3333 | 5 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 125.6 | 6 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 471.3333 | 28 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 5472 | 38 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | SF | Startup Failure | 2013 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 3371.25 | 775 | 1 | 1 | 0570-Other reheat steam problems | SF-Startup Failure | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Waste Heat | WH | 100 | Fossil-Steam | WECC | Off-Peak | 362.25 | 289.8 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1.7 | 2 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 7.6 | 8 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 68.7165 | 217 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 697.865 | 47.1 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 0.6 | 6 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1.2 | 8 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1.5 | 15 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1.75 | 15 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7 | 3.5 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9 | 2.25 | 2 | 3 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 13 | 13 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 16 | 4 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 25 | 5 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 37.3333 | 5 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 37.6 | 6 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 434.4667 | 4 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 6.5333 | 2 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 12.55 | 3 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 12.99 | 4.33 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 15.3333 | 5 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 21.96 | 2.44 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 25.5 | 5 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 100.9515 | 51.77 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 522.6666 | 28 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 758.7999 | 168 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2078.6667 | 8 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 664.95 | 429 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 13.9 | 3 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 33.75 | 3 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3 | 3 | 1 | 10 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6.99 | 2.33 | 1 | 2 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 12.96 | 1.62 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 14 | 3.5 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 30.94 | 1.82 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 49.4667 | 14 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 57.8 | 12 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 305.1382 | 4.13 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2.6 | 6 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3 | 1.5 | 1 | 3 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6 | 1 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6 | 1.2 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 61.1 | 2.35 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 659.75 | 13 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 2.25 | 3 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1.8167 | 1 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 20 | 8 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 20.2 | 6 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 66.1333 | 8 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 94.1333 | 8 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 219.5833 | 85 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 317.1332 | 268 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3 | 1 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3 | 1.5 | 1 | 8 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3.36 | 1.12 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4 | 2 | 1 | 4 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 11 | 2.75 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 11.85 | 3 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 24 | 12 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 24.9667 | 14 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 91.85 | 11 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 100.3333 | 10 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 120.2 | 12 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 218.75 | 15 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 0.41667 | 5 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2 | 2 | 2 | 3 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4 | 4 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5 | 2.5 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 6.2 | 4 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 11.4667 | 8 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 13.25 | 5 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 16.2 | 6 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 20 | 2 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 54.6 | 6 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 34151.6661 | 775 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 800 | Miscellaneous | MRO | Winter | 6279.895 | 286.1 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 800-Miscellaneous
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 121.1163 | 559 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 850-Combined Cycle Block
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | D2 | Forced - Delayed | 2013 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 3084.5997 | 477 | 1 | 1 | 0570-Other reheat steam problems | D2-Forced - Delayed | 850-Combined Cycle Block
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2013 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 1210.5831 | 365 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 850-Combined Cycle Block
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 6991.7333 | 157 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 851-CC GT units
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 851 | CC GT units | SERC | Summer | 5552.7 | 166 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 851-CC GT units
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 851 | CC GT units | SERC | Summer | 2416.2666 | 164 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 851-CC GT units
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 851 | CC GT units | WECC | Winter | 16.4149 | 196.98 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 851-CC GT units
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 851 | CC GT units | RFC | Winter | 220.8 | 192 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 851-CC GT units
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2013 | Gas | GG | 852 | CC steam units | SERC | Summer | 1629.5999 | 144 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 852-CC steam units
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 1517.5333 | 103 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 852-CC steam units
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 852 | CC steam units | RFC | Winter | 543.25 | 265 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 852-CC steam units
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 4052.5333 | 91 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 852-CC steam units
0580 | Desuperheater/attemperator piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 8723.1996 | 564 | 1 | 1 | 0580-Desuperheater/attemperator piping | U1-Forced - Immediate | 100-Fossil-Steam
0580 | Desuperheater/attemperator piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 725 | 100 | 1 | 1 | 0580-Desuperheater/attemperator piping | D1-Forced - Immediate | 100-Fossil-Steam
0580 | Desuperheater/attemperator piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6534.6662 | 676 | 1 | 1 | 0580-Desuperheater/attemperator piping | U1-Forced - Immediate | 100-Fossil-Steam
0580 | Desuperheater/attemperator piping | Boiler | Boiler Piping System | SF | Startup Failure | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1819.3 | 138 | 1 | 1 | 0580-Desuperheater/attemperator piping | SF-Startup Failure | 100-Fossil-Steam
0580 | Desuperheater/attemperator piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1628 | 60 | 1 | 1 | 0580-Desuperheater/attemperator piping | D1-Forced - Immediate | 100-Fossil-Steam
0580 | Desuperheater/attemperator piping | Boiler | Boiler Piping System | SF | Startup Failure | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 12059.9998 | 270 | 1 | 1 | 0580-Desuperheater/attemperator piping | SF-Startup Failure | 100-Fossil-Steam
0580 | Desuperheater/attemperator piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 32656.5 | 615 | 1 | 1 | 0580-Desuperheater/attemperator piping | U1-Forced - Immediate | 100-Fossil-Steam
0580 | Desuperheater/attemperator piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 20 | 10 | 1 | 1 | 0580-Desuperheater/attemperator piping | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 360.15 | 343 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 421.1666 | 95 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 383.3333 | 125 | 1 | 1 | 0590-Desuperheater/attemperator valves | D2-Forced - Delayed | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 199.7499 | 141 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 78 | 20 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 238.4 | 32 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1053.6666 | 290 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 339.066 | 14.04 | 1 | 1 | 0590-Desuperheater/attemperator valves | D2-Forced - Delayed | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 264.0166 | 73 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 817.705 | 38.3 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1664 | 128 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 300.8 | 141 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 676 | 130 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 177.3332 | 152 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 0 | 0 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 223.8332 | 170 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 11187.1665 | 602 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 150.1 | 57 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2795.65 | 221 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 365.8 | 124 | 1 | 1 | 0590-Desuperheater/attemperator valves | D2-Forced - Delayed | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2013 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 1611.7498 | 315 | 1 | 1 | 0590-Desuperheater/attemperator valves | D2-Forced - Delayed | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 388.6332 | 262 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 17.5666 | 31 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1276 | 116 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 26454.95 | 149 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 931 | 133 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1550 | 155 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D3 | Forced - Postponed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 2205.4332 | 218 | 1 | 1 | 0590-Desuperheater/attemperator valves | D3-Forced - Postponed | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2027.6316 | 322.7 | 1 | 1 | 0590-Desuperheater/attemperator valves | U1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 75947.25 | 393 | 1 | 1 | 0590-Desuperheater/attemperator valves | U1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 22.3166 | 103 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 63 | 3 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 129.0332 | 158 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 475 | 100 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1745.0666 | 128 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3361.0999 | 366 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 6819.7666 | 109 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 15762.4 | 68 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 576 | 96 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 0.49998 | 30 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 801.6666 | 130 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 590 | 118 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 107 | 21.4 | 1 | 1 | 0590-Desuperheater/attemperator valves | D2-Forced - Delayed | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 34895.8331 | 335 | 1 | 1 | 0590-Desuperheater/attemperator valves | U1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 66.1333 | 64 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 17775.4 | 188 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 145.1833 | 31 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 477.8333 | 122 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1688.8666 | 308 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2233.4999 | 90 | 1 | 1 | 0590-Desuperheater/attemperator valves | U1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3700.804 | 260.62 | 1 | 1 | 0590-Desuperheater/attemperator valves | U2-Forced - Delayed | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 257.15 | 139 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4098 | 45 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1005.8665 | 368 | 1 | 1 | 0590-Desuperheater/attemperator valves | D2-Forced - Delayed | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D3 | Forced - Postponed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 3396.6 | 222 | 1 | 1 | 0590-Desuperheater/attemperator valves | D3-Forced - Postponed | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 5961.9199 | 180.3 | 1 | 1 | 0590-Desuperheater/attemperator valves | U1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Other | WD | 650 | Fluidized Bed | RFC | Winter | 2225.8333 | 50 | 1 | 1 | 0590-Desuperheater/attemperator valves | U1-Forced - Immediate | 650-Fluidized Bed
0600 | Desuperheater/attemperator spray nozzles | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2486.25 | 13 | 1 | 1 | 0600-Desuperheater/attemperator spray nozzles | D1-Forced - Immediate | 100-Fossil-Steam
0600 | Desuperheater/attemperator spray nozzles | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 102.6666 | 110 | 1 | 1 | 0600-Desuperheater/attemperator spray nozzles | D1-Forced - Immediate | 100-Fossil-Steam
0610 | Desuperheater/attemperator drums | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 883.4999 | 342 | 1 | 1 | 0610-Desuperheater/attemperator drums | U1-Forced - Immediate | 100-Fossil-Steam
0610 | Desuperheater/attemperator drums | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 45.3 | 18 | 1 | 1 | 0610-Desuperheater/attemperator drums | D1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4.75 | 19 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 27.5333 | 28 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 218.9164 | 355 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 32 | 64 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5187.6 | 198 | 1 | 1 | 0620-Other desuperheater/attemperator problems | U1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 85.5 | 90 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 161.85 | 9 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1167.8333 | 130 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 562.6667 | 16 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 102.6666 | 70 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3.85 | 21 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 12.75 | 9 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 106.5666 | 46 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1702 | 37 | 1 | 1 | 0620-Other desuperheater/attemperator problems | U1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 36.8332 | 170 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 802.6667 | 16 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 4830.1333 | 16 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1921.8333 | 130 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3117.8333 | 130 | 1 | 2 | 0620-Other desuperheater/attemperator problems | D1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2013 | NULL | NULL | 100 | Fossil-Steam | RFC | Off-Peak | NULL | NULL | 1 | 1 | 0620-Other desuperheater/attemperator problems | U2-Forced - Delayed | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 13469.1 | 417 | 1 | 1 | 0620-Other desuperheater/attemperator problems | U2-Forced - Delayed | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | U3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 19659.0624 | 156.75 | 1 | 1 | 0620-Other desuperheater/attemperator problems | U3-Forced - Postponed | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 721.5996 | 528 | 1 | 1 | 0620-Other desuperheater/attemperator problems | U1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 687.6333 | 98 | 1 | 1 | 0620-Other desuperheater/attemperator problems | U1-Forced - Immediate | 100-Fossil-Steam
0630 | Startup bypass system piping (including drain lines up to heaters or condenser) | Boiler | Boiler Piping System | SF | Startup Failure | 2013 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 25961.4662 | 682 | 1 | 1 | 0630-Startup bypass system piping (including drain lines up to heaters or condenser) | SF-Startup Failure | 100-Fossil-Steam
0630 | Startup bypass system piping (including drain lines up to heaters or condenser) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2480.6663 | 610 | 1 | 1 | 0630-Startup bypass system piping (including drain lines up to heaters or condenser) | U1-Forced - Immediate | 100-Fossil-Steam
0630 | Startup bypass system piping (including drain lines up to heaters or condenser) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1936.6666 | 200 | 1 | 1 | 0630-Startup bypass system piping (including drain lines up to heaters or condenser) | U1-Forced - Immediate | 100-Fossil-Steam
0630 | Startup bypass system piping (including drain lines up to heaters or condenser) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2325.6496 | 579 | 1 | 1 | 0630-Startup bypass system piping (including drain lines up to heaters or condenser) | U1-Forced - Immediate | 100-Fossil-Steam
0630 | Startup bypass system piping (including drain lines up to heaters or condenser) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 9614.5 | 469 | 1 | 1 | 0630-Startup bypass system piping (including drain lines up to heaters or condenser) | U1-Forced - Immediate | 100-Fossil-Steam
0630 | Startup bypass system piping (including drain lines up to heaters or condenser) | Boiler | Boiler Piping System | SF | Startup Failure | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 23345.8329 | 650 | 1 | 1 | 0630-Startup bypass system piping (including drain lines up to heaters or condenser) | SF-Startup Failure | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | SF | Startup Failure | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 11211 | 606 | 1 | 1 | 0640-Startup bypass system valves | SF-Startup Failure | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 39401.775 | 605.25 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 20160 | 800 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 12361.9994 | 840 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 6300 | 840 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1612 | 80 | 1 | 1 | 0640-Startup bypass system valves | D1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 380.8 | 24 | 1 | 1 | 0640-Startup bypass system valves | D1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 22535.3328 | 770 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 44869.9994 | 840 | 1 | 1 | 0640-Startup bypass system valves | U2-Forced - Delayed | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 128.25 | 15 | 1 | 1 | 0640-Startup bypass system valves | D1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2637.6 | 336 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4153.3331 | 700 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 9863.683 | 527 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 31807.9994 | 840 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 3797.5 | 775 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 58451.6661 | 850 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2263.3331 | 700 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2943.7329 | 581 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 18046.5371 | 605.25 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 5767.9994 | 840 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 13369.9994 | 840 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 3374.85 | 453 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 9.083 | 545 | 1 | 2 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4400.7832 | 469 | 1 | 1 | 0640-Startup bypass system valves | U2-Forced - Delayed | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 30966.6664 | 400 | 1 | 1 | 0640-Startup bypass system valves | D1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | SF | Startup Failure | 2013 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 1575.8331 | 775 | 1 | 1 | 0640-Startup bypass system valves | SF-Startup Failure | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1542.1663 | 487 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 63362.4996 | 1110 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 10737.9997 | 840 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4918.6665 | 620 | 1 | 1 | 0640-Startup bypass system valves | U2-Forced - Delayed | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 475.4167 | 25 | 1 | 1 | 0640-Startup bypass system valves | D1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 6131.1997 | 768 | 1 | 1 | 0640-Startup bypass system valves | D1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | SF | Startup Failure | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9387.8164 | 469 | 1 | 1 | 0640-Startup bypass system valves | SF-Startup Failure | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | SF | Startup Failure | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 16046.25 | 825 | 1 | 1 | 0640-Startup bypass system valves | SF-Startup Failure | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | SF | Startup Failure | 2013 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 5968 | 746 | 1 | 1 | 0640-Startup bypass system valves | SF-Startup Failure | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4363.3331 | 595 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 67816.1665 | 545 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 3339.7498 | 657 | 1 | 1 | 0640-Startup bypass system valves | D1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | SF | Startup Failure | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 474 | 158 | 1 | 1 | 0640-Startup bypass system valves | SF-Startup Failure | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | SF | Startup Failure | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 15587.833 | 431 | 1 | 1 | 0640-Startup bypass system valves | SF-Startup Failure | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | SF | Startup Failure | 2013 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 1074.4497 | 495.9 | 1 | 1 | 0640-Startup bypass system valves | SF-Startup Failure | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | SF | Startup Failure | 2013 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 2643.25 | 545 | 1 | 1 | 0640-Startup bypass system valves | SF-Startup Failure | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 63.583 | 545 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 52771.2 | 736 | 1 | 1 | 0640-Startup bypass system valves | U2-Forced - Delayed | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 22554 | 840 | 1 | 1 | 0640-Startup bypass system valves | U2-Forced - Delayed | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U3 | Forced - Postponed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 10710 | 840 | 1 | 1 | 0640-Startup bypass system valves | U3-Forced - Postponed | 100-Fossil-Steam
0650 | Startup bypass tanks or flash tanks | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 63.583 | 545 | 1 | 1 | 0650-Startup bypass tanks or flash tanks | U1-Forced - Immediate | 100-Fossil-Steam
0650 | Startup bypass tanks or flash tanks | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 65.2433 | 85.1 | 1 | 1 | 0650-Startup bypass tanks or flash tanks | D1-Forced - Immediate | 100-Fossil-Steam
0650 | Startup bypass tanks or flash tanks | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10516.3665 | 638 | 1 | 1 | 0650-Startup bypass tanks or flash tanks | U1-Forced - Immediate | 100-Fossil-Steam
0655 | Steam by-pass system instrumentation and controls | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 2793.4997 | 453 | 1 | 1 | 0655-Steam by-pass system instrumentation and controls | U1-Forced - Immediate | 100-Fossil-Steam
0660 | Other startup bypass system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2368.8 | 658 | 1 | 1 | 0660-Other startup bypass system problems | U1-Forced - Immediate | 100-Fossil-Steam
0660 | Other startup bypass system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 143.75 | 75 | 1 | 1 | 0660-Other startup bypass system problems | D1-Forced - Immediate | 100-Fossil-Steam
0660 | Other startup bypass system problems | Boiler | Boiler Piping System | SF | Startup Failure | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3780.7997 | 816 | 1 | 1 | 0660-Other startup bypass system problems | SF-Startup Failure | 100-Fossil-Steam
0660 | Other startup bypass system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 822.12 | 88.4 | 1 | 1 | 0660-Other startup bypass system problems | D1-Forced - Immediate | 100-Fossil-Steam
0660 | Other startup bypass system problems | Boiler | Boiler Piping System | SF | Startup Failure | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 7928.7995 | 816 | 1 | 1 | 0660-Other startup bypass system problems | SF-Startup Failure | 100-Fossil-Steam
0660 | Other startup bypass system problems | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 13706.3665 | 638 | 1 | 1 | 0660-Other startup bypass system problems | U2-Forced - Delayed | 100-Fossil-Steam
0660 | Other startup bypass system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1198.9996 | 660 | 1 | 1 | 0660-Other startup bypass system problems | U1-Forced - Immediate | 100-Fossil-Steam
0660 | Other startup bypass system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1231.9996 | 660 | 1 | 1 | 0660-Other startup bypass system problems | U1-Forced - Immediate | 100-Fossil-Steam
0670 | Feedwater piping downstream of feedwater regulating valve | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10878.3 | 158 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | U1-Forced - Immediate | 100-Fossil-Steam
0670 | Feedwater piping downstream of feedwater regulating valve | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 2970.5664 | 406 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | U1-Forced - Immediate | 100-Fossil-Steam
0670 | Feedwater piping downstream of feedwater regulating valve | Boiler | Boiler Piping System | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2742.1099 | 273.3 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | D3-Forced - Postponed | 100-Fossil-Steam
0670 | Feedwater piping downstream of feedwater regulating valve | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 850 | Combined Cycle Block | MRO | Summer | 1783.4665 | 256 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | U1-Forced - Immediate | 850-Combined Cycle Block
0670 | Feedwater piping downstream of feedwater regulating valve | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2013 | Gas | GG | 850 | Combined Cycle Block | MRO | Summer | 535 | 25 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | D1-Forced - Immediate | 850-Combined Cycle Block
0670 | Feedwater piping downstream of feedwater regulating valve | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2013 | Gas | GG | 851 | CC GT units | SERC | Winter | 59.5 | 85 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | D1-Forced - Immediate | 851-CC GT units
0670 | Feedwater piping downstream of feedwater regulating valve | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2013 | Gas | GG | 851 | CC GT units | MRO | Winter | 3660.4167 | 35 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | D1-Forced - Immediate | 851-CC GT units
0670 | Feedwater piping downstream of feedwater regulating valve | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 851 | CC GT units | WECC | Winter | 1229.1499 | 183 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | U1-Forced - Immediate | 851-CC GT units
0670 | Feedwater piping downstream of feedwater regulating valve | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 821.6666 | 170 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | U1-Forced - Immediate | 851-CC GT units
0670 | Feedwater piping downstream of feedwater regulating valve | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 851 | CC GT units | MRO | Winter | 153.0666 | 164 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | U1-Forced - Immediate | 851-CC GT units
0670 | Feedwater piping downstream of feedwater regulating valve | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 851 | CC GT units | MRO | Winter | 155.8 | 164 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | U1-Forced - Immediate | 851-CC GT units
0670 | Feedwater piping downstream of feedwater regulating valve | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | SERC | Winter | 38.5 | 55 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | D1-Forced - Immediate | 852-CC steam units
0670 | Feedwater piping downstream of feedwater regulating valve | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | NPCC | Off-Peak | 463.4666 | 88 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | U1-Forced - Immediate | 852-CC steam units
0670 | Feedwater piping downstream of feedwater regulating valve | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 678.3833 | 101 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | D1-Forced - Immediate | 852-CC steam units
0670 | Feedwater piping downstream of feedwater regulating valve | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2013 | Gas | GG | 852 | CC steam units | MRO | Winter | 40 | 80 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | D1-Forced - Immediate | 852-CC steam units
0670 | Feedwater piping downstream of feedwater regulating valve | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 860 | Co-generator Block | TRE | Winter | 503.5499 | 81 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | U1-Forced - Immediate | 860-Co-generator Block
0670 | Feedwater piping downstream of feedwater regulating valve | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 860 | Co-generator Block | TRE | Winter | 1300.05 | 81 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | U1-Forced - Immediate | 860-Co-generator Block
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 162.9083 | 86.5 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 264.2082 | 186.5 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 34236.6666 | 200 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 4544.1665 | 190 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | U3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 51057.6 | 528 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U3-Forced - Postponed | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 23673.65 | 473 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U2-Forced - Delayed | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 371 | 53 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 1197.1666 | 110 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 12734.8664 | 406 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 35882.3015 | 538.1 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U2-Forced - Delayed | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | U3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5886.25 | 85 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U3-Forced - Postponed | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2033.625 | 280.5 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 13181.7 | 63 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 83902.75 | 545 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 168 | 84 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 188.5 | 39 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | U3 | Forced - Postponed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 24313 | 820 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U3-Forced - Postponed | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | U3 | Forced - Postponed | 2013 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 22576.3332 | 445 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U3-Forced - Postponed | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 14 | 7 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 3190.25 | 105 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2013 | Gas | GG | 850 | Combined Cycle Block | TRE | Off-Peak | 1230.25 | 259 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 850-Combined Cycle Block
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 2398.5 | 390 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 850-Combined Cycle Block
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 2756.5 | 370 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 850-Combined Cycle Block
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2013 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 6370.5 | 310 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 850-Combined Cycle Block
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 76.8499 | 159 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 851-CC GT units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 851 | CC GT units | MRO | Off-Peak | 155.8 | 164 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 851-CC GT units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 1179.75 | 143 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 851-CC GT units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 851 | CC GT units | TRE | Summer | 6566.8332 | 155 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 851-CC GT units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 851 | CC GT units | MRO | Off-Peak | 60.1332 | 164 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 851-CC GT units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 8.1333 | 61 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 851-CC GT units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 3389.3333 | 80 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 852-CC steam units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 60.4166 | 125 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 852-CC steam units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 281.25 | 75 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 852-CC steam units
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 68 | 17 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | D1-Forced - Immediate | 100-Fossil-Steam
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | Boiler | Boiler Piping System | SF | Startup Failure | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5086.3997 | 816 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | SF-Startup Failure | 100-Fossil-Steam
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 28 | 28 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | D1-Forced - Immediate | 100-Fossil-Steam
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 164.6666 | 52 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | D1-Forced - Immediate | 100-Fossil-Steam
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 478.44 | 35.44 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | D1-Forced - Immediate | 100-Fossil-Steam
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 851 | CC GT units | WECC | Winter | 173.7075 | 109.71 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | U1-Forced - Immediate | 851-CC GT units
0700 | Blowdown system valves A | Boiler | Boiler Piping System | SF | Startup Failure | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2396.5999 | 156.3 | 1 | 1 | 0700-Blowdown system valves A | SF-Startup Failure | 100-Fossil-Steam
0700 | Blowdown system valves A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 899.433 | 39.42 | 1 | 1 | 0700-Blowdown system valves A | U1-Forced - Immediate | 100-Fossil-Steam
0700 | Blowdown system valves A | Boiler | Boiler Piping System | U3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5690.4998 | 570 | 1 | 1 | 0700-Blowdown system valves A | U3-Forced - Postponed | 100-Fossil-Steam
0700 | Blowdown system valves A | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1380.4999 | 330 | 1 | 1 | 0700-Blowdown system valves A | D1-Forced - Immediate | 100-Fossil-Steam
0700 | Blowdown system valves A | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 5978.4 | 564 | 1 | 1 | 0700-Blowdown system valves A | U2-Forced - Delayed | 100-Fossil-Steam
0700 | Blowdown system valves A | Boiler | Boiler Piping System | U3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2982.25 | 151 | 1 | 1 | 0700-Blowdown system valves A | U3-Forced - Postponed | 100-Fossil-Steam
0700 | Blowdown system valves A | Boiler | Boiler Piping System | SF | Startup Failure | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 8088.3664 | 334 | 1 | 1 | 0700-Blowdown system valves A | SF-Startup Failure | 100-Fossil-Steam
0700 | Blowdown system valves A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 2111.85 | 24.7 | 1 | 1 | 0700-Blowdown system valves A | U1-Forced - Immediate | 100-Fossil-Steam
0700 | Blowdown system valves A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 345.8 | 24.7 | 1 | 1 | 0700-Blowdown system valves A | U1-Forced - Immediate | 100-Fossil-Steam
0700 | Blowdown system valves A | HRSG Boiler | HRSG Boiler Piping System | SF | Startup Failure | 2013 | Gas | GG | 851 | CC GT units | TRE | Winter | 148.3999 | 168 | 1 | 1 | 0700-Blowdown system valves A | SF-Startup Failure | 851-CC GT units
0700 | Blowdown system valves A | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 139.5666 | 158 | 1 | 1 | 0700-Blowdown system valves A | D1-Forced - Immediate | 852-CC steam units
0710 | Blowdown system piping B | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 60 | 60 | 1 | 1 | 0710-Blowdown system piping B | D1-Forced - Immediate | 100-Fossil-Steam
0710 | Blowdown system piping B | Boiler | Boiler Piping System | SF | Startup Failure | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 12138.2664 | 472 | 1 | 1 | 0710-Blowdown system piping B | SF-Startup Failure | 100-Fossil-Steam
0710 | Blowdown system piping B | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7568.4 | 238 | 1 | 1 | 0710-Blowdown system piping B | U1-Forced - Immediate | 100-Fossil-Steam
0710 | Blowdown system piping B | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 120 | 120 | 1 | 1 | 0710-Blowdown system piping B | D1-Forced - Immediate | 100-Fossil-Steam
0710 | Blowdown system piping B | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 643.5 | 330 | 1 | 1 | 0710-Blowdown system piping B | U1-Forced - Immediate | 100-Fossil-Steam
0710 | Blowdown system piping B | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 432 | 360 | 1 | 1 | 0710-Blowdown system piping B | D1-Forced - Immediate | 100-Fossil-Steam
0710 | Blowdown system piping B | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 180 | 180 | 1 | 1 | 0710-Blowdown system piping B | D1-Forced - Immediate | 100-Fossil-Steam
0710 | Blowdown system piping B | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 240 | 240 | 1 | 1 | 0710-Blowdown system piping B | D1-Forced - Immediate | 100-Fossil-Steam
0710 | Blowdown system piping B | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 300 | 300 | 1 | 1 | 0710-Blowdown system piping B | D1-Forced - Immediate | 100-Fossil-Steam
0710 | Blowdown system piping B | Boiler | Boiler Piping System | SF | Startup Failure | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 23523.75 | 615 | 1 | 1 | 0710-Blowdown system piping B | SF-Startup Failure | 100-Fossil-Steam
0710 | Blowdown system piping B | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 7083.8998 | 459 | 1 | 1 | 0710-Blowdown system piping B | U1-Forced - Immediate | 100-Fossil-Steam
0710 | Blowdown system piping B | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9471.75 | 365 | 1 | 1 | 0710-Blowdown system piping B | U2-Forced - Delayed | 100-Fossil-Steam
0710 | Blowdown system piping B | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 6247.9999 | 165 | 1 | 1 | 0710-Blowdown system piping B | U1-Forced - Immediate | 850-Combined Cycle Block
0720 | Blowdown system controls / instrumentation | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 247.5 | 66 | 1 | 1 | 0720-Blowdown system controls / instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0730 | Other blowdown system problems | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 934.7 | 78 | 1 | 1 | 0730-Other blowdown system problems | D2-Forced - Delayed | 100-Fossil-Steam
0730 | Other blowdown system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 654.75 | 27 | 1 | 1 | 0730-Other blowdown system problems | D1-Forced - Immediate | 100-Fossil-Steam
0730 | Other blowdown system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Off-Peak | 59.5 | 35 | 1 | 1 | 0730-Other blowdown system problems | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0730 | Other blowdown system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 313.5 | 165 | 1 | 1 | 0730-Other blowdown system problems | U1-Forced - Immediate | 850-Combined Cycle Block
0730 | Other blowdown system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 8619.9999 | 300 | 1 | 1 | 0730-Other blowdown system problems | U1-Forced - Immediate | 850-Combined Cycle Block
0730 | Other blowdown system problems | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2013 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 172.9 | 91 | 1 | 1 | 0730-Other blowdown system problems | D1-Forced - Immediate | 850-Combined Cycle Block
0730 | Other blowdown system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 882 | 315 | 1 | 1 | 0730-Other blowdown system problems | U1-Forced - Immediate | 850-Combined Cycle Block
0730 | Other blowdown system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 850 | Combined Cycle Block | WECC | Summer | 40.95 | 117 | 1 | 1 | 0730-Other blowdown system problems | U1-Forced - Immediate | 850-Combined Cycle Block
0730 | Other blowdown system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 307.9999 | 165 | 1 | 1 | 0730-Other blowdown system problems | U1-Forced - Immediate | 850-Combined Cycle Block
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1823.0498 | 303 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3184.35 | 69 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6677.5499 | 297 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 451 | 41 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1017.2499 | 195 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5521.1167 | 29 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4873.6 | 64 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 418467.5833 | 145 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 59.9999 | 180 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 80.1666 | 130 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 938.9999 | 180 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 227.1666 | 94 | 1 | 1 | 0740-Boiler recirculation pumps | D2-Forced - Delayed | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 94560.7997 | 816 | 1 | 1 | 0740-Boiler recirculation pumps | U1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 976.5 | 62 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 17114 | 199 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 12626.3666 | 53 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 22176.6 | 92 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 74.0998 | 342 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 253 | 230 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 3043.3333 | 166 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5064.5498 | 597 | 1 | 1 | 0740-Boiler recirculation pumps | U1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 192.3665 | 199 | 1 | 1 | 0740-Boiler recirculation pumps | U1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 567.4666 | 224 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1569.75 | 69 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3092.9999 | 90 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2756.25 | 175 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 336.05 | 33 | 1 | 1 | 0740-Boiler recirculation pumps | D2-Forced - Delayed | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 423.5831 | 299 | 1 | 1 | 0740-Boiler recirculation pumps | U1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 13711.6665 | 380 | 1 | 1 | 0740-Boiler recirculation pumps | U1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 44.85 | 23 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 144.5167 | 23 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 113950 | 50 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 81060 | 84 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 32.6666 | 140 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 98.0332 | 173 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 107.0665 | 292 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 1841.9999 | 180 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 4537.5 | 50 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D3 | Forced - Postponed | 2013 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 4071.1999 | 168 | 1 | 1 | 0740-Boiler recirculation pumps | D3-Forced - Postponed | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | SF | Startup Failure | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 35603.3331 | 550 | 1 | 1 | 0740-Boiler recirculation pumps | SF-Startup Failure | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 21258.9 | 598 | 1 | 1 | 0740-Boiler recirculation pumps | U1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 166.5 | 111 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2057.25 | 39 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4550.8667 | 26 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5650.95 | 303 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 129.9998 | 312 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 9630 | 180 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 17467.083 | 515 | 1 | 1 | 0740-Boiler recirculation pumps | U1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 503.2166 | 109 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2448 | 135 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 22409.6666 | 92 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 967.9997 | 480 | 1 | 1 | 0740-Boiler recirculation pumps | U1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 45.6 | 24 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 110.1333 | 118 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 35817.4166 | 145 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 761.95 | 147 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 6990.5 | 62 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 76636 | 92 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 46.6666 | 100 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 75.8 | 379 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 157.9164 | 379 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 11 | 55 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 462.8665 | 524 | 1 | 1 | 0740-Boiler recirculation pumps | U1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 414 | 92 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1044 | 90 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7096.65 | 17 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 47.25 | 63 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 471.5 | 205 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 20056 | 46 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D3 | Forced - Postponed | 2013 | Oil | OO | 100 | Fossil-Steam | NPCC | Off-Peak | 575.1 | 142 | 1 | 1 | 0740-Boiler recirculation pumps | D3-Forced - Postponed | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 563.6665 | 380 | 1 | 1 | 0740-Boiler recirculation pumps | U1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | OS | 650 | Fluidized Bed | RFC | Winter | 80 | 40 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 650-Fluidized Bed
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 256.9667 | 26 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 800-Miscellaneous
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 82.4 | 48 | 1 | 1 | 0740-Boiler recirculation pumps | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 3719.9998 | 288 | 1 | 1 | 0740-Boiler recirculation pumps | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 16550.1 | 518 | 1 | 1 | 0740-Boiler recirculation pumps | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0740 | Boiler recirculation pumps | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2013 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 248.5833 | 95 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 850-Combined Cycle Block
0740 | Boiler recirculation pumps | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 436.9832 | 167 | 1 | 1 | 0740-Boiler recirculation pumps | U1-Forced - Immediate | 850-Combined Cycle Block
0740 | Boiler recirculation pumps | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 850 | Combined Cycle Block | WECC | Summer | 88.5 | 90 | 1 | 1 | 0740-Boiler recirculation pumps | U1-Forced - Immediate | 850-Combined Cycle Block
0740 | Boiler recirculation pumps | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 850 | Combined Cycle Block | WECC | Summer | 77.9999 | 90 | 1 | 1 | 0740-Boiler recirculation pumps | U1-Forced - Immediate | 850-Combined Cycle Block
0740 | Boiler recirculation pumps | HRSG Boiler | HRSG Boiler Piping System | SF | Startup Failure | 2013 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 876.3666 | 61 | 1 | 1 | 0740-Boiler recirculation pumps | SF-Startup Failure | 851-CC GT units
0740 | Boiler recirculation pumps | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2013 | Gas | GG | 852 | CC steam units | TRE | Off-Peak | 2093 | 26 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 852-CC steam units
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 48290 | 550 | 1 | 1 | 0741-Boiler recirculation pumps - motors | U1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 7463.5166 | 133 | 1 | 1 | 0741-Boiler recirculation pumps - motors | U1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 79.5 | 45 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 593402 | 340 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2055.55 | 839 | 1 | 1 | 0741-Boiler recirculation pumps - motors | U1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 4386.6665 | 470 | 1 | 1 | 0741-Boiler recirculation pumps - motors | U1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 273 | 91 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4115.1333 | 17 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9037.5 | 125 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 82587.5 | 125 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 70 | 175 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2214.9999 | 300 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 16450 | 125 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 574 | 41 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 165.3333 | 80 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4284.8166 | 133 | 1 | 1 | 0741-Boiler recirculation pumps - motors | U1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 117 | 9 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 1975 | 50 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 10218 | 104 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 965430 | 340 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 6216 | 224 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 1341.9998 | 330 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | SF | Startup Failure | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 54373.2331 | 766 | 1 | 1 | 0741-Boiler recirculation pumps - motors | SF-Startup Failure | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 8033.8333 | 118 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0742 | Boiler recirculation pumps - motors - cooling system | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 52 | 52 | 1 | 1 | 0742-Boiler recirculation pumps - motors - cooling system | D1-Forced - Immediate | 100-Fossil-Steam
0742 | Boiler recirculation pumps - motors - cooling system | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3612 | 84 | 1 | 1 | 0742-Boiler recirculation pumps - motors - cooling system | D1-Forced - Immediate | 100-Fossil-Steam
0742 | Boiler recirculation pumps - motors - cooling system | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 971.5 | 134 | 1 | 1 | 0742-Boiler recirculation pumps - motors - cooling system | D2-Forced - Delayed | 100-Fossil-Steam
0742 | Boiler recirculation pumps - motors - cooling system | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1.2166 | 73 | 1 | 1 | 0742-Boiler recirculation pumps - motors - cooling system | D1-Forced - Immediate | 100-Fossil-Steam
0742 | Boiler recirculation pumps - motors - cooling system | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 183.6667 | 38 | 1 | 1 | 0742-Boiler recirculation pumps - motors - cooling system | D1-Forced - Immediate | 100-Fossil-Steam
0742 | Boiler recirculation pumps - motors - cooling system | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1159.2333 | 83 | 1 | 1 | 0742-Boiler recirculation pumps - motors - cooling system | D1-Forced - Immediate | 100-Fossil-Steam
0742 | Boiler recirculation pumps - motors - cooling system | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7281.75 | 73 | 1 | 1 | 0742-Boiler recirculation pumps - motors - cooling system | D1-Forced - Immediate | 100-Fossil-Steam
0742 | Boiler recirculation pumps - motors - cooling system | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2268 | 84 | 1 | 1 | 0742-Boiler recirculation pumps - motors - cooling system | D1-Forced - Immediate | 100-Fossil-Steam
0742 | Boiler recirculation pumps - motors - cooling system | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 123.75 | 55 | 1 | 1 | 0742-Boiler recirculation pumps - motors - cooling system | D1-Forced - Immediate | 100-Fossil-Steam
0742 | Boiler recirculation pumps - motors - cooling system | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 348 | 87 | 1 | 1 | 0742-Boiler recirculation pumps - motors - cooling system | D1-Forced - Immediate | 100-Fossil-Steam
0742 | Boiler recirculation pumps - motors - cooling system | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 432 | 108 | 1 | 1 | 0742-Boiler recirculation pumps - motors - cooling system | D1-Forced - Immediate | 100-Fossil-Steam
0742 | Boiler recirculation pumps - motors - cooling system | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 620 | 62 | 1 | 1 | 0742-Boiler recirculation pumps - motors - cooling system | D1-Forced - Immediate | 100-Fossil-Steam
0742 | Boiler recirculation pumps - motors - cooling system | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1260 | 84 | 1 | 1 | 0742-Boiler recirculation pumps - motors - cooling system | D1-Forced - Immediate | 100-Fossil-Steam
0742 | Boiler recirculation pumps - motors - cooling system | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1494.6 | 53 | 1 | 1 | 0742-Boiler recirculation pumps - motors - cooling system | D1-Forced - Immediate | 100-Fossil-Steam
0742 | Boiler recirculation pumps - motors - cooling system | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4469 | 82 | 1 | 1 | 0742-Boiler recirculation pumps - motors - cooling system | D1-Forced - Immediate | 100-Fossil-Steam
0742 | Boiler recirculation pumps - motors - cooling system | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2054.85 | 133 | 1 | 1 | 0742-Boiler recirculation pumps - motors - cooling system | U1-Forced - Immediate | 100-Fossil-Steam
0742 | Boiler recirculation pumps - motors - cooling system | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 224 | 30 | 1 | 1 | 0742-Boiler recirculation pumps - motors - cooling system | D1-Forced - Immediate | 100-Fossil-Steam
0742 | Boiler recirculation pumps - motors - cooling system | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 405 | 81 | 1 | 1 | 0742-Boiler recirculation pumps - motors - cooling system | D1-Forced - Immediate | 100-Fossil-Steam
0742 | Boiler recirculation pumps - motors - cooling system | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7443.3333 | 58 | 1 | 1 | 0742-Boiler recirculation pumps - motors - cooling system | D1-Forced - Immediate | 100-Fossil-Steam
0742 | Boiler recirculation pumps - motors - cooling system | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 19585.5833 | 65 | 1 | 1 | 0742-Boiler recirculation pumps - motors - cooling system | D1-Forced - Immediate | 100-Fossil-Steam
0742 | Boiler recirculation pumps - motors - cooling system | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 144.0333 | 58 | 1 | 1 | 0742-Boiler recirculation pumps - motors - cooling system | D1-Forced - Immediate | 100-Fossil-Steam
0742 | Boiler recirculation pumps - motors - cooling system | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 185.8666 | 68 | 1 | 1 | 0742-Boiler recirculation pumps - motors - cooling system | D1-Forced - Immediate | 100-Fossil-Steam
0742 | Boiler recirculation pumps - motors - cooling system | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 249.75 | 111 | 1 | 1 | 0742-Boiler recirculation pumps - motors - cooling system | D1-Forced - Immediate | 100-Fossil-Steam
0742 | Boiler recirculation pumps - motors - cooling system | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1582 | 84 | 1 | 1 | 0742-Boiler recirculation pumps - motors - cooling system | D1-Forced - Immediate | 100-Fossil-Steam
0742 | Boiler recirculation pumps - motors - cooling system | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1840.5333 | 58 | 1 | 1 | 0742-Boiler recirculation pumps - motors - cooling system | D1-Forced - Immediate | 100-Fossil-Steam
0742 | Boiler recirculation pumps - motors - cooling system | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 9402.5 | 30 | 1 | 1 | 0742-Boiler recirculation pumps - motors - cooling system | D1-Forced - Immediate | 100-Fossil-Steam
0742 | Boiler recirculation pumps - motors - cooling system | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3575.6666 | 68 | 1 | 1 | 0742-Boiler recirculation pumps - motors - cooling system | D1-Forced - Immediate | 100-Fossil-Steam
0742 | Boiler recirculation pumps - motors - cooling system | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4010.1333 | 73 | 1 | 1 | 0742-Boiler recirculation pumps - motors - cooling system | D1-Forced - Immediate | 100-Fossil-Steam
0742 | Boiler recirculation pumps - motors - cooling system | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 140 | 30 | 1 | 1 | 0742-Boiler recirculation pumps - motors - cooling system | D1-Forced - Immediate | 100-Fossil-Steam
0742 | Boiler recirculation pumps - motors - cooling system | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 164 | 82 | 1 | 1 | 0742-Boiler recirculation pumps - motors - cooling system | D1-Forced - Immediate | 100-Fossil-Steam
0742 | Boiler recirculation pumps - motors - cooling system | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 336 | 48 | 1 | 1 | 0742-Boiler recirculation pumps - motors - cooling system | D1-Forced - Immediate | 100-Fossil-Steam
0742 | Boiler recirculation pumps - motors - cooling system | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 420.8333 | 101 | 1 | 1 | 0742-Boiler recirculation pumps - motors - cooling system | D1-Forced - Immediate | 100-Fossil-Steam
0742 | Boiler recirculation pumps - motors - cooling system | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 717 | 239 | 1 | 1 | 0742-Boiler recirculation pumps - motors - cooling system | D2-Forced - Delayed | 100-Fossil-Steam
0750 | Boiler recirculation piping including downcomers | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 10258.8 | 412 | 1 | 1 | 0750-Boiler recirculation piping including downcomers | U1-Forced - Immediate | 100-Fossil-Steam
0750 | Boiler recirculation piping including downcomers | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 110.8333 | 190 | 1 | 1 | 0750-Boiler recirculation piping including downcomers | D1-Forced - Immediate | 100-Fossil-Steam
0750 | Boiler recirculation piping including downcomers | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 21038.0666 | 332.18 | 1 | 1 | 0750-Boiler recirculation piping including downcomers | U1-Forced - Immediate | 100-Fossil-Steam
0750 | Boiler recirculation piping including downcomers | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 151.6666 | 65 | 1 | 1 | 0750-Boiler recirculation piping including downcomers | D1-Forced - Immediate | 100-Fossil-Steam
0750 | Boiler recirculation piping including downcomers | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 58.3332 | 140 | 1 | 1 | 0750-Boiler recirculation piping including downcomers | D1-Forced - Immediate | 100-Fossil-Steam
0750 | Boiler recirculation piping including downcomers | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 597.5 | 50 | 1 | 1 | 0750-Boiler recirculation piping including downcomers | D1-Forced - Immediate | 100-Fossil-Steam
0750 | Boiler recirculation piping including downcomers | Boiler | Boiler Piping System | D3 | Forced - Postponed | 2013 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 417.183 | 50.67 | 1 | 1 | 0750-Boiler recirculation piping including downcomers | D3-Forced - Postponed | 100-Fossil-Steam
0760 | Boiler recirculation valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2017.083 | 515 | 1 | 1 | 0760-Boiler recirculation valves | U1-Forced - Immediate | 100-Fossil-Steam
0760 | Boiler recirculation valves | Boiler | Boiler Piping System | U3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 18409.5331 | 766 | 1 | 1 | 0760-Boiler recirculation valves | U3-Forced - Postponed | 100-Fossil-Steam
0760 | Boiler recirculation valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 61.2332 | 334 | 1 | 1 | 0760-Boiler recirculation valves | D1-Forced - Immediate | 100-Fossil-Steam
0760 | Boiler recirculation valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 33012.4995 | 750 | 1 | 1 | 0760-Boiler recirculation valves | U1-Forced - Immediate | 100-Fossil-Steam
0760 | Boiler recirculation valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 8758.9996 | 570 | 1 | 1 | 0760-Boiler recirculation valves | U1-Forced - Immediate | 100-Fossil-Steam
0760 | Boiler recirculation valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 11.25 | 27 | 1 | 1 | 0760-Boiler recirculation valves | D1-Forced - Immediate | 100-Fossil-Steam
0760 | Boiler recirculation valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3965 | 305 | 1 | 1 | 0760-Boiler recirculation valves | D1-Forced - Immediate | 100-Fossil-Steam
0760 | Boiler recirculation valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 3735.1996 | 552 | 1 | 1 | 0760-Boiler recirculation valves | U1-Forced - Immediate | 100-Fossil-Steam
0760 | Boiler recirculation valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 45.8185 | 20.67 | 1 | 1 | 0760-Boiler recirculation valves | D1-Forced - Immediate | 100-Fossil-Steam
0760 | Boiler recirculation valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 144.4999 | 102 | 1 | 1 | 0760-Boiler recirculation valves | D1-Forced - Immediate | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 335.6667 | 19 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 768 | 16 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 28 | 16 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 704 | 11 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 971.5 | 670 | 1 | 1 | 0770-Other boiler recirculation problems | U1-Forced - Immediate | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 65 | 13 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 167.2 | 152 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 180.5066 | 96.7 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4247.4666 | 176 | 1 | 1 | 0770-Other boiler recirculation problems | U2-Forced - Delayed | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 299.25 | 19 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2240 | 16 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 239.9333 | 122 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 161.115 | 46.7 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1216.3333 | 89 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1660.9999 | 330 | 1 | 1 | 0770-Other boiler recirculation problems | U1-Forced - Immediate | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1047 | 9 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 24.6667 | 8 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 47.25 | 9 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 850.5 | 9 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 14.8283 | 21.7 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 86.6667 | 13 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 800-Miscellaneous
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 1003.6 | 26 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 800-Miscellaneous
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 230.75 | 13 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 800-Miscellaneous
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 244.6167 | 13 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 800-Miscellaneous
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 325 | 13 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 800-Miscellaneous
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 8631.4333 | 62 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 800-Miscellaneous
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 587.6 | 13 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 800-Miscellaneous
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 894.25 | 49 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 800-Miscellaneous
0775 | Economizer piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 47.1833 | 19 | 1 | 1 | 0775-Economizer piping | D1-Forced - Immediate | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 84 | 42 | 1 | 1 | 0775-Economizer piping | D1-Forced - Immediate | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | OS | 100 | Fossil-Steam | SERC | Summer | 464.425 | 19.5 | 1 | 1 | 0775-Economizer piping | D1-Forced - Immediate | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 18918.6665 | 560 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 438 | 438 | 1 | 1 | 0775-Economizer piping | D1-Forced - Immediate | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Other | BM | 100 | Fossil-Steam | WECC | Off-Peak | 2514.8853 | 59.36 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 346.6667 | 13 | 1 | 1 | 0775-Economizer piping | D1-Forced - Immediate | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 532.5 | 18 | 1 | 1 | 0775-Economizer piping | D1-Forced - Immediate | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 6001.8 | 9 | 1 | 1 | 0775-Economizer piping | D1-Forced - Immediate | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 92 | 4 | 1 | 1 | 0775-Economizer piping | D1-Forced - Immediate | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | OS | 100 | Fossil-Steam | SERC | Off-Peak | 617.1 | 18 | 1 | 1 | 0775-Economizer piping | D1-Forced - Immediate | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 594.15 | 9 | 1 | 1 | 0775-Economizer piping | D1-Forced - Immediate | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 708.3 | 9 | 1 | 1 | 0775-Economizer piping | D1-Forced - Immediate | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 701.25 | 11 | 1 | 1 | 0775-Economizer piping | D1-Forced - Immediate | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | OS | 100 | Fossil-Steam | SERC | Summer | 409.2 | 18 | 1 | 1 | 0775-Economizer piping | D1-Forced - Immediate | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 1297.0999 | 102 | 1 | 1 | 0775-Economizer piping | D1-Forced - Immediate | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 111 | 45 | 1 | 1 | 0775-Economizer piping | D1-Forced - Immediate | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 2346.45 | 9 | 1 | 1 | 0775-Economizer piping | D1-Forced - Immediate | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 4322.2667 | 11 | 1 | 1 | 0775-Economizer piping | D1-Forced - Immediate | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1636.2 | 81 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 495.7333 | 52 | 1 | 1 | 0775-Economizer piping | D1-Forced - Immediate | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 4909.8 | 9 | 1 | 1 | 0775-Economizer piping | D1-Forced - Immediate | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 1113 | 20 | 1 | 1 | 0775-Economizer piping | D1-Forced - Immediate | 800-Miscellaneous
0775 | Economizer piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 5561.5 | 49 | 1 | 1 | 0775-Economizer piping | D1-Forced - Immediate | 800-Miscellaneous
0775 | Economizer piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 334.3333 | 20 | 1 | 1 | 0775-Economizer piping | D1-Forced - Immediate | 800-Miscellaneous
0775 | Economizer piping | Boiler | Boiler Piping System | D3 | Forced - Postponed | 2013 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 305.7 | 18 | 1 | 1 | 0775-Economizer piping | D3-Forced - Postponed | 800-Miscellaneous
0775 | Economizer piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 935 | 20 | 1 | 1 | 0775-Economizer piping | D1-Forced - Immediate | 800-Miscellaneous
0775 | Economizer piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 1767.3333 | 20 | 1 | 1 | 0775-Economizer piping | D1-Forced - Immediate | 800-Miscellaneous
0775 | Economizer piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Off-Peak | 9386.6666 | 80 | 1 | 1 | 0775-Economizer piping | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0775 | Economizer piping | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 1701.85 | 168.5 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 851-CC GT units
0775 | Economizer piping | HRSG Boiler | HRSG Boiler Piping System | U3 | Forced - Postponed | 2013 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 2140.3499 | 171 | 1 | 1 | 0775-Economizer piping | U3-Forced - Postponed | 851-CC GT units
0775 | Economizer piping | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 851 | CC GT units | RFC | Winter | 5486.8666 | 169 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 851-CC GT units
0775 | Economizer piping | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 4139.4999 | 127.5 | 1 | 1 | 0775-Economizer piping | D1-Forced - Immediate | 852-CC steam units
0775 | Economizer piping | HRSG Boiler | HRSG Boiler Piping System | D3 | Forced - Postponed | 2013 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 1289.2166 | 103 | 1 | 1 | 0775-Economizer piping | D3-Forced - Postponed | 852-CC steam units
0775 | Economizer piping | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2013 | Gas | GG | 852 | CC steam units | SERC | Off-Peak | 2754.81 | 289.98 | 1 | 1 | 0775-Economizer piping | D1-Forced - Immediate | 852-CC steam units
0775 | Economizer piping | Boiler | Boiler Piping System | U3 | Forced - Postponed | 2013 | Gas | GG | 860 | Co-generator Block | SERC | Winter | 788.2333 | 107 | 1 | 1 | 0775-Economizer piping | U3-Forced - Postponed | 860-Co-generator Block
0775 | Economizer piping | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2013 | Gas | GG | 860 | Co-generator Block | SERC | Off-Peak | 11361.35 | 158.9 | 1 | 1 | 0775-Economizer piping | U2-Forced - Delayed | 860-Co-generator Block
0780 | Headers between tube bundles | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 723.8166 | 317 | 1 | 1 | 0780-Headers between tube bundles | U1-Forced - Immediate | 100-Fossil-Steam
0780 | Headers between tube bundles | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 686.8331 | 317 | 1 | 1 | 0780-Headers between tube bundles | U1-Forced - Immediate | 100-Fossil-Steam
0780 | Headers between tube bundles | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1680.1666 | 85 | 1 | 1 | 0780-Headers between tube bundles | U1-Forced - Immediate | 100-Fossil-Steam
0780 | Headers between tube bundles | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1836.55 | 69 | 1 | 1 | 0780-Headers between tube bundles | U1-Forced - Immediate | 100-Fossil-Steam
0780 | Headers between tube bundles | HRSG Boiler | HRSG Boiler Piping System | D3 | Forced - Postponed | 2013 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 2942.3332 | 364 | 1 | 1 | 0780-Headers between tube bundles | D3-Forced - Postponed | 850-Combined Cycle Block
0780 | Headers between tube bundles | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 2764.3 | 77 | 1 | 1 | 0780-Headers between tube bundles | U1-Forced - Immediate | 851-CC GT units
0780 | Headers between tube bundles | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 851 | CC GT units | TRE | Summer | 474.8333 | 77 | 1 | 1 | 0780-Headers between tube bundles | U1-Forced - Immediate | 851-CC GT units
0780 | Headers between tube bundles | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 851 | CC GT units | TRE | Summer | 2125.2 | 77 | 1 | 1 | 0780-Headers between tube bundles | U1-Forced - Immediate | 851-CC GT units
0782 | Headers and caps | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 84609.9999 | 150 | 1 | 1 | 0782-Headers and caps | U1-Forced - Immediate | 100-Fossil-Steam
0782 | Headers and caps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 2532.4 | 24 | 1 | 1 | 0782-Headers and caps | D1-Forced - Immediate | 100-Fossil-Steam
0782 | Headers and caps | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 588.8 | 23 | 1 | 1 | 0782-Headers and caps | U1-Forced - Immediate | 100-Fossil-Steam
0782 | Headers and caps | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2243.9999 | 198 | 1 | 1 | 0782-Headers and caps | U1-Forced - Immediate | 100-Fossil-Steam
0782 | Headers and caps | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3247.2 | 198 | 1 | 1 | 0782-Headers and caps | U2-Forced - Delayed | 100-Fossil-Steam
0782 | Headers and caps | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5437.1332 | 191 | 1 | 1 | 0782-Headers and caps | U1-Forced - Immediate | 100-Fossil-Steam
0782 | Headers and caps | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 2131996.3163 | 547 | 1 | 1 | 0782-Headers and caps | U1-Forced - Immediate | 100-Fossil-Steam
0782 | Headers and caps | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6287.4999 | 150 | 1 | 1 | 0782-Headers and caps | U2-Forced - Delayed | 100-Fossil-Steam
0782 | Headers and caps | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 650 | Fluidized Bed | WECC | Summer | 8193.5 | 105 | 1 | 1 | 0782-Headers and caps | U1-Forced - Immediate | 650-Fluidized Bed
0790 | Pipe hangers; brackets; supports (general) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 121584.5831 | 775 | 1 | 1 | 0790-Pipe hangers; brackets; supports (general) | U1-Forced - Immediate | 100-Fossil-Steam
0790 | Pipe hangers; brackets; supports (general) | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 65133.75 | 825 | 1 | 1 | 0790-Pipe hangers; brackets; supports (general) | U2-Forced - Delayed | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Oil | OO | 100 | Fossil-Steam | RFC | Summer | 657.4166 | 115 | 1 | 1 | 0799-Other miscellaneous piping system problems | D1-Forced - Immediate | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1254.4 | 48 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4780.9665 | 374 | 1 | 1 | 0799-Other miscellaneous piping system problems | U2-Forced - Delayed | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | SF | Startup Failure | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2440.25 | 215 | 1 | 1 | 0799-Other miscellaneous piping system problems | SF-Startup Failure | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 20228.9997 | 495 | 1 | 1 | 0799-Other miscellaneous piping system problems | U2-Forced - Delayed | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 75.9 | 138 | 1 | 1 | 0799-Other miscellaneous piping system problems | D2-Forced - Delayed | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2459.85 | 69 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2528.1333 | 67 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4987.215 | 324.9 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 4050 | 405 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 25.1333 | 29 | 1 | 1 | 0799-Other miscellaneous piping system problems | D1-Forced - Immediate | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2295 | 270 | 1 | 1 | 0799-Other miscellaneous piping system problems | D1-Forced - Immediate | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 848 | 424 | 1 | 1 | 0799-Other miscellaneous piping system problems | D2-Forced - Delayed | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 10917.683 | 527 | 1 | 1 | 0799-Other miscellaneous piping system problems | U2-Forced - Delayed | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | SF | Startup Failure | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 578.3333 | 100 | 1 | 1 | 0799-Other miscellaneous piping system problems | SF-Startup Failure | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 1030.5166 | 77 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 851-CC GT units
0799 | Other miscellaneous piping system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 2440.2 | 166 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 851-CC GT units
0799 | Other miscellaneous piping system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 851 | CC GT units | TRE | Summer | 1320.4666 | 58 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 851-CC GT units
0799 | Other miscellaneous piping system problems | HRSG Boiler | HRSG Boiler Piping System | U2 | Forced - Delayed | 2013 | Gas | GG | 851 | CC GT units | TRE | Summer | 294.8333 | 58 | 1 | 1 | 0799-Other miscellaneous piping system problems | U2-Forced - Delayed | 851-CC GT units
0799 | Other miscellaneous piping system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 851 | CC GT units | MRO | Off-Peak | 1132.4 | 152 | 2 | 2 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 851-CC GT units
0799 | Other miscellaneous piping system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2013 | Gas | GG | 851 | CC GT units | TRE | Winter | 3729.45 | 141 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 851-CC GT units
0799 | Other miscellaneous piping system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 938.7 | 126 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 852-CC steam units
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 217.7666 | 278 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1001.7 | 477 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1100.8999 | 303 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 180.2 | 106 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1168.65 | 477 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 62.7 | 57 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | SF | Startup Failure | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2154.5998 | 486 | 1 | 1 | 0800-Drums and drum internals (single drum only) | SF-Startup Failure | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 434.5 | 395 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 485.9332 | 394 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 469.5833 | 25 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | SF | Startup Failure | 2013 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 3904 | 320 | 1 | 1 | 0800-Drums and drum internals (single drum only) | SF-Startup Failure | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 88.6666 | 152 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 12017.5833 | 85 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 36.5 | 10 | 1 | 1 | 0800-Drums and drum internals (single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 75.1666 | 82 | 1 | 1 | 0800-Drums and drum internals (single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1048.3332 | 340 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2221.4145 | 510.67 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Waste Heat | WH | 100 | Fossil-Steam | WECC | Off-Peak | 227.0099 | 289.8 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 750 | 20 | 1 | 1 | 0800-Drums and drum internals (single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | SF | Startup Failure | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2767.5 | 270 | 1 | 1 | 0800-Drums and drum internals (single drum only) | SF-Startup Failure | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 190 | 475 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 312.8 | 391 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 801.9 | 486 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2220.8329 | 650 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 171.1666 | 158 | 1 | 1 | 0800-Drums and drum internals (single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 219.9166 | 145 | 1 | 1 | 0800-Drums and drum internals (single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 254.8331 | 278 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1044.9 | 486 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1413.9998 | 303 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 709.2 | 394 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1094.8 | 138 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 125.8333 | 50 | 1 | 1 | 0800-Drums and drum internals (single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 454.3833 | 199 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 585.9165 | 395 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 764.1665 | 262 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1763.2329 | 626 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1959.3998 | 303 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 132.6665 | 199 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1153.7499 | 195 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 1371.9999 | 336 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 5180.6665 | 190 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1810.4166 | 275 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U2-Forced - Delayed | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 124.9666 | 46 | 1 | 1 | 0800-Drums and drum internals (single drum only) | D1-Forced - Immediate | 650-Fluidized Bed
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 7953.8666 | 112 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 650-Fluidized Bed
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 519.3332 | 328 | 1 | 1 | 0800-Drums and drum internals (single drum only) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0800 | Drums and drum internals (single drum only) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 7274.8665 | 262 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 850-Combined Cycle Block
0800 | Drums and drum internals (single drum only) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Gas | GG | 850 | Combined Cycle Block | WECC | Winter | 1486.4999 | 90 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 850-Combined Cycle Block
0800 | Drums and drum internals (single drum only) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 536.7333 | 166 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 851-CC GT units
0800 | Drums and drum internals (single drum only) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 15.1666 | 182 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 851-CC GT units
0800 | Drums and drum internals (single drum only) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 10480.7 | 168.5 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 851-CC GT units
0800 | Drums and drum internals (single drum only) | HRSG Boiler | HRSG Boiler Internals and Structures | SF | Startup Failure | 2013 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 101.1 | 168.5 | 1 | 1 | 0800-Drums and drum internals (single drum only) | SF-Startup Failure | 851-CC GT units
0800 | Drums and drum internals (single drum only) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Gas | GG | 852 | CC steam units | SERC | Off-Peak | 2094.9999 | 300 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 852-CC steam units
0800 | Drums and drum internals (single drum only) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Gas | GG | 852 | CC steam units | SERC | Off-Peak | 1480 | 148 | 1 | 1 | 0800-Drums and drum internals (single drum only) | D1-Forced - Immediate | 852-CC steam units
0800 | Drums and drum internals (single drum only) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Gas | GG | 852 | CC steam units | SERC | Off-Peak | 527.4999 | 150 | 1 | 1 | 0800-Drums and drum internals (single drum only) | D1-Forced - Immediate | 852-CC steam units
0800 | Drums and drum internals (single drum only) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Gas | GG | 852 | CC steam units | SERC | Off-Peak | 6157.5 | 150 | 1 | 1 | 0800-Drums and drum internals (single drum only) | D1-Forced - Immediate | 852-CC steam units
0800 | Drums and drum internals (single drum only) | HRSG Boiler | HRSG Boiler Internals and Structures | SF | Startup Failure | 2013 | Gas | GG | 852 | CC steam units | SERC | Off-Peak | 180 | 300 | 1 | 1 | 0800-Drums and drum internals (single drum only) | SF-Startup Failure | 852-CC steam units
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Gas | GG | 860 | Co-generator Block | RFC | Winter | 1.0833 | 13 | 1 | 1 | 0800-Drums and drum internals (single drum only) | D1-Forced - Immediate | 860-Co-generator Block
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Gas | GG | 860 | Co-generator Block | NPCC | Winter | 8129.6666 | 290 | 1 | 1 | 0800-Drums and drum internals (single drum only) | D1-Forced - Immediate | 860-Co-generator Block
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Gas | GG | 860 | Co-generator Block | NPCC | Winter | 186.4331 | 329 | 1 | 1 | 0800-Drums and drum internals (single drum only) | D1-Forced - Immediate | 860-Co-generator Block
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Gas | GG | 860 | Co-generator Block | RFC | Winter | 80 | 48 | 1 | 1 | 0800-Drums and drum internals (single drum only) | D1-Forced - Immediate | 860-Co-generator Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 3506.3331 | 314 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 175 | 500 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 167.3033 | 189.4 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 3420.3332 | 310 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 1846.7899 | 339.9 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Gas | GG | 850 | Combined Cycle Block | WECC | Summer | 7.5683 | 23.9 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 200 | 400 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 338 | 260 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 4044.1331 | 619 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 62.6266 | 134.2 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 237.86 | 339.8 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 4468.0331 | 311 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 3120.6665 | 620 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Gas | GG | 850 | Combined Cycle Block | WECC | Summer | 6.4 | 38.4 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Gas | GG | 850 | Combined Cycle Block | WECC | Winter | 82.8333 | 142 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | SF | Startup Failure | 2013 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 938.448 | 37.24 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | SF-Startup Failure | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 27.1333 | 44 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Gas | GG | 851 | CC GT units | MRO | Off-Peak | 70.8 | 118 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 127.5665 | 178 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Gas | GG | 851 | CC GT units | MRO | Off-Peak | 131.7666 | 118 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 1116.4999 | 165 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 4239.3999 | 246 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 892.8 | 144 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 904.75 | 164.5 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Gas | GG | 851 | CC GT units | RFC | Summer | 24.2 | 44 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U2 | Forced - Delayed | 2013 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 3220.8 | 122 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U2-Forced - Delayed | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | SF | Startup Failure | 2013 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 997.0499 | 153 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | SF-Startup Failure | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 787.8666 | 152 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Gas | GG | 851 | CC GT units | RFC | Summer | 27.1333 | 44 | 1 | 2 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Gas | GG | 851 | CC GT units | RFC | Summer | 46.2 | 44 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Gas | GG | 851 | CC GT units | SERC | Winter | 3504.6 | 177 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Gas | GG | 851 | CC GT units | WECC | Summer | 772.2 | 156 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Gas | GG | 851 | CC GT units | WECC | Winter | 22.7865 | 41.43 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | SF | Startup Failure | 2013 | Gas | OG | 851 | CC GT units | WECC | Off-Peak | 193.6634 | 173.43 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | SF-Startup Failure | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Gas | GG | 851 | CC GT units | RFC | Summer | 34.4667 | 44 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Gas | GG | 851 | CC GT units | RFC | Summer | 132.7333 | 44 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Gas | GG | 851 | CC GT units | WECC | Winter | 3607.6305 | 109.71 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U2 | Forced - Delayed | 2013 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 51038.4 | 144 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U2-Forced - Delayed | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | SF | Startup Failure | 2013 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 4950.8666 | 206 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | SF-Startup Failure | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 4923.4 | 206 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U2 | Forced - Delayed | 2013 | Gas | GG | 851 | CC GT units | RFC | Summer | 5720.4 | 126 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U2-Forced - Delayed | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 59.4999 | 255 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 289.85 | 187 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 106.86 | 164.4 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 680 | 127.5 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Gas | GG | 852 | CC steam units | MRO | Off-Peak | 64.0333 | 226 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 1092.4999 | 150 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 38 | 114 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 42.9566 | 184.1 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D2 | Forced - Delayed | 2013 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 1848 | 70 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D2-Forced - Delayed | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Gas | GG | 852 | CC steam units | WECC | Winter | 147.6 | 328 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 67.3666 | 94 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D2 | Forced - Delayed | 2013 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 1649.55 | 63 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D2-Forced - Delayed | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D2 | Forced - Delayed | 2013 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 2845.218 | 62.67 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D2-Forced - Delayed | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Gas | GG | 852 | CC steam units | SERC | Off-Peak | 6.4166 | 77 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 2827.2 | 152 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 9 | 90 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Gas | GG | 861 | CoG GT units | TRE | Summer | 6220.5 | 174 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 861-CoG GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Gas | GG | 861 | CoG GT units | WECC | Winter | 167.9 | 23 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 861-CoG GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | Boiler | Boiler Internals and Structures | SF | Startup Failure | 2013 | Gas | GG | 861 | CoG GT units | TRE | Winter | 117.1666 | 185 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | SF-Startup Failure | 861-CoG GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Gas | GG | 861 | CoG GT units | TRE | Off-Peak | 190 | 75 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 861-CoG GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Gas | GG | 861 | CoG GT units | TRE | Off-Peak | 4057.0999 | 174 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 861-CoG GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 862 | CoG steam units | TRE | Winter | 111.4666 | 176 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 862-CoG steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 862 | CoG steam units | TRE | Summer | 4826.25 | 135 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 862-CoG steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Gas | PC | 862 | CoG steam units | SERC | Winter | 864.5 | 34.58 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 862-CoG steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Gas | PC | 862 | CoG steam units | SERC | Winter | 1625.26 | 34.58 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 862-CoG steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 862 | CoG steam units | TRE | Off-Peak | 3147.7499 | 135 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 862-CoG steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Waste Heat | WH | 862 | CoG steam units | TRE | Off-Peak | 200.9332 | 274 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 862-CoG steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Gas | PC | 862 | CoG steam units | SERC | Winter | 138.32 | 34.58 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 862-CoG steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Gas | PC | 862 | CoG steam units | SERC | Winter | 1175.72 | 34.58 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 862-CoG steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 208.9999 | 165 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 139.9998 | 300 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 879.6664 | 364 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 27 | 180 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 64.7998 | 486 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 383.2498 | 315 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 72.3666 | 167 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U3 | Forced - Postponed | 2013 | Gas | GG | 851 | CC GT units | SERC | Summer | 1886.4999 | 165 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U3-Forced - Postponed | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U3 | Forced - Postponed | 2013 | Gas | GG | 851 | CC GT units | SERC | Summer | 1797.3333 | 160 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U3-Forced - Postponed | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U3 | Forced - Postponed | 2013 | Gas | GG | 851 | CC GT units | SERC | Summer | 1888 | 160 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U3-Forced - Postponed | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 467.5833 | 181 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Gas | GG | 851 | CC GT units | SERC | Summer | 2613.0666 | 164 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 99.8999 | 162 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 6.9 | 138 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U2 | Forced - Delayed | 2013 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 5808 | 144 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U2-Forced - Delayed | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Gas | GG | 851 | CC GT units | WECC | Winter | 152 | 160 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U3 | Forced - Postponed | 2013 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 1698.45 | 169 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U3-Forced - Postponed | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D3 | Forced - Postponed | 2013 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 1486.3333 | 130 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D3-Forced - Postponed | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | MRO | Winter | 418.3332 | 251 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 68.4666 | 158 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 2071.3333 | 130 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 261.6 | 218 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D3 | Forced - Postponed | 2013 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 1536.1666 | 130 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D3-Forced - Postponed | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 60.9092 | 228.41 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 4.5 | 90 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 119.6999 | 189 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 76 | 80 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D3 | Forced - Postponed | 2013 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 1460.3333 | 130 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D3-Forced - Postponed | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D3 | Forced - Postponed | 2013 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 1035.15 | 103 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D3-Forced - Postponed | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Gas | GG | 852 | CC steam units | WECC | Summer | 319.6999 | 138 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 2170.6666 | 185 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Gas | GG | 860 | Co-generator Block | WECC | Off-Peak | 106.2 | 236 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 860-Co-generator Block
0802 | IP Drum (including drum level trips not attributable to other causes) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Gas | GG | 861 | CoG GT units | WECC | Summer | 336.8666 | 163 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 861-CoG GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 862 | CoG steam units | WECC | Summer | 88.55 | 77 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 862-CoG steam units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 2490.5 | 170 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | SF | Startup Failure | 2013 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 159.7998 | 282 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | SF-Startup Failure | 850-Combined Cycle Block
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 2621.9665 | 238 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Gas | GG | 851 | CC GT units | WECC | Summer | 107.3333 | 70 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 1666.9332 | 152 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Gas | GG | 851 | CC GT units | RFC | Winter | 37.125 | 49.5 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Gas | GG | 851 | CC GT units | RFC | Winter | 23.1 | 49.5 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 1009.1666 | 70 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Gas | GG | 852 | CC steam units | RFC | Winter | 3.0916 | 26.5 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 187 | 187 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Gas | GG | 852 | CC steam units | WECC | Summer | 108.1766 | 70.55 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Gas | GG | 852 | CC steam units | RFC | Winter | 17.225 | 26.5 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 168 | 105 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Gas | GG | 852 | CC steam units | SERC | Summer | 49.6665 | 298 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Gas | GG | 852 | CC steam units | WECC | Winter | 164.2999 | 186 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Gas | GG | 852 | CC steam units | RFC | Winter | 6.5333 | 14 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Gas | GG | 852 | CC steam units | WECC | Winter | 433.9999 | 186 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 2763.5998 | 252 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0803 | LP Drum (including drum level trips not attributable to other causes) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Gas | GG | 861 | CoG GT units | TRE | Summer | 260.2832 | 161 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 861-CoG GT units
0803 | LP Drum (including drum level trips not attributable to other causes) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 862 | CoG steam units | TRE | Summer | 143.8833 | 89 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 862-CoG steam units
0810 | Boiler supports and structures (use code 1320 for tube supports) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 16580 | 60 | 1 | 1 | 0810-Boiler supports and structures (use code 1320 for tube supports) | D1-Forced - Immediate | 100-Fossil-Steam
0810 | Boiler supports and structures (use code 1320 for tube supports) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5156.8997 | 417 | 1 | 1 | 0810-Boiler supports and structures (use code 1320 for tube supports) | D1-Forced - Immediate | 100-Fossil-Steam
0810 | Boiler supports and structures (use code 1320 for tube supports) | Boiler | Boiler Internals and Structures | U3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 121923 | 620 | 1 | 1 | 0810-Boiler supports and structures (use code 1320 for tube supports) | U3-Forced - Postponed | 100-Fossil-Steam
0810 | Boiler supports and structures (use code 1320 for tube supports) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 48106.8 | 414 | 1 | 1 | 0810-Boiler supports and structures (use code 1320 for tube supports) | U1-Forced - Immediate | 100-Fossil-Steam
0810 | Boiler supports and structures (use code 1320 for tube supports) | HRSG Boiler | HRSG Boiler Internals and Structures | U2 | Forced - Delayed | 2013 | Gas | GG | 851 | CC GT units | WECC | Summer | 41220.5 | 190 | 1 | 1 | 0810-Boiler supports and structures (use code 1320 for tube supports) | U2-Forced - Delayed | 851-CC GT units
0810 | Boiler supports and structures (use code 1320 for tube supports) | HRSG Boiler | HRSG Boiler Internals and Structures | U2 | Forced - Delayed | 2013 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 15218 | 70 | 1 | 1 | 0810-Boiler supports and structures (use code 1320 for tube supports) | U2-Forced - Delayed | 852-CC steam units
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 24 | 36 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4159.9999 | 312 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 426.6 | 54 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U3 | Forced - Postponed | 2013 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 65789.3997 | 495.9 | 1 | 1 | 0820-Casing | U3-Forced - Postponed | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2287.8 | 27 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10192.5 | 135 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 134.5833 | 85 | 1 | 1 | 0820-Casing | D3-Forced - Postponed | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4820 | 30 | 1 | 1 | 0820-Casing | D3-Forced - Postponed | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 10556.6666 | 100 | 1 | 1 | 0820-Casing | U1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 42337.7499 | 195 | 1 | 1 | 0820-Casing | U1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 10506 | 120 | 1 | 1 | 0820-Casing | U1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6237.5052 | 260.62 | 1 | 1 | 0820-Casing | U2-Forced - Delayed | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U2 | Forced - Delayed | 2013 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 8051.9997 | 495 | 1 | 1 | 0820-Casing | U2-Forced - Delayed | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 942.0833 | 35 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1350 | 135 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 913.5 | 45 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3886.6666 | 176 | 1 | 1 | 0820-Casing | U1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4808.5333 | 196 | 1 | 1 | 0820-Casing | U1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 36331.1664 | 770 | 1 | 1 | 0820-Casing | U1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2843.3333 | 50 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 836.3333 | 52 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D3 | Forced - Postponed | 2013 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 236.5533 | 95.9 | 1 | 1 | 0820-Casing | D3-Forced - Postponed | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 7771.9999 | 240 | 1 | 1 | 0820-Casing | U1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6042.3849 | 264.63 | 1 | 1 | 0820-Casing | U3-Forced - Postponed | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 14635.5833 | 85 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 30.75 | 45 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 535.1329 | 698 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1307.9995 | 720 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 549.9999 | 150 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D3 | Forced - Postponed | 2013 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 951.34 | 365.9 | 1 | 1 | 0820-Casing | D3-Forced - Postponed | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 886.6666 | 100 | 1 | 1 | 0820-Casing | U1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 8083.3333 | 100 | 1 | 1 | 0820-Casing | U1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 28744.4165 | 205 | 1 | 1 | 0820-Casing | U1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 129928 | 872 | 1 | 1 | 0820-Casing | U1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 54225 | 180 | 1 | 1 | 0820-Casing | U1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1770.1665 | 190 | 1 | 1 | 0820-Casing | U2-Forced - Delayed | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1831.4999 | 135 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 14875 | 85 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 6137.3497 | 393 | 1 | 1 | 0820-Casing | U1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1258 | 51 | 1 | 1 | 0820-Casing | U2-Forced - Delayed | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 4108 | 52 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 3315 | 78 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 5665 | 100 | 1 | 1 | 0820-Casing | U1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 30.1333 | 16 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 77.9166 | 55 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 201.8662 | 757 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2160 | 720 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 242.5 | 50 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5089.3332 | 176 | 1 | 1 | 0820-Casing | U1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Gas | GG | 850 | Combined Cycle Block | MRO | Winter | 1260 | 30 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 850-Combined Cycle Block
0830 | Doors | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3 | 3 | 1 | 1 | 0830-Doors | D1-Forced - Immediate | 100-Fossil-Steam
0830 | Doors | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 340.56 | 42.57 | 1 | 1 | 0830-Doors | D1-Forced - Immediate | 100-Fossil-Steam
0830 | Doors | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 8579.3332 | 340 | 1 | 1 | 0830-Doors | U1-Forced - Immediate | 100-Fossil-Steam
0830 | Doors | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5440 | 340 | 1 | 1 | 0830-Doors | U1-Forced - Immediate | 100-Fossil-Steam
0830 | Doors | Boiler | Boiler Internals and Structures | U2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4155.79 | 264.7 | 1 | 1 | 0830-Doors | U2-Forced - Delayed | 100-Fossil-Steam
0830 | Doors | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 8244.25 | 49 | 1 | 1 | 0830-Doors | D1-Forced - Immediate | 100-Fossil-Steam
0830 | Doors | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 96.68 | 72.51 | 1 | 1 | 0830-Doors | D2-Forced - Delayed | 100-Fossil-Steam
0830 | Doors | Boiler | Boiler Internals and Structures | SF | Startup Failure | 2013 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 533.9499 | 177 | 1 | 1 | 0830-Doors | SF-Startup Failure | 100-Fossil-Steam
0830 | Doors | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 361.9999 | 120 | 1 | 1 | 0830-Doors | U1-Forced - Immediate | 100-Fossil-Steam
0830 | Doors | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 2038.5475 | 161.15 | 1 | 1 | 0830-Doors | U1-Forced - Immediate | 851-CC GT units
0830 | Doors | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Gas | GG | 851 | CC GT units | SERC | Summer | 4661.8333 | 166 | 1 | 1 | 0830-Doors | U1-Forced - Immediate | 851-CC GT units
0830 | Doors | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 6332.0832 | 167 | 1 | 1 | 0830-Doors | U1-Forced - Immediate | 851-CC GT units
0830 | Doors | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 6638.25 | 167 | 1 | 1 | 0830-Doors | U1-Forced - Immediate | 851-CC GT units
0830 | Doors | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 1231.7566 | 164.6 | 1 | 1 | 0830-Doors | D1-Forced - Immediate | 852-CC steam units
0830 | Doors | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Gas | GG | 852 | CC steam units | SERC | Summer | 1071 | 140 | 1 | 1 | 0830-Doors | D1-Forced - Immediate | 852-CC steam units
0830 | Doors | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Gas | GG | 852 | CC steam units | SERC | Summer | 252 | 140 | 1 | 1 | 0830-Doors | D1-Forced - Immediate | 852-CC steam units
0830 | Doors | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 5990.8332 | 158 | 1 | 1 | 0830-Doors | D1-Forced - Immediate | 852-CC steam units
0830 | Doors | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 6280.5 | 158 | 1 | 1 | 0830-Doors | D1-Forced - Immediate | 852-CC steam units
0830 | Doors | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Gas | GG | 861 | CoG GT units | NPCC | Off-Peak | 15.7167 | 23 | 1 | 1 | 0830-Doors | U1-Forced - Immediate | 861-CoG GT units
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 50.8 | 12.7 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 158.53 | 57.3 | 1 | 1 | 0840-Refractory and insulation | D2-Forced - Delayed | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 178.7566 | 65.8 | 1 | 1 | 0840-Refractory and insulation | D2-Forced - Delayed | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 194.625 | 51.9 | 1 | 1 | 0840-Refractory and insulation | D2-Forced - Delayed | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 269.9166 | 102.5 | 1 | 1 | 0840-Refractory and insulation | D2-Forced - Delayed | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 388.3367 | 23.8 | 1 | 1 | 0840-Refractory and insulation | D2-Forced - Delayed | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2379 | 30.5 | 1 | 1 | 0840-Refractory and insulation | D2-Forced - Delayed | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2438.1533 | 9.2 | 1 | 1 | 0840-Refractory and insulation | D2-Forced - Delayed | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4950.3 | 26.1 | 1 | 1 | 0840-Refractory and insulation | D2-Forced - Delayed | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3887.1333 | 199 | 1 | 1 | 0840-Refractory and insulation | U1-Forced - Immediate | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 101.4666 | 152.2 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 11242.3583 | 39.5 | 1 | 1 | 0840-Refractory and insulation | D2-Forced - Delayed | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 113.245 | 31.9 | 1 | 1 | 0840-Refractory and insulation | D2-Forced - Delayed | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 191.4 | 52.2 | 1 | 1 | 0840-Refractory and insulation | D2-Forced - Delayed | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 300.7333 | 26 | 1 | 1 | 0840-Refractory and insulation | D2-Forced - Delayed | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 580.8 | 24.2 | 1 | 1 | 0840-Refractory and insulation | D2-Forced - Delayed | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 66864 | 199 | 1 | 1 | 0840-Refractory and insulation | U1-Forced - Immediate | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | U2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1796.2999 | 138 | 1 | 1 | 0840-Refractory and insulation | U2-Forced - Delayed | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 187.52 | 29.3 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 955.4133 | 83.2 | 1 | 1 | 0840-Refractory and insulation | D2-Forced - Delayed | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 14.55 | 48.5 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 40.8283 | 144.1 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 325.1833 | 54.5 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 42 | 3.5 | 1 | 1 | 0840-Refractory and insulation | D2-Forced - Delayed | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 140.1583 | 5.5 | 1 | 1 | 0840-Refractory and insulation | D2-Forced - Delayed | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7938 | 81 | 1 | 1 | 0840-Refractory and insulation | D2-Forced - Delayed | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7638.3317 | 35.3 | 1 | 1 | 0840-Refractory and insulation | D2-Forced - Delayed | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3280.1833 | 199 | 1 | 1 | 0840-Refractory and insulation | U1-Forced - Immediate | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 14.6 | 6 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 79.8766 | 154.6 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 81.345 | 56.1 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 72 | 2 | 1 | 1 | 0840-Refractory and insulation | D2-Forced - Delayed | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 275.4 | 32.4 | 1 | 1 | 0840-Refractory and insulation | D2-Forced - Delayed | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 394.1166 | 110.5 | 1 | 1 | 0840-Refractory and insulation | D2-Forced - Delayed | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1875.72 | 40.6 | 1 | 1 | 0840-Refractory and insulation | D2-Forced - Delayed | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2064.16 | 22.4 | 1 | 1 | 0840-Refractory and insulation | D2-Forced - Delayed | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7764.3165 | 199 | 1 | 1 | 0840-Refractory and insulation | U1-Forced - Immediate | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | U2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 14371.15 | 197 | 1 | 1 | 0840-Refractory and insulation | U2-Forced - Delayed | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 82.5 | 7.5 | 1 | 1 | 0840-Refractory and insulation | D2-Forced - Delayed | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6045 | 30 | 1 | 1 | 0840-Refractory and insulation | D2-Forced - Delayed | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 9.46 | 17.2 | 1 | 1 | 0840-Refractory and insulation | D2-Forced - Delayed | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 85.5 | 1.9 | 1 | 1 | 0840-Refractory and insulation | D2-Forced - Delayed | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 420.28 | 39.9 | 1 | 1 | 0840-Refractory and insulation | D2-Forced - Delayed | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1339.8 | 7.7 | 1 | 1 | 0840-Refractory and insulation | D2-Forced - Delayed | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 11.0283 | 50.9 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 65.7066 | 140.8 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 554 | 24 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 275.2 | 6.4 | 1 | 1 | 0840-Refractory and insulation | D2-Forced - Delayed | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 144 | 3 | 1 | 1 | 0840-Refractory and insulation | D2-Forced - Delayed | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 456.4 | 21 | 1 | 1 | 0840-Refractory and insulation | D2-Forced - Delayed | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 652.46 | 7.6 | 1 | 1 | 0840-Refractory and insulation | D2-Forced - Delayed | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2272.305 | 11.9 | 1 | 1 | 0840-Refractory and insulation | D2-Forced - Delayed | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | U2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 990 | 150 | 1 | 1 | 0840-Refractory and insulation | U2-Forced - Delayed | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 13.4933 | 36.8 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 36.025 | 144.1 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3407.0167 | 9.5 | 1 | 1 | 0840-Refractory and insulation | D2-Forced - Delayed | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 365.2 | 4.4 | 1 | 1 | 0840-Refractory and insulation | D2-Forced - Delayed | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | U3 | Forced - Postponed | 2013 | Coal | CC | 650 | Fluidized Bed | WECC | Summer | 4508.7 | 38 | 1 | 1 | 0840-Refractory and insulation | U3-Forced - Postponed | 650-Fluidized Bed
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Off-Peak | 9850.5 | 90 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0845 | Windbox expansion joints | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 235.8333 | 5 | 1 | 1 | 0845-Windbox expansion joints | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0845 | Windbox expansion joints | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 673.3333 | 10 | 1 | 1 | 0845-Windbox expansion joints | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0845 | Windbox expansion joints | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 316.8 | 3 | 1 | 1 | 0845-Windbox expansion joints | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0845 | Windbox expansion joints | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 682.5 | 15 | 1 | 1 | 0845-Windbox expansion joints | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0845 | Windbox expansion joints | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 405 | 9 | 1 | 1 | 0845-Windbox expansion joints | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0845 | Windbox expansion joints | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 2623.8332 | 182 | 1 | 1 | 0845-Windbox expansion joints | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0845 | Windbox expansion joints | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 1432 | 179 | 1 | 1 | 0845-Windbox expansion joints | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0845 | Windbox expansion joints | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 14030 | 184 | 1 | 1 | 0845-Windbox expansion joints | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0847 | Other expansion joints | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 91 | 70 | 1 | 1 | 0847-Other expansion joints | D1-Forced - Immediate | 100-Fossil-Steam
0847 | Other expansion joints | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 1189 | 410 | 1 | 1 | 0847-Other expansion joints | D1-Forced - Immediate | 100-Fossil-Steam
0847 | Other expansion joints | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4082.875 | 44.5 | 1 | 1 | 0847-Other expansion joints | D2-Forced - Delayed | 100-Fossil-Steam
0847 | Other expansion joints | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Gas | GG | 650 | Fluidized Bed | SERC | Off-Peak | 10871.2 | 42.8 | 1 | 1 | 0847-Other expansion joints | D1-Forced - Immediate | 650-Fluidized Bed
0847 | Other expansion joints | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Gas | GG | 650 | Fluidized Bed | SERC | Off-Peak | 19954.6566 | 69.8 | 1 | 1 | 0847-Other expansion joints | D1-Forced - Immediate | 650-Fluidized Bed
0847 | Other expansion joints | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 595 | 100 | 1 | 1 | 0847-Other expansion joints | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0847 | Other expansion joints | HRSG Boiler | HRSG Boiler Internals and Structures | D2 | Forced - Delayed | 2013 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 11715.833 | 425 | 1 | 1 | 0847-Other expansion joints | D2-Forced - Delayed | 850-Combined Cycle Block
0847 | Other expansion joints | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Gas | GG | 851 | CC GT units | MRO | Summer | 4391.5666 | 118 | 1 | 1 | 0847-Other expansion joints | U1-Forced - Immediate | 851-CC GT units
0847 | Other expansion joints | HRSG Boiler | HRSG Boiler Internals and Structures | U2 | Forced - Delayed | 2013 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 3478.75 | 55 | 1 | 1 | 0847-Other expansion joints | U2-Forced - Delayed | 851-CC GT units
0847 | Other expansion joints | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 4242.6999 | 114 | 1 | 1 | 0847-Other expansion joints | U1-Forced - Immediate | 852-CC steam units
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Oil | DI | 100 | Fossil-Steam | SERC | Off-Peak | 1885.7666 | 37 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6913 | 620 | 1 | 1 | 0850-Other internal or structural problems | U1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1112024.6999 | 243 | 1 | 1 | 0850-Other internal or structural problems | U1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | U3 | Forced - Postponed | 2013 | Other | BM | 100 | Fossil-Steam | SERC | Winter | 1595.2083 | 47.5 | 1 | 1 | 0850-Other internal or structural problems | U3-Forced - Postponed | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 8.4 | 2 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2835.4999 | 321 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Oil | DI | 100 | Fossil-Steam | SERC | Summer | 25.9667 | 38 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 361 | 19 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0850 | Other internal or structural problems | HRSG Boiler | HRSG Boiler Internals and Structures | SF | Startup Failure | 2013 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 1020.0016 | 341.9 | 1 | 1 | 0850-Other internal or structural problems | SF-Startup Failure | 850-Combined Cycle Block
0850 | Other internal or structural problems | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 37.9667 | 17 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 850-Combined Cycle Block
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 42.7333 | 2 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 7579.4958 | 90.25 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | SF | Startup Failure | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1488.8833 | 56.9 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | SF-Startup Failure | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2188.6663 | 490 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 290.15 | 21 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 637 | 130 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 223.1666 | 130 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 632 | 32 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 150.7833 | 83 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 8977.4997 | 405 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 73.5 | 35 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2.76 | 2.76 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | U2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 7845.4164 | 475 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | U2-Forced - Delayed | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | U3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 10480 | 262 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | U3-Forced - Postponed | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 50.75 | 7 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 212.5 | 34 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3053 | 142 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 16582.5 | 330 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5420.2499 | 405 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 220 | 80 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 272.4999 | 150 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3120 | 130 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 12740.9983 | 463.59 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 719.0997 | 459 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1751.6667 | 5 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 38.2666 | 28 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 566.0998 | 459 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 43648 | 352 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 67 | 30 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1096.5375 | 25.65 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1732.323 | 178.59 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 249.6 | 128 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 53.25 | 71 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D2-Forced - Delayed | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 3030.0666 | 105.7 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Off-Peak | 1056 | 80 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0856 | HP Drum relief/safety valves | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 183.3333 | 22 | 1 | 1 | 0856-HP Drum relief/safety valves | D1-Forced - Immediate | 850-Combined Cycle Block
0859 | Tube external fins/membranes A | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 78715.6664 | 340 | 1 | 1 | 0859-Tube external fins/membranes A | U1-Forced - Immediate | 100-Fossil-Steam
0859 | Tube external fins/membranes A | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2013 | Coal | OS | 100 | Fossil-Steam | NPCC | Summer | 232.3333 | 20 | 1 | 1 | 0859-Tube external fins/membranes A | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 600 | 300 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 823.0166 | 113 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 346 | 20 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 36.3333 | 20 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 559.9999 | 240 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3960 | 99 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D2-Forced - Delayed | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1233 | 90 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D3-Forced - Postponed | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 220 | 110 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1214.1665 | 310 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 107.26 | 34.6 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 235.4667 | 2 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 489.8833 | 91 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 800 | 20 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D2-Forced - Delayed | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 183.75 | 75 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D3-Forced - Postponed | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 412.25 | 85 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D3-Forced - Postponed | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 12 | 60 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 196 | 120 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 526.5 | 117 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7680 | 160 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 864 | 32 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D3-Forced - Postponed | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8083.6167 | 13 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1555.5 | 85 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | U2-Forced - Delayed | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 119.9973 | 52.94 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 130 | 260 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 165 | 220 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 660 | 15 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2074.9998 | 300 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 84.3333 | 55 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2544 | 53 | 2 | 2 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3120.6666 | 40 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D2-Forced - Delayed | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 499.4166 | 65 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D3-Forced - Postponed | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | SF | Startup Failure | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 8611.2 | 414 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | SF-Startup Failure | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 18 | 40 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 55 | 110 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 100 | 20 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1237.5 | 150 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2763 | 307 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 151.2333 | 26 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1833.3333 | 100 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4224 | 88 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 108.5 | 30 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D2-Forced - Delayed | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 58.3332 | 140 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 125 | 50 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1418.6665 | 190 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 35.8333 | 2 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 398.3333 | 100 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 88.5 | 90 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D3-Forced - Postponed | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 0.6 | 1 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 64.5 | 5 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 92.1667 | 5 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 150.15 | 39 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 226.25 | 15 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3465 | 30 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 165 | 300 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2031.25 | 75 | 1 | 1 | 0870-Soot blowers - steam | D2-Forced - Delayed | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 15270 | 200 | 1 | 1 | 0870-Soot blowers - steam | U2-Forced - Delayed | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 0.7205 | 1.31 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 42 | 7 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 457.1665 | 422 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1051.2016 | 263.9 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 14.3333 | 10 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 16.0333 | 26 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 168 | 40 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 369 | 90 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 514.5 | 30 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 0.1925 | 0.55 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 256.6666 | 200 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 776.9145 | 224.11 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1500 | 600 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 0.25 | 0.25 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 434 | 217 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 330 | 30 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 306.8 | 39 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 706.16 | 18.2 | 1 | 1 | 0870-Soot blowers - steam | D2-Forced - Delayed | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 479.75 | 101 | 1 | 1 | 0870-Soot blowers - steam | D3-Forced - Postponed | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 130 | 30 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 42 | 10 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 860.3833 | 247 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3894.5 | 30 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 683.6066 | 250.1 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 0.5 | 3 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 28.4166 | 55 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 258.0833 | 95 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2655.6665 | 620 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 18.6666 | 28 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 104 | 30 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 207 | 3 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1030 | 30 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 0.37583 | 2.05 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1248 | 72 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 141.25 | 75 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 15578.6662 | 736 | 1 | 1 | 0870-Soot blowers - steam | U2-Forced - Delayed | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1.1667 | 2 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 212.7 | 3 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 412 | 30 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 778.6667 | 5 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1426.4499 | 141 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4633 | 820 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1793 | 32.6 | 1 | 1 | 0870-Soot blowers - steam | D2-Forced - Delayed | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 266.1999 | 132 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2134.5 | 30 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 0.64067 | 1.24 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 59.01 | 19.67 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 129.2 | 38 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6.15 | 3 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 17 | 30 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 68.15 | 87 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 132.5 | 30 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 353.4666 | 88 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1121.9 | 6 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 269.1666 | 85 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 86.9167 | 35 | 1 | 1 | 0870-Soot blowers - steam | D2-Forced - Delayed | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 749.5833 | 35 | 1 | 1 | 0870-Soot blowers - steam | D2-Forced - Delayed | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 927.5 | 35 | 1 | 1 | 0870-Soot blowers - steam | D2-Forced - Delayed | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 24 | 6 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 650-Fluidized Bed
0871 | Soot blowers - sonic | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 0.15 | 0.2 | 1 | 1 | 0871-Soot blowers - sonic | D1-Forced - Immediate | 100-Fossil-Steam
0872 | Soot blowers - water | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 0.45 | 0.2 | 1 | 1 | 0872-Soot blowers - water | D2-Forced - Delayed | 100-Fossil-Steam
0872 | Soot blowers - water | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6 | 1.5 | 1 | 1 | 0872-Soot blowers - water | D1-Forced - Immediate | 100-Fossil-Steam
0872 | Soot blowers - water | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 0.4375 | 0.35 | 1 | 1 | 0872-Soot blowers - water | D1-Forced - Immediate | 100-Fossil-Steam
0872 | Soot blowers - water | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6822.0933 | 7.3 | 1 | 1 | 0872-Soot blowers - water | D1-Forced - Immediate | 100-Fossil-Steam
0872 | Soot blowers - water | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 0.0375 | 0.05 | 1 | 1 | 0872-Soot blowers - water | D1-Forced - Immediate | 100-Fossil-Steam
0872 | Soot blowers - water | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3 | 1 | 1 | 1 | 0872-Soot blowers - water | D1-Forced - Immediate | 100-Fossil-Steam
0872 | Soot blowers - water | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8 | 2 | 1 | 1 | 0872-Soot blowers - water | D1-Forced - Immediate | 100-Fossil-Steam
0872 | Soot blowers - water | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 171.25 | 75 | 1 | 1 | 0872-Soot blowers - water | D1-Forced - Immediate | 100-Fossil-Steam
0872 | Soot blowers - water | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 637.5 | 170 | 1 | 1 | 0872-Soot blowers - water | D1-Forced - Immediate | 100-Fossil-Steam
0872 | Soot blowers - water | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 886.6667 | 35 | 1 | 1 | 0872-Soot blowers - water | D1-Forced - Immediate | 100-Fossil-Steam
0872 | Soot blowers - water | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 8228.0666 | 166 | 1 | 1 | 0872-Soot blowers - water | D1-Forced - Immediate | 100-Fossil-Steam
0873 | Soot blower drives | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1411.1333 | 61 | 1 | 1 | 0873-Soot blower drives | D2-Forced - Delayed | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 93.8666 | 128 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 328.25 | 101 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 418.6666 | 160 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 569.25 | 115 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 679.2333 | 142 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 809.1 | 93 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 368.3333 | 10 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 150.5 | 70 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 127.4667 | 16 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 624.0332 | 194 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 746.9 | 194 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 165.3331 | 320 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 591.5 | 91 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 64.6666 | 40 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 101.5 | 30 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 242.6666 | 80 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 558 | 90 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 249.75 | 27.75 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 525.4167 | 25 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 643.8 | 444 | 1 | 1 | 0876-Soot blower controls | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 331.2 | 8 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 348.3333 | 50 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 738 | 82 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 23.5 | 94 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1514.6665 | 256 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2623.5332 | 236 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1514.75 | 73 | 2 | 2 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 20 | 10 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 21.0927 | 10.91 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 122.85 | 39 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 228 | 38 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 135.2 | 39 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D2-Forced - Delayed | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 2964 | 36 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | U1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1589.5 | 102 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8047 | 260 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4236.6665 | 620 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5.4667 | 8 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 120 | 72 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 443 | 12 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 9.1667 | 10 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 18.3333 | 11 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 92 | 16 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 0.75133 | 6.44 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 35 | 14 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 60 | 10 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 85.2 | 14.2 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 317.7499 | 93 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 493.5 | 210 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 867.7667 | 14 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 8333.3333 | 160 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1047.4999 | 150 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 204 | 102 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1889.5832 | 125 | 2 | 2 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 968 | 66 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1650.4166 | 85 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2290.3999 | 168 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4845.8332 | 125 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4875 | 125 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 22.6666 | 34 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 212.3333 | 28 | 2 | 2 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 390 | 90 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 594.5 | 41 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1211 | 173 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Other | BM | 100 | Fossil-Steam | SERC | Off-Peak | 409.4183 | 18.47 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 24.75 | 3.3 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 168 | 140 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D2-Forced - Delayed | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 827.25 | 45 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | U1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 253.5 | 30 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 276.6667 | 20 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1056 | 72 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 49 | 42 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 86 | 8 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 506.3332 | 140 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 14.6667 | 11 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 24 | 1.2 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 87.2 | 16 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 114.8 | 14 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D2-Forced - Delayed | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1705.6 | 328 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | U1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 94.3333 | 20 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 222.8 | 24 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 69.3333 | 52 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 118.9999 | 210 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 213.75 | 45 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1540 | 400 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 95 | 38 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 140 | 70 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 600.8333 | 103 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2711.5 | 110 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 18.75 | 45 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 34.5333 | 3.7 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1393 | 199 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 4.55 | 13 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 55.552 | 13.02 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2756.6999 | 162 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D2-Forced - Delayed | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 426.6 | 54 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | U1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 3440.7 | 54 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | U1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 49.5 | 110 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 213.5167 | 23 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3105 | 135 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 530.469 | 89.91 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 1085 | 175 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 86.6667 | 26 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 562.1 | 8.4 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 24.846 | 14.76 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 650 | Fluidized Bed | SERC | Winter | 5148 | 165 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 650-Fluidized Bed
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 3640 | 70 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 650-Fluidized Bed
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Gas | GG | 650 | Fluidized Bed | SERC | Summer | 4066.0799 | 154.8 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 650-Fluidized Bed
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 1147.6665 | 313 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 5605.6665 | 268 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 11323 | 268 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 240.7999 | 168 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0885 | Fly ash Removal System - wet transport | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 105 | 105 | 1 | 1 | 0885-Fly ash Removal System - wet transport | D1-Forced - Immediate | 100-Fossil-Steam
0885 | Fly ash Removal System - wet transport | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 957.6666 | 170 | 1 | 1 | 0885-Fly ash Removal System - wet transport | D1-Forced - Immediate | 100-Fossil-Steam
0885 | Fly ash Removal System - wet transport | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1599.75 | 237 | 1 | 1 | 0885-Fly ash Removal System - wet transport | D1-Forced - Immediate | 100-Fossil-Steam
0885 | Fly ash Removal System - wet transport | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2013 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 1246.9035 | 437.51 | 1 | 1 | 0885-Fly ash Removal System - wet transport | U1-Forced - Immediate | 100-Fossil-Steam
0885 | Fly ash Removal System - wet transport | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 217.5 | 290 | 1 | 1 | 0885-Fly ash Removal System - wet transport | D1-Forced - Immediate | 100-Fossil-Steam
0885 | Fly ash Removal System - wet transport | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 302.5 | 110 | 1 | 1 | 0885-Fly ash Removal System - wet transport | D1-Forced - Immediate | 100-Fossil-Steam
0885 | Fly ash Removal System - wet transport | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1057.5 | 90 | 1 | 1 | 0885-Fly ash Removal System - wet transport | D1-Forced - Immediate | 100-Fossil-Steam
0885 | Fly ash Removal System - wet transport | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2756.5 | 370 | 1 | 1 | 0885-Fly ash Removal System - wet transport | D1-Forced - Immediate | 100-Fossil-Steam
0885 | Fly ash Removal System - wet transport | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 845.4998 | 267 | 1 | 1 | 0885-Fly ash Removal System - wet transport | D1-Forced - Immediate | 100-Fossil-Steam
0885 | Fly ash Removal System - wet transport | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 846.4332 | 379 | 1 | 1 | 0885-Fly ash Removal System - wet transport | D3-Forced - Postponed | 100-Fossil-Steam
0885 | Fly ash Removal System - wet transport | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2142.2499 | 165 | 1 | 1 | 0885-Fly ash Removal System - wet transport | D1-Forced - Immediate | 100-Fossil-Steam
0885 | Fly ash Removal System - wet transport | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7397.3331 | 320 | 1 | 1 | 0885-Fly ash Removal System - wet transport | D1-Forced - Immediate | 100-Fossil-Steam
0885 | Fly ash Removal System - wet transport | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 412.5 | 110 | 1 | 1 | 0885-Fly ash Removal System - wet transport | D1-Forced - Immediate | 100-Fossil-Steam
0885 | Fly ash Removal System - wet transport | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8602.5 | 370 | 1 | 1 | 0885-Fly ash Removal System - wet transport | D1-Forced - Immediate | 100-Fossil-Steam
0885 | Fly ash Removal System - wet transport | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 747.3332 | 152 | 1 | 1 | 0885-Fly ash Removal System - wet transport | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 131.15 | 43 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | OS | 100 | Fossil-Steam | NPCC | Summer | 4.1667 | 5 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | OS | 100 | Fossil-Steam | NPCC | Winter | 5.6667 | 4 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 51346.7496 | 555 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 39.5832 | 125 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 65.55 | 21.85 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 61.25 | 105 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 98 | 12.25 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 275.1999 | 96 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 595 | 140 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1518 | 138 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 1752.75 | 42.75 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 646.7499 | 195 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 774.9999 | 300 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1160.7666 | 194 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 50.9332 | 191 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D3-Forced - Postponed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1559.6667 | 20 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D3-Forced - Postponed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 22.2333 | 46 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 51.3 | 17.1 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 592.8 | 45.6 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 1159.95 | 31.35 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3923.2665 | 196 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | OS | 100 | Fossil-Steam | NPCC | Off-Peak | 44.3333 | 28 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 59.43 | 12.6 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 81939.9997 | 510 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 15752.8 | 812 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1.4667 | 2 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 977.3 | 337 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | OS | 100 | Fossil-Steam | NPCC | Off-Peak | 15.7 | 2 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | OS | 100 | Fossil-Steam | NPCC | Summer | 77.25 | 9 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | OS | 100 | Fossil-Steam | NPCC | Winter | 36.3333 | 4 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 115656 | 395 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 31.35 | 10.45 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 164.39 | 164.39 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 313.5 | 31.35 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1451.9166 | 131 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2902.6666 | 140 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 375.4693 | 16.48 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | OS | 100 | Fossil-Steam | NPCC | Summer | 16.3333 | 5 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 69.5833 | 25 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 754 | 58 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 43723.1161 | 817 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 110905.6664 | 812 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 80162.1331 | 616 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 43.7 | 21.85 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 382.6999 | 267 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1437.73 | 205.39 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 32.25 | 43 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 62.7 | 31.35 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 78 | 78 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 7998 | 186 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | OS | 100 | Fossil-Steam | NPCC | Summer | 36.6667 | 5 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | OS | 100 | Fossil-Steam | NPCC | Winter | 60 | 5 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | OS | 100 | Fossil-Steam | SERC | Winter | 138.0917 | 36.5 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1244.4366 | 186.2 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 1097.9999 | 216 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 29820 | 700 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 7590.2307 | 154.85 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U3-Forced - Postponed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 468 | 78 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 3682.2 | 36.1 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 13.6 | 8 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 65.4333 | 1.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 474 | 158 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3197.25 | 105 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2001.9999 | 105 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 20 | 60 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 72.2 | 18.05 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 496.8666 | 257 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 775.2 | 45.6 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1773.3331 | 350 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 58 | 58 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 190 | 23.75 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 207.1666 | 110 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 611.1332 | 206 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1973.9999 | 252 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 233.75 | 46.75 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 348 | 58 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 175.8667 | 8 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D3-Forced - Postponed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 12867.75 | 817 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 90930.4664 | 812 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 100 | 12 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 650-Fluidized Bed
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 420 | 30 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 650-Fluidized Bed
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 134.4 | 32 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 650-Fluidized Bed
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 134.3333 | 62 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 4387.1333 | 49 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 348 | 29 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 69.7667 | 13 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2013 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 88 | 22 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D3-Forced - Postponed | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 168.45 | 9 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 1440 | 30 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 359.0167 | 13 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 225.1167 | 13 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 1232 | 56 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 312 | 13 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 660 | 30 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 300 | 30 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 139.1 | 26 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 380.25 | 13 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 778.9166 | 65 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 3223.2 | 36 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Winter | 237.1137 | 12.91 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 564.167 | 12.91 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 355.68 | 10.8 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 161.7027 | 4.91 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Winter | 468.5778 | 9.91 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 215.549 | 4.91 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Winter | 530.3502 | 9.91 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Off-Peak | 220 | 20 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Winter | 510.66 | 10.8 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 471.96 | 10.8 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Off-Peak | 474.12 | 10.8 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 587.5 | 235 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 17001.833 | 494 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | U1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3561.25 | 385 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | U2-Forced - Delayed | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | U3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 11193.6 | 352 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | U3-Forced - Postponed | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 539.4 | 124 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2016.5166 | 227 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 159.5817 | 18.1 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | U1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 28.4166 | 55 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 56.25 | 75 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 62.5 | 125 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 735.5332 | 236 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 79999.9995 | 750 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | U1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 2942.7 | 577 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | U1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 7999.9995 | 750 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | U1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 40.5333 | 16 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 255 | 170 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8628.3329 | 620 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 412 | 206 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 9982.5 | 330 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | U1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 837.8 | 23.6 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | U1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 100 | 200 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 131.25 | 175 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 157.9998 | 237 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1212 | 202 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 50 | 25 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 800-Miscellaneous
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 16.65 | 1 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 183.5166 | 121 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 518.0999 | 198 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 16 | 16 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 43 | 21.5 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 43.5 | 43.5 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 45.16 | 45.16 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 46.04 | 46.04 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 51 | 25.5 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | OS | 100 | Fossil-Steam | NPCC | Summer | 180.25 | 21 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9082.6666 | 320 | 1 | 1 | 0892-Bottom ash clinker grinders | U1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5983 | 193 | 1 | 1 | 0892-Bottom ash clinker grinders | U1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1381.3667 | 29 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2293.9999 | 120 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 7 | 7 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 14 | 14 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 15 | 15 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 35.5 | 35.5 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 49.11 | 49.11 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 73.2416 | 79.9 | 1 | 1 | 0892-Bottom ash clinker grinders | D3-Forced - Postponed | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 145.3833 | 79.3 | 1 | 1 | 0892-Bottom ash clinker grinders | D3-Forced - Postponed | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | U3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3814.5332 | 469 | 1 | 1 | 0892-Bottom ash clinker grinders | U3-Forced - Postponed | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 412.5333 | 208 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2148.2665 | 304 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 511.75 | 69 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1133.2665 | 178 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 39 | 39 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 47.04 | 47.04 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 351.87 | 117.29 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 305.6 | 12 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 12.5 | 25 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 960.1333 | 76 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 38.66 | 38.66 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 312 | 18 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 274.505 | 102.3 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 35.36 | 35.36 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 41 | 41 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 0 | 0 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4369.7 | 118.1 | 1 | 1 | 0892-Bottom ash clinker grinders | D2-Forced - Delayed | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 52.7999 | 79.2 | 1 | 1 | 0892-Bottom ash clinker grinders | D3-Forced - Postponed | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 55.9333 | 83.9 | 1 | 1 | 0892-Bottom ash clinker grinders | D3-Forced - Postponed | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 104.25 | 83.4 | 1 | 1 | 0892-Bottom ash clinker grinders | D3-Forced - Postponed | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1557 | 54 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3138.7333 | 178 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 20 | 20 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 28 | 28 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 40.83 | 40.83 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 43.6 | 43.6 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 46.88 | 46.88 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 78 | 39 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 48.24 | 80.4 | 1 | 1 | 0892-Bottom ash clinker grinders | D3-Forced - Postponed | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 990 | 220 | 1 | 1 | 0892-Bottom ash clinker grinders | U1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 438.3333 | 100 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 27 | 27 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 35 | 17.5 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 41.5 | 41.5 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 42.79 | 42.79 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 53.7333 | 80.6 | 1 | 1 | 0892-Bottom ash clinker grinders | D3-Forced - Postponed | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 956.8165 | 307 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 21.16 | 21.16 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 24 | 24 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 31 | 15.5 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 33 | 33 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 36 | 36 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 42.73 | 42.73 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 57 | 28.5 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 134.9833 | 13 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 800-Miscellaneous
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2013 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 643.5 | 22 | 1 | 1 | 0892-Bottom ash clinker grinders | U1-Forced - Immediate | 800-Miscellaneous
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 378.7 | 14 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 800-Miscellaneous
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 19.5 | 13 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 800-Miscellaneous
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 95.1167 | 13 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 800-Miscellaneous
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 511.3333 | 26 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 800-Miscellaneous
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 196.95 | 13 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 800-Miscellaneous
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 3134.3 | 39 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 800-Miscellaneous
0893 | Bottom ash water pumps and motors | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 513.0832 | 131 | 1 | 1 | 0893-Bottom ash water pumps and motors | D1-Forced - Immediate | 100-Fossil-Steam
0893 | Bottom ash water pumps and motors | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3573.3333 | 160 | 1 | 1 | 0893-Bottom ash water pumps and motors | D1-Forced - Immediate | 100-Fossil-Steam
0893 | Bottom ash water pumps and motors | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3721.5833 | 85 | 1 | 1 | 0893-Bottom ash water pumps and motors | D1-Forced - Immediate | 100-Fossil-Steam
0893 | Bottom ash water pumps and motors | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3064.25 | 85 | 1 | 1 | 0893-Bottom ash water pumps and motors | D1-Forced - Immediate | 100-Fossil-Steam
0893 | Bottom ash water pumps and motors | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 11.6666 | 100 | 1 | 1 | 0893-Bottom ash water pumps and motors | D1-Forced - Immediate | 100-Fossil-Steam
0893 | Bottom ash water pumps and motors | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 21.6667 | 13 | 1 | 1 | 0893-Bottom ash water pumps and motors | D1-Forced - Immediate | 800-Miscellaneous
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 93.5 | 187 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 198 | 99 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1773.75 | 165 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2045.4833 | 53.5 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 98.3 | 98.3 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1572.5 | 170 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 225 | 225 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 57.75 | 77 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 372.1666 | 110 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 536.6666 | 350 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2179.3 | 57 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5663.3332 | 200 | 1 | 1 | 0894-Bottom ash piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 334.83 | 111.61 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 621.4 | 155.35 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 85.25 | 31 | 1 | 1 | 0894-Bottom ash piping and valves | D2-Forced - Delayed | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 650 | Fluidized Bed | WECC | Summer | 1265.14 | 37.21 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 650-Fluidized Bed
0895 | Ashpit trouble | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 298.6666 | 112 | 1 | 1 | 0895-Ashpit trouble | D1-Forced - Immediate | 100-Fossil-Steam
0895 | Ashpit trouble | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 349.9999 | 168 | 1 | 1 | 0895-Ashpit trouble | D1-Forced - Immediate | 100-Fossil-Steam
0895 | Ashpit trouble | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 33.7333 | 46 | 1 | 1 | 0895-Ashpit trouble | D1-Forced - Immediate | 100-Fossil-Steam
0895 | Ashpit trouble | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 268.755 | 36.9 | 1 | 1 | 0895-Ashpit trouble | D1-Forced - Immediate | 100-Fossil-Steam
0896 | Bottom ash dewatering bin system; instruments and controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3007.7499 | 159 | 1 | 1 | 0896-Bottom ash dewatering bin system; instruments and controls | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 251.7333 | 118 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 298.8331 | 326 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3025.6665 | 313 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4766.6665 | 220 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 2140.4332 | 409 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 116.2 | 12 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 281.6333 | 119 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 929.3333 | 205 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1087.3332 | 233 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1834.6665 | 256 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 2531.5 | 305 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 904.7 | 218 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 907.3 | 211 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 936.3499 | 183 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1065.9332 | 236 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 1740 | 150 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 922.25 | 119 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 225.7 | 61 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1854.6165 | 223 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 367.8666 | 124 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 0 | 0 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 1320 | 24 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 316 | 158 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 364.8333 | 110 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 710.9499 | 177 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1003.3999 | 174 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 588.8666 | 146 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 397.4999 | 90 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 421.1666 | 133 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 966.1666 | 170 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 20764.3332 | 385 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2286.5499 | 417 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 145.5999 | 96 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 309.3333 | 160 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 5320.9998 | 255 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 7193.9 | 239 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 106.3333 | 55 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 2726.4 | 284 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 0 | 0 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2592 | 324 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 473.7666 | 61 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 3614.6498 | 249 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 6441.6163 | 523 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 60103.3331 | 760 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 437.8332 | 185 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 127.6 | 22 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 108 | 108 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1040 | 208 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 200.5833 | 145 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1915.9666 | 251 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 468 | 130 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 44076.2496 | 555 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2013 | Oil | DI | 100 | Fossil-Steam | SERC | Winter | 580 | 58 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 11808.9998 | 588 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 567 | 126 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 78 | 78 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 227.4999 | 273 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 660.4849 | 237.3 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 630.8 | 152 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 799.9666 | 206 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 99673 | 812 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1020.1416 | 161.5 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 394.8 | 188 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 77.7333 | 53 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 530.8333 | 130 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 444.95 | 33 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 155 | 10 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 931.5 | 207 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 7449.8665 | 208 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 722.65 | 149 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 177.3333 | 56 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 897.5166 | 157 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2547.9997 | 840 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 5770.4581 | 351.5 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 293.8333 | 86 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1127.25 | 167 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1679.9999 | 288 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Oil | DI | 100 | Fossil-Steam | SERC | Winter | 376.8 | 36 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Oil | DI | 100 | Fossil-Steam | SERC | Winter | 843 | 36 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1248 | 208 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2360.1665 | 238 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 409.05 | 101 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1506.5 | 262 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 5277.5665 | 494 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 7147.6663 | 523 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 84798 | 840 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 30497.5996 | 588 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 964.2665 | 226 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 730.9166 | 179 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1471.5 | 218 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 2091.9998 | 240 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 201.8333 | 10 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 1204 | 14 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1263.7498 | 225 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1449.1665 | 235 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 635.1 | 174 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1147.4665 | 208 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 3171.3498 | 273 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 22515.5665 | 446 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 1042.0667 | 44 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2013 | Other | WD | 800 | Miscellaneous | WECC | Summer | 228.225 | 17.9 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U2-Forced - Delayed | 800-Miscellaneous
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 667.3333 | 26 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 800-Miscellaneous
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 129.5667 | 26 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 800-Miscellaneous
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 960.9167 | 13 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 800-Miscellaneous
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 734.5 | 26 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 800-Miscellaneous
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2013 | Other | WD | 800 | Miscellaneous | WECC | Summer | 714.5083 | 17.9 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U2-Forced - Delayed | 800-Miscellaneous
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 171.1667 | 26 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 800-Miscellaneous
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 133.25 | 13 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 800-Miscellaneous
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 222.3 | 26 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 800-Miscellaneous
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2013 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Summer | 1080.16 | 25.8 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0898 | Bottom ash pyrite hopper (pulverizer reject) system | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 91.2499 | 75 | 1 | 1 | 0898-Bottom ash pyrite hopper (pulverizer reject) system | D1-Forced - Immediate | 100-Fossil-Steam
0898 | Bottom ash pyrite hopper (pulverizer reject) system | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1203.75 | 75 | 1 | 1 | 0898-Bottom ash pyrite hopper (pulverizer reject) system | D1-Forced - Immediate | 100-Fossil-Steam
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 27.4666 | 206 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | D1-Forced - Immediate | 100-Fossil-Steam
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 123.4999 | 195 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | U1-Forced - Immediate | 100-Fossil-Steam
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 7556.25 | 93 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | U1-Forced - Immediate | 100-Fossil-Steam
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 258.85 | 93 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | D1-Forced - Immediate | 100-Fossil-Steam
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 117 | 78 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | D1-Forced - Immediate | 100-Fossil-Steam
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 179.9425 | 25.05 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | U1-Forced - Immediate | 100-Fossil-Steam
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 525.213 | 193.33 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | D1-Forced - Immediate | 100-Fossil-Steam
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 66.3 | 78 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | D1-Forced - Immediate | 100-Fossil-Steam
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 463.5999 | 114 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | D1-Forced - Immediate | 100-Fossil-Steam
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1001 | 143 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | D1-Forced - Immediate | 100-Fossil-Steam
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4315.9999 | 195 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | U1-Forced - Immediate | 100-Fossil-Steam
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3408.8333 | 113 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | U1-Forced - Immediate | 100-Fossil-Steam
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2231.3663 | 511 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | U1-Forced - Immediate | 100-Fossil-Steam
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1741.6665 | 190 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | D3-Forced - Postponed | 100-Fossil-Steam
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6635.85 | 83 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | U1-Forced - Immediate | 100-Fossil-Steam
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 23890.9 | 587 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | U1-Forced - Immediate | 100-Fossil-Steam
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 18808.9999 | 210 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | U1-Forced - Immediate | 100-Fossil-Steam
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2049.1667 | 50 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | D1-Forced - Immediate | 100-Fossil-Steam
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 5514.9 | 93 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | U1-Forced - Immediate | 100-Fossil-Steam
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 94363.15 | 359 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | U2-Forced - Delayed | 100-Fossil-Steam
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2040 | 200 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | U1-Forced - Immediate | 100-Fossil-Steam
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 120.2499 | 195 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | U1-Forced - Immediate | 100-Fossil-Steam
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 7836 | 120 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | U1-Forced - Immediate | 100-Fossil-Steam
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 4180.5664 | 334 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | U2-Forced - Delayed | 100-Fossil-Steam
0910 | Slag-tap (other than cyclone furnace) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 26.1667 | 10 | 1 | 1 | 0910-Slag-tap (other than cyclone furnace) | D1-Forced - Immediate | 100-Fossil-Steam
0910 | Slag-tap (other than cyclone furnace) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 531.8999 | 81 | 1 | 1 | 0910-Slag-tap (other than cyclone furnace) | D1-Forced - Immediate | 100-Fossil-Steam
0910 | Slag-tap (other than cyclone furnace) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3935.5333 | 247 | 1 | 1 | 0910-Slag-tap (other than cyclone furnace) | U1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 21.1666 | 127 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 212.5 | 170 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 261 | 174 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 545.05 | 33 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 33.8333 | 70 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 65.6667 | 20 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 869.4 | 108 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1030 | 120 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1538.5 | 170 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1589 | 227 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 350 | 70 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 774.3333 | 202 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 816.4999 | 213 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1452 | 242 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2000 | 250 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 39.8898 | 17.47 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 57.9422 | 17.47 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 32.5115 | 13.27 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 132.1772 | 6.67 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 1491.55 | 23 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 15.9 | 5.3 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 19.1708 | 46.01 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 28.8 | 72 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 32.4 | 72 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 33.5988 | 65.03 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 35.2 | 42.24 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 38 | 76 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 8 | 48 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 11.855 | 71.13 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 14.3 | 33 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 20.043 | 70.74 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 32.1008 | 55.03 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 37.5025 | 64.29 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 38 | 76 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 385 | 35 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2376 | 237.6 | 1 | 1 | 0920-Other slag and ash removal problems A | D3-Forced - Postponed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 18867.6664 | 460 | 1 | 1 | 0920-Other slag and ash removal problems A | U1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 40166.5 | 670 | 1 | 1 | 0920-Other slag and ash removal problems A | U1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 18928.3331 | 820 | 1 | 1 | 0920-Other slag and ash removal problems A | U1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 33.5 | 67 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 79.5 | 53 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 650 | 125 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1947 | 330 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 11105.3333 | 80 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 56.3333 | 10 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 668 | 167 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 4095 | 135 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 22.4 | 56 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 8.649 | 8.37 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 668 | 167 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1401 | 233.5 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 9.33 | 55.98 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 12.6616 | 75.97 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 25.3 | 66 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 32.0925 | 58.35 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 32.4983 | 57.35 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 33.7499 | 81 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 36.85 | 67 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 35.8291 | 85.99 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6875 | 275 | 1 | 1 | 0920-Other slag and ash removal problems A | D3-Forced - Postponed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7468.2 | 248.94 | 1 | 1 | 0920-Other slag and ash removal problems A | D3-Forced - Postponed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 895.9 | 527 | 1 | 1 | 0920-Other slag and ash removal problems A | U1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 1530 | 45 | 1 | 1 | 0920-Other slag and ash removal problems A | U1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 3156.3 | 334 | 1 | 1 | 0920-Other slag and ash removal problems A | U2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 96.6667 | 20 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 102.6667 | 22 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 481.3999 | 174 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 39.25 | 157 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 131 | 262 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 193.8 | 68 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 682.2332 | 194 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1170 | 260 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3629.9999 | 225 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 14.1667 | 5 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 428 | 107 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3822 | 120 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 39.1 | 102 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 141.3333 | 106 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 28.3093 | 13.27 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 208 | 26 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 240 | 96 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 790.8331 | 365 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 21.8693 | 82.01 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 22.6666 | 68 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 40.5 | 81 | 1 | 2 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 71.4583 | 85.75 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 113.4332 | 340.3 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 27.3333 | 82 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 17.5 | 50 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 30 | 60 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 32.77 | 32.77 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 3053.5 | 394 | 1 | 1 | 0920-Other slag and ash removal problems A | D3-Forced - Postponed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 245.8267 | 20.6 | 1 | 1 | 0920-Other slag and ash removal problems A | D3-Forced - Postponed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 71158.1 | 431 | 1 | 1 | 0920-Other slag and ash removal problems A | U1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 693.3333 | 20 | 1 | 1 | 0920-Other slag and ash removal problems A | U1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5957.3 | 82 | 1 | 1 | 0920-Other slag and ash removal problems A | U2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 27.4667 | 8 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 291 | 97 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 870 | 174 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 921.4333 | 154 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1153.1666 | 110 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9.3333 | 5 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 41.6667 | 10 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1219.1665 | 190 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 927.9666 | 194 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1343 | 170 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1468.1331 | 308 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 30.9 | 20.6 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 20.2382 | 15.77 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Oil | DI | 100 | Fossil-Steam | SERC | Summer | 107.6667 | 38 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 32.66 | 32.66 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 17.6 | 70.4 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 19.7333 | 37 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 21.5333 | 76 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 21.5999 | 81 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 26.4 | 72 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 28.6 | 52 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 31.2043 | 72.01 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 34.6666 | 52 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 35.3333 | 42.4 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 73.1859 | 102.12 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2624.4164 | 409 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 19.131 | 81.99 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 46.74 | 93.48 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 12.3016 | 33.55 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 35.4713 | 76.01 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 37.3266 | 55.99 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 300 | 150 | 1 | 1 | 0920-Other slag and ash removal problems A | D3-Forced - Postponed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 950 | 475 | 1 | 1 | 0920-Other slag and ash removal problems A | D3-Forced - Postponed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 661.5 | 294 | 1 | 1 | 0920-Other slag and ash removal problems A | D3-Forced - Postponed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 9165.15 | 93 | 1 | 1 | 0920-Other slag and ash removal problems A | U1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 101292.7997 | 816 | 1 | 1 | 0920-Other slag and ash removal problems A | U1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 357 | 20 | 1 | 1 | 0920-Other slag and ash removal problems A | U1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 7485.8329 | 650 | 1 | 1 | 0920-Other slag and ash removal problems A | U2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 31 | 15.5 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1377.5 | 290 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2169.1 | 109 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 550 | 50 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2315.7499 | 177 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 298 | 149 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 376.8333 | 95 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 487.3333 | 172 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 724.9999 | 174 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 22.7802 | 13.27 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 30.6885 | 14.97 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 21.199 | 12.47 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 27.8928 | 16.57 | 1 | 2 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 30.938 | 14.97 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 42.5297 | 16.57 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 139.8333 | 10 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 192 | 24 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 4.5 | 30 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 18.7 | 66 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 20.67 | 62.01 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 21.4705 | 56.01 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 29.5791 | 70.99 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 34.1708 | 82.01 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 37.2 | 72 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 41 | 82 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 41.9 | 50.28 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 57.5983 | 98.74 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 778.7498 | 267 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 18.0708 | 43.37 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 50.1 | 66.8 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 56.9013 | 72.64 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1543.01 | 220.43 | 1 | 1 | 0920-Other slag and ash removal problems A | D3-Forced - Postponed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 352 | 88 | 1 | 1 | 0920-Other slag and ash removal problems A | D3-Forced - Postponed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 66139.9998 | 600 | 1 | 1 | 0920-Other slag and ash removal problems A | U1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 1162.4998 | 450 | 1 | 1 | 0920-Other slag and ash removal problems A | U1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1697.8332 | 334 | 1 | 1 | 0920-Other slag and ash removal problems A | U2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2883.5332 | 334 | 1 | 1 | 0920-Other slag and ash removal problems A | U2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 233.75 | 127.5 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2725.9999 | 120 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 280 | 60 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 4523.3332 | 460 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 248.2 | 73 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1462 | 120 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 317.52 | 12.6 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 34.1815 | 14.97 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 86.5765 | 14.97 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 617.4 | 196 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 12.404 | 31.01 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 34.8 | 72 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 37.295 | 74.59 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 171.9691 | 121.39 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 10742.533 | 452 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 25.8 | 86 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 22.4 | 56 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 33.5958 | 36.65 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1984.96 | 248.12 | 1 | 1 | 0920-Other slag and ash removal problems A | D3-Forced - Postponed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2346.03 | 260.67 | 1 | 1 | 0920-Other slag and ash removal problems A | D3-Forced - Postponed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 976 | 244 | 1 | 1 | 0920-Other slag and ash removal problems A | D3-Forced - Postponed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 16528.4165 | 247 | 1 | 1 | 0920-Other slag and ash removal problems A | U1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 18759.2 | 524 | 1 | 1 | 0920-Other slag and ash removal problems A | U1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 281.0666 | 136 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 316 | 120 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 361.05 | 87 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 783 | 174 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1305.08 | 46.61 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 181.25 | 75 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 260.8333 | 10 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 319.2 | 18 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 376.25 | 175 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2341.6665 | 250 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2739.7499 | 117 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4861.8666 | 128 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6076 | 217 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7074.3333 | 190 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 749.6499 | 141 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 847.3332 | 248 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3348.75 | 141 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 67.8892 | 19.87 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 10.1747 | 5.87 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | OS | 100 | Fossil-Steam | MRO | Summer | 99.301 | 14.97 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 121.9 | 5.3 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 27.4867 | 13.3 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 408 | 34 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 668 | 167 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1529.3333 | 148 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 11.25 | 33.75 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 28.9 | 57.8 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 34.5 | 69 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 61.0999 | 91.65 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 17.2663 | 47.09 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 32.5 | 48.75 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 32.8041 | 78.73 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 34.2 | 76 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 39.402 | 35.82 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 44.8 | 44.8 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7828.3332 | 275 | 1 | 1 | 0920-Other slag and ash removal problems A | D3-Forced - Postponed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 14924.4165 | 395 | 1 | 1 | 0920-Other slag and ash removal problems A | U1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1547.9996 | 540 | 1 | 1 | 0920-Other slag and ash removal problems A | U1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 46483.5 | 570 | 1 | 1 | 0920-Other slag and ash removal problems A | U1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 120 | 20 | 1 | 1 | 0920-Other slag and ash removal problems A | U1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 704.7333 | 124 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1303.3332 | 170 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 92.25 | 135 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1530 | 85 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2199.7999 | 204 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3821.1666 | 227 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 797.3333 | 184 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1332.4165 | 271 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2448 | 136 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | OS | 100 | Fossil-Steam | MRO | Off-Peak | 99.9723 | 16.57 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 25.6667 | 5 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 16.8 | 72 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 17.7301 | 55.99 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 23.3291 | 55.99 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 25.3333 | 76 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 25.43 | 76.29 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 32.32 | 48.48 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 46.8 | 52 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 645 | 215 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 27.9 | 83.7 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 33.005 | 66.01 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 35.1 | 78 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 471.8716 | 182.66 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2581 | 145 | 1 | 1 | 0920-Other slag and ash removal problems A | D3-Forced - Postponed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2191 | 313 | 1 | 1 | 0920-Other slag and ash removal problems A | D3-Forced - Postponed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1102.5 | 294 | 1 | 1 | 0920-Other slag and ash removal problems A | D3-Forced - Postponed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1176 | 294 | 1 | 7 | 0920-Other slag and ash removal problems A | D3-Forced - Postponed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 3152 | 394 | 1 | 1 | 0920-Other slag and ash removal problems A | D3-Forced - Postponed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 379.9999 | 120 | 1 | 1 | 0920-Other slag and ash removal problems A | U1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 24178.45 | 93 | 1 | 1 | 0920-Other slag and ash removal problems A | U1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 84 | 3.5 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 650-Fluidized Bed
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2013 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 287.0833 | 32.5 | 1 | 1 | 0920-Other slag and ash removal problems A | U1-Forced - Immediate | 650-Fluidized Bed
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 7 | 3.5 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 650-Fluidized Bed
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 47.875 | 7.5 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 650-Fluidized Bed
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2013 | Coal | OS | 800 | Miscellaneous | SERC | Winter | 4 | 2 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 800-Miscellaneous
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 341.1667 | 23 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 800-Miscellaneous
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 2041 | 13 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 800-Miscellaneous
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 2018.25 | 39 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 800-Miscellaneous
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 624 | 26 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 800-Miscellaneous
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 2232.75 | 13 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 800-Miscellaneous
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 84.2833 | 13 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 800-Miscellaneous
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2013 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 129.5667 | 13 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 800-Miscellaneous
0930 | Bed material coolers | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2013 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 6416 | 320 | 1 | 1 | 0930-Bed material coolers | D1-Forced - Immediate | 650-Fluidized Bed
0930 | Bed material coolers | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2013 | Coal | CC | 650 | Fluidized Bed | SERC | Winter | 30152.85 | 329 | 1 | 1 | 0930-Bed material coolers | D1-Forced - Immediate | 650-Fluidized Bed
0931 | Bed material transport piping/valves | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2013 | Gas | GG | 650 | Fluidized Bed | SERC | Winter | 4153.95 | 325.8 | 1 | 1 | 0931-Bed material transport piping/valves | D1-Forced - Immediate | 650-Fluidized Bed
0931 | Bed material transport piping/valves | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2013 | Gas | GG | 650 | Fluidized Bed | SERC | Winter | 10273.5599 | 325.8 | 1 | 1 | 0931-Bed material transport piping/valves | D1-Forced - Immediate | 650-Fluidized Bed
0932 | Bed material transport tanks/hoppers | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2013 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 15984 | 320 | 1 | 1 | 0932-Bed material transport tanks/hoppers | D1-Forced - Immediate | 650-Fluidized Bed
0932 | Bed material transport tanks/hoppers | Boiler | Bed Material Removal System (fbc) | U1 | Forced - Immediate | 2013 | Gas | PC | 862 | CoG steam units | SERC | Summer | 137.7437 | 34.58 | 1 | 1 | 0932-Bed material transport tanks/hoppers | U1-Forced - Immediate | 862-CoG steam units
0933 | Bed material fans/blowers | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2013 | Gas | GG | 650 | Fluidized Bed | SERC | Winter | 76.3666 | 58 | 1 | 1 | 0933-Bed material fans/blowers | D1-Forced - Immediate | 650-Fluidized Bed
0933 | Bed material fans/blowers | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2013 | Gas | GG | 650 | Fluidized Bed | SERC | Winter | 143.1 | 53 | 1 | 1 | 0933-Bed material fans/blowers | D1-Forced - Immediate | 650-Fluidized Bed
0933 | Bed material fans/blowers | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2013 | Gas | GG | 650 | Fluidized Bed | SERC | Winter | 82 | 328 | 1 | 1 | 0933-Bed material fans/blowers | D1-Forced - Immediate | 650-Fluidized Bed
0933 | Bed material fans/blowers | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2013 | Gas | GG | 650 | Fluidized Bed | SERC | Winter | 2431.66 | 315.8 | 1 | 1 | 0933-Bed material fans/blowers | D1-Forced - Immediate | 650-Fluidized Bed
0936 | Bed material conveyors B | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2013 | Coal | OS | 650 | Fluidized Bed | RFC | Off-Peak | 230.1333 | 16 | 1 | 1 | 0936-Bed material conveyors B | D1-Forced - Immediate | 650-Fluidized Bed
0950 | Other bed material system problems | NULL | NULL | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 21 | 7 | 1 | 1 | 0950-Other bed material system problems | D1-Forced - Immediate | 100-Fossil-Steam
0950 | Other bed material system problems | NULL | NULL | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 216.6 | 36.1 | 1 | 1 | 0950-Other bed material system problems | D1-Forced - Immediate | 100-Fossil-Steam
0950 | Other bed material system problems | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2013 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 766.6666 | 115 | 1 | 1 | 0950-Other bed material system problems | D1-Forced - Immediate | 650-Fluidized Bed
0950 | Other bed material system problems | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2013 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 2090 | 110 | 1 | 1 | 0950-Other bed material system problems | D1-Forced - Immediate | 650-Fluidized Bed
0950 | Other bed material system problems | Boiler | Bed Material Removal System (fbc) | D3 | Forced - Postponed | 2013 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 2025 | 90 | 1 | 1 | 0950-Other bed material system problems | D3-Forced - Postponed | 650-Fluidized Bed
0950 | Other bed material system problems | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2013 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 3 | 10 | 1 | 1 | 0950-Other bed material system problems | D1-Forced - Immediate | 650-Fluidized Bed
0950 | Other bed material system problems | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2013 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 71.5 | 33 | 1 | 1 | 0950-Other bed material system problems | D1-Forced - Immediate | 650-Fluidized Bed
0950 | Other bed material system problems | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2013 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 510.7333 | 163 | 1 | 1 | 0950-Other bed material system problems | D1-Forced - Immediate | 650-Fluidized Bed
0950 | Other bed material system problems | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2013 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 1173 | 51 | 1 | 1 | 0950-Other bed material system problems | D1-Forced - Immediate | 650-Fluidized Bed
0950 | Other bed material system problems | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2013 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 62.5 | 75 | 1 | 1 | 0950-Other bed material system problems | D1-Forced - Immediate | 650-Fluidized Bed
0950 | Other bed material system problems | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2013 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 458.3333 | 125 | 1 | 1 | 0950-Other bed material system problems | D1-Forced - Immediate | 650-Fluidized Bed
0950 | Other bed material system problems | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2013 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 1658.3333 | 100 | 1 | 1 | 0950-Other bed material system problems | D1-Forced - Immediate | 650-Fluidized Bed
0950 | Other bed material system problems | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2013 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 5687.5 | 75 | 1 | 1 | 0950-Other bed material system problems | D1-Forced - Immediate | 650-Fluidized Bed
0950 | Other bed material system problems | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2013 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 668.75 | 107 | 1 | 1 | 0950-Other bed material system problems | D1-Forced - Immediate | 650-Fluidized Bed
0950 | Other bed material system problems | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2013 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 12518.7499 | 75 | 1 | 1 | 0950-Other bed material system problems | D1-Forced - Immediate | 650-Fluidized Bed
0950 | Other bed material system problems | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2013 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 2378 | 60 | 1 | 1 | 0950-Other bed material system problems | D1-Forced - Immediate | 650-Fluidized Bed
0950 | Other bed material system problems | Boiler | Bed Material Removal System (fbc) | D3 | Forced - Postponed | 2013 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 200 | 80 | 1 | 1 | 0950-Other bed material system problems | D3-Forced - Postponed | 650-Fluidized Bed
0950 | Other bed material system problems | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2013 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 12646.6665 | 280 | 1 | 1 | 0950-Other bed material system problems | D1-Forced - Immediate | 650-Fluidized Bed
0950 | Other bed material system problems | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2013 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 3600 | 150 | 1 | 1 | 0950-Other bed material system problems | D1-Forced - Immediate | 650-Fluidized Bed
0950 | Other bed material system problems | Boiler | Bed Material Removal System (fbc) | D3 | Forced - Postponed | 2013 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 1076.6666 | 95 | 1 | 1 | 0950-Other bed material system problems | D3-Forced - Postponed | 650-Fluidized Bed
0950 | Other bed material system problems | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Off-Peak | 378.6666 | 80 | 1 | 1 | 0950-Other bed material system problems | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0950 | Other bed material system problems | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Off-Peak | 852 | 80 | 1 | 1 | 0950-Other bed material system problems | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0950 | Other bed material system problems | Boiler | Bed Material Removal System (fbc) | U1 | Forced - Immediate | 2013 | Gas | PC | 862 | CoG steam units | SERC | Summer | 4979.52 | 34.58 | 1 | 1 | 0950-Other bed material system problems | U1-Forced - Immediate | 862-CoG steam units
0972 | Flue gas-solids separator controls | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2013 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 58.94 | 8.42 | 1 | 1 | 0972-Flue gas-solids separator controls | D1-Forced - Immediate | 650-Fluidized Bed
0981 | High pressure loop seal recirculation fan/blower motors | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2013 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 395.65 | 316.52 | 1 | 1 | 0981-High pressure loop seal recirculation fan/blower motors | D1-Forced - Immediate | 650-Fluidized Bed
0981 | High pressure loop seal recirculation fan/blower motors | Boiler | Bed Solids Recirculation (fbc) | U1 | Forced - Immediate | 2013 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 34770 | 570 | 1 | 1 | 0981-High pressure loop seal recirculation fan/blower motors | U1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2013 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 294.6 | 49.1 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2013 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 175 | 25 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | U1 | Forced - Immediate | 2013 | Coal | OS | 650 | Fluidized Bed | SERC | Summer | 4780.7831 | 293 | 1 | 1 | 0989-Other bed solids recirculation problems | U1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 7.1667 | 10 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 4289.9999 | 90 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0990 | Refractory | Boiler | External Fluid Bed Heat Exchanger (fbc) | U2 | Forced - Delayed | 2013 | Gas | GG | 650 | Fluidized Bed | TRE | Off-Peak | 12987 | 130 | 1 | 1 | 0990-Refractory | U2-Forced - Delayed | 650-Fluidized Bed
0990 | Refractory | Boiler | External Fluid Bed Heat Exchanger (fbc) | D1 | Forced - Immediate | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Off-Peak | 5999.9701 | 87.23 | 1 | 1 | 0990-Refractory | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0991 | Tube leaks | Boiler | External Fluid Bed Heat Exchanger (fbc) | D1 | Forced - Immediate | 2013 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 1342.0333 | 19 | 1 | 1 | 0991-Tube leaks | D1-Forced - Immediate | 800-Miscellaneous
0991 | Tube leaks | Boiler | External Fluid Bed Heat Exchanger (fbc) | D1 | Forced - Immediate | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Off-Peak | 24418.4999 | 90 | 1 | 1 | 0991-Tube leaks | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0991 | Tube leaks | Boiler | External Fluid Bed Heat Exchanger (fbc) | D1 | Forced - Immediate | 2013 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Winter | 6043.5 | 85 | 1 | 1 | 0991-Tube leaks | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0991 | Tube leaks | HRSG Boiler | External Fluid Bed Heat Exchanger (fbc) | U1 | Forced - Immediate | 2013 | Waste Heat | WH | 850 | Combined Cycle Block | TRE | Summer | 29060.4166 | 125 | 1 | 1 | 0991-Tube leaks | U1-Forced - Immediate | 850-Combined Cycle Block
0991 | Tube leaks | HRSG Boiler | External Fluid Bed Heat Exchanger (fbc) | U2 | Forced - Delayed | 2013 | Gas | GG | 850 | Combined Cycle Block | TRE | Summer | 14093.4164 | 172.89 | 1 | 1 | 0991-Tube leaks | U2-Forced - Delayed | 850-Combined Cycle Block
0991 | Tube leaks | HRSG Boiler | External Fluid Bed Heat Exchanger (fbc) | U1 | Forced - Immediate | 2013 | Waste Heat | WH | 850 | Combined Cycle Block | SERC | Summer | 11750.8363 | 75.82 | 1 | 1 | 0991-Tube leaks | U1-Forced - Immediate | 850-Combined Cycle Block
0991 | Tube leaks | HRSG Boiler | External Fluid Bed Heat Exchanger (fbc) | U1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | SERC | Winter | 6406.8666 | 28 | 1 | 1 | 0991-Tube leaks | U1-Forced - Immediate | 852-CC steam units
0991 | Tube leaks | HRSG Boiler | External Fluid Bed Heat Exchanger (fbc) | U1 | Forced - Immediate | 2013 | Waste Heat | WH | 852 | CC steam units | SERC | Winter | 238610.4 | 28 | 1 | 1 | 0991-Tube leaks | U1-Forced - Immediate | 852-CC steam units
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9.5333 | 11 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1287 | 33 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3643.25 | 59 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4173.6166 | 71 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6160.5 | 45 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 247.25 | 21.5 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 290.9497 | 25.01 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3575.4333 | 223 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6262.4 | 64 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 468.3331 | 562 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 968.75 | 31 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2547 | 54 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 2775 | 185 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5595.1333 | 46 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 733.3333 | 100 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2013 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 476.25 | 15 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2013 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 719.8 | 12 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 53.5332 | 292 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 160.0833 | 85 | 1 | 1 | 1000-Waterwall (Furnace wall) | D3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10944.84 | 490.8 | 1 | 1 | 1000-Waterwall (Furnace wall) | SF-Startup Failure | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 9577.3332 | 176 | 1 | 1 | 1000-Waterwall (Furnace wall) | SF-Startup Failure | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 14280 | 595 | 1 | 1 | 1000-Waterwall (Furnace wall) | SF-Startup Failure | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1083.3333 | 50 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1691.5 | 199 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2474.55 | 117 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5867.28 | 69.6 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 6948.75 | 75 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 8274.6253 | 241.36 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 12870 | 650 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 14811.4585 | 241.36 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 19999.3663 | 493 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 29817.9997 | 510 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 36734.75 | 635 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 42767.133 | 524 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 104843.55 | 651 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1495.75 | 193 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1739.7666 | 67 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4379.8333 | 110 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 5143.6 | 84 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6132.1 | 178 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6659.5499 | 81 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8882.5 | 190 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9945.7166 | 163 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 10940.8333 | 95 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 17640.9983 | 238.93 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 27846 | 520 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 28235.3331 | 410 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 44232.5 | 650 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 50611.5 | 815 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 51480 | 195 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 51760.7663 | 622 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 54325.6666 | 158 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 71919.45 | 639 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 82446.6497 | 507 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1996.5 | 90 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 4790.3305 | 249.28 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5858.9166 | 167 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5926.6665 | 175 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 9516.6665 | 250 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 12722.85 | 577 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 27911 | 380 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 34418.7615 | 246.7 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 34522.3666 | 182 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 49280 | 770 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 8196.3331 | 335 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 12566.1599 | 334.8 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 4410 | 126 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 11004 | 393 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 51515.85 | 177 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 54969.75 | 135 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 6365 | 335 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Oil | OO | 100 | Fossil-Steam | RFC | Summer | 27484.7333 | 107 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 29732.25 | 435 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 295626 | 435 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10571.1665 | 205 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 13928.2331 | 562 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 102531.5497 | 831 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4655 | 95 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 25021 | 191 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 27194.1832 | 469 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 32487.4665 | 608 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 44279.3329 | 680 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6560 | 200 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 18427.5 | 455 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 40036.3996 | 606 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 13478.4999 | 210 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7385.4332 | 149 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 15998.8997 | 417 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 343 | 49 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1800 | 40 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2462.95 | 217 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 143.726 | 65.33 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 587.25 | 27 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 883.0249 | 253.5 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 204.5 | 409 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 340.8332 | 409 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1912.6666 | 40 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2305.3333 | 40 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 2548.2 | 18 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1800 | 120 | 1 | 1 | 1000-Waterwall (Furnace wall) | D2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 402.3466 | 94.3 | 1 | 1 | 1000-Waterwall (Furnace wall) | D2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 36871.45 | 427 | 1 | 1 | 1000-Waterwall (Furnace wall) | SF-Startup Failure | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1315 | 50 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1357.5 | 50 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7028.9333 | 238 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9525.6466 | 131.6 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10600.38 | 131.6 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 11969.1665 | 271 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 13924.2 | 138 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 14393.8331 | 335 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 14800.9187 | 510.67 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 17078.6 | 132 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 18778.65 | 627 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 21578.083 | 497 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 22347 | 180 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 24492.4996 | 606 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 34479.9 | 546 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 35125.3331 | 320 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 40080.6665 | 590 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 78565.5 | 790 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 130402.9997 | 780 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 262147.1665 | 205 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7777 | 110 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7856.3332 | 370 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9574.4 | 132 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 26037.0666 | 251 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 28122.4999 | 210 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 29662.2664 | 427 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 35453.0331 | 766 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 39517.3329 | 584 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 40606.5 | 230 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 41235.9998 | 732 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 46506.2 | 577 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 50994.0665 | 644 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 52997.45 | 577 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 142429.7999 | 414 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 510.67 | 510.67 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1720.8333 | 50 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6578 | 110 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 11465.6666 | 110 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 15219.9996 | 600 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 16630.25 | 595 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 17815.9998 | 255 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 19130.7666 | 163 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 19197 | 135 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 29028 | 615 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 30753 | 612 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 35735.5331 | 577 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 42482.1664 | 830 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 43506.6664 | 650 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 56317.75 | 235 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 64443.9998 | 240 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 10794.6666 | 320 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 20332.2166 | 209 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 29044.5 | 335 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 7597.3333 | 220 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 8549.3331 | 320 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 2679.9998 | 240 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Oil | OO | 100 | Fossil-Steam | RFC | Summer | 16991.6 | 107 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Other | BM | 100 | Fossil-Steam | WECC | Winter | 11373.75 | 45 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6241.6665 | 175 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 23923.0497 | 387 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 29875.9996 | 660 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 67155 | 407 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 92019.5831 | 425 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 95272.3329 | 614 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 147658.5 | 785 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 8362.9332 | 176 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 31486.9 | 499 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 34965 | 540 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 79995.9997 | 840 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1839.1666 | 50 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 11851.833 | 470 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2556.75 | 105 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 16137.9 | 417 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 10177.9999 | 210 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2013 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 12183.8331 | 410 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1664.5833 | 25 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2268 | 42 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2755 | 190 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3720 | 40 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1400.9999 | 180 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 779.1667 | 25 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2013 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1000.008 | 294.12 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2013 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 226.8 | 24 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2013 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 601.6 | 24 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2013 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 2127.2 | 24 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 218.04 | 54.51 | 2 | 2 | 1000-Waterwall (Furnace wall) | D2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D3 | Forced - Postponed | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2300.7833 | 143.5 | 1 | 1 | 1000-Waterwall (Furnace wall) | D3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3428.1665 | 307 | 1 | 1 | 1000-Waterwall (Furnace wall) | SF-Startup Failure | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 15915.1 | 334 | 1 | 1 | 1000-Waterwall (Furnace wall) | SF-Startup Failure | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 16297.5 | 530 | 1 | 1 | 1000-Waterwall (Furnace wall) | SF-Startup Failure | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 27778.5662 | 658 | 1 | 1 | 1000-Waterwall (Furnace wall) | SF-Startup Failure | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4142.515 | 131.3 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9255.7166 | 197 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9789 | 251 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 14810.4 | 374 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 20546.6665 | 575 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 24310.9331 | 577 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 28090.2831 | 577 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 29898.75 | 595 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 33726.4165 | 395 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 33802.3998 | 564 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 56615 | 670 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 73883.8328 | 830 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 80495.7875 | 151.75 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 93899.866 | 994 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 116244.3328 | 770 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 118727.6665 | 590 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 136431.1664 | 770 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3270.4466 | 50.6 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4623.0432 | 129.8 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4695.0666 | 92 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5052.3499 | 111 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5684.5833 | 175 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7096.2666 | 104 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7252.6666 | 115 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10630.6665 | 238 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 10798.3333 | 110 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 18514.0833 | 163 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 20724.9997 | 750 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 21612.5 | 175 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 21704.9 | 307 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 21926.6663 | 598 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 23818.5 | 670 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 29778.6663 | 520 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 35246.7666 | 281 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 47991.7665 | 178 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 48255.8331 | 395 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 72308.1663 | 598 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 84297.0829 | 659 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1519.98 | 131.6 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1793.3333 | 50 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2495.7 | 84.6 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3654.4 | 57.1 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3700.1532 | 131.6 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5754.4165 | 199 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6442.6666 | 128 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6574.1666 | 115 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 10571.256 | 242.46 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 14900.68 | 246.7 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 15367.2232 | 241.37 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 17267.4 | 477 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 18216 | 138 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 18613.6665 | 380 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 20853.3332 | 400 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 39040.8331 | 550 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 40245.3331 | 320 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 82961.3328 | 860 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 96178.3329 | 650 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 15040 | 235 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 76760.0164 | 749 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 1619.7333 | 32 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 15041.6665 | 500 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 47410 | 220 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 64639.2 | 552 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Gas | GG | 100 | Fossil-Steam | RFC | Winter | 8775 | 135 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2013 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 17523.9333 | 172 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2013 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3496.9666 | 98 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam